DEVELOPMENT OF 1200 KV UHVAC BY POWERGRID

1.0	Need for UHVAC 1200 kV transmission system

During the next 4-5 years, large number  of generation projects are proposed to be set-up progressively in Chhattisgarh State in eastern part of Western Region (WR). In addition, various other generation projects are also planned in Orissa State in Eastern Region (ER) and major quantum of the power is proposed to be injected at eastern part of WR. Power from these generation projects is envisaged to be transferred to various beneficiaries in central and western part of Western/ Northern Region.

In order to facilitate exchange of above quantum of power from these generation project, strengthening of East-West transmission corridors in WR through high capacity links (to address right-of-way matter) is required. Further, it has been observed that with the increasing number of interconnection at 400kV/765 kV level, short circuit level at various existing Extra High Voltage (EHV) substations is expected to approach the limit which is presently 40 kA. Nevertheless, use of 50kA/63kA rated equipment at major new substations is being explored.

Accordingly, to address increase in short circuit level and to conserve precious Right-of-Way (RoW), a high capacity 1200 kV transmission corridor is proposed between Wardha (central part of WR) and Aurangabad (western part of WR). This 1200 kV AC line would enable transfer of 6000-7000 MW power (as compared to 2000-2500 MW for 765 kV level) which shall help in utilizing the Right-of-Way in an optimal manner and will also ensure protection of forest, flora & fauna and scarce natural resource like land etc. Details of RoW for various voltage levels is as follows:

As per CERC order 29.3.2004

| Sl. No. | Line voltage | Power Carrying Capacity | Right-of-Way (RoW) in meter | RoW required for 7000 MW |
| --- | --- | --- | --- | --- |
| 1. | 400 kV D/C | 1382 MW | 46 | 46 X 5 = 230 m |
| 2. | 765 kV S/C | 2250 MW | 64 | 64 X 3 = 192 m |
| 3. | 1200 kV | 7000 MW | 91 | 91 X 1 = 91 m |

It may be noted that, for the same power carrying capacity, RoW requirement for 1200 kV transmission line is only 40% of 400 kV D/C and less than 50% of 765 kV S/C. Therefore, implementation of 1200 kV transmission line will go a long way in optimizing RoW thereby minimizing environmental and social impacts.

However, as the generation projects are being developed in a phased manner requiring lesser power transfer requirement initially, proposed high capacity 1200 kV East-West transmission corridor is to be operated initially at 400 kV level. Accordingly, with suitable design, 1200 kV S/C line (octagonal sub-conductors bundle) is proposed to be operated initially as 400 kV D/C line (Quad) so that system redundancy can be maintained. Subsequently, with the increase in power transfer requirement through this corridor, this line is envisaged to be upgraded/operated at 1200 kV level in next 7-8 years time frame. Schematic diagram of the proposed perspective plan for 1200 kV East-West transmission corridor in WR is enclosed at Annexure-I.

Keeping in view the long-term requirement, issues in development of high capacity transmission corridors like Right-of-Way, high short circuit level etc., investment towards transmission system is optimized. Further, development of this technology would pave the way for strengthening of National Grid capacity to take care of future power transfer requirement of the country with minimum possible impact on environment and other natural resources.

2.0	Technical details of transmission line

The maximum system voltage (1200 kV) and other major electric system parameters like insulation levels (Switching impulse & Lightening impulse withstand levels) considered for the design of the 1200 kV transmission line have been finalized and selected based on agreement reached during the IEC-TC 28 meeting held in India on November 28-30, 2007. In this respect, amendment to IEC standard (committee draft for vote) for insulation co-ordination which includes the finalized values of insulation levels for 1200 kV is enclosed at Annexure-II.

Tower design: The proposed towers are being designed in such a manner that at present  though they will be operating as 400 kV D/C (Quad) but in future they can operate as 1200 kV S/C with changes in insulator strings and bunching of conductor bundles. To achieve this, the towers are designed with adequate height to meet minimum ground clearance stipulations required for 1200 kV. Further, the towers are being designed to meet minimum air gap clearances for both 400 kV D/C and 1200 kV S/C. The air gap clearances required for 1200 kV have been validated by POWERGRID during full scale testing at UHV laboratory, Central Power Research Institute, Hyderabad which is an accredited laboratory.

Testing & Standards POWERGRID shall design the tower, foundation and test the prototype tower.  The towers shall be tested for the loadings of 400 kV D/C towers with quad conductor and also for the loadings of 1200 kV S/C with octagonal conductor.  As the number of conductors in case of 400 kV D/C towers with quad conductor and 1200 kV S/C with octagonal conductor shall be the same, i.e. 24 numbers, the total loadings shall be in the same range.  No extra technology for manufacturing of towers is anticipated as the section sizes required for the proposed towers shall be similar to many of the towers already being used in various POWERGRID lines.

Indicative sketch of suspension tower showing 400 kV D/C line with quadruple conductor as well as sketch of the same tower after the line is upgraded to 1200 kV is enclosed at Annexure-III.

Regarding standards to be followed for testing of towers, POWERGRID is following  the Indian standard IS-802 (Part-III) which is in-line with IEC-60652.  These standards are applicable for testing of transmission line towers of any voltage level.

Six type of tower are envisaged under the project, namely Type-A (0 degree deviation), Type-AS (0-7 degree deviation), Type-B (7-15 degree deviation), Type-C (15-30 degree deviation), Type-D (30-45 degree deviation), Type-E (45-60 degree deviation).  The work for prototype testing of 1200 kV tower has been assigned to three contractors for which award has already been placed.  A, B & D towers have been already been designed and given to the contractor for fabrication of tower parts & testing of the same is expected to be completed by July, 2009. However, the present status is as follows:

- NIT: September 1, 2009,

- OBD: November 20, 2009,

- Award: Evaluation under process.

- No tower has been tested till date.

- The work for prototype testing of 1200 kV tower were awarded on February 6, 2009 to following three contractors:

- KEC (Type- A& C),

- KPTL (Type-D & AS),

- Jyoti (Type-B & E).

- Testing of A, B & D towers is expected as per following:

| Tower Type | Party | Testing |
| --- | --- | --- |
| A | KEC | End of January, 2010 |
| D | KPTL | February, 2010 |
| B | Jyoti | February, 2010 |

- For rest of the towers, testing is being tied up.

Bidding Methodology for Testing of Towers: The award for the subject testing packages have been placed though limited tender. Bids were issued to the parties who have adequate testing facilities and are reputed laboratories which conducts testing for International clients also. In the subject package, awards have been placed on three parties (two towers each).

****.