## SOP OCT 2016
Standard of Performance data for the month of OCT- 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION - I
'ANNEXURE - A
Sl. No. | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | DETAILS OF OUTAGE |  | Total outage in days (1) | OUTAGE |  | RESTORATION |  |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Category | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | No. of Tower damaged | No.of insulators failed |  | DATE | TIME | DATE | TIME | TOTAL | ISTS Licensee | OTHERS | System constraint/ Natural calmity/ Militancy | Deemed Available
1 | ER1L1 | 132kV ARA-ARA | 1.7 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A | ERPC
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
2 | ER1L2 | 132kV Dehri-SSRM | 62 | ER1 | -- | -- | -- | -- | 2016-10-22 | 18:10 | 2016-10-27 | 13:03 | 114.8833 | 0 | 114.8833 | 0 | 0 | OMSU | T- point made by BSPTCL to feed the power to Kudra Railway from this line. Melting of T-connector caused the snapping of conductor, due to this two no. cross arm of R-ph at loc no 165 & 166 got bent. | N/A | N/A | N/A
[9 empty] | 2016-10-28 | 16:07 | 2016-10-28 | 18:17 | 2.1667 | 0 | 0 | 0 | 2.1667 | OSPD | S/D TAKEN BY BSPTCL to attend clearance problem of 132 kV Pusauli (Nadokhar)-Sasaram line with 132 kV Sasaram (PG)-Kudra line
[5 empty] | -- | -- | -- | -- |  |  |  |  | 117.05 | 0 | 114.8833 | 0 | 2.1667 |  |  | N/A | N/A | N/A |  | 100
3 | ER1L3 | 132kV SSRM- KARAMNASA | 29 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
4 | ER1L4 | 132kV DMRN-ARA | 1.7 | ER1 | -- | -- | -- | -- | 2016-10-24 | 13:07 | 2016-10-24 | 13:28 | 0.35 | 0 | 0.35 | 0 | 0 | OMSU | TRIPPED ON B-N FAULT. F.D.= 47.4 KM FROM ARA END, F.C.= 1.3 KA.( FAULT WAS UNDER BSPTCL JURISDICTION ) | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0.35 | 0 | 0.35 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
5 | ER1L5 | 132kV PNR-DLK (LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
6 | ER1L6 | 132kV PNR-PRN(LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
7 | ER1L7 | 220kV DALKHOLA-PURNEA I | 41 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
8 | ER1L8 | 220kV DALKHOLA-PURNEA II | 41 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
9 | ER1L9 | 220 kV PRN-NPRN-I | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
10 | ER1L10 | 220 kV PRN-NPRN-II | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
11 | ER1L11 | 220kV SASARAM-NADOKHAR -II | 112 | ER1 | [8 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
12 | ER1L11 | 220kV NADOKHAR -ARRAH II | 112 | ER1 |  |  |  |  | 2016-10-01 | 0:00 | 2016-10-20 | 10:51 | 466.85 | 0 | 0 | 0 | 466.85 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-25 | 9:07 | 2016-10-25 | 10:46 | 1.65 | 0 | 0 | 0 | 1.65 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 468.5 | 0 | 0 | 0 | 468.5
13 | ER1L12 | 220kV SASARAM-ARRAH I | 112 | ER1 |  |  |  |  | 2016-10-09 | 9:33 | 2016-10-09 | 18:30 | 8.95 | 0 | 0 | 0 | 8.95 | LVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-28 | 10:22 | 2016-10-28 | 17:51 | 7.4833 | 7.4833 | 0 | 0 | 0 | OSPT | S/OFF FOR REPLACEMENT OF Y PHASE LINE CVT DUE TO SECONDARY VOLTAGE VIOLATION AND AMP OF SAID BAY AT SASARAM
[9 empty] | 2016-10-25 | 9:07 | 2016-10-25 | 11:07 | 2 | 0 | 0 | 0 | 2 | LVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 18.4333 | 7.4833 | 0 | 0 | 10.95
14 | ER1L13 | 220kV ARA-KHAGOL I | 48.44 | ER1 |  |  |  |  | 2016-10-01 | 0:00 | 2016-10-09 | 9:17 | 201.2833 | 0 | 0 | 0 | 201.2833 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-18 | 19:29 | 2016-10-20 | 11:05 | 39.6 | 0 | 0 | 0 | 39.6 | LPRD | S.OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-20 | 15:37 | 2016-10-25 | 8:56 | 113.3167 | 0 | 0 | 0 | 113.3167 | LPRD | H/T FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-25 | 17:25 | 2016-11-01 | 0:00 | 150.5833 | 0 | 0 | 0 | 150.5833 | LPRD | S.OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 504.7833 | 0 | 0 | 0 | 504.7833
15 | ER1L14 | 220kV ARA-KHAGOL II | 48.44 | ER1 | -- | -- | -- | -- | 2016-10-01 | 0:00 | 2016-10-20 | 11:05 | 467.0833 | 0 | 0 | 0 | 467.0833 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-20 | 15:32 | 2016-10-25 | 10:47 | 115.25 | 0 | 0 | 0 | 115.25 | LPRD | S.OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-25 | 17:27 | 2016-11-01 | 0:00 | 150.55 | 0 | 0 | 0 | 150.55 | LPRD | S.OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 732.8833 | 0 | 0 | 0 | 732.8833
16 | ER1L15 | 220kV DEHRI-PUSAULI | 4.88 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
17 | ER1L16 | 220kV SASARAM-SAHUPURI | 4.88 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
18 | ER1L17 | 220kV RANCHI-CHANDIL I | 8.06 | ER1 | -- | -- | -- | -- | 2016-10-21 | 10:09 | 2016-10-23 | 19:09 | 57 | 0 | 0 | 0 | 57 | OSPD | S/D TAKEN BY JUSNL FOR REPLACEMENT OF OLD 220 KV LINE ISOLATOR BY NEW 220 KV MOTORISED ISOLATOR AT CHANDIL END. | N/A | N/A | N/A
[13 empty] | 57 | 0 | 0 | 0 | 57
19 | ER1L18 | 220kV RNC-CHANDIL-II (LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
20 | ER1L19 | 220kV RNC-HATIA-I (LILO) | 8.06 | ER1 | -- | -- | -- | -- | 2016-09-30 | 13:50 | 2016-09-30 | 16:04 | 2.2333 | 0 | 0 | 0 | 2.2333 | OSPD | S/D TAKEN BY JUSNL FOR FACILITATING S/D OF 220KV BUS-2 AT HATIA. | N/A | N/A | N/A
[13 empty] | 2.2333 | 0 | 0 | 0 | 2.2333
21 | ER1L20 | 220kV RNC-HATIA-II(LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
22 | ER1L21 | 220kV GAYA-DEHRI -I(LILO PART) | 11 | ER1 |  |  |  |  | 2016-10-01 | 00:00:00 | 2016-11-01 | 0:00 | 744 | 0 | 744 | 0 | 0 | OMSU | TRIPPED DUE TO Y-B FAULT,F.D.=83.5KM FROM GAYA END, F.C.=Iy=2.79KA, IB=2.32KA. TRIPPED DUE TO COLLAPSE OF D/C TOWER AT LOC. 275 AT SONE RIVER IN BSPTCL JURISDICTION.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 744 | 0 | 744 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
23 | ER1L22 | 220kV GAYA-BODHGAYA(BSEB) I | 12.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
24 | ER1L23 | 220kV GAYA-DEHRI-II (LILO PART) | 11 | ER1 | -- | -- | -- | -- | 2016-10-01 | 00:00:00 | 2016-11-01 | 0:00 | 744 | 0 | 744 | 0 | 0 | OMSU | TRIPPED DUE TO Y-B FAULT,F.D.=83.5KM FROM GAYA END, F.C.=Iy=2.79KA, IB=2.32KA. TRIPPED DUE TO COLLAPSE OF D/C TOWER AT LOC. 275 AT SONE RIVER IN BSPTCL JURISDICTION. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 744 | 0 | 744 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
25 | ER1L24 | 220kV GAYA-BODHGAYA(BSEB) II | 12.7 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
26 | ER1L25 | 400kV FARAKKA-KAHALGAON I | [10 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
27 | ER1L26 | 400kV FARAKKA-KAHALGAON II | [6 empty] | 2016-10-01 | 0:00 | 2016-10-01 | 16:37 | 16.6167 | 0 | 0 | 0 | 16.6167 | OSFD | E/S/D TAKEN BY NTPC/KHLG DUE TO SOME PROBLEM AT NTPC/KHLG END.DETAIL INFORMATION NOT RECEIVED FROM NTPC END.
[9 empty] | 2016-10-01 | 23:33 | 2016-10-05 | 17:05 | 89.5333 | 0 | 0 | 0 | 89.5333 | OSFD | E/S/D TAKEN BY NTPC/KHLG DUE TO SOME PROBLEM AT NTPC/KHLG END.DETAIL INFORMATION NOT RECEIVED FROM NTPC END.
[13 empty] | 106.15 | 0 | 0 | 0 | 106.15
28 | ER1L27 | 400kV KAHALGAON-FARAKKA III | 95.25 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
29 | ER1L28 | 400kV KAHALGAON-FARAKKA IV | 95.25 | ER1 | -- | -- | -- | -- | 2016-10-20 | 10:36 | 2016-10-20 | 18:19 | 7.7167 | 0 | 0 | 0 | 7.7167 | OSPD | S/D TAKEN FOR RELAY AND CT TESTING WORK AT FARAKKA NTPC END | N/A | N/A | N/A
[9 empty] | 2016-10-21 | 10:32 | 2016-10-21 | 16:34 | 6.0333 | 0 | 0 | 0 | 6.0333 | OSPD | S/D TAKEN BY NTPC/FKK FOR RELAY AND CT TESTING WORK AT FARAKKA END.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 13.75 | 0 | 0 | 0 | 13.75 |  |  | N/A | N/A | N/A |  | 100
30 | ER1L29 | 400kV KAHALGAON-LAKHISARAI I | 145 | ER1 | -- | -- | -- | -- | 2016-10-07 | 13:25 | 2016-10-07 | 14:20 | 0.91667 | 0 | 0.91667 | 0 | 0 | OMSU | TRIPPED ONLY FROM NTPC, KAHALGAON END DUE TO PROBLEM AT NTPC, KAHALGAON. | N/A | N/A | N/A
[13 empty] | 0.91667 | 0 | 0.91667 | 0 | 0
31 | ER1L30 | 400kV BIHARSHARIFF-LAKHISARAI I | 89 | ER1 | -- | -- | -- | -- | 2016-10-07 | 8:42 | 2016-10-07 | 18:18 | 9.6 | 0 | 0 | 0 | 9.6 | LCSD | S/D TAKEN FOR CONSTRUCTION WORK RELATED TO SPLIT BUS FOR CVT STRUCTURE ERECTION IN BUS SECTION-I. | N/A | N/A | N/A
[13 empty] | 9.6 | 0 | 0 | 0 | 9.6
| ER1L31A | 400kV KAHALGAON-LAKHISARAI II | 145 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
32 |  |  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1L31B | 400kV BIHARSHARIF-LAKHISARAI II | 89 | ER1 | -- | -- | -- | -- | 2016-10-13 | 9:16 | 2016-10-13 | 20:55 | 11.65 | 0 | 0 | 0 | 11.65 | LCSD | S/D TAKEN FOR CONSTRUCTION WORK RELATED TO SPLIT BUS FOR CVT STRUCTURE ERECTION IN BUS SECTION-I. | N/A | N/A | N/A
33 |  |  |  |  | -- | -- | -- | -- |  |  |  |  | 11.65 | 0 | 0 | 0 | 11.65 |  |  | N/A | N/A | N/A |  | 100
| ER1L32 | 400kV KAHALGAON-BANKA-I | 47.7 | ER1 | -- | -- | -- | -- | 2016-10-20 | 10:13 | 2016-10-20 | 19:03 | 8.8333 | 0 | 0 | 0 | 8.8333 | LCSD | S/D TAKEN FOR MODIFICATION OF CONNECTION ARRANGEMENT OF BPI AND LA AT BANKA. THE WOEK WAS BEING CARRIED OUT UNDER CONSTRUCTION HEAD. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 8.8333 | 0 | 0 | 0 | 8.8333 |  |  | N/A | N/A | N/A |  | 100
34 | ER1L33 | 400KV BIHARSHARIF-BANKA I | 184.54 | ER1 | -- | -- | -- | -- | 2016-10-10 | 5:48 | 2016-10-10 | 5:48 | 0 | 0 | 0 | 0 | 0 | LART | A/R SUCCESSFUL IN B-N FAULT.F.D.=44.62 KM FROM BSF,F.C.=6.285 KA | N/A | N/A | N/A
[9 empty] | 2016-10-18 | 9:53 | 2016-10-18 | 21:47 | 11.9 | 0 | 0 | 0 | 11.9 | LCSD | S/D TAKEN FOR MODIFICATION OF CONNECTION ARRANGEMENT OF BPI AND LA AT BANKA. THE WOEK IS BEING CARRIED OUT UNDER CONSTRUCTION HEAD.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 11.9 | 0 | 0 | 0 | 11.9 |  |  | N/A | N/A | N/A |  | 100
35 | ER1L34 | 400kV KAHALGAON-BANKA-II | 47.7 | ER1 | -- | -- | -- | -- | 2016-10-21 | 9:42 | 2016-10-21 | 18:37 | 8.9167 | 0 | 0 | 0 | 8.9167 | LCSD | S/D TAKEN FOR MODIFICATION OF CONNECTION ARRANGEMENT OF BPI AND LA AT BANKA. THE WOEK WAS BEING CARRIED OUT UNDER CONSTRUCTION HEAD. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 8.9167 | 0 | 0 | 0 | 8.9167 |  |  | N/A | N/A | N/A |  | 100
| ER1L35 | 400KV BIHARSHARIF-BANKA II | 184.54 | ER1 | -- | -- | -- | -- | 2016-10-19 | 9:40 | 2016-10-19 | 19:53 | 10.2167 | 0 | 0 | 0 | 10.2167 | LCSD | S/D TAKEN FOR MODIFICATION OF CONNECTION ARRANGEMENT OF BPI AND LA AT BANKA. THE WOEK WAS BEING CARRIED OUT UNDER CONSTRUCTION HEAD. | N/A | N/A | N/A
36 |  |  |  |  | -- | -- | -- | -- |  |  |  |  | 10.2167 | 0 | 0 | 0 | 10.2167 |  |  | N/A | N/A | N/A |  | 100
| ER1L36A | 400kV JAMSHEDPUR-CHAIBASA I | 46.14 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
37 | ER1L36B | 400kV CHAIBASA-ROURKELA I | 131.48 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
| ER1L37 | 400kV JAMSHEDPUR-ROURKELA II | 153 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
38 |  |  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1L38 | 400kV MAITHON-KAHALGAON I | 172 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
39 | ER1L39 | 400kV MAITHON-KAHALGAON II | 172 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
40 | ER1L40 | 400kV BIHARSHARIF-SASARAM-I | 210 | ER1 | -- | -- | -- | -- | 2016-10-05 | 6:25 | 2016-10-05 | 18:12 | 11.7833 | 0 | 0 | 0 | 11.7833 | LCSD | S/D TAKEN BY BSF FOR CONSTN. WORK RELATED TO BUS SPLITTING AT BSF. FOR ERECTION OF ISOL. FOR BUS SECTION-I | N/A | N/A | N/A
[13 empty] | 11.7833 | 0 | 0 | 0 | 11.7833
41 | ER1L41 | 400kV BIHARSHARIF-SASARAM-II | 210 | ER1 | -- | -- | -- | -- | 2016-10-06 | 8:38 | 2016-10-06 | 19:12 | 10.5667 | 0 | 0 | 0 | 10.5667 | LCSD | S/D TAKEN FOR CONSTN. WORK RELATED TO BUS SPLITTING AT BSF FOR ERECTION OF CT STRUCTURE IN BUS SCTION-I | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 10.5667 | 0 | 0 | 0 | 10.5667 |  |  | N/A | N/A | N/A |  | 100
42 | ER1L42 | 400KV PATNA-BARH III | 68.66 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
43 | ER1L43 | 400KV PATNA-BARH IV | 68.66 | ER1 | -- | -- | -- | -- | 2016-10-15 | 13:58 | 2016-10-15 | 13:58 | 0 | 0 | 0 | 0 | 0 | LART | AUTORECLOSED DUE TO R-N FAULT, F.D=22 KM FROM PATNA, F.C=8.15 KA AT PATNA | N/A | N/A | N/A
[9 empty] | 2016-10-18 | 10:02 | 2016-10-18 | 15:13 | 5.1833 | 0 | 0 | 5.1833 | 0 | LMCC | S/D TAKEN FOR REPLACEMENT OF INSULATORS AT LOC. NO., 129 .INSULATORS WERE DAMAGED BY THE MISCREANTS.
[13 empty] | 5.1833 | 0 | 0 | 5.1833 | 0
44 | ER1L44 | 400KV MUZAFFARPUR-BIHARSHARIF I | 133.3 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
45 | ER1L45 | 400KV MUZAFFARPUR-BIHARSHARIF II | 133.3 | ER1 | -- | -- | -- | -- | 2016-10-08 | 17:26 | 2016-10-08 | 17:26 | 0 | 0 | 0 | 0 | 0 | LART | A/R OPERATED SUCCESSFULLY FROM BOTH END DUE TO R-N FAULT,F.D.=14.36KM FRM BSF,F.C.=12.68KA,F.D.=116KM FROM MUZ,F.C.=2.5KA | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
46 | ER1L46 | 400kV KAHALGAON-BARH I | 217.24 | ER1
[13 empty] | 0 | 0 | 0 | 0 | 0
47 | ER1L47 | 400kV KAHALGAON-BARH II | 217.24 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
48 | ER1L48 | 400kV PATNA-BARH I | 93 | ER1 | -- | -- | -- | -- | 2016-10-27 | 15:20 | 2016-10-27 | 18:31 | 3.1833 | 0 | 3.1833 | 0 | 0 | OMSU | S/OFF ON EMERGENCY BASIS FOR GETTING DOWN A MENTALLY DISTURBED PERSON WHO CLIMBED ON TOWER AT LOC NO 624. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 3.1833 | 0 | 3.1833 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
49 | ER1L49 | 400kV PATNA-BARH II | 93 | ER1 | -- | -- | -- | -- | 2016-10-27 | 15:20 | 2016-10-27 | 18:28 | 3.1333 | 0 | 3.1333 | 0 | 0 | OMSU | S/OFF ON EMERGENCY BASIS FOR GETTING DOWN A MENTALLY DISTURBED PERSON WHO CLIMBED ON TOWER AT LOC NO 624. | N/A | N/A | N/A
[13 empty] | 3.1333 | 0 | 3.1333 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
50 | ER1L50 | 400kV MAITHON-RANCHI I | 199.81 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
51 | ER1L51 | 400kV RAGHUNATHPUR-MAITHON | 44.02 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
52 | ER1L52 | 400kV RANCHI-RAGHUNATHPUR I | 155.79 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
53 | ER1L53 | 400kV MAITHON RB-RANCHI I | 187.64 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
54 | ER1L54 | 400kV MAITHON RB-RANCHI II | 187.64 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
55 | ER1L55 | 400kV RANCHI-ROURKELA I | 144.45 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
56 | ER1L56 | 400kV RANCHI-ROURKELA II | 144.45 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
57 | ER1L57 | 400kV BIHARSHARIF-KODERMA I | 110.69 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
58 | ER1L58 | 400kV BIHARSHARIF-KODERMA II | 110.69 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
59 | ER1L59 | 400kV BIHARSHARIF-VARANASI - I |  | ER1 | -- | -- | -- | -- | 2016-10-17 | 10:16 | 2016-10-17 | 10:30 | 0.23333 | 0.23333 | 0 | 0 | 0 | SPLT | TRIPPED ONLY FROM VARANASI END DUE TO PLCC MAL OPERATION AT VARANASI END. | N/A | N/A | N/A
[9 empty] | 2016-10-12 | 13:40 | 2016-10-12 | 13:40 | 0 | 0 | 0 | 0 | 0 | LART | A/R OPERATED SUCCESSFULLY FROM BOTH END DUE TO Y-N FAULT,F.D.=289KM FROM BSF(NR-3 JURISDICTION), F.C.=2.198KA, ZONE-2.
[13 empty] | 0.23333 | 0.23333 | 0 | 0 | 0 | [6 empty] | 100
60 | ER1L60A | 400kV BIHARSHARIF-VARANASI - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
61 | ER1L61A | 765kV GAYA-BALLIA | 237.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
62 | ER1L62 | 400kV JAMSHEDPUR(DVC)-BARIPADA | 108.29 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
63 | ER1L63 | 400kV BARIPADA-JAMSHEDPUR II | 140.28 | ER1 | -- | -- | -- | -- | 2016-10-03 | 8:18 | 2016-10-03 | 18:52 | 10.5667 | 0 | 10.5667 | 0 | 0 | OMSU | S/D TAKEN BY ER-II FOR ERECTION OF OPGW WORK. THE WORK HAS BEEN CARRIED OUT UNDER CONSTRUCTION PACKAGE. | N/A | N/A | N/A
[9 empty] | 2016-10-04 | 8:11 | 2016-10-04 | 18:34 | 10.3833 | 0 | 10.3833 | 0 | 0 | OMSU | S/D TAKEN BY ER-II FOR ERECTION OF OPGW WORK. THE WORK HAS BEEN CARRIED OUT UNDER CONSTRUCTION PACKAGE.
[9 empty] | 2016-10-06 | 11:34 | 2016-10-06 | 17:50 | 6.2667 | 6.2667 | 0 | 0 | 0 | OSPT | S/OFF TO REPLACE THE FAULTY B-PH ISOLATOR AT BARIPADA END.
[9 empty] | 2016-10-05 | 8:11 | 2016-10-05 | 19:17 | 11.1 | 0 | 11.1 | 0 | 0 | OMSU | S/D TAKEN BY ER-II FOR ERECTION OF OPGW WORK. THE WORK HAS BEEN CARRIED OUT UNDER CONSTRUCTION PACKAGE.
[13 empty] | 38.3167 | 6.2667 | 32.05 | 0 | 0 | [6 empty] | 99.12
64 | ER1L64 | 400kV JAMSHEDPUR-JAMSHEDPUR(DVC) | 32 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
65 | ER1L65 | SSRM - NABINAGAR I | 81.65 | ER1 | -- | -- | -- | -- | 2016-10-19 | 6:19 | 2016-10-19 | 11:11 | 4.8667 | 0 | 4.8667 | 0 | 0 | OMSU | S/OFF BY NABINAGAR DUE TO PROBLEM AT THEIR END.DETAIL INFORMATION NOT RECEIVED FROM NABINAGAR END. | N/A | N/A | N/A
[13 empty] | 4.8667 | 0 | 4.8667 | 0 | 0
66 | ER1L66 | SSRM - NABINAGAR II | 81.65 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
67 | ER1L67A | 400KV GAYA - KODERMA - II | 118.2 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
68 | ER1L67B | 400kV GAYA-MAITHON II | 277 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
69 | ER1L68A | 400kV GAYA-KODERMA-I | 118.2 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
70 | ER1L68B | 400kV GAYA-MAITHON-I | 277 | ER1 |  |  |  |  | 2016-10-03 | 0:45 | 2016-10-03 | 0:45 | 0 | 0 | 0 | 0 | 0 | LART | A/R OPERATED SUCCESSFULLY FROM BOTH END DUE TO Y-N FAULT, F.D. = 124.8KM FROM GAYA,F.C.=2.42KA.
[13 empty] | 0 | 0 | 0 | 0 | 0
71 | ER1L69 | 400kV RANCHI-RANCHI(NEW) II | 78.6 | ER1 | -- | -- | -- | -- | 2016-10-04 | 8:30 | 2016-10-04 | 19:29 | 10.9833 | 0 | 0 | 0 | 10.9833 | OSPD | S/OFF FOR POWERLINE CROSSING OF D/C 400 KV RANCHI-PURULIA LINE.S/D TAKEN BY PKTCL. | N/A | N/A | N/A
[9 empty] | 2016-10-03 | 8:28 | 2016-10-03 | 20:46 | 12.3 | 0 | 0 | 0 | 12.3 | OSPD | S/OFF FOR POWERLINE CROSSING OF D/C 400 KV RANCHI-PURULIA LINE.S/D TAKEN BY PKTCL.
[13 empty] | 23.2833 | 0 | 0 | 0 | 23.2833 | [6 empty] | 100
72 | ER1L70 | 400kV RANCHI-RANCHI(NEW) I | 78.6 | ER1 | -- | -- | -- | -- | 2016-10-03 | 8:28 | 2016-10-03 | 20:47 | 12.3167 | 0 | 0 | 0 | 12.3167 | OSPD | S/OFF FOR POWER LINE CROSSING OF D/C 400 KV RANCHI-PURULIA LINE.S/D TAKEN BY PKTCL | N/A | N/A | N/A
[9 empty] | 2016-10-04 | 8:29 | 2016-10-04 | 19:31 | 11.0333 | 0 | 0 | 0 | 11.0333 | OSPD | S/OFF FOR POWERLINE CROSSING OF D/C 400 KV RANCHI-PURULIA LINE.S/D TAKEN BY PKTCL.
[13 empty] | 23.35 | 0 | 0 | 0 | 23.35 | [6 empty] | 100
73 | ER1L71 | 400kV RANCHI-RANCHI(NEW) III | 78.6 | ER1 | -- | -- | -- | -- | 2016-10-01 | 9:00 | 2016-10-01 | 19:08 | 10.1333 | 0 | 0 | 0 | 10.1333 | OSPD | S/D TAKEN BY M/S PKTCL FOR POWERLINE CROSSING WORK OF 400 KV D/C RANCHI - PARULIA T/L. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 10.1333 | 0 | 0 | 0 | 10.1333 |  |  | N/A | N/A | N/A |  | 100
74 | ER1L72 | 400kV RANCHI-RANCHI(NEW) IV | 78.6 | ER1 | -- | -- | -- | -- | 2016-10-01 | 9:02 | 2016-10-01 | 19:01 | 9.9833 | 0 | 0 | 0 | 9.9833 | OSPD | S/D TAKEN BY M/S PKTCL FOR POWERLINE CROSSING WORK OF 400 KV D/C RANCHI - PARULIA T/L. | N/A | N/A | N/A
[13 empty] | 9.9833 | 0 | 0 | 0 | 9.9833
75 | ER1L73 | 400 KV BOKARO-KODERMA-I | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
76 | ER1L74 | 400 KV BOKARO-KODERMA-II | 100 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
77 | ER1L75 | 400 KV BARH - GORAKHPUR - I | 349.16 | ER1 | -- | -- | -- | -- | 2016-10-06 | 18:11 | 2016-10-06 | 20:07 | 1.9333 | 0 | 1.9333 | 0 | 0 | OMSU | TRIPPED DUE TO D/T RECEIVED AT GKP END DUE TO PROBLEM AT NTPC BARH END. PROTECTION/PLCC EQUIPMENTS AT BARH END BELONGS TO NTPC. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 1.9333 | 0 | 1.9333 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
78 | ER1L76 | 400 KV BARH - GORAKHPUR - II | 349.16 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
79 | ER1L77 | 400 KVPATNA - KISHANGANJ -I |  | ER1 | -- | -- | -- | -- | 2016-10-01 | 0:00 | 2016-11-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER. | N/A | N/A | N/A
[13 empty] | 744 | 0 | 0 | 744 | 0 | [6 empty] | 100
80 | ER1L78 | 400 KVPATNA - KISHANGANJ -II |  | ER1 | -- | -- | -- | -- | 2016-10-01 | 0:00 | 2016-11-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER. | N/A | N/A | N/A
[13 empty] | 744 | 0 | 0 | 744 | 0 | [6 empty] | 100
81 | ER1L77 | 765 KV GAYA - VARANASI - II |  | ER1 | -- | -- | -- | -- | 2016-10-07 | 16:20 | 2016-10-07 | 18:57 | 2.6167 | 2.6167 | 0 | 0 | 0 | OSPT | S/D TAKEN TO ATTEND OIL LEAKAGE FROM MOG OF ITS L/R AT VARANASI.S/D TAKEN BY NR-III. | N/A | N/A | N/A
[13 empty] | 2.6167 | 2.6167 | 0 | 0 | 0
82 | ER1L77 | 400 KV GAYA - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
83 | ER1L77 | 400 KV GAYA - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
84 | ER1L77 | 400 KV NEW RANCHI - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | 2016-10-14 | 8:52 | 2016-10-14 | 19:49 | 10.95 | 0 | 0 | 0 | 10.95 | OSPD | S/D TAKEN BY PKTCL FOR POWERLINE CROSSING OF 400KV PURULIA-RNC LINE. | N/A | N/A | N/A
[9 empty] | 2016-10-15 | 9:24 | 2016-10-15 | 17:53 | 8.4833 | 0 | 0 | 0 | 8.4833 | OSPD | S/D TAKEN BY PKTCL FOR POWERLINE CROSSING OF 400 KV RANCHI - PURULIA LINE.
[13 empty] | 19.4333 | 0 | 0 | 0 | 19.4333 | [6 empty] | 100
85 | ER1L77 | 400 KV NEW RANCHI - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | 2016-10-14 | 9:06 | 2016-10-14 | 19:54 | 10.8 | 0 | 0 | 0 | 10.8 | OSPD | S/D TAKEN BY PKTCL FOR POWERLINE CROSSING OF 400KV PURULIA-RNC LINE. | N/A | N/A | N/A
[9 empty] | 2016-10-15 | 9:25 | 2016-10-15 | 17:55 | 8.5 | 0 | 0 | 0 | 8.5 | OSPD | S/D TAKEN BY PKTCL FOR POWERLINE CROSSING OF 400 KV RANCHI - PURULIA LINE.
[13 empty] | 19.3 | 0 | 0 | 0 | 19.3
86 | ER1T1 | 400/220kV ICT1 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
87 | ER1T2 | 400/220kV ICT2 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2016-10-25 | 11:03 | 2016-10-25 | 11:28 | 0.41667 | 0 | 0.41667 | 0 | 0 | OMSU | TRIPPED ON INTER TRIP DUE TO OVER CURRENT PROTECTION OPERATION OPERATED AT BSPTCL SYSTEM. 220KV SIDE PROTECTION SYSTEM BELONGS TO BSPTCL END. | N/A | N/A | N/A
[13 empty] | 0.41667 | 0 | 0.41667 | 0 | 0
88 | ER1T3 | 400/220kV ICT3 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2016-10-04 | 12:29 | 2016-10-04 | 15:45 | 3.2667 | 0 | 3.2667 | 0 | 0 | OMSU | S/D TAKEN BY BSPTCL TO ATTEND HOT SPOT IN ITS 220 KV SIDE BUS ISOLATOR IN BSPTCL S/Y. EQUIPMENT BELONGS TO BSPTCL. | N/A | N/A | N/A
[9 empty] | 2016-10-25 | 11:03 | 2016-10-25 | 11:20 | 0.28333 | 0 | 0.28333 | 0 | 0 | OMSU | TRIPPED ONLY FROM BSPTCL SIDE. THE REASON OF TRIPPING YET TO BE IDENTIFIED. A SUSPECTED WIRE IN THE RELAY PANELS TERMINATEDE BY BSPTCL END HAS BEEN IDENTIFIED.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 3.55 | 0 | 3.55 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
89 | ER1T4 | 400/220kV ICT1 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2016-10-07 | 16:19 | 2016-10-07 | 16:52 | 0.55 | 0 | 0.55 | 0 | 0 | OMSU | TRIPPED DUE TO PROBLEM AT RAMCHANDRAPUR, JUSNL SYSTEM | N/A | N/A | N/A
[9 empty] | 2016-10-22 | 19:15 | 2016-10-22 | 20:12 | 0.95 | 0 | 0.95 | 0 | 0 | OMSU | TRIPPED DUE TO R PHASE CT BLASTED OF 220 KV SIDE OF ICT-II AT JUSNL END
[5 empty] | -- | -- | -- | -- |  |  |  |  | 1.5 | 0 | 1.5 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
90 | ER1T5 | 400/220kV ICT2 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2016-10-05 | 9:51 | 2016-10-05 | 19:14 | 9.3833 | 0 | 0 | 0 | 9.3833 | SCSD | S/D TAKEN FOR ICT-3 BAY CONSTRUCTION WORK AT JAMSHEDPUR END. | N/A | N/A | N/A
[9 empty] | 2016-10-07 | 16:19 | 2016-10-07 | 16:50 | 0.51667 | 0 | 0.51667 | 0 | 0 | OMSU | TRIPPED DUE TO PROBLEM AT RAMCHANDRAPUR, JUSNL SYSTEM
[9 empty] | 2016-10-22 | 19:15 | 2016-10-24 | 18:32 | 47.2833 | 0 | 47.2833 | 0 | 0 | OMSU | TRIPPED DUE TO R PHASE CT BLASTED OF 220 KV SIDE OF ICT-II AT JUSNL END
[5 empty] | -- | -- | -- | -- |  |  |  |  | 57.1833 | 0 | 47.8 | 0 | 9.3833 |  |  | N/A | N/A | N/A |  | 100
91 | ER1T6 | 400/220kV ICT1 NEW PURNEA | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
92 | ER1T7 | 400/220kV ICT2 NEW PURNEA | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
93 | ER1T8 | 400/220kV ICT1 SSRM | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
94 | ER1T9 | 400/220kV ICT2 SSRM | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
95 | ER1T10 | 400/220kV ICT1 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
96 | ER1T11 | 400/220kV ICT2 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
97 | ER1T12 | 400/220kV ICT1 PATNA | 315 | ER1 | -- | -- | -- | -- | 2016-10-20 | 11:16 | 2016-10-20 | 14:50 | 3.5667 | 0 | 0 | 0 | 3.5667 | SCSD | S/D TAKEN FOR CSD COMMISSIONING WORK.THE RELAY COULD NOT BE COMMISSIONED DUE TO MEET THE CHARGING SCHEDULE OF ERLDC GIVEN TO POWERGRID. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 3.5667 | 0 | 0 | 0 | 3.5667 |  |  | N/A | N/A | N/A |  | 100
98 | ER1T13 | 400/220kV ICT2 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
99 | ER1T14 | 400/220kV ICT1 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
100 | ER1T15 | 400/220kV ICT2 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
101 | ER1T16 | 400/220kV ICT1 GAYA | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
102 | ER1T17 | 400/220kV ICT2 GAYA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
103 | ER1T18 | 400/132kV ICT1 BANKA | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
104 | ER1T19 | 400/132kV ICT 2 BANKA | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
105 | ER1T20 | 765/400kV ICT1 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
106 | ER1T21 | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
107 | ER1T22 | 765/400kV ICT3 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
108 | ER1T23 | 220/132kV ICT1 PRN | 160 | ER1 | -- | -- | -- | -- | 2016-10-20 | 9:23 | 2016-10-20 | 18:13 | 8.8333 | 0 | 0 | 0 | 8.8333 | SCSD | S/D TAKEN FOR 132 kV GIS BAY CONSTRUCTION WORK AT PURNEA. | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 8.8333 | 0 | 0 | 0 | 8.8333 |  |  | N/A | N/A | N/A |  | 100
109 | ER1T24 | 220/132kV ICT2 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
110 | ER1T25 | 220/132kV ICT3 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
111 | ER1T26 | 220/132kV ICT1 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
112 | ER1T27 | 220/132kV ICT2 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
113 | ER1T28 | 765/400/220 kV ICT 1 SASARAM | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
114 | ER1T29 | 765/400kV ICT1 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
115 | ER1T30 | 765/400kV ICT2 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
116 | ER1T31 | 400/132kV ICT1 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
117 | ER1T32 | 400/132kV ICT 2 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | 2016-10-28 | 11:03 | 2016-10-28 | 11:47 | 0.73333 | 0 | 0.73333 | 0 | 0 | OMSU | TRIPPED DUE TO OPERATION OF EARTH FAULT OVERCURRENT PROTECTION DUE TO JUMPING OF A MONKEY ON LA . | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0.73333 | 0 | 0.73333 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
118 | ER1T33 | 400/220kV ICT 2 CHAIBASA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
119 | ER1T34 | 400/220kV ICT 1 CHAIBASA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
120 | ER1T35 | 220/132kV ICT3 ARRAH | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
121 | ER1T36 | 400/220kV ICT3 MUZ | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
122 | ER1T36 | 400/220kV ICT2 KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
123 | ER1T37 | 400/220 kV ICT2 AT KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
124 | ER1R1 | 50 MVAR B/R-1 AT BSF | 50 | ER1 | -- | -- | -- | -- | 2016-10-06 | 18:50 | 2016-10-08 | 13:47 | 42.95 | 0 | 0 | 0 | 42.95 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-29 | 17:44 | 2016-10-30 | 9:51 | 16.1167 | 0 | 0 | 0 | 16.1167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[5 empty] | -- | -- | -- | -- |  |  |  |  | 59.0667 | 0 | 0 | 0 | 59.0667 |  |  | N/A | N/A | N/A |  | 100
125 | ER1R2 | 50 MVAR B/R-1 AT JSR | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
126 | ER1R3 | 50 MVAR BUS REACTOR-II, JAMSHEDPUR II | 50 | ER1 | -- | -- | -- | -- | 2016-10-19 | 9:40 | 2016-10-19 | 19:16 | 9.6 | 0 | 0 | 0 | 9.6 | SCSD | S/D FOR BAY CONSTRUCTION WORK FOR UPCOMING 125MVAR BUS REACTOR IN PARALLEL TO EXISTING 50 MVAR BUS REACTOR. | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 9.6 | 0 | 0 | 0 | 9.6 |  |  | N/A | N/A | N/A |  | 100
127 | ER1R4 | 400kV BUS REACTOR MUZAFFARPUR | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
128 | ER1R5 | 80 MVAR B/R AT PTN | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
129 | ER1R6 | 400kV BUS REACTOR RANCHI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
130 | ER1R7 | 80 MVAR B/R AT BSF | 80 | ER1 | -- | -- | -- | -- | 2016-10-04 | 19:20 | 2016-10-07 | 7:36 | 60.2667 | 0 | 0 | 0 | 60.2667 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC | N/A | N/A | N/A
[9 empty] | 2016-10-29 | 17:41 | 2016-10-30 | 9:50 | 16.15 | 0 | 0 | 0 | 16.15 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 76.4167 | 0 | 0 | 0 | 95.6167 |  |  | N/A | N/A | N/A |  | 100
131 | ER1R8 | 125 MVAR B/R - I AT NPRN | 125 | ER1 | -- | -- | -- | -- | 2016-10-05 | 19:15 | 2016-10-12 | 17:15 | 166 | 0 | 0 | 0 | 166 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[13 empty] | 166 | 0 | 0 | 0 | 166
132 | ER1R9 | 125 MVAR B/R - II AT NPRN | 125 | ER1 | -- | -- | -- | -- | 2016-10-06 | 18:54 | 2016-10-12 | 17:16 | 142.3667 | 0 | 0 | 0 | 142.3667 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 142.3667 | 0 | 0 | 0 | 142.3667 |  |  | N/A | N/A | N/A |  | 100
133 | ER1R10 | 50 MVAR MTN RB-1 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
134 | ER1R11 | 50 MVAR MTN RB-2 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
135 | ER1R12 | 50 MVAR GAYA L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
136 | ER1R13 | 50 MVAR SSRM-III L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
137 | ER1R14 | 400kV BUS REACTOR-I, GAYA 125MVAR | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
138 | ER1R15 | 400kV BUS REACTOR II,GAYA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
139 | ER1R16 | 765kV BUS REACTOR II, GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
140 | ER1R17 | 765kV BUS REACTOR1-GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
141 | ER1R18 | 125 MVAR B/R - I AT PSL | 125 | ER1 | -- | -- | -- | -- | 2016-10-29 | 17:39 | 2016-10-31 | 0:50 | 31.1833 | 0 | 0 | 0 | 31.1833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-28 | 18:28 | 2016-10-28 | 23:26 | 4.9667 | 0 | 0 | 0 | 4.9667 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[13 empty] | 36.15 | 0 | 0 | 0 | 36.15 |  |  | N/A | N/A | N/A
142 | ER1R19 | 125 MVAR B/R - II AT PSL | 125 | ER1 | -- | -- | -- | -- | 2016-10-29 | 17:40 | 2016-10-29 | 22:53 | 5.2167 | 0 | 0 | 0 | 5.2167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-28 | 18:30 | 2016-10-28 | 23:29 | 4.9833 | 0 | 0 | 0 | 4.9833 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[9 empty] | 2016-10-30 | 17:33 | 2016-10-31 | 0:12 | 6.65 | 0 | 0 | 0 | 6.65 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[9 empty] | 2016-10-22 | 8:42 | 2016-10-25 | 21:26 | 84.7333 | 0 | 0 | 0 | 84.7333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-31 | 19:27 | 2016-11-01 | 0:00 | 4.55 | 0 | 0 | 0 | 4.55 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[13 empty] | 106.1333 | 0 | 0 | 0 | 106.1333 | [6 empty] | 100
143 | ER1R20 | 63 MVAR GKP - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
144 | ER1R21 | 63 MVAR GKP - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
145 | ER1R22 | 63 MVAR NPRN - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
146 | ER1R23 | 63 MVAR NPRN - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
147 | ER1R24 | 63 MVAR MUZ - I L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
148 | ER1R25 | 63 MVAR MUZ- II L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
149 | ER1R26 | 63 MVAR BSF- I L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
150 | ER1R27 | 63 MVAR BSF- II L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
151 | ER1R28 | 50 MVAR BSF- III L/R AT PSL | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
152 | ER1R29 | 50 MVAR BALIA L/R AT PSL | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
153 | ER1R30 | 63 MVAR ALLAHABAD-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
154 | ER1R31 | 63 MVAR SARNATH-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
155 | ER1R32 | 50 MVAR B/R - I AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
156 | ER1R33 | 50 MVAR B/R - II AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
157 | ER1R34 | 50 MVAR L/R - I AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
158 | ER1R35 | 50 MVAR L/R - 2 AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
159 | ER1R36 | 80 MVAR B/R - 1 AT BANKA | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
160 | ER1R37 | 3*110 MVAR 1 PH B/R - I AT SASARAM | 330 | ER1 | -- | -- | -- | -- | 2016-10-02 | 18:53 | 2016-10-04 | 7:08 | 36.25 | 0 | 0 | 0 | 36.25 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC /NLDC INSTRUCTION. | N/A | N/A | N/A
[9 empty] | 2016-10-09 | 18:46 | 2016-10-10 | 22:36 | 27.8333 | 0 | 0 | 0 | 27.8333 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC
[9 empty] | 2016-10-04 | 18:44 | 2016-10-06 | 2:59 | 32.25 | 0 | 0 | 0 | 32.25 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC
[9 empty] | 2016-10-06 | 11:12 | 2016-10-08 | 6:53 | 43.6833 | 0 | 0 | 0 | 43.6833 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC
[9 empty] | 2016-10-12 | 18:50 | 2016-10-13 | 8:19 | 13.4833 | 0 | 0 | 0 | 13.4833 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-14 | 12:42 | 2016-10-15 | 7:07 | 18.4167 | 0 | 0 | 0 | 18.4167 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-16 | 19:36 | 2016-10-21 | 8:41 | 109.0833 | 0 | 0 | 0 | 109.0833 | SVRD | S/OFF FOR VOLTAGE REGUATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-15 | 18:45 | 2016-10-16 | 7:15 | 12.5 | 0 | 0 | 0 | 12.5 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-24 | 18:58 | 2016-10-30 | 10:00 | 135.0333 | 0 | 0 | 0 | 135.0333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-30 | 18:04 | 2016-11-01 | 0:00 | 29.9333 | 0 | 0 | 0 | 29.9333 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[13 empty] | 458.4667 | 0 | 0 | 0 | 458.4667 | [6 empty] | 100
161 | ER1R38 | 3*110 MVAR 1 PH L/R - I AT SASARAM (AS B/R) | 330 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
162 | ER1R39 | 125 MVAR BUS REACTOR-1 RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
163 | ER1R40 | 125 MVAR BUS REACTOR-1 PATNA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
164 | ER1R41 | 80 MVAR PURNEA-1 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
165 | ER1R42 | 80 MVAR PURNEA-2 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
166 | ER1R43 | 125 MVAR BUS REACTOR-2 PATNA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
167 | ER1R44 | 125 MVAR BUS REACTOR-1 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
168 | ER1R45 | 125 MVAR BUS REACTOR-2 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
169 | ER1R46 | 3*80MVAR 1 PH L/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
170 | ER1R47 | 3*80MVAR 1 PH B/R - II AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
171 | ER1R48 | 80 MVAR B/R - 1 AT LAKHISARAI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
172 | ER1R49 | 3*80MVAR 1 PH B/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
173 | ER1R50 | 63MVAR KISHANGANJ LR-I AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
174 | ER1R51 | 63MVAR KISHANGANJ LR-II AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
175 | ER1R52 | 3*80 MVAR DHRAMJAYGARH LR-II AS BR AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
176 | ER1R53 | 125 MVAR BR-II AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2016-10-01 | 0:00 | 2016-10-03 | 6:18 | 54.3 | 0 | 0 | 0 | 54.3 | SVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-09 | 18:53 | 2016-10-10 | 6:26 | 11.55 | 0 | 0 | 0 | 11.55 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC
[9 empty] | 2016-10-13 | 22:04 | 2016-10-17 | 22:47 | 96.7167 | 0 | 0 | 0 | 96.7167 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-03 | 19:51 | 2016-10-07 | 7:20 | 83.4833 | 0 | 0 | 0 | 83.4833 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC
[9 empty] | 2016-10-10 | 18:25 | 2016-10-10 | 22:26 | 4.0167 | 0 | 0 | 0 | 4.0167 | SVRD | S/OFF OR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-13 | 1:57 | 2016-10-13 | 8:26 | 6.4833 | 0 | 0 | 0 | 6.4833 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-07 | 18:40 | 2016-10-09 | 8:48 | 38.1333 | 0 | 0 | 0 | 38.1333 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC
[9 empty] | 2016-10-30 | 17:38 | 2016-10-31 | 0:14 | 6.6 | 0 | 0 | 0 | 6.6 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-27 | 18:57 | 2016-10-28 | 23:22 | 28.4167 | 0 | 0 | 0 | 28.4167 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-19 | 17:29 | 2016-10-21 | 8:32 | 39.05 | 0 | 0 | 0 | 39.05 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-24 | 19:05 | 2016-10-25 | 21:28 | 26.3833 | 0 | 0 | 0 | 26.3833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-26 | 18:36 | 2016-10-26 | 22:10 | 3.5667 | 0 | 0 | 0 | 3.5667 | SVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-29 | 17:32 | 2016-10-29 | 22:52 | 5.3333 | 0 | 0 | 0 | 5.3333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-22 | 18:03 | 2016-10-23 | 6:39 | 12.6 | 0 | 0 | 0 | 12.6 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-31 | 17:42 | 2016-11-01 | 0:00 | 6.3 | 0 | 0 | 0 | 6.3 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 422.9333 | 0 | 0 | 0 | 422.9333 | [6 empty] | 100
177 | ER1R54 | 125 MVAR BR-I AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2016-10-01 | 0:00 | 2016-10-07 | 7:29 | 151.4833 | 0 | 0 | 0 | 151.4833 | SVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-09 | 18:58 | 2016-10-10 | 6:30 | 11.5333 | 0 | 0 | 0 | 11.5333 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC
[9 empty] | 2016-10-13 | 1:59 | 2016-10-17 | 22:57 | 116.9667 | 0 | 0 | 0 | 116.9667 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-10 | 18:26 | 2016-10-10 | 22:29 | 4.05 | 0 | 0 | 0 | 4.05 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-10-27 | 18:45 | 2016-10-28 | 23:39 | 28.9 | 0 | 0 | 0 | 28.9 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-10-29 | 17:34 | 2016-10-29 | 23:08 | 5.5667 | 0 | 0 | 0 | 5.5667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-30 | 17:32 | 2016-10-31 | 14:10 | 20.6333 | 0 | 0 | 0 | 20.6333 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-25 | 18:21 | 2016-10-25 | 21:26 | 3.0833 | 0 | 0 | 0 | 3.0833 | SVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-26 | 18:40 | 2016-10-26 | 22:21 | 3.6833 | 0 | 0 | 0 | 3.6833 | SVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLD INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-10-31 | 18:03 | 2016-11-01 | 0:00 | 5.95 | 0 | 0 | 0 | 5.95 | SVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[13 empty] | 351.85 | 0 | 0 | 0 | 351.85
178 | ER1R55 | 125 MVAR BR-III AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | 2016-10-02 | 18:48 | 2016-10-03 | 6:40 | 11.8667 | 0 | 0 | 0 | 11.8667 | SVRD | HANDTRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[9 empty] | 2016-10-04 | 18:10 | 2016-10-07 | 7:26 | 61.2667 | 0 | 0 | 0 | 61.2667 | SVRD | HANDTRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[9 empty] | 2016-10-22 | 18:03 | 2016-10-23 | 6:37 | 12.5667 | 0 | 0 | 0 | 12.5667 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 85.7 | 0 | 0 | 0 | 85.7 |  |  | N/A | N/A | N/A |  | 100
179 | ER1R55 | 125 MVAR BR-I AT Kishanganj | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
180 | ER1R57 | 125 MVAR BR-I AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
181 | ER1R58 | 125 MVAR BR-II AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100

## SOP NOV 2016
Standard of Performance data for the month of Nov- 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION - I
'ANNEXURE - A
S.no | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | DETAILS OF OUTAGE |  | Total outage in days (1) | OUTAGE |  | RESTORATION |  |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Category | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | No. of Tower damaged | No.of insulators failed |  | DATE | TIME | DATE | TIME | TOTAL | ISTS Licensee | OTHERS | System constraint/ Natural calmity/ Militancy | Deemed Available
1 | ER1L1 | 132kV ARA-ARA | 1.7 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A | ERPC
[13 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
2 | ER1L2 | 132kV Dehri-SSRM | 62 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
3 | ER1L3 | 132kV SSRM- KARAMNASA | 29 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
4 | ER1L4 | 132kV DMRN-ARA | 1.7 | ER1 | -- | -- | -- | -- | 2016-11-03 | 19:22 | 2016-11-03 | 19:40 | 0.3 | 0 | 0.3 | 0 | 0 | OMSU | TRIPPED DUE TO Y-N FAULT,F.D.=32.72KM FROM ARA(BSPTCL JURISDICTION) = ,F.C.=1.91KA. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0.3 | 0 | 0.3 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
5 | ER1L5 | 132kV PNR-DLK (LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
6 | ER1L6 | 132kV PNR-PRN(LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
7 | ER1L7 | 220kV DALKHOLA-PURNEA I | 41 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0.6 | 0 | 0.6 | 0 | 0
8 | ER1L8 | 220kV DALKHOLA-PURNEA II | 41 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
9 | ER1L9 | 220 kV PRN-NPRN-I | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
10 | ER1L10 | 220 kV PRN-NPRN-II | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
11 | ER1L11 | 220kV SASARAM-NADOKHAR | 112 | ER1 | [8 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
12 | ER1L11 | 220kV NADOKHAR -ARRAH I | 112 | ER1 |  |  |  |  | 2016-11-04 | 12:30 | 2016-11-24 | 17:23 | 484.8833 | 0 | 0 | 0 | 484.8833 | LVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-26 | 2:42 | 2016-12-01 | 0:00 | 117.3 | 0 | 0 | 0 | 117.3 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 602.1833 | 0 | 0 | 0 | 602.1833
13 | ER1L12 | 220kV SASARAM-ARRAH II | 112 | ER1
[13 empty] | 0 | 0 | 0 | 0 | 0
14 | ER1L13 | 220kV ARA-KHAGOL I | 48.44 | ER1 |  |  |  |  | 2016-11-01 | 0:00 | 2016-11-01 | 14:15 | 14.25 | 0 | 0 | 0 | 14.25 | LPRD | S.OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-11-03 | 18:20 | 2016-12-01 | 0:00 | 653.6667 | 0 | 0 | 0 | 653.6667 | LVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 667.9167 | 0 | 0 | 0 | 667.9167
15 | ER1L14 | 220kV ARA-KHAGOL II | 48.44 | ER1 | -- | -- | -- | -- | 2016-11-01 | 0:00 | 2016-11-01 | 14:15 | 14.25 | 0 | 0 | 0 | 14.25 | LPRD | S.OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[9 empty] | 2016-11-03 | 18:09 | 2016-12-01 | 0:00 | 653.85 | 0 | 0 | 0 | 653.85 | LVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 668.1 | 0 | 0 | 0 | 668.1
16 | ER1L15 | 220kV DEHRI-PUSAULI | 4.88 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
17 | ER1L16 | 220kV SASARAM-SAHUPURI | 4.88 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
18 | ER1L17 | 220kV RANCHI-CHANDIL I | 8.06 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
19 | ER1L18 | 220kV RNC-CHANDIL-II (LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
20 | ER1L19 | 220kV RNC-HATIA-I (LILO) | 8.06 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
21 | ER1L20 | 220kV RNC-HATIA-II(LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
22 | ER1L21 | 220kV GAYA-DEHRI -I(LILO PART) | 11 | ER1 |  |  |  |  | 2016-11-01 | 00:00:00 | 2016-12-01 | 0:00 | 720 | 0 | 720 | 0 | 0 | OMSU | TRIPPED DUE TO Y-B FAULT,F.D.=83.5KM FROM GAYA(BSPTCL JURISDICTION), F.C.=Iy=2.79KA, IB=2.32KA. TRIPPED DUE TO COLLAPSE OF D/C TOWER AT LOC. 275 AT SONE RIVER IN BSPTCL JURISDICTION.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 720 | 0 | 720 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
23 | ER1L22 | 220kV GAYA-BODHGAYA(BSEB) I | 12.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
24 | ER1L23 | 220kV GAYA-DEHRI-II (LILO PART) | 11 | ER1 | -- | -- | -- | -- | 2016-11-01 | 00:00:00 | 2016-11-30 | 19:24 | 715.4 | 0 | 715.4 | 0 | 0 | OMSU | TRIPPED DUE TO Y-B FAULT,F.D.=83.5KM FROM GAYA(BSPTCL JURISDICTION), F.C.=Iy=2.79KA, IB=2.32KA. TRIPPED DUE TO COLLAPSE OF D/C TOWER AT LOC. 275 AT SONE RIVER IN BSPTCL JURISDICTION. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 715.4 | 0 | 715.4 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
25 | ER1L24 | 220kV GAYA-BODHGAYA(BSEB) II | 12.7 | ER1 | -- | -- | -- | -- | 2016-11-16 | 12:37 | 2016-11-16 | 14:31 | 1.9 | 1.9 | 0 | 0 | 0 | OSPT | S/D TAKEN BY GAYA(PG) TO ATTEND HOT SPOT IN ITS LINE ISOLTOR AT GAYA END. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.74
26 | ER1L25 | 400kV FARAKKA-KAHALGAON I | [6 empty] | 2016-11-03 | 10:05 | 2016-11-03 | 12:50 | 2.75 | 0 | 0 | 0 | 2.75 | OSPD | S/D TAKEN FOR DGA ANALYSIS OF CT AT KAHALGAON
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
27 | ER1L26 | 400kV FARAKKA-KAHALGAON II | [6 empty] | 2016-11-18 | 9:32 | 2016-11-18 | 17:26 | 7.9 | 0 | 0 | 0 | 7.9 | OSPD | S/D TAKEN BY NTPC/FKK FOR BREAKER CRM & TIMIMG TESTING AT FARAKKA END.
[13 empty] | 7.9 | 0 | 0 | 0 | 7.9
28 | ER1L27 | 400kV KAHALGAON-FARAKKA III | 95.25 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
29 | ER1L28 | 400kV KAHALGAON-FARAKKA IV | 95.25 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
30 | ER1L29 | 400kV KAHALGAON-LAKHISARAI I | 145 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
31 | ER1L30 | 400kV BIHARSHARIFF-LAKHISARAI I | 89 | ER1 | -- | -- | -- | -- | 2016-11-28 | 13:45 | 2016-11-29 | 1:10 | 11.4167 | 0 | 0 | 0 | 11.4167 | LCSD | S/D TAKEN FOR CONSTRUCTION WORK RELATED TO BUS SPLITTING AT BSF. | N/A | N/A | N/A
[13 empty] | 11.4167 | 0 | 0 | 0 | 11.4167
32 | ER1L31A | 400kV KAHALGAON-LAKHISARAI II | 145 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 22.8333 |  |  | N/A | N/A | N/A |  | 100
33 | ER1L31B | 400kV BIHARSHARIF-LAKHISARAI II | 89 | ER1 | -- | -- | -- | -- | 2016-11-09 | 9:03 | 2016-11-09 | 20:24 | 11.35 | 11.35 | 0 | 0 | 0 | OSPT | S/OFF FOR OVERHAULING AND REPLACEMENT OF GASKETS OF ITS L/R AT BSF. | N/A | N/A | N/A
[9 empty] | 2016-11-22 | 9:25 | 2016-11-22 | 17:48 | 8.3833 | 8.3833 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR ERECTION OF BUSHING OF ITS L/R AFTER OVERHAULING AT BIHARSHRIF.
[9 empty] | 2016-11-28 | 13:45 | 2016-11-29 | 1:12 | 11.45 | 0 | 0 | 0 | 11.45 | LCSD | S/D TAKEN FOR CONSTRUCTION WORK RELATED TO BUS SPLITTING AT BSF.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 31.1833 | 19.7333 | 0 | 0 | 11.45 |  |  | N/A | N/A | N/A |  | 97.35
34 | ER1L32 | 400kV KAHALGAON-BANKA-I | 47.7 | ER1 | -- | -- | -- | -- | 2016-11-21 | 12:48 | 2016-11-21 | 16:18 | 3.5 | 3.5 | 0 | 0 | 0 | OSPT | S/D TAKEN TO ATTEND Broken of strands of one conductor near line to IPS tube connector joint in sky bus dropping of R-Ph of 400 KV Banka Kahalgaon Ckt -1 at Banka end. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 3.5 | 3.5 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.53
35 | ER1L33 | 400KV BIHARSHARIF-BANKA I | 184.54 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
36 | ER1L34 | 400kV KAHALGAON-BANKA-II | 47.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
37 | ER1L35 | 400KV BIHARSHARIF-BANKA II | 184.54 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
38 | ER1L36A | 400kV JAMSHEDPUR-CHAIBASA I | 46.14 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
39 | ER1L36B | 400kV CHAIBASA-ROURKELA I | 131.48 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
40 | ER1L37 | 400kV JAMSHEDPUR-ROURKELA II | 153 | ER1 | -- | -- | -- | -- | 2016-11-18 | 12:32 | 2016-11-19 | 23:28 | 34.9333 | 0 | 0 | 0 | 34.9333 | LCSD | S/D TAKEN BY CHAIBASA FOR LILO OF SAID LINE AT CHAIBASA END. AFTER LILO AT CHAIBASA. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 34.9333 | 0 | 0 | 0 | 34.9333 |  |  | N/A | N/A | N/A |  | 100
41 | ER1L38 | 400kV MAITHON-KAHALGAON I | 172 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
42 | ER1L39 | 400kV MAITHON-KAHALGAON II | 172 | ER1 | -- | -- | -- | -- | 2016-11-02 | 10:25 | 2016-11-02 | 13:04 | 2.65 | 0 | 0 | 0 | 2.65 | OSPD | S/D TAKEN BY NTPC/KHLG FOR CT OIL SAMPLING FOR DGA & P.M. | N/A | N/A | N/A
[13 empty] | 2.65 | 0 | 0 | 0 | 2.65
43 | ER1L40 | 400kV BIHARSHARIF-SASARAM-I | 210 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
44 | ER1L41 | 400kV BIHARSHARIF-SASARAM-II | 210 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
45 | ER1L42 | 400KV PATNA-BARH III | 68.66 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
46 | ER1L43 | 400KV PATNA-BARH IV | 68.66 | ER1 | -- | -- | -- | -- | 2016-11-26 | 8:03 | 2016-11-26 | 11:47 | 3.7333 | 0 | 3.7333 | 0 | 0 | OMSU | TRIPPED DUE TO CABLE DAMAGED BY MONKEY (CABLE WHICH WAS COMING FROM SWITCHYARD TO CONTROL ROOM) AT PATNA | N/A | N/A | N/A
[13 empty] | 3.7333 | 0 | 3.7333 | 0 | 0
47 | ER1L44 | 400KV MUZAFFARPUR-BIHARSHARIF I | 133.3 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
48 | ER1L45 | 400KV MUZAFFARPUR-BIHARSHARIF II | 133.3 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
49 | ER1L46 | 400kV KAHALGAON-BARH I | 217.24 | ER1
[13 empty] | 0 | 0 | 0 | 0 | 0
50 | ER1L47 | 400kV KAHALGAON-BARH II | 217.24 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
51 | ER1L48 | 400kV PATNA-BARH I | 93 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
52 | ER1L49 | 400kV PATNA-BARH II | 93 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
53 | ER1L50 | 400kV MAITHON-RANCHI I | 199.81 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
54 | ER1L51 | 400kV RAGHUNATHPUR-MAITHON | 44.02 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
55 | ER1L52 | 400kV RANCHI-RAGHUNATHPUR I | 155.79 | ER1 | -- | -- | -- | -- | 2016-11-22 | 16:49 | 2016-11-22 | 20:23 | 3.5667 | 0 | 3.5667 | 0 | 0 | OMSU | TRIPPED ON RECEIPT OF DT SIGNAL AT RANCHI DUE TO FAULT IN MAIN BUS -1 AT RAGHUNATHPUR. | N/A | N/A | N/A
[13 empty] | 3.5667 | 0 | 3.5667 | 0 | 0
56 | ER1L53 | 400kV MAITHON RB-RANCHI I | 187.64 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
57 | ER1L54 | 400kV MAITHON RB-RANCHI II | 187.64 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
58 | ER1L55 | 400kV RANCHI-ROURKELA I | 144.45 | ER1 | -- | -- | -- | -- | 2016-11-03 | 9:32 | 2016-11-03 | 21:26 | 11.9 | 11.9 | 0 | 0 | 0 | OSPT | S/D TEKEN FOR AMP WORK | N/A | N/A | N/A
[13 empty] | 11.9 | 11.9 | 0 | 0 | 0 | [6 empty] | 98.4
59 | ER1L56 | 400kV RANCHI-ROURKELA II | 144.45 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
60 | ER1L57 | 400kV BIHARSHARIF-KODERMA I | 110.69 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
61 | ER1L58 | 400kV BIHARSHARIF-KODERMA II | 110.69 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
62 | ER1L59 | 400kV BIHARSHARIF-VARANASI - I |  | ER1 | -- | -- | -- | -- | 2016-11-01 | 13:04 | 2016-11-01 | 13:04 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSE OPERATED DUE TO R-N FAULT, F.D=229.3 KM FROM BSF, F.C=1.97KA AT BSF. | N/A | N/A | N/A
[9 empty] | 2016-11-10 | 13:50 | 2016-11-10 | 13:50 | NA | NA | 0 | 0 | 0 | LART | AUTO RECLOSED SUCCESSFULLY FROM BOTH SIDES ON Y-N FAULT. F.D.= 260.1 KM FROM BSF (NR-3 JURISDICTION) WITH F.C.= 2.486 KA.
[9 empty] | 2016-11-13 | 12:45 | 2016-11-13 | 15:24 | 2.65 | 2.65 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR TRIMMING OF TREES BY VNS(NR-3 ) END
[13 empty] | 2.65 | 2.65 | 0 | 0 | 0 | [6 empty] | 99.64
63 | ER1L60A | 400kV BIHARSHARIF-VARANASI - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
64 | ER1L61A | 765kV GAYA-BALLIA | 237.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
65 | ER1L62 | 400kV JAMSHEDPUR(DVC)-BARIPADA | 108.29 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
66 | ER1L63 | 400kV BARIPADA-JAMSHEDPUR II | 140.28 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
67 | ER1L64 | 400kV JAMSHEDPUR-JAMSHEDPUR(DVC) | 32 | ER1 | -- | -- | -- | -- | 2016-11-01 | 9:26 | 2016-11-01 | 14:09 | 4.7167 | 0 | 0 | 0 | 4.7167 | OSPD | S/D TAKEN BY DVC TO ATTEND HOT SPOT AT TISCO END. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 4.7167 | 0 | 0 | 0 | 4.7167 |  |  | N/A | N/A | N/A |  | 100
68 | ER1L65 | SSRM - NABINAGAR I | 81.65 | ER1 | -- | -- | -- | -- | 2016-11-19 | 12:53 | 2016-11-19 | 21:59 | 9.1 | 0 | 0 | 0 | 9.1 | OSPD | FOR COMMISSIONING WORK OF BUS -2 AT NABINAGAR. S/D TAKEN BY NTPC/ BRBCL/ NABINAGAR. | N/A | N/A | N/A
[9 empty] | 2016-11-21 | 15:15 | 2016-11-21 | 17:15 | 2 | 0 | 2 | 0 | 0 | OMSU | TRIPPED DUE TO D/T RECEIVED AT SSRM CAUSED BY PROBLEM AT BRBCL NABINAGAR.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 11.1 | 0 | 2 | 0 | 9.1 |  |  | N/A | N/A | N/A |  | 100
69 | ER1L66 | SSRM - NABINAGAR II | 81.65 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
70 | ER1L67A | 400KV GAYA - KODERMA - II | 118.2 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
71 | ER1L67B | 400kV GAYA-MAITHON II | 277 | ER1 | -- | -- | -- | -- | 2016-11-08 | 10:52 | 2016-11-08 | 14:59 | 4.1167 | 0 | 0 | 0 | 4.1167 | SCSD | S/D TAKEN FOR REMOVAL OF BUS PIPE FOR RETROFITTING WORK OF 400 KV TIE BAY OF ICT-II & GAYA-I AT MAITHON END. | N/A | N/A | N/A
[9 empty] | 2016-11-19 | 10:37 | 2016-11-19 | 14:49 | 4.2 | 0 | 0 | 0 | 4.2 | SCSD | FOR ERECTION OF REMOVED BUS PIPES I.R.O. RETOFITTING WORK OF 400 KV TIE BAY OF ICT-2 & GAYA -2 AT MAITHAN.
[13 empty] | 8.3167 | 0 | 0 | 0 | 8.3167
72 | ER1L68A | 400kV GAYA-KODERMA-I | 118.2 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
73 | ER1L68B | 400kV GAYA-MAITHON-I | 277 | ER1
[13 empty] | 0 | 0 | 0 | 0 | 0
74 | ER1L69 | 400kV RANCHI-RANCHI(NEW) II | 78.6 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
75 | ER1L70 | 400kV RANCHI-RANCHI(NEW) I | 78.6 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
76 | ER1L71 | 400kV RANCHI-RANCHI(NEW) III | 78.6 | ER1 | -- | -- | -- | -- | 2016-11-09 | 10:42 | 2016-11-09 | 12:38 | 1.9333 | 1.9333 | 0 | 0 | 0 | OSPT | Shutdown to rectify the hotspot problem observed in tie bay ranchi ranchi 3 line side isolator at Ranchi end. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 1.9333 | 1.9333 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.74
77 | ER1L72 | 400kV RANCHI-RANCHI(NEW) IV | 78.6 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
78 | ER1L73 | 400 KV BOKARO-KODERMA-I | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
79 | ER1L74 | 400 KV BOKARO-KODERMA-II | 100 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
80 | ER1L75 | 400 KV BARH - GORAKHPUR - I | 349.16 | ER1 | -- | -- | -- | -- | 2016-11-01 | 12:40 | 2016-11-01 | 18:45 | 6.0833 | 6.0833 | 0 | 0 | 0 | OSPT | S/D TAKEN BY GORAKHPUR TO ATTEND HOT SPOT IN Y-PH OF LINE SIDE ISOLATOR. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 6.0833 | 6.0833 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.18
81 | ER1L76 | 400 KV BARH - GORAKHPUR - II | 349.16 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
82 | ER1L77 | 400 KVPATNA - KISHANGANJ -I |  | ER1 |  |  |  |  | 2016-11-01 | 00:00:00 | 2016-12-01 | 0:00 | 720 | 0 | 0 | 720 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER.
[13 empty] | 720 | 0 | 0 | 720 | 0
83 | ER1L78 | 400 KVPATNA - KISHANGANJ -II |  | ER1 |  |  |  |  | 2016-11-01 | 00:00:00 | 2016-12-01 | 0:00 | 720 | 0 | 0 | 720 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER.
[13 empty] | 720 | 0 | 0 | 720 | 0
84 | ER1L77 | 765 KV GAYA - VARANASI - II |  | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
85 | ER1L77 | 400 KV GAYA - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | 2016-11-15 | 15:15 | 2016-11-15 | 17:50 | 2.5833 | 2.5833 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR RECTIFICATION OF CONTINUOUS SPARKING IN WAVE TRAPS OF R & y PHASE AT CHANDWA END. | N/A | N/A | N/A
[9 empty] | 2016-11-17 | 15:03 | 2016-11-17 | 17:55 | 2.8667 | 2.8667 | 0 | 0 | 0 | OSPT | S/D TAKEN BY CHANDWA FOR ATTENDING SPARKING PROBLEM IN Y PH WAVE TRAP AT CHANDWA END.
[5 empty] | -- | -- | -- | -- | [5 empty] | 5.45 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.27
86 | ER1L77 | 400 KV GAYA - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
87 | ER1L77 | 400 KV NEW RANCHI - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
88 | ER1L77 | 400 KV NEW RANCHI - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
89 | ER1T1 | 400/220kV ICT1 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2016-11-28 | 13:45 | 2016-11-29 | 1:17 | 11.5333 | 0 | 0 | 0 | 11.5333 | SCSD | S/D TAKEN FOR CONSTRUCTION WORK RELATED TO BUS SPLITTING AT BSF. | N/A | N/A | N/A
[13 empty] | 11.5333 | 0 | 0 | 0 | 11.5333
90 | ER1T2 | 400/220kV ICT2 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
91 | ER1T3 | 400/220kV ICT3 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
92 | ER1T4 | 400/220kV ICT1 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2016-11-16 | 8:13 | 2016-11-17 | 11:02 | 26.8167 | 0 | 0 | 0 | 26.8167 | SCSD | S/D TAKEN BY JSR FOR BAY EXTENSION WORK AT JSR. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 26.8167 | 0 | 0 | 0 | 26.8167 |  |  | N/A | N/A | N/A |  | 100
93 | ER1T5 | 400/220kV ICT2 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2016-11-24 | 10:26 | 2016-11-24 | 20:23 | 9.95 | 0 | 0 | 0 | 9.95 | SCSD | S/D TAKEN FOR BAY CONSTRUCTION WORK OF ICT-3 AT JAMSHEDPUR. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 9.95 | 0 | 0 | 0 | 9.95 |  |  | N/A | N/A | N/A |  | 100
94 | ER1T6 | 400/220kV ICT1 NEW PURNEA | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
95 | ER1T7 | 400/220kV ICT2 NEW PURNEA | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
96 | ER1T8 | 400/220kV ICT1 SSRM | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
97 | ER1T9 | 400/220kV ICT2 SSRM | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
98 | ER1T10 | 400/220kV ICT1 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
99 | ER1T11 | 400/220kV ICT2 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
100 | ER1T12 | 400/220kV ICT1 PATNA | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
101 | ER1T13 | 400/220kV ICT2 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
102 | ER1T14 | 400/220kV ICT1 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
103 | ER1T15 | 400/220kV ICT2 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
104 | ER1T16 | 400/220kV ICT1 GAYA | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
105 | ER1T17 | 400/220kV ICT2 GAYA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
106 | ER1T18 | 400/132kV ICT1 BANKA | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
107 | ER1T19 | 400/132kV ICT 2 BANKA | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
108 | ER1T20 | 765/400kV ICT1 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
109 | ER1T21 | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
110 | ER1T22 | 765/400kV ICT3 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
111 | ER1T23 | 220/132kV ICT1 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
112 | ER1T24 | 220/132kV ICT2 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T25 | 220/132kV ICT3 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T26 | 220/132kV ICT1 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T27 | 220/132kV ICT2 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T28 | 765/400/220 kV ICT 1 SASARAM | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T29 | 765/400kV ICT1 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | 2016-11-11 | 11:52 | 2016-11-11 | 19:29 | 7.6167 | 0 | 7.6167 | 0 | 0 | OMSU | S/D TAKEN FOR SWITCHING OF B-PH UNIT WITH SPARE ICT UNIT AS PER ADVICE OF MANUFACTURER. ICT UNDER WARRANTY. | N/A | N/A | N/A
[9 empty] | 2016-11-21 | 8:23 | 2016-11-21 | 18:59 | 10.6 | 0 | 10.6 | 0 | 0 | OMSU | S/D TAKEN FOR DISMANTALING OF B PH UNIT AS PER ADVISE OF MANUFACTURER. ICT UNDER WARRANTY.
[9 empty] | 2016-11-22 | 13:11 | 2016-11-22 | 17:34 | 4.3781 | 0 | 4.3781 | 0 | 0 | OMSU | S/D TAKEN FOR BALANCE WORK OF DISMENTLING OF BUSHING OF B PHASE UNIT. ICT UNDER WARRANTY.
[9 empty] | 2016-11-28 | 8:24 | 2016-11-28 | 18:38 | 10.2333 | 0 | 10.2333 | 0 | 0 | OMSU | S/D TAKEN FOR CARRYING OUT BUSHING ERECTION WORK IN B PH UNIT. WHICH WAS DISMANTALED EARLIER ON MANUFACTURER ADVICE. ICT UNDER WARRANTY.
[5 empty] | -- | -- | -- | -- |  |  |  |  | 32.8281 | 0 | 32.8281 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T30 | 765/400kV ICT2 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | 2016-11-02 | 10:05 | 2016-11-02 | 16:30 | 6.4167 | 6.4167 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR ATTENDING HOT SPOT OF 220KV SIDE T ISOLATOR AT RNC. | N/A | N/A | N/A
|  | SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 6.4167 | 6.4167 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.14
| ER1T31 | 400/132kV ICT1 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T32 | 400/132kV ICT 2 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T33 | 400/220kV ICT 2 CHAIBASA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T34 | 400/220kV ICT 1 CHAIBASA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T35 | 220/132kV ICT3 ARRAH | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T36 | 400/220kV ICT3 MUZ | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1T36 | 400/220kV ICT2 KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
| ER1T37 | 400/220 kV ICT2 AT KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R1 | 50 MVAR B/R-1 AT BSF | 50 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R2 | 50 MVAR B/R-1 AT JSR | 50 | ER1 | -- | -- | -- | -- | 2016-11-21 | 9:33 | 2016-11-21 | 18:35 | 9.0333 | 9.0333 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR AMP WORK | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 9.0333 | 9.0333 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.79
| ER1R3 | 50 MVAR BUS REACTOR-II, JAMSHEDPUR II | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R4 | 400kV BUS REACTOR MUZAFFARPUR | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R5 | 80 MVAR B/R AT PTN | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R6 | 400kV BUS REACTOR RANCHI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R7 | 80 MVAR B/R AT BSF | 80 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[20 empty] | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R8 | 125 MVAR B/R - I AT NPRN | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
| ER1R9 | 125 MVAR B/R - II AT NPRN | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R10 | 50 MVAR MTN RB-1 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R11 | 50 MVAR MTN RB-2 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R12 | 50 MVAR GAYA L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R13 | 50 MVAR SSRM-III L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R14 | 400kV BUS REACTOR-I, GAYA 125MVAR | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R15 | 400kV BUS REACTOR II,GAYA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R16 | 765kV BUS REACTOR II, GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R17 | 765kV BUS REACTOR1-GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R18 | 125 MVAR B/R - I AT PSL | 125 | ER1 | -- | -- | -- | -- | 2016-11-12 | 3:23 | 2016-11-12 | 6:14 | 2.85 | 0 | 0 | 0 | 2.85 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-12 | 18:00 | 2016-11-13 | 20:12 | 26.2 | 0 | 0 | 0 | 26.2 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-17 | 4:48 | 2016-11-19 | 23:28 | 66.6667 | 0 | 0 | 0 | 66.6667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-25 | 18:10 | 2016-11-26 | 21:47 | 27.6167 | 0 | 0 | 0 | 27.6167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-29 | 9:32 | 2016-12-01 | 0:00 | 38.4667 | 0 | 0 | 0 | 38.4667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[13 empty] | 161.8 | 0 | 0 | 0 | 161.8 | [6 empty] | 100
| ER1R19 | 125 MVAR B/R - II AT PSL | 125 | ER1 | -- | -- | -- | -- | 2016-11-01 | 0:00 | 2016-11-01 | 12:25 | 12.4167 | 0 | 0 | 0 | 12.4167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-01 | 17:57 | 2016-11-10 | 0:53 | 198.9333 | 0 | 0 | 0 | 198.9333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-13 | 16:28 | 2016-11-13 | 20:14 | 3.7667 | 0 | 0 | 0 | 3.7667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-17 | 5:00 | 2016-11-18 | 23:01 | 42.0167 | 0 | 0 | 0 | 42.0167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-29 | 9:34 | 2016-11-30 | 0:17 | 14.7167 | 0 | 0 | 0 | 14.7167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[13 empty] | 271.85 | 0 | 0 | 0 | 271.85 | [6 empty] | 100
| ER1R20 | 63 MVAR GKP - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R21 | 63 MVAR GKP - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R22 | 63 MVAR NPRN - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R23 | 63 MVAR NPRN - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R24 | 63 MVAR MUZ - I L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R25 | 63 MVAR MUZ- II L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R26 | 63 MVAR BSF- I L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R27 | 63 MVAR BSF- II L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R28 | 50 MVAR BSF- III L/R AT PSL | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R29 | 50 MVAR BALIA L/R AT PSL | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R30 | 63 MVAR ALLAHABAD-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R31 | 63 MVAR SARNATH-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R32 | 50 MVAR B/R - I AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R33 | 50 MVAR B/R - II AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R34 | 50 MVAR L/R - I AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R35 | 50 MVAR L/R - 2 AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R36 | 80 MVAR B/R - 1 AT BANKA | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R37 | 3*110 MVAR 1 PH B/R - I AT SASARAM | 330 | ER1 | -- | -- | -- | -- | 2016-11-01 | 0:00 | 2016-11-01 | 12:33 | 12.55 | 0 | 0 | 0 | 12.55 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-03 | 18:18 | 2016-11-03 | 23:43 | 5.4167 | 0 | 0 | 0 | 5.4167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-04 | 5:58 | 2016-11-04 | 12:09 | 6.1833 | 0 | 0 | 0 | 6.1833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-04 | 17:29 | 2016-11-06 | 8:17 | 38.8 | 0 | 0 | 0 | 38.8 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-09 | 17:24 | 2016-11-12 | 3:13 | 57.8167 | 0 | 0 | 0 | 57.8167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-12 | 6:12 | 2016-11-13 | 16:21 | 34.15 | 0 | 0 | 0 | 34.15 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-13 | 18:12 | 2016-11-17 | 0:23 | 78.1833 | 0 | 0 | 0 | 78.1833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-17 | 17:27 | 2016-11-17 | 22:00 | 4.55 | 0 | 0 | 0 | 4.55 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-11-19 | 5:49 | 2016-11-26 | 2:20 | 164.5167 | 0 | 0 | 0 | 164.5167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-26 | 18:25 | 2016-11-27 | 21:19 | 26.9 | 0 | 0 | 0 | 26.9 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[13 empty] | 429.0667 | 0 | 0 | 0 | 429.0667 | [6 empty] | 100
| ER1R38 | 3*110 MVAR 1 PH L/R - I AT SASARAM (AS B/R) | 330 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R39 | 125 MVAR BUS REACTOR-1 RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R40 | 125 MVAR BUS REACTOR-1 PATNA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R41 | 80 MVAR PURNEA-1 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R42 | 80 MVAR PURNEA-2 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R43 | 125 MVAR BUS REACTOR-2 PATNA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R44 | 125 MVAR BUS REACTOR-1 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R45 | 125 MVAR BUS REACTOR-2 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R46 | 3*80MVAR 1 PH L/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R47 | 3*80MVAR 1 PH B/R - II AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R48 | 80 MVAR B/R - 1 AT LAKHISARAI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R49 | 3*80MVAR 1 PH B/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  | Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R50 | 63MVAR KISHANGANJ LR-I AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R51 | 63MVAR KISHANGANJ LR-II AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R52 | 3*80 MVAR DHRAMJAYGARH LR-II AS BR AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R53 | 125 MVAR BR-II AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2016-11-05 | 17:47 | 2016-11-06 | 8:33 | 14.7667 | 0 | 0 | 0 | 14.7667 | SVRD | HANDSTRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[9 empty] | 2016-11-06 | 18:32 | 2016-11-07 | 9:03 | 14.5167 | 0 | 0 | 0 | 14.5167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-08 | 17:52 | 2016-11-08 | 22:16 | 4.4 | 0 | 0 | 0 | 4.4 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-10 | 17:43 | 2016-11-10 | 22:05 | 4.3667 | 0 | 0 | 0 | 4.3667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-11 | 17:33 | 2016-11-11 | 22:09 | 4.6 | 0 | 0 | 0 | 4.6 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-12 | 17:33 | 2016-11-12 | 23:53 | 6.3333 | 0 | 0 | 0 | 6.3333 | SVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2016-11-14 | 17:31 | 2016-11-15 | 0:17 | 6.7667 | 0 | 0 | 0 | 6.7667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-15 | 18:19 | 2016-11-15 | 22:47 | 4.4667 | 0 | 0 | 0 | 4.4667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-16 | 17:50 | 2016-11-16 | 23:58 | 6.1333 | 0 | 0 | 0 | 6.1333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-19 | 17:49 | 2016-11-19 | 21:19 | 3.5 | 0 | 0 | 0 | 3.5 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[9 empty] | 2016-11-25 | 18:15 | 2016-11-26 | 21:47 | 27.5333 | 0 | 0 | 0 | 27.5333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[13 empty] | 97.3833 | 0 | 0 | 0 | 97.3833 | [6 empty] | 100
| ER1R54 | 125 MVAR BR-I AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2016-11-01 | 0:00 | 2016-11-01 | 13:25 | 13.4167 | 0 | 0 | 0 | 13.4167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-02 | 18:02 | 2016-11-02 | 22:00 | 3.9667 | 0 | 0 | 0 | 3.9667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-03 | 17:49 | 2016-11-03 | 22:03 | 4.2333 | 0 | 0 | 0 | 4.2333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-04 | 17:26 | 2016-11-04 | 22:00 | 4.5667 | 0 | 0 | 0 | 4.5667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-05 | 17:46 | 2016-11-06 | 8:22 | 14.6 | 0 | 0 | 0 | 14.6 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-06 | 18:28 | 2016-11-07 | 8:56 | 14.4667 | 0 | 0 | 0 | 14.4667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-08 | 17:50 | 2016-11-08 | 22:18 | 4.4667 | 0 | 0 | 0 | 4.4667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-10 | 17:45 | 2016-11-10 | 22:15 | 4.5 | 0 | 0 | 0 | 4.5 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-11 | 17:35 | 2016-11-11 | 21:58 | 4.3833 | 0 | 0 | 0 | 4.3833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-12 | 17:32 | 2016-11-12 | 23:33 | 6.0167 | 0 | 0 | 0 | 6.0167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-13 | 18:18 | 2016-11-13 | 22:22 | 4.0667 | 0 | 0 | 0 | 4.0667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-14 | 17:32 | 2016-11-15 | 0:02 | 6.5 | 0 | 0 | 0 | 6.5 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-15 | 18:20 | 2016-11-15 | 22:28 | 4.1333 | 0 | 0 | 0 | 4.1333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-16 | 17:45 | 2016-11-16 | 23:54 | 6.15 | 0 | 0 | 0 | 6.15 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-17 | 17:28 | 2016-11-18 | 0:46 | 7.3 | 0 | 0 | 0 | 7.3 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-19 | 17:51 | 2016-11-19 | 21:16 | 3.4167 | 0 | 0 | 0 | 3.4167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-28 | 17:43 | 2016-12-01 | 0:00 | 54.2833 | 0 | 0 | 0 | 54.2833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A |  | 100
[13 empty] | 160.4667 | 0 | 0 | 0 | 160.4667
| ER1R55 | 125 MVAR BR-III AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | 2016-11-01 | 17:58 | 2016-11-02 | 14:58 | 21 | 0 | 0 | 0 | 21 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[9 empty] | 2016-11-03 | 18:12 | 2016-11-03 | 21:14 | 3.0333 | 0 | 0 | 0 | 3.0333 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 24.0333 | 0 | 0 | 0 | 24.0333 |  |  | N/A | N/A | N/A |  | 100
| ER1R55 | 125 MVAR BR-I AT Kishanganj | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[13 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R57 | 125 MVAR BR-I AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
| ER1R58 | 125 MVAR BR-II AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100

## SOP Dec 2016
Standard of Performance data for the month of DEC- 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION - I
'ANNEXURE - A
Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | DETAILS OF OUTAGE |  | Total outage in days (1) | OUTAGE |  | RESTORATION |  |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Category | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[5 empty] | No. of Tower damaged | No.of insulators failed |  | DATE | TIME | DATE | TIME | TOTAL | ISTS Licensee | OTHERS | System constraint/ Natural calmity/ Militancy | Deemed Available
ER1L1 | 132kV ARA-ARA | 1.7 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A | ERPC
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L2 | 132kV Dehri-SSRM | 62 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L3 | 132kV SSRM- KARAMNASA | 29 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L4 | 132kV DMRN-ARA | 1.7 | ER1 | -- | -- | -- | -- | 2016-12-09 | 11:37 | 2016-12-09 | 13:45 | 2.1333 | 0 | 0 | 0 | 2.1333 | OSPD | S/D TAKEN BY BSPTCL | N/A | N/A | N/A
[8 empty] | 2016-12-19 | 10:44 | 2016-12-19 | 18:20 | 7.6 | 0 | 0 | 0 | 7.6 | OSPD | S/D TAKEN BY BSPTCC
[8 empty] | 2016-12-31 | 23:08 | 2016-12-31 | 23:52 | 0.73333 | 0 | 0.73333 | 0 | 0 | OMSU | TRIPPED IN R-N FAULT.F.D.=12.39 KM FROM ARA (BSPTCL JURIDISCTION).F.C.=2.328 KAMP
|  |  |  | -- | -- | -- | -- |  |  |  |  | 10.4667 | 0 | 0.73333 | 0 | 9.7333 |  |  | N/A | N/A | N/A |  | 100
ER1L5 | 132kV PNR-DLK (LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L6 | 132kV PNR-PRN(LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L7 | 220kV DALKHOLA-PURNEA I | 41 | ER1 | -- | -- | -- | -- | 2016-12-09 | 9:23 | 2016-12-09 | 14:26 | 5.05 | 5.05 | 0 | 0 | 0 | OSPT | S/D TAKEN BY DALKHOLA/ER-2 FOR TAN DELTA AND DCRM TEST AT DALKHOLA END. | N/A | N/A | N/A
[12 empty] | 5.05 | 5.05 | 0 | 0 | 0 | [6 empty] | 99.31
ER1L8 | 220kV DALKHOLA-PURNEA II | 41 | ER1 | -- | -- | -- | -- | 2016-12-10 | 9:27 | 2016-12-10 | 16:30 | 7.0533 | 7.0533 | 0 | 0 | 0 | OSPT | S/D TAKEN BY ER-2 FOR TAN DELTA AND DCRM TESTING AT DAKHOLA. | N/A | N/A | N/A
[12 empty] | 7.0533 | 7.0533 | 0 | 0 | 0 | [6 empty] | 99.05
ER1L9 | 220 kV PRN-NPRN-I | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L10 | 220 kV PRN-NPRN-II | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L11 | 220kV SASARAM-NADOKHAR | 112 | ER1 |  |  |  |  | 2016-12-10 | 23:05 | 2016-12-10 | 23:54 | 0.81667 | 0 | 0.81667 | 0 | 0 | OMSU | TRIPPED ONLY FROM NADOKHAR END DUE TO PROBLEM AT NADOKHAR, BSPTCL.
[12 empty] | 0.81667 | 0 | 0.81667 | 0 | 0
ER1L11 | 220kV NADOKHAR -ARRAH I | 112 | ER1 |  |  |  |  | 2016-12-01 | 0:00 | 2016-12-03 | 18:36 | 66.6 | 0 | 0 | 0 | 66.6 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[8 empty] | 2016-12-04 | 1:35 | 2016-12-10 | 23:17 | 165.7 | 0 | 0 | 0 | 165.7 | LVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-11 | 0:02 | 2016-12-25 | 13:14 | 349.2 | 0 | 0 | 0 | 349.2 | LVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-25 | 16:04 | 2017-01-01 | 0:00 | 151.9333 | 0 | 0 | 0 | 151.9333 | LVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[12 empty] | 733.4333 | 0 | 0 | 0 | 733.4333
ER1L12 | 220kV SASARAM-ARRAH II | 112 | ER1
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L13 | 220kV ARA-KHAGOL I | 48.44 | ER1 |  |  |  |  | 2016-12-01 | 0:00 | 2016-12-03 | 18:23 | 66.3833 | 0 | 0 | 0 | 66.3833 | LVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[8 empty] | 2016-12-04 | 17:48 | 2016-12-25 | 12:59 | 499.1833 | 0 | 0 | 0 | 499.1833 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-25 | 15:53 | 2016-12-29 | 16:25 | 96.5333 | 0 | 0 | 0 | 96.5333 | LPRD | S/OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-29 | 17:29 | 2017-01-01 | 0:00 | 54.5167 | 0 | 0 | 0 | 54.5167 | LPRD | H/T FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[12 empty] | 716.6167 | 0 | 0 | 0 | 716.6167
ER1L14 | 220kV ARA-KHAGOL II | 48.44 | ER1 | -- | -- | -- | -- | 2016-12-01 | 0:00 | 2016-12-03 | 18:23 | 66.3833 | 0 | 0 | 0 | 66.3833 | LVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[8 empty] | 2016-12-04 | 17:37 | 2016-12-25 | 13:00 | 499.3833 | 0 | 0 | 0 | 499.3833 | LVRD | S.OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION FOR VOLTAGE REGULATION
[8 empty] | 2016-12-25 | 15:53 | 2016-12-29 | 16:26 | 96.55 | 0 | 0 | 0 | 96.55 | LPRD | S/OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-29 | 17:29 | 2017-01-01 | 0:00 | 54.5167 | 0 | 0 | 0 | 54.5167 | LPRD | H/T FOR POWER REGULATION AS PER ERLDC INSTRUCTION.
[12 empty] | 716.8333 | 0 | 0 | 0 | 716.8333
ER1L15 | 220kV DEHRI-PUSAULI | 4.88 | ER1 | -- | -- | -- | -- | 2016-12-04 | 10:28 | 2017-01-01 | 0:00 | 661.5333 | 0 | 0 | 0 | 661.5333 | LPRD | OPENED FROM SSRM AS PER ERLDC INSTRUCTION FOR POWER REGULATION. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 661.5333 | 0 | 0 | 0 | 661.5333 |  |  | N/A | N/A | N/A |  | 100
ER1L16 | 220kV SASARAM-SAHUPURI | 4.88 | ER1 | -- | -- | -- | -- | 2016-12-10 | 23:03 | 2016-12-11 | 16:30 | 17.45 | 0 | 17.45 | 0 | 0 | OMSU | TRIPPED DUE TO R-N FAULT.F.D.=51.1KM FROM SASARAM (UPPCL JURISDICTION) ,F.C.=1.96 KA. | N/A | N/A | N/A
[8 empty] | 2016-12-24 | 11:13 | 2016-12-24 | 20:22 | 9.15 | 0 | 0 | 0 | 9.15 | OSPD | S/D TAKEN BY BSPTCL FOR DISMENTALING 2 NOS BENT TOWER OF THE LINE AND SHIFTING OF CONDUCTOR ON ERS.
[8 empty] | 2016-12-26 | 5:30 | 2016-12-26 | 19:56 | 14.4333 | 0 | 14.4333 | 0 | 0 | OMSU | TRIPPED DUE TO Y-N FAULT,F.D.=44.17KM FROM SSRM(UPPCL JURISDICTION) = ,F.C.=3.059KA
[8 empty] | 2016-12-31 | 20:58 | 2016-12-31 | 23:48 | 2.8333 | 0 | 2.8333 | 0 | 0 | OMSU | TRIPPED IN THREE PHASE FAULT.F.D=85.56 KM ( UPPCL JURIDISCTION) FROM PUSAULI.
[12 empty] | 43.8667 | 0 | 34.7167 | 0 | 9.15
ER1L17 | 220kV RANCHI-CHANDIL I | 8.06 | ER1 | -- | -- | -- | -- | 2016-12-20 | 11:38 | 2016-12-22 | 12:26 | 48.8 | 0 | 0 | 0 | 48.8 | OSPD | S/D TAKEN BY JUSNL. | N/A | N/A | N/A
[12 empty] | 48.8 | 0 | 0 | 0 | 48.8
ER1L18 | 220kV RNC-CHANDIL-II (LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L19 | 220kV RNC-HATIA-I (LILO) | 8.06 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L20 | 220kV RNC-HATIA-II(LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L21 | 220kV GAYA-DEHRI -I(LILO PART) | 11 | ER1 |  |  |  |  | 2016-12-01 | 0:00 | 2016-12-04 | 15:59 | 87.9833 | 0 | 87.9833 | 0 | 0 | OMSU | TRIPPED DUE TO Y-B FAULT,F.D.=83.5KM FROM GAYA(BSPTCL JURISDICTION), F.C.=Iy=2.79KA, IB=2.32KA. TRIPPED DUE TO COLLAPSE OF D/C TOWER AT LOC. 275 AT SONE RIVER IN BSPTCL JURISDICTION.
[8 empty] | 2016-12-14 | 12:01 | 2016-12-14 | 17:18 | 5.2833 | 0 | 5.2833 | 0 | 0 | OMSU | TRIPPED DUE TO Y-B FAULT,F.D.=73.1KM FROM GAYA(BSPTCL JURISDICTION) F.C.- Iy=2.51KA,Ib=2.36KA.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 93.2667 | 0 | 93.2667 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L22 | 220kV GAYA-BODHGAYA(BSEB) I | 12.7 | ER1 | -- | -- | -- | -- | 2016-12-04 | 8:22 | 2016-12-04 | 15:29 | 7.1167 | 0 | 0 | 0 | 7.1167 | OSPD | S/D TAKEN BY BSPTCL FOR NORMALIZING SON NAGAR-1 BAY & BODHGAYA-1 BAY AT GAYA. | N/A | N/A | N/A
[8 empty] | 2016-12-28 | 1:10 | 2016-12-28 | 7:48 | 6.6333 | 0 | 0 | 0 | 6.6333 | LVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[12 empty] | 13.75 | 0 | 0 | 0 | 13.75
ER1L23 | 220kV GAYA-DEHRI-II (LILO PART) | 11 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L24 | 220kV GAYA-BODHGAYA(BSEB) II | 12.7 | ER1 | -- | -- | -- | -- | 2016-12-04 | 8:25 | 2016-12-04 | 15:29 | 7.0667 | 0 | 0 | 0 | 7.0667 | OSPD | S/D TAKEN BY BSPTCL FOR NORMALIZING SNNAGAR-1 BAY & BODHGAYA-1 BAY AT GAYA. | N/A | N/A | N/A
[8 empty] | 2016-12-11 | 2:27 | 2016-12-11 | 10:49 | 8.3667 | 0 | 0 | 0 | 8.3667 | LVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
|  |  |  | -- | -- | -- | -- |  |  |  |  | 15.4333 | 0 | 0 | 0 | 15.4333 |  |  | N/A | N/A | N/A |  | 100
ER1L25 | 400kV FARAKKA-KAHALGAON I | [10 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L26 | 400kV FARAKKA-KAHALGAON II
ER1L27 | 400kV KAHALGAON-FARAKKA III | 95.25 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L28 | 400kV KAHALGAON-FARAKKA IV | 95.25 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L29 | 400kV KAHALGAON-LAKHISARAI I | 145 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L30 | 400kV BIHARSHARIFF-LAKHISARAI I | 89 | ER1 | -- | -- | -- | -- | 2016-12-16 | 10:50 | 2016-12-16 | 20:33 | 9.7167 | 0 | 0 | 0 | 9.7167 | LCSD | S/D TAKEN BY BSF FOR INTERCONNECTION OF 400KV BUS-2 & 4 AT BSF UNDER BUS SPLITTING WORK. | N/A | N/A | N/A
[8 empty] | 2016-12-19 | 12:43 | 2016-12-19 | 15:10 | 2.45 | 0 | 0 | 2.45 | 0 | LNCC | TRIPPED DUE TO R-B FUALT, F.D=41.42 KM FROM BSF, F.C= Ir=9.301 ka, Ib=8.859 KA AT BSF. TRIPPED DUE TO EXCESSIVE DENSE FOG
[12 empty] | 12.1667 | 0 | 0 | 2.45 | 9.7167
ER1L31A | 400kV KAHALGAON-LAKHISARAI II | 145 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L31B | 400kV BIHARSHARIF-LAKHISARAI II | 89 | ER1 | -- | -- | -- | -- | 2016-12-06 | 6:16 | 2016-12-06 | 16:16 | 10 | 0 | 0 | 10 | 0 | LNCC | TRIPPED IN B-N FAULT.F.D.=14.55 KM FROM BIHARSHARIF,F.C.=13.66 KAMP.THERE WAS INULTOR DECAPPING AT LOC.N.O.491 DUE TO DENSE FOG. | N/A | N/A | N/A
[8 empty] | 2016-12-16 | 10:40 | 2016-12-16 | 20:43 | 10.05 | 0 | 0 | 0 | 10.05 | LCSD | S/D TAKEN BY BSF FOR INTERCONNECTION OF 400KV BUS-2 & 4 AT BSF UNDER BUS SPLITTING WORK.
[8 empty] | 2016-12-23 | 13:45 | 2016-12-23 | 16:10 | 2.4167 | 0 | 2.4167 | 0 | 0 | OMSU | S/D TAKEN FOR CHARGING OF 50MVAR, 400KV BSF-LAKHISARAI-2 L/R AT BSF AFTER OVERHAULING WORK.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 22.4667 | 0 | 2.4167 | 10 | 10.05 |  |  | N/A | N/A | N/A |  | 100
ER1L32 | 400kV KAHALGAON-BANKA-I | 47.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 2.4167 | 10 | 10.05 |  |  | N/A | N/A | N/A |  | 100
ER1L33 | 400KV BIHARSHARIF-BANKA I | 184.54 | ER1 | -- | -- | -- | -- | 2016-12-05 | 7:27 | 2016-12-05 | 20:41 | 13.2333 | 0 | 0 | 13.2333 | 0 | LNCC | TRIPPED DUE TO B-N FAULT, F.D=27.7 KM FROM BSF, F.C=7.04KA AT BSF. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 13.2333 | 0 | 2.4167 | 23.2333 | 10.05 |  |  | N/A | N/A | N/A |  | 100
ER1L34 | 400kV KAHALGAON-BANKA-II | 47.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
ER1L35 | 400KV BIHARSHARIF-BANKA II | 184.54 | ER1 | -- | -- | -- | -- | 2016-12-29 | 7:13 | 2016-12-29 | 7:13 | NA | NA | 0 | 0 | 0 | LART | A/R OPERATED SUCCESSFULLY FROM BOTH END DUE TO B-N FAULT,F.D.= 184.5KM FROM BSF, F.C.=1.859kA. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
ER1L36A | 400kV JAMSHEDPUR-CHAIBASA I | 46.14 | ER1 | -- | -- | -- | -- | 2016-12-20 | 17:25 | 2016-12-20 | 18:29 | 1.0667 | 1.0667 | 0 | 0 | 0 | OSPT | S/D TAKEN TO ATTEND HOT SPOT IN ITS TIE BAY AT JAMSHEDPUR. | N/A | N/A | N/A
[12 empty] | 1.0667 | 1.0667 | 0 | 0 | 0 | [6 empty] | 99.85
ER1L36B | 400kV CHAIBASA-ROURKELA I | 131.48 | ER1 | -- | -- | -- | -- | 2016-12-06 | 8:42 | 2016-12-07 | 15:45 | 31.05 | 0 | 0 | 0 | 31.05 | LCSD | S/D TAKEN TO CARRY OUT RETROFITTING WORK OF CGL MAKE PLCC PANELS AT BOTH ENDS. | N/A | N/A | N/A
[12 empty] | 31.05 | 0 | 0 | 0 | 31.05
ER1L37 | 400kV JAMSHEDPUR-ROURKELA II | 153 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L38 | 400kV MAITHON-KAHALGAON I | 172 | ER1 | -- | -- | -- | -- | 2016-12-29 | 10:05 | 2016-12-29 | 17:51 | 7.7667 | 7.7667 | 0 | 0 | 0 | OSPT | S/D TAKEN BY ER-2 FOR AMP WORK AT MTN END. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 7.7667 | 7.7667 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.95
ER1L39 | 400kV MAITHON-KAHALGAON II | 172 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
ER1L40 | 400kV BIHARSHARIF-SASARAM-I | 210 | ER1 | -- | -- | -- | -- | 2016-12-19 | 10:17 | 2016-12-19 | 18:38 | 8.35 | 0 | 0 | 0 | 8.35 | LCSD | S/D TAKEN FOR 400 KV BUS-I SPLITTING WORK AT BSF | N/A | N/A | N/A
[8 empty] | 2016-12-28 | 9:43 | 2016-12-28 | 18:27 | 8.7333 | 0 | 8.7333 | 0 | 0 | OMSU | S/D TAKEN TO FACILITATE S/D OF L/R OF 400KV BSF-SSRM-1 AT BSF FOR DISMANTLING OF BUSHING OF ITS L/R AT BSF.
[12 empty] | 8.35 | 0 | 0 | 0 | 8.35
ER1L41 | 400kV BIHARSHARIF-SASARAM-II | 210 | ER1 | -- | -- | -- | -- | 2016-12-19 | 12:43 | 2016-12-19 | 13:26 | 0.71667 | 0 | 0 | 0.71667 | 0 | LNCC | TRIPPED DUE TO B-N FAULT, F.D=19.33 KM FROM BSF, F.C=12.19 KA AT BSF. THE LINE TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0.71667 | 0 | 0 | 0.71667 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L42 | 400KV PATNA-BARH III | 68.66 | ER1 | insulator failure | -- | -- | 0.93333 | 2016-12-03 | 23:56 | 2016-12-04 | 22:20 | 22.4 | 0 | 0 | 22.4 | 0 | LNCC | TRIPPED ON B-N FAULT . F.D.= 20.9 KM FROM PATNA WITH F.C.= 6.28 KA. LINE WAS ATTEMPTED TO CHARE AT 2:45 HRS ON 04.12.2017. AFTER PETROLING INSULATOR DECAPING WAS FOUND AT LOC NO. 145. SAME WAS RESTORED AND SHUTDOWN WAS EXTENDED FOR REPLACEMENT OF PORCELAIN INSULATORS WITH POLYMER INSULATORS. | 1 | N | -0.066667
[8 empty] | 2016-12-07 | 1:52 | 2016-12-07 | 3:12 | 1.3333 | 0 | 1.3333 | 0 | 0 | OMSU | TRIPPED DUE TO PROBLEM AT NTPC/BARH. D/T RECD. AT PATNA END.
[8 empty] | 2016-12-07 | 3:12 | 2016-12-07 | 19:37 | 16.4167 | 0 | 0 | 16.4167 | 0 | LNCC | TRIPPED ON B-N FAULT IMMEDIATELY AFTER LINE WAS TAKEN INTO SERVICE DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA.
[8 empty] | 2016-12-11 | 12:14 | 2016-12-11 | 18:14 | 6 | 0 | 0 | 6 | 0 | LNCC | S/D TAKEN TO ATTEND INSULATOR DECAPPING AT LOC. NO. 144 CAUSED DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA.
[8 empty] | 2016-12-11 | 4:11 | 2016-12-11 | 5:06 | 0.91667 | 0 | 0.91667 | 0 | 0 | OMSU | A/R SUCCESSFUL AT PATNA(PG) END ONLY. Y-N FAULT,F.D.=16.3 KM FROM PATNA = ,F.C.=9.6 KAMP.LINE TRIPPED FROM NTPC/BARH ONLY DUE TO PROBLEM AT THEIR END.
[8 empty] | 2016-12-24 | 11:28 | 2016-12-24 | 17:46 | 6.3 | 0 | 0 | 0 | 6.3 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED PORCELEIN INSULATOR WITH POLYMER INSULATOR
[8 empty] | 2016-12-25 | 9:48 | 2016-12-25 | 16:01 | 6.2167 | 0 | 0 | 0 | 6.2167 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED PORCELEIN INSULATOR WITH POLYMER INSULATOR
[8 empty] | 2016-12-26 | 10:35 | 2016-12-26 | 17:37 | 7.0333 | 0 | 0 | 0 | 7.0333 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED PORCELEIN INSULATOR WITH POLYMER INSULATOR CAUSED BY DENSE FOG.
[8 empty] | 2016-12-27 | 1:50 | 2016-12-27 | 20:14 | 18.4 | 0 | 0 | 18.4 | 0 | LNCC | TRIPPED ON Y-N FAULT. F.D.= 63.4 KM FROM PTN WITH F.C.= 5.46 KA. CAUSED BY EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA.
[8 empty] | 2016-12-28 | 11:00 | 2016-12-28 | 17:57 | 6.95 | 0 | 6.95 | 0 | 6.95 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED PORCELEIN INSULATOR WITH POLYMER INSULATOR CAUSED BY DENSE FOG.
[12 empty] | 91.9667 | 0 | 9.2 | 63.2167 | 26.5
ER1L43 | 400KV PATNA-BARH IV | 68.66 | ER1 | -- | -- | -- | -- | 2016-12-03 | 23:39 | 2016-12-04 | 1:27 | 1.8 | 0 | 0 | 1.8 | 0 | LNCC | TRIPPED ON R-N FAULT. F.D.= 0.3 KM FROM PATNA WITH F.C.= 11 KA.TRIPPED DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA. | N/A | N/A | N/A
[8 empty] | 2016-12-04 | 2:20 | 2016-12-04 | 2:20 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED ON Y-N FAULT. F.D.= 99.4 KM FROM PATNA
[8 empty] | 2016-12-04 | 2:31 | 2016-12-04 | 2:31 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED ON Y-N FAULT. F.D.= 24.8 KM FROM PATNA WITH F.C.= 5.57 KA
[8 empty] | 2016-12-04 | 3:03 | 2016-12-04 | 9:20 | 6.2833 | 0 | 0 | 6.2833 | 0 | LNCC | TRIPPED ON R-N FAULT DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA. F.D.= 49.1 KM FROM PATNA WITH F.C.= 5.59 KA
[8 empty] | 2016-12-05 | 2:23 | 2016-12-05 | 22:49 | 20.4333 | 0 | 0 | 20.4333 | 0 | LNCC | TRIPPED ON R-N FAULT DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA. F.D.= 23.9 KM FROM PATNA WITH F.C.= 7.38 KA
[8 empty] | 2016-12-07 | 1:52 | 2016-12-07 | 3:34 | 1.7 | 0 | 0 | 1.7 | 0 | LNCC | TRIPPED ON R-N FAULT DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA. F.D.=68.5KM FROM PATNA WITH F.C.= 7.34 KA.
[8 empty] | 2016-12-07 | 13:03 | 2016-12-07 | 19:38 | 6.5833 | 0 | 0 | 0 | 6.5833 | OMSU | S/D TAKEN FOR ATTENDING INSULATOR DECAPPING AT LOC. 22 CAUSED DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA.
[8 empty] | 2016-12-08 | 3:21 | 2016-12-08 | 6:32 | 3.1833 | 0 | 0 | 3.1833 | 0 | LNCC | TRIPPED DUE TO Y-N FAULT, F.D=21.4 KM FROM PATNA, F.C=7.73 KA AT PATNA CAUSED BY DENSE FOG AROUND THE FAULT AREA.
[8 empty] | 2016-12-08 | 12:34 | 2016-12-09 | 18:31 | 29.95 | 0 | 0 | 0 | 29.95 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED INSULATORS AT LOC. NO.131.LINE WAS CHARGED AT 21:54 HRS BUT COULD NOT HOLD AND TRIPED ON SOTF, FAULT WAS SHOWING DISTANCE 64 KM FROM PATNA END. AFTER PETROLING , INSULATOR DECAPING WAS FOUND AT LOC NO. 19 AND SAME WAS REPLACED WITH POLYMER INSULATORS. SHUTDOWN WAS CONTINUED FOR REPLACEMENT OF PORCELAIN INSULATORS WITH POLYMER ONES IN OTHER LOCATIONS.THE LINE WAS FINALY CHARGED 18:31 hrs.
[8 empty] | 2016-12-23 | 6:55 | 2016-12-23 | 6:55 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED ON R-N FAULT. F.D.= 22.9 KM FROM PATNA WITH F.C.= 7.9 KA
[8 empty] | 2016-12-23 | 9:55 | 2016-12-23 | 18:09 | 8.2333 | 0 | 0 | 0 | 8.2333 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED INSULATORS DUE TO DENSE FOG, WITH POLYMER INSULATOR.
[8 empty] | 2016-12-29 | 10:47 | 2016-12-29 | 18:14 | 7.45 | 0 | 0 | 0 | 7.45 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED PORCELAIN INSULATOR WITH POLYMER INSULATOR CAUSED BY DENSE FOG.
[8 empty] | 2016-12-30 | 11:59 | 2016-12-30 | 17:08 | 5.15 | 0 | 0 | 0 | 5.15 | OMSU | S/D TAKEN FOR REPLACEMENT OF DECAPPED PORCELAIN INSULATOR WITH POLYMER INSULATOR CAUSED BY DENSE FOG.
[8 empty] | 2016-12-31 | 10:24 | 2016-12-31 | 16:46 | 6.3667 | 0 | 0 | 0 | 6.3667 | OMSU | S/D TAKEN FOR REPLACEMENT OF PORCELAIN INSULATORS WITH POLYMER INSULATOR CAUSED BY EXCESSIVE DENSE FOG.
[12 empty] | 97.1333 | 0 | 0 | 33.4 | 63.7333 | [6 empty] | 100
ER1L44 | 400KV MUZAFFARPUR-BIHARSHARIF I | 133.3 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L45 | 400KV MUZAFFARPUR-BIHARSHARIF II | 133.3 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A |  | 100
ER1L46 | 400kV KAHALGAON-BARH I | 217.24 | ER1 |  |  |  |  | 2016-12-05 | 3:56 | 2016-12-05 | 5:56 | 2 | 0 | 0 | 2 | 0 | LNCC | TRIPPED DUE TO R-N FAULT, F.D=40 KM FROM BARH, F.C=5 KA. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[8 empty] | 2016-12-07 | 3:12 | 2016-12-08 | 18:25 | 39.2167 | 0 | 39.2167 | 0 | 0 | OMSU | TRIPPED DUE TO PROBLEM AT NTPC/KAHALGAON.
[8 empty] | 2016-12-13 | 10:49 | 2016-12-13 | 18:32 | 7.7167 | 0 | 0 | 0 | 7.7167 | OSPD | S/D TAKEN BY NTPC/KHLG FOR RELAY REPLACEMENT AT NTPC/KHLG.
[12 empty] | 48.9333 | 0 | 39.2167 | 2 | 7.7167 | [6 empty] | 100
ER1L47 | 400kV KAHALGAON-BARH II | 217.24 | ER1 | -- | -- | -- | -- | 2016-12-05 | 4:13 | 2016-12-05 | 6:50 | 2.6167 | 0 | 0 | 2.6167 | 0 | LNCC | TRIPPED DUE TO B-N FAULT, F.D=40 KM FROM BARH, F.C=8 KA. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA. | N/A | N/A | N/A
[8 empty] | 2016-12-08 | 20:36 | 2016-12-09 | 17:07 | 20.5167 | 0 | 0 | 0 | 20.5167 | OSFD | EMERGENCY S/D TAKEN BY NTPC/KHLG TO ATTEND HOT SPOT IN R-PH LINE SIDE ISOLATOR(3389L) AT NTPC/KHLG END.
[8 empty] | 2016-12-14 | 10:44 | 2016-12-14 | 18:34 | 7.8333 | 0 | 0 | 7.8333 | 0 | LNCC | S/D TAKEN TO FACILITATE S/D OF 400KV PATNA-BARH-1 FOR ATTENDING DECAPPED PILOT INSULATORS AT LOC NO M/C 05 CAUSED BY DENSE FOG.
[8 empty] | 2016-12-15 | 10:31 | 2016-12-15 | 18:09 | 7.6333 | 0 | 0 | 0 | 7.6333 | OSFD | EMERGENCY S/D TAKEN BY NTPC/KHLG FOR REPLACEMENT OF R-POLE OF ITS MAIN BAY CB AT NTPC /KHLG END
|  |  |  | -- | -- | -- | -- |  |  |  |  | 38.6 | 0 | 0 | 10.45 | 28.15 |  |  | N/A | N/A | N/A |  | 100
ER1L48 | 400kV PATNA-BARH I | 93 | ER1 | -- | -- | -- | -- | 2016-12-04 | 0:05 | 2016-12-04 | 0:05 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED ON B-N FAULT. F.D.= 126.8 KM FROM PATNA WITH F.C.= 4.9 KA | N/A | N/A | N/A
[8 empty] | 2016-12-04 | 1:16 | 2016-12-04 | 3:26 | 2.1667 | 0 | 0 | 2.1667 | 0 | LNCC | TRIPPED ON B-N FAULT DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA. F.D.= 104.4 KM FROM PATNA WITH F.C.= 2.05 KA
[8 empty] | 2016-12-05 | 5:09 | 2016-12-05 | 9:56 | 4.7833 | 0 | 0 | 4.7833 | 0 | LNCC | TRIPPED ON B-N FAULT, F.D=21.43 KM FROM PATNA, F.C=7.23 KA AT PATNA. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[8 empty] | 2016-12-14 | 10:29 | 2016-12-14 | 19:14 | 8.75 | 0 | 0 | 0 | 8.75 | OMSU | S/D TAKEN FOR ATTENDING DECAPPED PILOT INSULATORS AT LOC NO M/C 05 CAUSED BY DENSE FOG.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 15.7 | 0 | 0 | 6.95 | 8.75 |  |  | N/A | N/A | N/A |  | 100
ER1L49 | 400kV PATNA-BARH II | 93 | ER1 | -- | -- | -- | -- | 2016-12-04 | 1:36 | 2016-12-04 | 1:36 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED SUCCESSFULLY ON B-N FAULT . F.D.= 85.9 KM FROM PATNA WITH F.C.= 1.97 KA. | N/A | N/A | N/A
[8 empty] | 2016-12-04 | 1:43 | 2016-12-04 | 1:43 | NA | NA | 0 | 0 | 0 | LART | AUTO RECLOSED ON B-N FAULT. F.D.= 82.2 KM FROM PATNA WITH F.C.= 1.82 KA
[8 empty] | 2016-12-05 | 4:30 | 2016-12-05 | 4:30 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED DUE TO R-N FAULT, F.D=33.59KM FROM PATNA, F.C=6.12KA.
[8 empty] | 2016-12-05 | 5:00 | 2016-12-05 | 9:31 | 4.5167 | 0 | 0 | 4.5167 | 0 | LNCC | TRIPPED DUE TO R-N FAULT, F.D=23.93 KM FROM PATNA, F.C=6.94 KA. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[8 empty] | 2016-12-13 | 10:52 | 2016-12-13 | 19:09 | 8.2833 | 0 | 0 | 0 | 8.2833 | OMSU | S/D TAKEN FOR ATTENDING DECAPPED PILOT INSULATORS(CAUSED BY DENSE FOG) AT LOC NO M/C 06.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 12.8 | 0 | 0 | 4.5167 | 8.2833 |  |  | N/A | N/A | N/A |  | 100
ER1L50 | 400kV MAITHON-RANCHI I | 199.81 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L51 | 400kV RAGHUNATHPUR-MAITHON | 44.02 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L52 | 400kV RANCHI-RAGHUNATHPUR I | 155.79 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L53 | 400kV MAITHON RB-RANCHI I | 187.64 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L54 | 400kV MAITHON RB-RANCHI II | 187.64 | ER1 | -- | -- | -- | -- | 2016-12-03 | 10:15 | 2016-12-03 | 19:57 | 9.7 | 0 | 0 | 0 | 9.7 | OSPD | S/D TAKEN FOR REPLACEMENT OF THE DAMAGED STUD OF 416-89L AND ISOLATOR MODIFICATION JOB AT MPL. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 9.7 | 0 | 0 | 0 | 9.7 |  |  | N/A | N/A | N/A |  | 100
ER1L55 | 400kV RANCHI-ROURKELA I | 144.45 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L56 | 400kV RANCHI-ROURKELA II | 144.45 | ER1 | -- | -- | -- | -- | 2016-12-09 | 9:53 | 2016-12-09 | 20:06 | 10.2167 | 0 | 0 | 10.2167 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCRANTS. | N/A | N/A | N/A
[12 empty] | 10.2167 | 0 | 0 | 10.2167 | 0 | [6 empty] | 100
ER1L57 | 400kV BIHARSHARIF-KODERMA I | 110.69 | ER1 | -- | -- | -- | -- | 2016-12-05 | 6:31 | 2016-12-05 | 6:31 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED DUE TO Y-N FAULT, F.D=32.07 KM FROM BSF, F.C=8.443 KA AT BSF. | N/A | N/A | N/A
[8 empty] | 2016-12-05 | 6:33 | 2016-12-05 | 20:01 | 13.4667 | 0 | 0 | 13.4667 | 0 | LNCC | TRIPPED DUE TO Y-N FAULT, F.D=15.2 KM FROM BSF, F.C=11.9 KA AT BSF. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAUTL AREA..
[8 empty] | 2016-12-06 | 2:24 | 2016-12-06 | 2:24 | NA | NA | 0 | 0 | 0 | LART | A/R SUCCESSFULLY OPERATED IN Y-N FAULT.F.D.=15.83 KM FROM BSF = ,F.C.=12.74KAMP
[8 empty] | 2016-12-06 | 2:26 | 2016-12-06 | 2:26 | NA | NA | 0 | 0 | 0 | LART | A/R SUCCESSFULLY OPERATED IN Y-N FAULT.F.D.=15.34KM FROM BSF,F.C.=12.83 KAMP
[8 empty] | 2016-12-06 | 2:33 | 2016-12-06 | 2:56 | 0.38333 | 0 | 0 | 0.38333 | 0 | LNCC | TRIPPED IN Y-N FAULT DUE TO DENSE FOG IN THE AFFECTED AREA.F.D.=13.6 KM FROM BSF,F.C.=13.70 KAMP
[8 empty] | 2016-12-22 | 15:12 | 2016-12-22 | 15:35 | 0.38333 | 0 | 0.38333 | 0 | 0 | OMSU | TRIPPED ONLY FROM BSF END DUE TO D/T RECEIVED AT BIHARSHARIFF FROM DVC/KODERMA(PROBLEM IN DVC/ KODERMA END).
[8 empty] | 2016-12-22 | 15:57 | 2016-12-22 | 17:26 | 1.4833 | 0 | 1.4833 | 0 | 0 | OMSU | TRIPPED ONLY FROM BSF END DUE TO D/T RECEIVED AT BIHARSHARIFF FROM DVC/KODERMA(PROBLEM IN DVC/ KODERMA).
[8 empty] | 2016-12-23 | 9:32 | 2016-12-23 | 12:03 | 2.5167 | 0 | 0 | 0 | 2.5167 | OSPD | S/D TAKEN BY DVC KODERMA TO ATTEND PROBLEM IN DT CIRCUIT AT KODERMA
[12 empty] | 18.2333 | 0 | 1.8667 | 13.85 | 2.5167 | [6 empty] | 100
ER1L58 | 400kV BIHARSHARIF-KODERMA II | 110.69 | ER1 | -- | -- | -- | -- | 2016-12-05 | 6:05 | 2016-12-05 | 6:05 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED DUE TO Y-N FAULT, F.D=28.39 KM FROM BSF, F.C=8.527 KA AT BSF. | N/A | N/A | N/A
[8 empty] | 2016-12-05 | 6:14 | 2016-12-05 | 19:50 | 13.6 | 0 | 0 | 13.6 | 0 | LNCC | TRIPPED DUE TO Y-N FAULT, F.D=13.56 KM FROM BSF, F.C=14.09 KA AT BSF. LINE TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[12 empty] | 13.6 | 0 | 0 | 13.6 | 0 | [6 empty] | 100
ER1L59 | 400kV BIHARSHARIF-VARANASI - I |  | ER1 | -- | -- | -- | -- | 2016-12-01 | 6:43 | 2016-12-01 | 18:25 | 11.7 | 0 | 0 | 11.7 | 0 | LNCC | TRIPPED DUE TO R-N FAULT,F.D.=26.20KM FROM BSF,F.C.=9.956KA CAUSED BY DENSE FOG IN THE AFFECTED AREA. | N/A | N/A | N/A
[8 empty] | 2016-12-05 | 5:03 | 2016-12-05 | 5:40 | 0.61667 | 0 | 0 | 0.61667 | 0 | LNCC | TRIPPED DUE TO R-N FAULT, F.D=21.63 KM FROM BSF, F.C=11.40 KA AT BSF. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[8 empty] | 2016-12-05 | 6:13 | 2016-12-05 | 8:47 | 2.5667 | 0 | 0 | 2.5667 | 0 | LNCC | TRIPPED DUE TO R-N FAULT, F.D=28.59 KM FROM BSF, F.C=9.578 KA AT BSF. LINE TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[12 empty] | 14.8833 | 0 | 0 | 14.8833 | 0 | [6 empty] | 100
ER1L60A | 400kV BIHARSHARIF-VARANASI - II |  | ER1 | -- | -- | -- | -- | 2016-12-01 | 6:21 | 2016-12-01 | 18:30 | 12.15 | 0 | 0 | 12.15 | 0 | LNCC | TRIPPED DUE TO B-N FAULT,F.D.=20.56KM FROM BSF,F.C.=11.35KA CAUSED BY DENSE FOG IN THE AFFECTED AREA. | N/A | N/A | N/A
[8 empty] | 2016-12-05 | 5:46 | 2016-12-05 | 6:28 | 0.7 | 0 | 0 | 0.7 | 0 | LNCC | TRIPPED DUE TO B-N FAULT, F.D=19.33 KM FROM BSF, F.C=12.19 KA AT BSF. THE LINE TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[8 empty] | 2016-12-05 | 6:52 | 2016-12-05 | 8:25 | 1.55 | 0 | 0 | 1.55 | 0 | LNCC | TRIPPED DUE TO B-N FAULT, F.D=26.55 KM FROM BSF, F.C=8.832 KA AT BSF. TRIPPED DUE TO EXCESSIVE DENSE FOG AROUND THE FAULT AREA.
[12 empty] | 14.4 | 0 | 0 | 14.4 | 0 | [6 empty] | 100
ER1L61A | 765kV GAYA-BALLIA | 237.7 | ER1 | -- | -- | -- | -- | 2016-12-03 | 3:39 | 2016-12-03 | 3:39 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED DUE TO Y-N FAULT, F.D=106.1 KM FROM GAYA, F.C=5.39 KA AT GAYA. HAPPENED DUE TO EXCESSIVE DENSE FOG IN AND AROUND THE FAULT AREA. | N/A | N/A | N/A
[8 empty] | 2016-12-22 | 9:20 | 2016-12-22 | 19:12 | 9.8667 | 0 | 0 | 9.8667 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 9.8667 | 0 | 0 | 9.8667 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L62 | 400kV JAMSHEDPUR(DVC)-BARIPADA | 108.29 | ER1 | -- | -- | -- | -- | 2016-12-28 | 6:41 | 2016-12-28 | 13:12 | 6.5167 | 0 | 0 | 6.5167 | 0 | LNCC | TRIPPED DUE TO Y-N FAULT.F.D.= 56.9 KM FROM BARIPADA WITH F.C.= 4.07 KA CAUSED BY EXCESSIVE DENSE FOG . | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 6.5167 | 0 | 0 | 6.5167 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L63 | 400kV BARIPADA-JAMSHEDPUR II | 140.28 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L64 | 400kV JAMSHEDPUR-JAMSHEDPUR(DVC) | 32 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L65 | SSRM - NABINAGAR I | 81.65 | ER1 | -- | -- | -- | -- | 2016-12-15 | 9:26 | 2016-12-15 | 16:02 | 6.6 | 0 | 0 | 0 | 6.6 | OSFD | EMERGENCY S/D TAKEN BY BRBCL FOR COMPLETION OF ERECTION WORK OF 400 KV NABINAGAR -SASARAM -2 AT BRBCL(NABINAGAR END). | N/A | N/A | N/A
[8 empty] | 2016-12-15 | 18:25 | 2016-12-15 | 19:10 | 0.75 | 0.75 | 0 | 0 | 0 | OSPT | S/D TAKEN BY SSRM FOR ATTENDING HOT SPOT IN R PH LINE ISOLATOR AT SASARAM END.
[8 empty] | 2016-12-28 | 9:14 | 2016-12-28 | 9:58 | 0.73333 | 0 | 0.73333 | 0 | 0 | OMSU | TRIPPED DUE TO D/T RECEIVED AT SSRM END.PROBLEM IN BRBCL NABINAGAR END.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 8.0833 | 0.75 | 0.73333 | 0 | 6.6 |  |  | N/A | N/A | N/A |  | 99.89
ER1L66 | SSRM - NABINAGAR II | 81.65 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L67A | 400KV GAYA - KODERMA - II | 118.2 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L67B | 400kV GAYA-MAITHON II | 277 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L68A | 400kV GAYA-KODERMA-I | 118.2 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L68B | 400kV GAYA-MAITHON-I | 277 | ER1 |  |  |  |  | 2016-12-14 | 13:36 | 2016-12-14 | 16:13 | 2.6167 | 2.6167 | 0 | 0 | 0 | OSPT | S/D TAKEN BY ER-2 TO ATTEND HOT SPOT IN ITS LINE ISOLATOR AT MTN END.
[12 empty] | 2.6167 | 2.6167 | 0 | 0 | 0 | [6 empty] | 99.65
ER1L69 | 400kV RANCHI-RANCHI(NEW) II | 78.6 | ER1 | -- | -- | -- | -- | 2016-12-07 | 9:09 | 2016-12-07 | 18:56 | 9.7833 | 0 | 0 | 9.7833 | 0 | LMAC | REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS. | N/A | N/A | N/A
[12 empty] | 9.7833 | 0 | 0 | 9.7833 | 0 | [6 empty] | 100
ER1L70 | 400kV RANCHI-RANCHI(NEW) I | 78.6 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L71 | 400kV RANCHI-RANCHI(NEW) III | 78.6 | ER1 | -- | -- | -- | -- | 2016-12-10 | 9:08 | 2016-12-10 | 18:09 | 9.0167 | 0 | 0 | 9.0167 | 0 | LMAC | S/D FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCRIENTS. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 9.0167 | 0 | 0 | 9.0167 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L72 | 400kV RANCHI-RANCHI(NEW) IV | 78.6 | ER1 | -- | -- | -- | -- | 2016-12-07 | 9:07 | 2016-12-07 | 18:59 | 9.8667 | 0 | 0 | 9.8667 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT FOR INSULATORS DAMAGED BY MISCREANTS. | N/A | N/A | N/A
[12 empty] | 9.8667 | 0 | 0 | 9.8667 | 0
ER1L73 | 400 KV BOKARO-KODERMA-I | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L74 | 400 KV BOKARO-KODERMA-II | 100 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L75 | 400 KV BARH - GORAKHPUR - I | 349.16 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L76 | 400 KV BARH - GORAKHPUR - II | 349.16 | ER1 | -- | -- | -- | -- | 2016-12-17 | 7:31 | 2016-12-17 | 7:31 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED DUE TO Y-N FAULT, F.D=19.9 KM FROM BARH, F.C=11.0 KA AT BARH. LINE AUTORECLOSED DUE TO DENSE FOG AROUND THE FAULT AREA. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L77 | 400 KVPATNA - KISHANGANJ -I |  | ER1 |  |  |  |  | 2016-12-01 | 00:00:00 | 2017-01-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER.
[12 empty] | 744 | 0 | 0 | 744 | 0 | [6 empty] | 100
ER1L78 | 400 KVPATNA - KISHANGANJ -II |  | ER1 |  |  |  |  | 2016-12-01 | 00:00:00 | 2017-01-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER.
[12 empty] | 744 | 0 | 0 | 744 | 0 | [6 empty] | 100
ER1L79 | 765 KV GAYA - VARANASI - II |  | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L80 | 400 KV GAYA - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L81 | 400 KV GAYA - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L82 | 400 KV NEW RANCHI - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L83 | 400 KV NEW RANCHI - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1T1 | 400/220kV ICT1 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2016-12-16 | 10:50 | 2016-12-16 | 20:41 | 9.85 | 0 | 0 | 0 | 9.85 | SCSD | S/D TAKEN BY BSF FOR INTERCONNECTION OF 400KV BUS-2 & 4 AT BSF UNDER BUS SPLITTING WORK. | N/A | N/A | N/A
[8 empty] | 2016-12-19 | 12:43 | 2016-12-19 | 13:34 | 0.85 | 0 | 0.85 | 0 | 0 | OMSU | ICT -1 AT BSF TRIPPED DUE TO TRIPPING OF 400 KV BSF- LAKHISARAI -1 (CAUSED BY DENSE FOG). DUE TO S/D OF 400 KV BUS-1 AT BSF.
[8 empty] | 2016-12-19 | 14:55 | 2016-12-19 | 15:27 | 0.53333 | 0 | 0.53333 | 0 | 0 | OMSU | ICT SWITCHED OFF TO FACILITATE CHARGING OF 400 KV BSF-LAKHISARAI-1 AT BSF, AS THE SAID ICT WAS EARLIER TAKEN INTO SERVICE WITH MAIN BAY OF LAKHISARI -1 (ITS TIE BAY COMMON TO ICT-1) BY ISOLATING LINE ISOLATOR OF LAKHISARI -1 AT BSF.
[12 empty] | 11.2333 | 0 | 1.3833 | 0 | 9.85 | [6 empty] | 100
ER1T2 | 400/220kV ICT2 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2016-12-19 | 10:12 | 2016-12-19 | 18:15 | 8.05 | 0 | 0 | 0 | 8.05 | SCSD | S/D TAKEN FOR 400 KV BUS-I SPLITTING WORK AT BSF | N/A | N/A | N/A
[12 empty] | 8.05 | 0 | 0 | 0 | 8.05 | [6 empty] | 100
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T4 | 400/220kV ICT1 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2016-12-08 | 8:41 | 2016-12-10 | 19:19 | 58.6333 | 0 | 0 | 0 | 58.6333 | OSPD | S/D TAKEN BY JUSNL FOR REPLACEMENT OF OLD CB AT 220 KV SIDE AT RAMCHANDRAPUR S/S OF JUSNL | N/A | N/A | N/A
[8 empty] | 2016-12-29 | 10:42 | 2016-12-29 | 14:23 | 3.6833 | 0 | 0 | 0 | 3.6833 | SCSD | S/D TAKEN FOR ICT-3 BAY CONSTRUCTION WORK AT JSR.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 62.3167 | 0 | 0 | 0 | 62.3167 |  |  | N/A | N/A | N/A |  | 100
ER1T5 | 400/220kV ICT2 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2016-12-17 | 9:44 | 2016-12-18 | 13:53 | 28.15 | 0 | 0 | 0 | 28.15 | OSPD | S/D TAKEN BY JUSNL FOR relay testing WORK AT JUSNL, RAMCHANDRAPUR | N/A | N/A | N/A
[8 empty] | 2016-12-26 | 10:15 | 2016-12-26 | 21:52 | 11.6167 | 0 | 0 | 0 | 11.6167 | SCSD | S/D TAKEN FOR BAY CONSTRUCTION WORK OF ICT-3 AT JSR.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 39.7667 | 0 | 0 | 0 | 39.7667 |  |  | N/A | N/A | N/A |  | 100
ER1T6 | 400/220kV ICT1 NEW PURNEA | 500 | ER1 | -- | -- | -- | -- | 2016-12-01 | 11:37 | 2016-12-01 | 17:13 | 5.6 | 0 | 5.6 | 0 | 0 | OMSU | S/D TAKEN FOR CSD COMMISSIONING WORK AT NPRN. | N/A | N/A | N/A
[8 empty] | 2016-12-03 | 9:51 | 2016-12-03 | 20:16 | 10.4167 | 0 | 0 | 0 | 10.4167 | SCSD | For CSD commissioning and PRV replacement.
[8 empty] | 2016-12-04 | 13:30 | 2016-12-04 | 16:42 | 3.2 | 0 | 0 | 0 | 3.2 | SCSD | S/D TAKEN FOR CSD COMMISSIONING WORK.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 19.2167 | 0 | 5.6 | 0 | 13.6167 |  |  | N/A | N/A | N/A |  | 100
ER1T7 | 400/220kV ICT2 NEW PURNEA | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1T8 | 400/220kV ICT1 SSRM | 500 | ER1 | -- | -- | -- | -- | 2016-12-29 | 15:54 | 2016-12-29 | 18:19 | 2.4167 | 2.4167 | 0 | 0 | 0 | OMST | TRIPPED DUE TO MALOPERATION OF PRD. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 2.4167 | 2.4167 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.68
ER1T9 | 400/220kV ICT2 SSRM | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T10 | 400/220kV ICT1 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T11 | 400/220kV ICT2 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T12 | 400/220kV ICT1 PATNA | 315 | ER1 | -- | -- | -- | -- | 2016-12-25 | 13:19 | 2016-12-25 | 15:32 | 2.2167 | 2.2167 | 0 | 0 | 0 | OSPT | S/D TAKEN TO ARREST OIL LEAKAGE IN ISPECTION COVER. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 7.05 | 7.05 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.7
ER1T13 | 400/220kV ICT2 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 7.05 | 7.05 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T14 | 400/220kV ICT1 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T15 | 400/220kV ICT2 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T16 | 400/220kV ICT1 GAYA | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T17 | 400/220kV ICT2 GAYA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T18 | 400/132kV ICT1 BANKA | 200 | ER1 | -- | -- | -- | -- | 2016-12-01 | 10:09 | 2016-12-01 | 19:02 | 8.8833 | 8.8833 | 0 | 0 | 0 | OSPT | S/D TAKEN BY BANKA FOR AMP WORK. | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 8.8833 | 8.8833 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.8
ER1T19 | 400/132kV ICT 2 BANKA | 200 | ER1 | -- | -- | -- | -- | 2016-12-02 | 10:07 | 2016-12-02 | 18:18 | 8.1833 | 8.1833 | 0 | 0 | 0 | OSPT | S/D TAKEN BY BANKA FOR AMP WORK. | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 8.1833 | 8.1833 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.9
ER1T20 | 765/400kV ICT1 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T21 | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T22 | 765/400kV ICT3 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T23 | 220/132kV ICT1 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T24 | 220/132kV ICT2 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T25 | 220/132kV ICT3 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T26 | 220/132kV ICT1 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T27 | 220/132kV ICT2 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T28 | 765/400/220 kV ICT 1 SASARAM | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T29 | 765/400kV ICT1 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | 2016-12-24 | 9:24 | 2016-12-24 | 17:41 | 8.2833 | 0 | 8.2833 | 0 | 0 | OMSU | S/D TAKEN FOR RTV COATING OF TRENCH MAKE BUSHING BY MANUFACTURERE DUE TO DESIGN ISSUE. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 8.2833 | 0 | 8.2833 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T30 | 765/400kV ICT2 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T31 | 400/132kV ICT1 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 57.75 | 41.1833 | 16.5667 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T32 | 400/132kV ICT 2 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 57.75 | 41.1833 | 16.5667 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T33 | 400/220kV ICT 2 CHAIBASA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T34 | 400/220kV ICT 1 CHAIBASA | 315 | ER1 | -- | -- | -- | -- | 2016-12-09 | 9:44 | 2016-12-09 | 18:21 | 8.6167 | 8.6167 | 0 | 0 | 0 | OSPT | S/D TAKEN BY CHAIBASA FOR AMP WORK. | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.84
ER1T35 | 220/132kV ICT3 ARRAH | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T36 | 400/220kV ICT3 MUZ | 500 | ER1 | -- | -- | -- | -- | 2016-12-06 | 10:34 | 2016-12-06 | 18:31 | 7.95 | 0 | 0 | 0 | 7.95 | SCSD | S/D FOR CSD WORK | N/A | N/A | N/A
[8 empty] | 2016-12-24 | 13:31 | 2016-12-24 | 14:39 | 1.1333 | 0 | 0 | 1.1333 | 0 | SNCC | TRIPPED DUE TO MAL OPERATION OF PRV DUE TO DENSE FOG.
[12 empty] | 9.0833 | 0 | 0 | 1.1333 | 7.95 | [6 empty] | 100
ER1T36 | 400/220kV ICT2 KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1T37 | 400/220 kV ICT2 AT KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R1 | 50 MVAR B/R-1 AT BSF | 50 | ER1 | -- | -- | -- | -- | 2016-12-19 | 10:18 | 2016-12-19 | 17:02 | 6.7333 | 0 | 0 | 0 | 6.7333 | SCSD | S/D TAKEN FOR 400 KV BUS-I SPLITTING WORK AT BSF | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 6.7333 | 0 | 0 | 0 | 6.7333 |  |  | N/A | N/A | N/A |  | 100
ER1R2 | 50 MVAR B/R-1 AT JSR | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R3 | 50 MVAR BUS REACTOR-II, JAMSHEDPUR II | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R4 | 400kV BUS REACTOR MUZAFFARPUR | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R5 | 80 MVAR B/R AT PTN | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R6 | 400kV BUS REACTOR RANCHI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R7 | 80 MVAR B/R AT BSF | 80 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[19 empty] | N/A | N/A | N/A
[19 empty] | N/A | N/A | N/A
[19 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R8 | 125 MVAR B/R - I AT NPRN | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1R9 | 125 MVAR B/R - II AT NPRN | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R10 | 50 MVAR MTN RB-1 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R11 | 50 MVAR MTN RB-2 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R12 | 50 MVAR GAYA L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R13 | 50 MVAR SSRM-III L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R14 | 400kV BUS REACTOR-I, GAYA 125MVAR | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R15 | 400kV BUS REACTOR II,GAYA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R16 | 765kV BUS REACTOR II, GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R17 | 765kV BUS REACTOR1-GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R18 | 125 MVAR B/R - I AT PSL | 125 | ER1 | -- | -- | -- | -- | 2016-12-01 | 0:00 | 2016-12-02 | 23:52 | 47.8667 | 0 | 0 | 0 | 47.8667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-06 | 10:19 | 2016-12-14 | 3:58 | 185.65 | 0 | 0 | 0 | 185.65 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-14 | 6:54 | 2016-12-15 | 23:21 | 40.45 | 0 | 0 | 0 | 40.45 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-27 | 7:51 | 2017-01-01 | 0:00 | 112.15 | 0 | 0 | 0 | 112.15 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[12 empty] | 386.1167 | 0 | 0 | 0 | 386.1167 | [6 empty] | 100
ER1R19 | 125 MVAR B/R - II AT PSL | 125 | ER1 | -- | -- | -- | -- | 2016-12-03 | 17:34 | 2016-12-14 | 3:54 | 250.3333 | 0 | 0 | 0 | 250.3333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-27 | 7:53 | 2016-12-28 | 0:26 | 16.55 | 0 | 0 | 0 | 16.55 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[12 empty] | 266.8833 | 0 | 0 | 0 | 266.8833 | [6 empty] | 100
ER1R20 | 63 MVAR GKP - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R21 | 63 MVAR GKP - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R22 | 63 MVAR NPRN - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R23 | 63 MVAR NPRN - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R24 | 63 MVAR MUZ - I L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R25 | 63 MVAR MUZ- II L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R26 | 63 MVAR BSF- I L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R27 | 63 MVAR BSF- II L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R28 | 50 MVAR BSF- III L/R AT PSL | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R29 | 50 MVAR BALIA L/R AT PSL | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R30 | 63 MVAR ALLAHABAD-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R31 | 63 MVAR SARNATH-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R32 | 50 MVAR B/R - I AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R33 | 50 MVAR B/R - II AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R34 | 50 MVAR L/R - I AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R35 | 50 MVAR L/R - 2 AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R36 | 80 MVAR B/R - 1 AT BANKA | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R37 | 3*110 MVAR 1 PH B/R - I AT SASARAM | 330 | ER1 | -- | -- | -- | -- | 2016-12-02 | 17:47 | 2016-12-04 | 23:56 | 54.15 | 0 | 0 | 0 | 54.15 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-05 | 9:50 | 2016-12-05 | 23:54 | 14.0667 | 0 | 0 | 0 | 14.0667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-06 | 15:48 | 2016-12-06 | 20:37 | 4.8167 | 0 | 0 | 0 | 4.8167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-09 | 11:42 | 2016-12-10 | 0:15 | 12.55 | 0 | 0 | 0 | 12.55 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-10 | 9:25 | 2016-12-10 | 23:14 | 13.8167 | 0 | 0 | 0 | 13.8167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-14 | 9:41 | 2016-12-15 | 0:36 | 14.9167 | 0 | 0 | 0 | 14.9167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-15 | 7:38 | 2016-12-16 | 0:19 | 16.6833 | 0 | 0 | 0 | 16.6833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-16 | 5:12 | 2016-12-21 | 2:36 | 117.4 | 0 | 0 | 0 | 117.4 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-21 | 5:51 | 2016-12-22 | 1:08 | 19.2833 | 0 | 0 | 0 | 19.2833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-22 | 5:49 | 2016-12-22 | 23:05 | 17.2667 | 0 | 0 | 0 | 17.2667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-25 | 9:14 | 2016-12-25 | 16:12 | 6.9667 | 0 | 0 | 0 | 6.9667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-26 | 16:19 | 2016-12-26 | 23:34 | 7.25 | 0 | 0 | 0 | 7.25 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[12 empty] | 299.1667 | 0 | 0 | 0 | 299.1667 | [6 empty] | 100
ER1R38 | 3*110 MVAR 1 PH L/R - I AT SASARAM (AS B/R) | 330 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R39 | 125 MVAR BUS REACTOR-1 RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R40 | 125 MVAR BUS REACTOR-1 PATNA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R41 | 80 MVAR PURNEA-1 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R42 | 80 MVAR PURNEA-2 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R43 | 125 MVAR BUS REACTOR-2 PATNA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R44 | 125 MVAR BUS REACTOR-1 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R45 | 125 MVAR BUS REACTOR-2 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R46 | 3*80MVAR 1 PH L/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | 2016-12-30 | 10:02 | 2016-12-30 | 19:16 | 9.2333 | 9.2333 | 0 | 0 | 0 | OSPT | S/D TAKEN BY NRNC FOR AMP WORK. | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 9.2333 | 9.2333 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.7
ER1R47 | 3*80MVAR 1 PH B/R - II AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R48 | 80 MVAR B/R - 1 AT LAKHISARAI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R49 | 3*80MVAR 1 PH B/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R50 | 63MVAR KISHANGANJ LR-I AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R51 | 63MVAR KISHANGANJ LR-II AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R52 | 3*80 MVAR DHRAMJAYGARH LR-II AS BR AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R53 | 125 MVAR BR-II AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2016-12-01 | 0:00 | 2016-12-02 | 0:11 | 24.1833 | 0 | 0 | 0 | 24.1833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-05 | 17:55 | 2016-12-05 | 21:49 | 3.9 | 0 | 0 | 0 | 3.9 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-06 | 18:03 | 2016-12-06 | 21:57 | 3.9 | 0 | 0 | 0 | 3.9 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-07 | 18:48 | 2016-12-07 | 23:10 | 4.3667 | 0 | 0 | 0 | 4.3667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-08 | 17:13 | 2016-12-09 | 0:28 | 7.25 | 0 | 0 | 0 | 7.25 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-09 | 17:25 | 2016-12-10 | 0:04 | 6.65 | 0 | 0 | 0 | 6.65 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-10 | 18:13 | 2016-12-11 | 0:13 | 6 | 0 | 0 | 0 | 6 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-11 | 17:45 | 2016-12-12 | 0:57 | 7.2 | 0 | 0 | 0 | 7.2 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-13 | 17:36 | 2016-12-14 | 1:27 | 7.85 | 0 | 0 | 0 | 7.85 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-14 | 17:36 | 2016-12-14 | 22:54 | 5.3 | 0 | 0 | 0 | 5.3 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-15 | 17:51 | 2016-12-15 | 22:50 | 4.9833 | 0 | 0 | 0 | 4.9833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-16 | 12:24 | 2016-12-17 | 0:19 | 11.9167 | 0 | 0 | 0 | 11.9167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-17 | 18:34 | 2016-12-18 | 0:10 | 5.6 | 0 | 0 | 0 | 5.6 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-18 | 18:57 | 2016-12-20 | 0:40 | 29.7167 | 0 | 0 | 0 | 29.7167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-22 | 17:25 | 2016-12-22 | 23:04 | 5.65 | 0 | 0 | 0 | 5.65 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-24 | 18:12 | 2016-12-24 | 22:50 | 4.6333 | 0 | 0 | 0 | 4.6333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-25 | 17:33 | 2016-12-25 | 23:16 | 5.7167 | 0 | 0 | 0 | 5.7167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-27 | 17:46 | 2016-12-28 | 1:20 | 7.5667 | 0 | 0 | 0 | 7.5667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[12 empty] | 152.3833 | 0 | 0 | 0 | 152.3833 | [6 empty] | 100
ER1R54 | 125 MVAR BR-I AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2016-12-01 | 17:26 | 2016-12-02 | 0:14 | 6.8 | 0 | 0 | 0 | 6.8 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-05 | 17:55 | 2016-12-05 | 21:52 | 3.95 | 0 | 0 | 0 | 3.95 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-06 | 18:02 | 2016-12-06 | 21:51 | 3.8167 | 0 | 0 | 0 | 3.8167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-07 | 18:47 | 2016-12-07 | 23:22 | 4.5833 | 0 | 0 | 0 | 4.5833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-08 | 17:13 | 2016-12-09 | 0:33 | 7.3333 | 0 | 0 | 0 | 7.3333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-09 | 17:24 | 2016-12-10 | 0:09 | 6.75 | 0 | 0 | 0 | 6.75 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-10 | 18:12 | 2016-12-11 | 0:11 | 5.9833 | 0 | 0 | 0 | 5.9833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-11 | 17:47 | 2016-12-12 | 0:59 | 7.2 | 0 | 0 | 0 | 7.2 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-13 | 17:37 | 2016-12-14 | 3:54 | 10.2833 | 0 | 0 | 0 | 10.2833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-16 | 18:23 | 2016-12-17 | 0:13 | 5.8333 | 0 | 0 | 0 | 5.8333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2016-12-17 | 18:34 | 2016-12-18 | 0:14 | 5.6667 | 0 | 0 | 0 | 5.6667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-24 | 18:09 | 2016-12-24 | 23:08 | 4.9833 | 0 | 0 | 0 | 4.9833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2016-12-25 | 17:33 | 2016-12-25 | 23:28 | 5.9167 | 0 | 0 | 0 | 5.9167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[12 empty] | 79.1 | 0 | 0 | 0 | 79.1 | [6 empty] | 100
ER1R55 | 125 MVAR BR-III AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | 2016-12-19 | 10:13 | 2016-12-19 | 17:05 | 6.8667 | 0 | 0 | 0 | 6.8667 | SCSD | S/D TAKEN FOR 400 KV BUS-I SPLITTING WORK AT BSF | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 6.8667 | 0 | 0 | 0 | 6.8667 |  |  | N/A | N/A | N/A |  | 100
ER1R55 | 125 MVAR BR-I AT Kishanganj | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R57 | 125 MVAR BR-I AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R58 | 125 MVAR BR-II AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100

## SOP JAN 2017
Standard of Performance data for the month of Jan- 2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION - I
'ANNEXURE - A
Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | DETAILS OF OUTAGE |  | Total outage in days (1) | OUTAGE |  | RESTORATION |  |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Category | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[5 empty] | No. of Tower damaged | No.of insulators failed |  | DATE | TIME | DATE | TIME | TOTAL | ISTS Licensee | OTHERS | System constraint/ Natural calmity/ Militancy | Deemed Available
ER1L1 | 132kV ARA-ARA | 1.7 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A | ERPC
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L2 | 132kV Dehri-SSRM | 62 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L3 | 132kV SSRM- KARAMNASA | 29 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L4 | 132kV DMRN-ARA | 1.7 | ER1 | -- | -- | -- | -- | 2017-01-12 | 10:34 | 2017-01-12 | 17:22 | 6.8 | 0 | 0 | 0 | 6.8 | OSPD | S/D TAKEN BY BSPTCL FOR BSPTCL WORK | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 6.8 | 0 | 0 | 0 | 6.8 |  |  | N/A | N/A | N/A |  | 100
ER1L5 | 132kV PNR-DLK (LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L6 | 132kV PNR-PRN(LILO PART) | 0.5 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L7 | 220kV DALKHOLA-PURNEA I | 41 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 13.6 | [6 empty] | 100
ER1L8 | 220kV DALKHOLA-PURNEA II | 41 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L9 | 220 kV PRN-NPRN-I | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L10 | 220 kV PRN-NPRN-II | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L11 | 220kV SASARAM-NADOKHAR | 112 | ER1 | [8 empty] | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L11 | 220kV NADOKHAR -ARRAH I | 112 | ER1 |  |  |  |  | 2017-01-01 | 0:00 | 2017-01-13 | 10:43 | 298.7167 | 0 | 0 | 0 | 298.7167 | LVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-19 | 23:28 | 2017-01-24 | 15:39 | 112.1833 | 0 | 0 | 0 | 112.1833 | LVRD | S.OFF for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-28 | 0:30 | 2017-01-31 | 0:00 | 71.5 | 0 | 0 | 0 | 71.5 | LVRD | H/T for V/R AS PER ERLDC INSTRUCTION |  |  |  |  | 100
[12 empty] | 482.4 | 0 | 0 | 0 | 482.4
ER1L12 | 220kV SASARAM-ARRAH II | 112 | ER1 | [19 empty] | 100
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L13 | 220kV ARA-KHAGOL I | 48.44 | ER1 |  |  |  |  | 2017-01-01 | 0:00 | 2017-01-13 | 10:47 | 298.7833 | 0 | 0 | 0 | 298.7833 | LPRD | H/T FOR POWER REGULATION AS PER ERLDC INSTRUCTION. |  |  |  |  | 100
[8 empty] | 2017-01-13 | 17:28 | 2017-01-24 | 15:30 | 262.0333 | 0 | 0 | 0 | 262.0333 | LPRD | S/OFF FOR POWER REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-24 | 18:31 | 2017-01-31 | 0:00 | 149.4833 | 0 | 0 | 0 | 149.4833 | LPRD | H/T ON POWER REGULATION AS PER ERLDC INSTRUCTION |  |  |  |  | 100
[12 empty] | 710.3 | 0 | 0 | 0 | 710.3
ER1L14 | 220kV ARA-KHAGOL II | 48.44 | ER1 | -- | -- | -- | -- | 2017-01-01 | 0:00 | 2017-01-13 | 10:48 | 298.8 | 0 | 0 | 0 | 298.8 | LPRD | H/T FOR POWER REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[8 empty] | 2017-01-13 | 17:28 | 2017-01-24 | 15:30 | 262.0333 | 0 | 0 | 0 | 262.0333 | LPRD | S/OFF FOR POWER REGULATION A SPER ERLDC INSTRUCTION
[8 empty] | 2017-01-24 | 18:32 | 2017-01-31 | 0:00 | 149.4667 | 0 | 0 | 0 | 149.4667 | LPRD | H/T ON POWER REGULATION AS PER ERLDC INSTRUCTION
[12 empty] | 710.3 | 0 | 0 | 0 | 710.3 | [6 empty] | 100
ER1L15 | 220kV DEHRI-PUSAULI | 4.88 | ER1 | -- | -- | -- | -- | 2017-01-01 | 0:00 | 2017-01-13 | 19:47 | 307.7833 | 0 | 0 | 0 | 307.7833 | LPRD | OPENED FROM SSRM AS PER ERLDC INSTRUCTION FOR POWER REGULATION. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 307.7833 | 0 | 0 | 0 | 307.7833 |  |  | N/A | N/A | N/A |  | 100
ER1L16 | 220kV SASARAM-SAHUPURI | 4.88 | ER1 | -- | -- | -- | -- | 2017-01-03 | 12:12 | 2017-01-04 | 0:05 | 11.8833 | 0 | 0 | 0 | 11.8833 | OSPD | S/D TAKEN BY BSPTCL FOR SHIFTING OF CONDUCTORS FROM ERS TO NEWLY CONSTRUCTED TOWER LOC NO. 172 AND 174 AND RETROFITTING WORK OF TOP SECTION AT LOC NO. 171. | N/A | N/A | N/A
[12 empty] | 11.8833 | 0 | 0 | 0 | 11.8833
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L17 | 220kV RANCHI-CHANDIL I | 8.06 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L18 | 220kV RNC-CHANDIL-II (LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L19 | 220kV RNC-HATIA-I (LILO) | 8.06 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L20 | 220kV RNC-HATIA-II(LILO) | 6.92 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L21 | 220kV GAYA-DEHRI -I(LILO PART) | 11 | ER1 |  |  |  |  | 2017-01-13 | 12:49 | 2017-01-13 | 14:43 | 1.9 | 0 | 1.9 | 0 | 0 | OMSU | DUE TO PROBLEM IN DOWNSTRAM SYSTEM (BSPTCL) , THE HOT SPOT DEVELOPED IN Y PHASE BUS ISOLATOR OF 220 KV GAYA-BODHGAYA-II AT GAYA DUE TO THIS 220 KV BUS-I AT GAYA TRIPPED AND 220 KV GAYA-DEHRI-I TRIPPED ALSO.
[8 empty] | 2017-01-25 | 12:41 | 2017-01-25 | 22:38 | 9.95 | 0 | 0 | 0 | 9.95 | OSPD | S/D TAKEN BY BSPTCL
|  |  |  | -- | -- | -- | -- |  |  |  |  | 11.85 | 0 | 1.9 | 0 | 9.95 |  |  | N/A | N/A | N/A |  | 100
ER1L22 | 220kV GAYA-BODHGAYA(BSEB) I | 12.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L23 | 220kV GAYA-DEHRI-II (LILO PART) | 11 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L24 | 220kV GAYA-BODHGAYA(BSEB) II | 12.7 | ER1 | -- | -- | -- | -- | 2017-01-13 | 12:49 | 2017-01-13 | 14:41 | 1.8667 | 0 | 1.8667 | 0 | 0 | OMSU | DUE TO PROBLEM IN DOWNSTRAM SYSTEM (BSPTCL) , THE HOT SPOT DEVELOPED IN Y PHASE BUS ISOLATOR OF 220 KV GAYA-BODHGAYA-II AT GAYA DUE TO THIS 220 KV BUS-I AT GAYA TRIPPED AND 220 KV GAYA-BODHGAYA-II TRIPPED ALSO. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 1.8667 | 0 | 1.8667 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L25 | 400kV FARAKKA-KAHALGAON I | [10 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L26 | 400kV FARAKKA-KAHALGAON II
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L27 | 400kV KAHALGAON-FARAKKA III | 95.25 | ER1 | -- | -- | -- | -- | 2017-01-21 | 10:22 | 2017-01-21 | 10:42 | 0.33333 | 0 | 0.33333 | 0 | 0 | OMSU | TRIPPED DUE TO DT SIGNAL RECEIVED AT KAHALGAON, NTPC DUE TO PROBLEM AT FARAKKA, NTPC END. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0.33333 | 0 | 0.33333 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L28 | 400kV KAHALGAON-FARAKKA IV | 95.25 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L29 | 400kV KAHALGAON-LAKHISARAI I | 145 | ER1 | -- | -- | -- | -- | 2017-01-11 | 12:28 | 2017-01-11 | 13:52 | 1.4 | 0 | 1.4 | 0 | 0 | OMSU | TRIPPED DUE TO PROBLEM IN NTPC KHALGAON END. DT RECEIVED AT LAKHISSARAI END. | N/A | N/A | N/A
[12 empty] | 1.4 | 0 | 1.4 | 0 | 0
ER1L30 | 400kV BIHARSHARIFF-LAKHISARAI I | 89 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L31A | 400kV KAHALGAON-LAKHISARAI II | 145 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L31B | 400kV BIHARSHARIF-LAKHISARAI II | 89 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L32 | 400kV KAHALGAON-BANKA-I | 47.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L33 | 400KV BIHARSHARIF-BANKA I | 184.54 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L34 | 400kV KAHALGAON-BANKA-II | 47.7 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L35 | 400KV BIHARSHARIF-BANKA II | 184.54 | ER1 | -- | -- | -- | -- | 2017-01-19 | 12:44 | 2017-01-19 | 15:25 | 2.6833 | 0 | 2.6833 | 0 | 0 | OMSU | TRIPPED ON R-N FAULT DUE TO OPGW WORK IN THE CKT. F.D.= 4.7 KM FROM BANKA WITH F.C.= 11.43 KA | N/A | N/A | N/A
[8 empty] | 2017-01-29 | 14:21 | 2017-01-29 | 16:27 | 2.1 | 0 | 2.1 | 0 | 0 | OMSU | TRIPPED DUE TO LACK OF OPGW CLEARANCE DURING CONSTRUCTION WORK
|  |  |  | -- | -- | -- | -- |  |  |  |  | 4.7833 | 0 | 4.7833 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L36A | 400kV JAMSHEDPUR-CHAIBASA I | 46.14 | ER1 | -- | -- | -- | -- | 2017-01-18 | 9:17 | 2017-01-18 | 19:37 | 10.3333 | 10.3333 | 0 | 0 | 0 | OSPT | LA REPLACEMENT AT JAMSHEDPUR | N/A | N/A | N/A
[12 empty] | 10.3333 | 10.3333 | 0 | 0 | 0 | [6 empty] | 98.62
ER1L36B | 400kV JAMSHEDPUR-CHAIBASA II | 46.14 | ER1 | -- | -- | -- | -- | 2017-01-13 | 9:36 | 2017-01-13 | 17:06 | 7.5 | 7.5 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR ISOLATOR BLADE REPLACEMENT WORK AT JSR. | N/A | N/A | N/A
[12 empty] | 7.5 | 7.5 | 0 | 0 | 0 | [6 empty] | 98.99
ER1L36C | 400kV CHAIBASA-ROURKELA I | 131.48 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L37 | 400kV CHAIBASA-ROURKELA II | 131.48 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1L38 | 400kV MAITHON-KAHALGAON I | 172 | ER1 | -- | -- | -- | -- | 2017-01-23 | 9:36 | 2017-01-25 | 21:58 | 60.3667 | 0 | 0 | 0 | 60.3667 | LCSD | S/D TAKEN FOR CONSTN.OF NEW LINE FOR SHIFTING OF 400 KV KHLG -BANKA TL FROM STAGE -1 SIDE TO STAGE -2 SIDE UNDER BUS SPLIT SCHEME AT NTPC/KHLG S/Y ( INVOLVING POWERLINE CROSSING OF 400 KV KHLG - MTN TL ) | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 60.3667 | 0 | 0 | 0 | 60.3667 |  |  | N/A | N/A | N/A |  | 100
ER1L39 | 400kV MAITHON-KAHALGAON II | 172 | ER1 | -- | -- | -- | -- | 2017-01-23 | 9:39 | 2017-01-25 | 22:06 | 60.45 | 0 | 0 | 0 | 60.45 | LCSD | S/D TAKEN FOR CONSTN.OF NEW LINE FOR SHIFTING OF 400 KV KHLG -BANKA TL FROM STAGE -1 SIDE TO STAGE -2 SIDE UNDER BUS SPLIT SCHEME AT NTPC/KHLG S/Y ( INVOLVING POWERLINE CROSSING OF 400 KV KHLG - MTN TL ) | N/A | N/A | N/A
[12 empty] | 60.45 | 0 | 0 | 0 | 60.45 | [6 empty] | 100
ER1L40 | 400kV BIHARSHARIF-SASARAM-I | 210 | ER1 | -- | -- | -- | -- | 2017-01-03 | 12:25 | 2017-01-03 | 13:36 | 1.1833 | 1.1833 | 0 | 0 | 0 | OSPT | S/D TAKEN TO ATTEND SPARK IN LINE ISOLATOR AT PUSALI END | N/A | N/A | N/A
[8 empty] | 2017-01-07 | 8:50 | 2017-01-07 | 20:27 | 11.6167 | 0 | 0 | 0 | 11.6167 | LCSD | S/D TAKEN TO FACILITATE S/D OF 400KV BUS-1 <(>&<)> 3 UNDER BUS SPILITTING WORK AT BSF.
[8 empty] | 2017-01-30 | 15:40 | 2017-01-30 | 20:10 | 4.5 | 4.5 | 0 | 0 | 0 | OMST | S/D TAKEN FOR TAKING INTO SERVICE ITS L/R AT BSF WHICH WAS UNDER S/D FOR OVERHAULING WORK.
[12 empty] | 138.2 | 5.6833 | 0 | 0 | 132.5167 | [6 empty] | 99.23
ER1L41 | 400kV BIHARSHARIF-SASARAM-II | 210 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L42 | 400KV PATNA-BARH III | 68.66 | ER1 | -- | -- | -- | -- | 2017-01-25 | 8:18 | 2017-01-25 | 19:54 | 11.6 | 0 | 11.6 | 0 | 0 | OMSU | S/D FOR REPLACEMENT OF PORCELEIN INSULATOR WITH POLYMER INSULATOR | N/A | N/A | N/A
[8 empty] | 2017-01-28 | 7:56 | 2017-01-28 | 19:40 | 11.7333 | 0 | 11.7333 | 0 | 0 | OMSU | S/D FOR REPLACEMENT OF PORCELEIN INSULATOR WITH POLYMER
[8 empty] | 2017-01-24 | 8:55 | 2017-01-24 | 19:22 | 10.45 | 0 | 10.45 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF PORCELAIN INSULATORS WITH POLYMER INSULATOR
[8 empty] | 2017-01-26 | 7:46 | 2017-01-26 | 19:17 | 11.5167 | 0 | 11.5167 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF PORCELAIN INSULATORS WITH POLYMER ONES.
[8 empty] | 2017-01-30 | 5:24 | 2017-01-30 | 5:24 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSE SUCCESSFULLY OPERATED DUE TO B-N FAULT.F.D.=18.19 KM FROM PATNA,F.C.=9.16KAMP
[8 empty] | 2017-01-30 | 6:02 | 2017-01-30 | 6:02 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSE SUCCESSFULLY OPERATED DUE TO R-N FAULT.F.D.=21.0KM FROM PATNA,F.C.=8.61 KAMP
[8 empty] | 2017-01-29 | 8:15 | 2017-01-29 | 19:05 | 10.8333 | 0 | 10.8333 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF PORCELEIN INSULATOR WITH POLYMER
|  |  |  | -- | -- | -- | -- |  |  |  |  | 56.1333 | 0 | 56.1333 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L43 | 400KV PATNA-BARH IV | 68.66 | ER1 | -- | -- | -- | -- | 2017-01-02 | 9:58 | 2017-01-02 | 17:29 | 7.5167 | 0 | 7.5167 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF INSULATORS WITH POLYMER INSULATOR | N/A | N/A | N/A
[8 empty] | 2017-01-01 | 9:46 | 2017-01-01 | 16:31 | 6.75 | 0 | 6.75 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF INSULATORS WITH POLYMER INSULATOR
[8 empty] | 2017-01-30 | 5:54 | 2017-01-30 | 5:54 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSE SUCCESSFULLY OPERATED DUE TO R-N FAULT.F.D.=18.19 KM FROM PATNA,F.C.=9.16KAMP
[8 empty] | 2017-01-30 | 6:02 | 2017-01-30 | 6:02 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSE SUCCESSFULLY OPERATED DUE TO R-N FAULT.F.D.=52.9KM FROM PATNA,F.C.=4.32 KAMP
|  |  |  | INSULATOR DECAPPING |  |  | 0.00625 | 2017-01-30 | 6:19 | 2017-01-30 | 6:28 | 0.15 | 0 | 0 | 0.15 | 0 | LNCC | TRIPPED IN B-N FAULT DUE TO INSULATOR DECAPPING AT LOC NO.103 DUE TO DENSE FOG | 1 | N | -0.99375
[8 empty] | 2017-01-30 | 5:09 | 2017-01-30 | 5:09 | NA | NA | 0 | 0 | 0 | LART | A/R SUCCESSFULLY OPERATED DUE TO Y-N FAULT.F.D.=96.0 KM FROM PATNA = ,F.C.=3.736 KAMP
[8 empty] | 2017-01-30 | 11:21 | 2017-01-30 | 20:50 | 9.4833 | 0 | 9.4833 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF INSULATORS ( DECAPPED DURING DENSE FOG )WITH POLYMER ONES.
[8 empty] | 2017-01-31 | 10:17 | 2017-01-31 | 19:20 | 9.05 | 0 | 9.05 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF INSULATORS ( DECAPPED DURING DENSE FOG ) WITH POLYMER ONES
[12 empty] | 32.95 | 0 | 32.8 | 0.15 | 0 | [6 empty] | 100
ER1L44 | 400KV MUZAFFARPUR-BIHARSHARIF I | 133.3 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L45 | 400KV MUZAFFARPUR-BIHARSHARIF II | 133.3 | ER1 | -- | -- | -- | -- | 2017-01-16 | 8:04 | 2017-01-16 | 20:05 | 12.0167 | 0 | 0 | 12.0167 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS. | N/A | N/A | N/A
[12 empty] | 12.0167 | 0 | 0 | 12.0167 | 0 | [6 empty] | 100
ER1L46 | 400kV KAHALGAON-BARH I | 217.24 | ER1
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L47 | 400kV KAHALGAON-BARH II | 217.24 | ER1 | -- | -- | -- | -- | 2017-01-06 | 10:55 | 2017-01-06 | 20:48 | 9.8833 | 0 | 0 | 0 | 9.8833 | LCSD | S/D taken for OPGW modification work under construction. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 9.8833 | 0 | 0 | 0 | 9.8833 |  |  | N/A | N/A | N/A |  | 100
ER1L48 | 400kV PATNA-BARH I | 93 | ER1 | -- | -- | -- | -- | 2017-01-06 | 11:01 | 2017-01-06 | 20:51 | 9.8333 | 0 | 9.8333 | 0 | 0 | OMSU | S/D taken for OPGW rectification work. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 9.8333 | 0 | 9.8333 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L49 | 400kV PATNA-BARH II | 93 | ER1 | -- | -- | -- | -- | 2017-01-01 | 4:48 | 2017-01-01 | 4:48 | NA | NA | 0 | 0 | 0 | LART | A/R SUCCESSFUL IN B-N FAULT .F.D.=75.39 KIM FROM PATNA,F.C.=5.95 KAMP | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L50 | 400kV MAITHON-RANCHI I | 199.81 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 19.6667 | 0 | 19.7667 | [6 empty] | 100
ER1L51 | 400kV RAGHUNATHPUR-MAITHON | 44.02 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L52 | 400kV RANCHI-RAGHUNATHPUR I | 155.79 | ER1 | -- | -- | -- | -- | 2017-01-11 | 18:56 | 2017-01-11 | 19:14 | 0.3 | 0 | 0.3 | 0 | 0 | OMSU | TRIPPED ON RECEIPT OF DT SIGNAL AT RANCHI END DUE TO PROBLEM AT RAGHUNATHPUR, DVC. | N/A | N/A | N/A
[12 empty] | 0.3 | 0 | 0.3 | 0 | 0 | [6 empty] | 100
ER1L53 | 400kV MAITHON RB-RANCHI I | 187.64 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L54 | 400kV MAITHON RB-RANCHI II | 187.64 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L55 | 400kV RANCHI-ROURKELA I | 144.45 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L56 | 400kV RANCHI-ROURKELA II | 144.45 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L57 | 400kV BIHARSHARIF-KODERMA I | 110.69 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L58 | 400kV BIHARSHARIF-KODERMA II | 110.69 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L59 | 400kV BIHARSHARIF-VARANASI - I |  | ER1 | -- | -- | -- | -- | 2017-01-30 | 6:15 | 2017-01-30 | 6:15 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSE SUCCESSFULLY OPERATED DUE TO Y-N FAULT . F.D.=11.25 KM FROM BSF,F.C.=15.15 KAMP | N/A | N/A | N/A
[8 empty] | 2017-01-09 | 14:11 | 2017-01-09 | 14:56 | 0.75 | 0 | 0.75 | 0 | 0 | OMSU | TRIPPED DURING BUS BAR PROTN. SPLITTING WORK AT BSF (UNDER BUS SPLITTING CONSTN. WORK AT BSF )
[12 empty] | 0.75 | 0 | 0.75 | 0 | 0 | [6 empty] | 100
ER1L60A | 400kV BIHARSHARIF-VARANASI - II |  | ER1 | -- | -- | -- | -- | 2017-01-30 | 6:16 | 2017-01-30 | 6:16 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSE SUCCESSFULLY OPERATED DUE TO Y-N FAULT.F.D.=11.08 KM FROM BSF,F.C.=14.73 KAMP | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L61A | 765kV GAYA-BALLIA | 237.7 | ER1 | -- | -- | -- | -- | 2017-01-28 | 1:24 | 2017-01-28 | 1:24 | NA | NA | 0 | 0 | 0 | LART | AUTORECLOSED SUCCESSFULLY DUE TO R-N FAULT, F.D=251.9 KM FROM GAYA, F.C=3.11KA | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L62 | 400kV JAMSHEDPUR(DVC)-BARIPADA | 108.29 | ER1 | -- | -- | -- | -- | 2017-01-11 | 9:01 | 2017-01-11 | 18:34 | 9.55 | 0 | 0 | 9.55 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATOR DAMAGED BY MISCREANTS. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 9.55 | 0 | 0 | 9.55 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L63 | 400kV BARIPADA-JAMSHEDPUR II | 140.28 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L64 | 400kV JAMSHEDPUR-JAMSHEDPUR(DVC) | 32 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L65 | SSRM - NABINAGAR I | 81.65 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L66 | SSRM - NABINAGAR II | 81.65 | ER1 | -- | -- | -- | -- | 2017-01-06 | 20:44 | 2017-01-07 | 17:46 | 21.0333 | 0 | 0 | 0 | 21.0333 | OSFD | S/OFF FROM NABINAGAR END ON EMERGENCY BASIS TO ATTEND BUS BAR PROTECTION ISSUE AT NABINAGAR END. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 21.0333 | 0 | 0 | 0 | 21.0333 |  |  | N/A | N/A | N/A |  | 100
ER1L67A | 400KV GAYA - KODERMA - II | 118.2 | ER1 | -- | -- | -- | -- | 2017-01-14 | 9:29 | 2017-01-14 | 18:01 | 8.5333 | 0 | 0 | 8.5333 | 0 | LMAC | S/D TAKEN FOR DAMAGED INSULATOR REPLACEMENT WORK(DAMAGED BY MISCREANTS). | N/A | N/A | N/A
[12 empty] | 8.5333 | 0 | 0 | 8.5333 | 0 | [6 empty] | 100
ER1L67B | 400kV GAYA-MAITHON II | 277 | ER1 | -- | -- | -- | -- | 2017-01-13 | 9:13 | 2017-01-13 | 19:20 | 10.1167 | 0 | 0 | 10.1167 | 0 | LMAC | S/D TAKEN BY GAYA FOR INSULATOR REPLACEMENT WORK(DAMAGED BY MISCREANTS). | N/A | N/A | N/A
[12 empty] | 10.1167 | 0 | 0 | 10.1167 | 0 | [6 empty] | 100
ER1L68A | 400kV GAYA-KODERMA-I | 118.2 | ER1 | -- | -- | -- | -- | 2017-01-02 | 21:59 | 2017-01-02 | 21:59 | NA | NA | 0 | 0 | 0 | LART | A/R OPERATED SUCCESSFULLY FROM BOTH END DUE TO R-N FAULT,F.D.=68.1KM FROM GAYA,F.C.=4.18KA. | N/A | N/A | N/A
[8 empty] | 2017-01-13 | 9:50 | 2017-01-13 | 19:37 | 9.7833 | 0 | 0 | 9.7833 | 0 | LMAC | S/D TAKEN BY GAYA FOR INSULATOR REPLACEMENT WORK(DAMAGED BY MISCREANTS).
[12 empty] | 9.7833 | 0 | 0 | 9.7833 | 0 | [6 empty] | 100
ER1L68B | 400kV GAYA-MAITHON-I | 277 | ER1 |  |  |  |  | 2017-01-14 | 9:34 | 2017-01-14 | 18:28 | 8.9 | 0 | 0 | 8.9 | 0 | LMAC | S/D TAKEN FOR DAMAGED INSULATOR REPLACEMENT WORK(DAMAGED BY MISCREANTS).
[12 empty] | 8.9 | 0 | 0 | 8.9 | 0 | [6 empty] | 100
ER1L69 | 400kV RANCHI-RANCHI(NEW) II | 78.6 | ER1 | -- | -- | -- | -- | 2017-01-24 | 8:38 | 2017-01-24 | 19:53 | 11.25 | 0 | 11.25 | 0 | 0 | OMSU | THE LINE S/OFF TO AVAIL S/D OF 400 KV BUS-2 AT RANCHI. THE LINE IS ON SINGLE BAY DUE TO NON COMMISSIONING OF MAIN AND TIE BAY OF CPL. | N/A | N/A | N/A
[12 empty] | 11.25 | 0 | 11.25 | 0 | 0 | [6 empty] | 100
ER1L70 | 400kV RANCHI-RANCHI(NEW) I | 78.6 | ER1 | -- | -- | -- | -- | 2017-01-24 | 8:38 | 2017-01-24 | 19:55 | 11.2833 | 0 | 11.2833 | 0 | 0 | OMSU | THE LINE S/OFF TO AVAIL S/D OF 400 KV BUS-2 AT RANCHI. THE LINE IS ON SINGLE BAY DUE TO NON COMMISSIONING OF MAIN AND TIE BAY OF CPL. | N/A | N/A | N/A
[12 empty] | 11.2833 | 0 | 11.2833 | 0 | 0 | [6 empty] | 100
ER1L71 | 400kV RANCHI-RANCHI(NEW) III | 78.6 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L72 | 400kV RANCHI-RANCHI(NEW) IV | 78.6 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1L73 | 400 KV BOKARO-KODERMA-I | 100 | ER1 | -- | -- | -- | -- | 2017-01-09 | 11:42 | 2017-01-09 | 18:43 | 7.0167 | 0 | 7.0167 | 0 | 0 | OMSU | S/D TAKEN FOR REPLACEMENT OF INSULATORS WITH POLYMER INSULATOR | N/A | N/A | N/A
[12 empty] | 7.0167 | 0 | 7.0167 | 0 | 0 | [6 empty] | 100
ER1L75 | 400 KV BARH - GORAKHPUR - I | 349.16 | ER1 | -- | -- | -- | -- | 2017-01-04 | 8:55 | 2017-01-04 | 19:23 | 10.4667 | 10.4667 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR CONDUCTOR RECTIFICATION WORK | N/A | N/A | N/A
[8 empty] | 2017-01-19 | 15:10 | 2017-01-19 | 19:17 | 4.1167 | 0 | 4.1167 | 0 | 0 | OMSU | TRIPPED DUE TO OPERATION OF DIFFERENTIAL PROTN. OF ITS L/R AT NTPC/BARH END.
[8 empty] | 2017-01-30 | 8:25 | 2017-01-30 | 20:23 | 11.9667 | 0 | 0 | 11.9667 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS.
[8 empty] | 2017-01-31 | 8:14 | 2017-01-31 | 19:18 | 11.0667 | 0 | 0 | 11.0667 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 37.6167 | 10.4667 | 4.1167 | 23.0333 | 0 |  |  | N/A | N/A | N/A |  | 98.59
ER1L76 | 400 KV BARH - GORAKHPUR - II | 349.16 | ER1 | -- | -- | -- | -- | 2017-01-05 | 9:32 | 2017-01-05 | 19:55 | 10.3833 | 10.3833 | 0 | 0 | 0 | OSPT | S/D FOR CONDUCTOR RECTIFICATION WORK. | N/A | N/A | N/A
[8 empty] | 2017-01-27 | 12:33 | 2017-01-27 | 15:27 | 2.9 | 0 | 0 | 2.9 | 0 | LNCC | TRIPPED DUE TO R-Y FAULT, F.D=287 KM FROM BARH, Z-2, F.C=Ir=2.1KA, Iy=2.0KA. THE LINE TRIPPED DUE TO HEAVY FIRE IN BUSH BELOW THE CONDUCTOR.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 13.2833 | 10.3833 | 0 | 2.9 | 0 |  |  | N/A | N/A | N/A |  | 98.6
ER1L77 | 400 KVPATNA - KISHANGANJ -I |  | ER1 |  |  |  |  | 2017-01-01 | 0:00 | 2017-02-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER.
[12 empty] | 744 | 0 | 0 | 744 | 0 | [6 empty] | 100
ER1L78 | 400 KVPATNA - KISHANGANJ -II |  | ER1 |  |  |  |  | 2017-01-01 | 0:00 | 2017-02-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC | LINE UNDER B/D DUE TO COLLAPSE OF TOWER AT LOC. NO. 51 DUE TO UNPRECEDENTED FLASH FLOOD IN KANKAI RIVER.
[12 empty] | 744 | 0 | 0 | 744 | 0 | [6 empty] | 100
ER1L77 | 765 KV GAYA - VARANASI - II |  | ER1 | -- | -- | -- | -- | 2017-01-10 | 10:01 | 2017-01-10 | 18:30 | 8.4833 | 0 | 0 | 8.4833 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCRIENTS | N/A | N/A | N/A
[8 empty] | 2017-01-16 | 8:35 | 2017-01-16 | 9:34 | 0.98333 | 0 | 0 | 0.98333 | 0 | LNCC | TRIPPED ON R-Y FAULT CAUSED BY EXCESSIVE DENSE FOG IN THE FAULT AREA. F.D.= 267.9 KM FROM GAYA WITH F.C.= Ir=Iy=3.3 KA.
[12 empty] | 9.4667 | 0 | 0 | 9.4667 | 0 | [6 empty] | 100
ER1L77 | 400 KV GAYA - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | 2017-01-16 | 11:37 | 2017-01-16 | 18:39 | 7.0333 | 0 | 0 | 7.0333 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS. | N/A | N/A | N/A
[8 empty] | 2017-01-17 | 10:01 | 2017-01-17 | 17:54 | 7.8833 | 0 | 0 | 7.8833 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS.
|  |  |  | -- | -- | -- | -- |  |  |  |  | 14.9167 | 0 | 0 | 14.9167 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L77 | 400 KV GAYA - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1L77 | 400 KV NEW RANCHI - CHANDAWA - I |  | ER1 | -- | -- | -- | -- | 2017-01-18 | 10:07 | 2017-01-18 | 16:52 | 6.75 | 0 | 0 | 6.75 | 0 | LMAC | REPLACEMENT OF INSULATORS DAMAGED BY MISCRIENTS | N/A | N/A | N/A
[12 empty] | 6.75 | 0 | 0 | 6.75 | 0
ER1L77 | 400 KV NEW RANCHI - CHANDAWA - II |  | ER1 | -- | -- | -- | -- | 2017-01-19 | 10:04 | 2017-01-19 | 16:51 | 6.7833 | 0 | 0 | 6.7833 | 0 | LMAC | S/D TAKEN FOR REPLACEMENT OF INSULATORS DAMAGED BY MISCREANTS. | N/A | N/A | N/A
[12 empty] | 6.7833 | 0 | 0 | 6.7833 | 0 | [6 empty] | 100
ER1T1 | 400/220kV ICT1 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1T2 | 400/220kV ICT2 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2017-01-07 | 8:51 | 2017-01-07 | 20:14 | 11.3833 | 0 | 0 | 0 | 11.3833 | SCSD | S/D TAKEN TO FACILITATE S/D OF 400KV BUS-1 & 3 UNDER BUS SPILITTING WORK AT BSF. | N/A | N/A | N/A
[8 empty] | 2017-01-08 | 18:06 | 2017-01-08 | 18:47 | 0.68333 | 0 | 0.68333 | 0 | 0 | OMSU | TRIPPED DUE TO OPERATION OF 220KV OVERCURRENT PROTECTION CAUSED BY PROBLEM IN BSPTCL SYSTEM
[12 empty] | 12.0667 | 0 | 0.68333 | 0 | 11.3833 | [6 empty] | 100
ER1T3 | 400/220kV ICT3 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T4 | 400/220kV ICT1 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2017-01-30 | 13:54 | 2017-01-30 | 14:39 | 0.75 | 0 | 0.75 | 0 | 0 | SEFU | TRIPPED DUE TO PROBLEM AT JUSNL END. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0.75 | 0 | 0.75 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T5 | 400/220kV ICT2 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2017-01-04 | 9:55 | 2017-01-04 | 19:05 | 9.1667 | 0 | 0 | 0 | 9.1667 | SCSD | S/D TAKEN FOR BAY EXTENSION WORK JUSNL SIDE | N/A | N/A | N/A
[8 empty] | 2017-01-30 | 13:54 | 2017-01-30 | 14:47 | 0.88333 | 0 | 0.88333 | 0 | 0 | SEFU | TRIPPED DUE TO PRBLEM AT JUSNL END
|  |  |  | -- | -- | -- | -- |  |  |  |  | 10.05 | 0 | 0.88333 | 0 | 9.1667 |  |  | N/A | N/A | N/A |  | 100
ER1T6 | 400/220kV ICT1 NEW PURNEA | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T7 | 400/220kV ICT2 NEW PURNEA | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
ER1T8 | 400/220kV ICT1 SSRM | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T9 | 400/220kV ICT2 SSRM | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T10 | 400/220kV ICT1 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T11 | 400/220kV ICT2 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T12 | 400/220kV ICT1 PATNA | 315 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T13 | 400/220kV ICT2 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T14 | 400/220kV ICT1 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T15 | 400/220kV ICT2 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T16 | 400/220kV ICT1 GAYA | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T17 | 400/220kV ICT2 GAYA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T18 | 400/132kV ICT1 BANKA | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T19 | 400/132kV ICT 2 BANKA | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T20 | 765/400kV ICT1 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T21 | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T22 | 765/400kV ICT3 GAYA | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T23 | 220/132kV ICT1 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T24 | 220/132kV ICT2 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T25 | 220/132kV ICT3 PRN | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T26 | 220/132kV ICT1 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T27 | 220/132kV ICT2 ARRAH | 100 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T28 | 765/400/220 kV ICT 1 SASARAM | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T29 | 765/400kV ICT1 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T30 | 765/400kV ICT2 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | 2017-01-09 | 9:00 | 2017-01-09 | 18:42 | 9.7 | 9.7 | 0 | 0 | 0 | OSPT | S/D TAKEN BY NRNC FOR AMP WORK. | N/A | N/A | N/A
| SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 9.7 | 9.7 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.7
ER1T31 | 400/132kV ICT1 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T32 | 400/132kV ICT 2 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T33 | 400/220kV ICT 2 CHAIBASA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T34 | 400/220kV ICT 1 CHAIBASA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T35 | 220/132kV ICT3 ARRAH | 160 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T36 | 400/220kV ICT3 MUZ | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1T36 | 400/220kV ICT2 KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1T37 | 400/220 kV ICT2 AT KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R1 | 50 MVAR B/R-1 AT BSF | 50 | ER1 | -- | -- | -- | -- | 2017-01-07 | 8:52 | 2017-01-07 | 20:17 | 11.4167 | 0 | 0 | 0 | 11.4167 | SCSD | S/D TAKEN TO FACILITATE S/D OF 400KV BUS-1 & 3 UNDER BUS SPILITTING WORK AT BSF. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 11.4167 | 0 | 0 | 0 | 11.4167 |  |  | N/A | N/A | N/A |  | 100
ER1R2 | 50 MVAR B/R-1 AT JSR | 50 | ER1 | -- | -- | -- | -- | 2017-01-06 | 9:37 | 2017-01-06 | 19:36 | 9.9833 | 0 | 0 | 0 | 9.9833 | SCSD | S/D TAKEN FOR BAY CONSTRUCTION WORK AT JSR. | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 9.9833 | 0 | 0 | 0 | 9.9833 |  |  | N/A | N/A | N/A |  | 100
ER1R3 | 50 MVAR BUS REACTOR-II, JAMSHEDPUR II | 50 | ER1 | -- | -- | -- | -- | 2017-01-07 | 9:57 | 2017-01-07 | 17:45 | 7.8 | 0 | 0 | 0 | 7.8 | SCSD | S/D TAKEN FOR BAY CONST. WORK AT JSR. | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 7.8 | 0 | 0 | 0 | 7.8 |  |  | N/A | N/A | N/A |  | 100
ER1R4 | 400kV BUS REACTOR MUZAFFARPUR | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R5 | 80 MVAR B/R AT PTN | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R6 | 400kV BUS REACTOR RANCHI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R7 | 80 MVAR B/R AT BSF | 80 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R8 | 125 MVAR B/R - I AT NPRN | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100
ER1R9 | 125 MVAR B/R - II AT NPRN | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R10 | 50 MVAR MTN RB-1 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R11 | 50 MVAR MTN RB-2 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R12 | 50 MVAR GAYA L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R13 | 50 MVAR SSRM-III L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R14 | 400kV BUS REACTOR-I, GAYA 125MVAR | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R15 | 400kV BUS REACTOR II,GAYA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R16 | 765kV BUS REACTOR II, GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R17 | 765kV BUS REACTOR1-GAYA | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
| SUB TOTAL |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R18 | 125 MVAR B/R - I AT PSL | 125 | ER1 | -- | -- | -- | -- | 2017-01-08 | 7:02 | 2017-01-08 | 23:40 | 16.6333 | 0 | 0 | 0 | 16.6333 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRCUTION | N/A | N/A | N/A
[8 empty] | 2017-01-07 | 8:57 | 2017-01-07 | 21:26 | 12.4833 | 0 | 0 | 0 | 12.4833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[8 empty] | 2017-01-09 | 6:17 | 2017-01-09 | 10:17 | 4 | 0 | 0 | 0 | 4 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-17 | 5:18 | 2017-01-17 | 14:05 | 8.7833 | 0 | 0 | 0 | 8.7833 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[8 empty] | 2017-01-15 | 8:52 | 2017-01-16 | 0:22 | 15.5 | 0 | 0 | 0 | 15.5 | SVRD | S/OFF FOR VOLTAGE REGULATION REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-24 | 5:35 | 2017-01-24 | 22:37 | 17.0333 | 0 | 0 | 0 | 17.0333 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-25 | 6:16 | 2017-01-26 | 0:16 | 18 | 0 | 0 | 0 | 18 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[12 empty] | 92.4333 | 0 | 0 | 0 | 92.4333 | [6 empty] | 100
ER1R19 | 125 MVAR B/R - II AT PSL | 125 | ER1 | -- | -- | -- | -- | 2017-01-09 | 6:18 | 2017-01-09 | 23:14 | 16.9333 | 0 | 0 | 0 | 16.9333 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-06 | 7:36 | 2017-01-07 | 0:42 | 17.1 | 0 | 0 | 0 | 17.1 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-08 | 7:04 | 2017-01-08 | 23:40 | 16.6 | 0 | 0 | 0 | 16.6 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-07 | 8:59 | 2017-01-07 | 21:24 | 12.4167 | 0 | 0 | 0 | 12.4167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION.
[8 empty] | 2017-01-14 | 6:49 | 2017-01-14 | 23:09 | 16.3333 | 0 | 0 | 0 | 16.3333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION.
[8 empty] | 2017-01-15 | 8:54 | 2017-01-16 | 0:22 | 15.4667 | 0 | 0 | 0 | 15.4667 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-17 | 5:20 | 2017-01-18 | 0:22 | 19.0333 | 0 | 0 | 0 | 19.0333 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-24 | 5:38 | 2017-01-24 | 20:13 | 14.5833 | 0 | 0 | 0 | 14.5833 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-27 | 16:16 | 2017-01-27 | 22:03 | 5.7833 | 0 | 0 | 0 | 5.7833 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-25 | 6:15 | 2017-01-25 | 12:06 | 5.85 | 0 | 0 | 0 | 5.85 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-30 | 18:38 | 2017-01-31 | 13:15 | 18.6167 | 0 | 0 | 0 | 18.6167 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[12 empty] | 158.7167 | 0 | 0 | 0 | 158.7167 | [6 empty] | 100
ER1R20 | 63 MVAR GKP - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R21 | 63 MVAR GKP - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R22 | 63 MVAR NPRN - I L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R23 | 63 MVAR NPRN - II L/R AT MUZ | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R24 | 63 MVAR MUZ - I L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R25 | 63 MVAR MUZ- II L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R26 | 63 MVAR BSF- I L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R27 | 63 MVAR BSF- II L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R28 | 50 MVAR BSF- III L/R AT PSL | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R29 | 50 MVAR BALIA L/R AT PSL | 500 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R30 | 63 MVAR ALLAHABAD-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R31 | 63 MVAR SARNATH-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R32 | 50 MVAR B/R - I AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R33 | 50 MVAR B/R - II AT GAYA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R34 | 50 MVAR L/R - I AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R35 | 50 MVAR L/R - 2 AT BANKA | 50 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R36 | 80 MVAR B/R - 1 AT BANKA | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R37 | 3*110 MVAR 1 PH B/R - I AT SASARAM | 330 | ER1 | -- | -- | -- | -- | 2017-01-07 | 17:12 | 2017-01-07 | 23:10 | 5.9667 | 0 | 0 | 0 | 5.9667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[8 empty] | 2017-01-09 | 9:50 | 2017-01-11 | 0:14 | 38.4 | 0 | 0 | 0 | 38.4 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC /NLDC INSTRUCTION.
[8 empty] | 2017-01-03 | 10:01 | 2017-01-06 | 0:19 | 62.3 | 0 | 0 | 0 | 62.3 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRCUTION.
[8 empty] | 2017-01-11 | 18:32 | 2017-01-11 | 21:03 | 2.5167 | 0 | 0 | 0 | 2.5167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-17 | 8:07 | 2017-01-22 | 23:29 | 135.3667 | 0 | 0 | 0 | 135.3667 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC/NLDC INSTRUCTION
[8 empty] | 2017-01-12 | 9:58 | 2017-01-14 | 0:12 | 38.2333 | 0 | 0 | 0 | 38.2333 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-16 | 7:20 | 2017-01-17 | 0:50 | 17.5 | 0 | 0 | 0 | 17.5 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC /NLDC INSTRUCTION.
[8 empty] | 2017-01-23 | 6:31 | 2017-01-24 | 0:54 | 18.3833 | 0 | 0 | 0 | 18.3833 | SVRD | H/T for VOLTAGE REGULATION AS PER ERLDC/NLDC INSTRUCTION.
[8 empty] | 2017-01-25 | 8:20 | 2017-01-26 | 23:58 | 39.6333 | 0 | 0 | 0 | 39.6333 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-28 | 9:01 | 2017-01-30 | 2:08 | 41.1167 | 0 | 0 | 0 | 41.1167 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-30 | 5:20 | 2017-01-30 | 13:28 | 8.1333 | 0 | 0 | 0 | 8.1333 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-30 | 15:50 | 2017-01-30 | 23:08 | 7.3 | 0 | 0 | 0 | 7.3 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-24 | 18:01 | 2017-01-24 | 23:50 | 5.8167 | 0 | 0 | 0 | 5.8167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-27 | 17:25 | 2017-01-28 | 2:48 | 9.3833 | 0 | 0 | 0 | 9.3833 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-31 | 6:22 | 2017-02-01 | 0:00 | 17.6333 | 0 | 0 | 0 | 17.6333 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION
[12 empty] | 447.6833 | 0 | 0 | 0 | 447.6833 | [6 empty] | 100
ER1R38 | 3*110 MVAR 1 PH L/R - I AT SASARAM (AS B/R) | 330 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R39 | 125 MVAR BUS REACTOR-1 RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R40 | 125 MVAR BUS REACTOR-1 PATNA | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R41 | 80 MVAR PURNEA-1 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R42 | 80 MVAR PURNEA-2 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R43 | 125 MVAR BUS REACTOR-2 PATNA | 125 | ER1 | -- | -- | -- | -- | 2017-01-12 | 9:36 | 2017-01-12 | 18:28 | 8.8667 | 8.8667 | 0 | 0 | 0 | OSPT | S/OFF FOR AMP WORK | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 8.8667 | 8.8667 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 98.8
ER1R44 | 125 MVAR BUS REACTOR-1 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R45 | 125 MVAR BUS REACTOR-2 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R46 | 3*80MVAR 1 PH L/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R47 | 3*80MVAR 1 PH B/R - II AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.55
ER1R48 | 80 MVAR B/R - 1 AT LAKHISARAI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R49 | 3*80MVAR 1 PH B/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | 2017-01-17 | 10:24 | 2017-01-17 | 17:09 | 6.75 | 6.75 | 0 | 0 | 0 | OSPT | S/D TAKEN FOR AMP WORK | N/A | N/A | N/A
| Sub-Total= |  |  | -- | -- | -- | -- |  |  |  |  | 6.75 | 6.75 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 99.09
ER1R50 | 63MVAR KISHANGANJ LR-I AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R51 | 63MVAR KISHANGANJ LR-II AT PATNA | 63 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R52 | 3*80 MVAR DHRAMJAYGARH LR-II AS BR AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R53 | 125 MVAR BR-II AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2017-01-05 | 18:01 | 2017-01-05 | 21:28 | 3.45 | 0 | 0 | 0 | 3.45 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-04 | 19:02 | 2017-01-05 | 1:17 | 6.25 | 0 | 0 | 0 | 6.25 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-09 | 18:04 | 2017-01-09 | 21:46 | 3.7 | 0 | 0 | 0 | 3.7 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-02 | 17:48 | 2017-01-02 | 22:21 | 4.55 | 0 | 0 | 0 | 4.55 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-10 | 18:00 | 2017-01-10 | 23:19 | 5.3167 | 0 | 0 | 0 | 5.3167 | SVRD | H/T FOR VOLTAGE REGULATION AS PER ERLDC instruction.
[8 empty] | 2017-01-20 | 17:43 | 2017-01-21 | 23:06 | 29.3833 | 0 | 0 | 0 | 29.3833 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-18 | 18:36 | 2017-01-18 | 22:42 | 4.1 | 0 | 0 | 0 | 4.1 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION.
[8 empty] | 2017-01-13 | 18:15 | 2017-01-13 | 21:38 | 3.3833 | 0 | 0 | 0 | 3.3833 | SVRD | S/OFF FOR VOLTAGE REGULATION A SPER ERLDC INSTRUCTION
[8 empty] | 2017-01-12 | 17:46 | 2017-01-12 | 22:30 | 4.7333 | 0 | 0 | 0 | 4.7333 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-19 | 17:28 | 2017-01-19 | 23:16 | 5.8 | 0 | 0 | 0 | 5.8 | SVRD | S.OFF for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-17 | 18:22 | 2017-01-18 | 0:20 | 5.9667 | 0 | 0 | 0 | 5.9667 | SVRD | S.OFF FOR V/R AS PER ERLDC INSTRUCTION.
[8 empty] | 2017-01-23 | 18:31 | 2017-01-23 | 23:16 | 4.75 | 0 | 0 | 0 | 4.75 | SVRD | H/T for VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[8 empty] | 2017-01-26 | 19:34 | 2017-01-26 | 23:01 | 3.45 | 0 | 0 | 0 | 3.45 | SVRD | S.OFF for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-30 | 18:39 | 2017-01-31 | 0:24 | 5.75 | 0 | 0 | 0 | 5.75 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-25 | 17:45 | 2017-01-25 | 23:12 | 5.45 | 0 | 0 | 0 | 5.45 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-24 | 18:00 | 2017-01-24 | 22:36 | 4.6 | 0 | 0 | 0 | 4.6 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-31 | 17:55 | 2017-02-01 | 0:00 | 6.0833 | 0 | 0 | 0 | 6.0833 | SVRD | S.OFF for V/R AS PER ERLDC INSTRUCTION
[12 empty] | 106.7167 | 0 | 0 | 0 | 106.7167 | [6 empty] | 100
ER1R54 | 125 MVAR BR-I AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2017-01-05 | 18:08 | 2017-01-05 | 21:31 | 3.3833 | 0 | 0 | 0 | 3.3833 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-09 | 18:01 | 2017-01-09 | 21:58 | 3.95 | 0 | 0 | 0 | 3.95 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-03 | 17:44 | 2017-01-04 | 0:12 | 6.4667 | 0 | 0 | 0 | 6.4667 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-02 | 17:47 | 2017-01-02 | 22:34 | 4.7833 | 0 | 0 | 0 | 4.7833 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-19 | 18:02 | 2017-01-19 | 23:17 | 5.25 | 0 | 0 | 0 | 5.25 | SVRD | S.OFF for V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-17 | 18:22 | 2017-01-18 | 0:36 | 6.2333 | 0 | 0 | 0 | 6.2333 | SVRD | S.OFF FOR V/R AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-13 | 18:16 | 2017-01-13 | 21:45 | 3.4833 | 0 | 0 | 0 | 3.4833 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[8 empty] | 2017-01-18 | 18:35 | 2017-01-18 | 22:51 | 4.2667 | 0 | 0 | 0 | 4.2667 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION. | N/A | N/A | N/A
[8 empty] | 2017-01-24 | 18:14 | 2017-01-24 | 22:51 | 4.6167 | 0 | 0 | 0 | 4.6167 | SVRD | H/T ON V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-25 | 17:46 | 2017-01-25 | 23:24 | 5.6333 | 0 | 0 | 0 | 5.6333 | SVRD | H/T for V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-28 | 18:15 | 2017-01-28 | 23:05 | 4.8333 | 0 | 0 | 0 | 4.8333 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-30 | 18:38 | 2017-01-31 | 0:27 | 5.8167 | 0 | 0 | 0 | 5.8167 | SVRD | S/OFF FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | N/A | N/A | N/A
[8 empty] | 2017-01-26 | 19:32 | 2017-01-26 | 23:06 | 3.5667 | 0 | 0 | 0 | 3.5667 | SVRD | S.OFF for V/R AS PER ERLDC INSTRUCTION | N/A | N/A | N/A |  | 100
[12 empty] | 62.2833 | 0 | 0 | 0 | 62.2833
ER1R55 | 125 MVAR BR-III AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | 2017-01-07 | 8:51 | 2017-01-07 | 20:10 | 11.3167 | 0 | 0 | 0 | 11.3167 | SCSD | S/D TAKEN TO FACILITATE S/D OF 400KV BUS-1 & 3 UNDER BUS SPILITTING WORK AT BSF. | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 11.3167 | 0 | 0 | 0 | 11.3167 |  |  | N/A | N/A | N/A |  | 100
ER1R55 | 125 MVAR BR-I AT Kishanganj | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | 0
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R57 | 125 MVAR BR-I AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100
ER1R58 | 125 MVAR BR-II AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [11 empty] | N/A | N/A | N/A
|  |  |  | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | N/A | N/A | N/A |  | 100