## SOP APR 2019
Standard of Performance data for the month of April-2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION-I
'ANNEXURE - A
Sr.No. | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | DETAILS OF OUTAGE |  | Total outage in days (1) | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  |  | Category | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | No. of Tower damaged | No.of insulators failed |  | DATE | TIME | DATE | TIME | TOTAL | ISTS Licensee | OTHERS | System constraint/ Natural calmity/ Militancy | Deemed Available
1 | ER1L1 | 132kV ARA-ARA | 1.7 | ER1 | -- | -- | -- | -- | 2019-04-06 | 23:20 | 2019-04-07 | 0:11 | 0.85 | 0 | 0.85 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO Y-B FAULT IN ZONE-3 (BSPTCL JURISDICTION).FD-29.88KM FROM ARA(PG) AND FC-IY-2.226KA AND IB-2.141KA | ERPC | 100
[9 empty] | 2019-04-09 | 13:59 | 2019-04-09 | 14:57 | 0.97 | 0 | 0.97 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON Y-N FAULT,F.D.=1.89 KM FROM ARA (BSPTCL JURIDISCTION) = ,F.C.=4.5 KAMP.
| TOTAL | [11 empty] | 1.82 | 0 | 1.82 | 0 | 0
2 | ER1L2 | 132kV DEHRI - KUDRA | 40 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
3 | ER1L3 | 132kV KUDRA - SASARAM | 17 | ER1 | -- | -- | -- | -- | 2019-04-03 | 13:48 | 2019-04-03 | 14:29 | 0.68 | 0 | 0.68 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON B-N FAULT.F.D.=6.94 KM FROM PUSAULI (BSPTCL JURIDISCTION) = ,F.C.=7.67 KAMP | ERPC | 100
[9 empty] | 2019-04-05 | 8:09 | 2019-04-05 | 8:53 | 0.73 | 0 | 0.73 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON Y-N FAULT.F.D.=49.14 KM FROM PUSAULI (BSPTCL JURIDISCTION) = ,F.C.=2.50 KAMP
| TOTAL | [11 empty] | 1.41 | 0 | 1.41 | 0 | 0
4 | ER1L4 | 132kV Dehri-SASARAM | 62 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
5 | ER1L5 | 132kV SASARAM- KARAMNASA | 29 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
6 | ER1L6 | 132kV SASARAM-MOHANIA | 13 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
7 | ER1L7 | 132kV MOHANIA - KARMASA | 11 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
8 | ER1L8 | 132kV DUMRAON-ARA | 1.7 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
9 | ER1L9 | 132kV PURNEA-DALKHOLA (LILO PART) | 0.5 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
10 | ER1L10 | 132kV PNR-PRN(LILO PART) | 0.5 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
11 | ER1L11 | 220kV DALKHOLA-PURNEA I | 41 | ER1 | -- | -- | -- | -- | 2019-04-06 | 15:20 | 2019-04-06 | 15:20 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTORECLOSED DUE TO R-N FAULT, F.D= 2.835 KM FROM PURNEA, F.C=13.37 KA. | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
12 | ER1L12 | 220kV DALKHOLA-PURNEA II | 41 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
13 | ER1L13 | 220 kV PURNEA - NEW PURNEA-I | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
14 | ER1L14 | 220 kV PURNEA - NEW PURNEA-II | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
15 | ER1L15 | 220kV SASARAM-NADOKHAR | 5 | ER1 |  |  |  |  | 2019-04-17 | 8:01 | 2019-04-17 | 9:10 | 1.15 | 0 | 0 | 0 | 1.15 | LVRD |  |  |  |  | HAND TRIPPED ON VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
| TOTAL | [11 empty] | 1.15 | 0 | 0 | 0 | 1.15
16 | ER1L16 | 220kV NADOKHAR -ARRAH I | 107 | ER1 |  |  |  |  | 2019-04-17 | 8:05 | 2019-04-17 | 8:25 | 0.33 | 0 | 0 | 0.33 | 0 | GOVC |  |  |  |  | TRIPPED ON O/V ONLY FROM NADOKHAR END | ERPC | 100
[9 empty] | 2019-04-17 | 8:28 | 2019-04-17 | 8:33 | 0.08 | 0 | 0 | 0.08 | 0 | GOVC |  |  |  |  | TRIPPED ON O/V ONLY FROM NADOKHAR END
[9 empty] | 2019-04-17 | 8:33 | 2019-04-18 | 7:33 | 23 | 0 | 0 | 0 | 23 | LVRD |  |  |  |  | KEPT OPEN FOR V/R AS PER ERLDC INSTRUCTION
| TOTAL | [11 empty] | 23.41 | 0 | 0 | 0.41 | 23
17 | ER1L17 | 220kV SASARAM-ARRAH I | 112 | ER1 |  |  |  |  | 2019-04-05 | 10:42 | 2019-04-05 | 18:04 | 7.37 | 7.37 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR RELAY RETROFITTING AND ISOLATOR ALLIGNMENT AT PUSAULI. | ERPC | 98.97
[9 empty] | 2019-04-07 | 1:24 | 2019-04-07 | 5:43 | 4.32 | 0 | 0 | 0 | 4.32 | LVRD |  |  |  |  | HAND TRIPPED ON VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-09 | 14:35 | 2019-04-09 | 18:23 | 3.8 | 0 | 0 | 0 | 3.8 | LVRD |  |  |  |  | HAND TRIPPED ON VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-28 | 11:44 | 2019-04-28 | 18:12 | 6.47 | 0 | 0 | 0 | 6.47 | LVRD |  |  |  |  | HAND TRIPPED ON VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 21.96 | 7.37 | 0 | 0 | 14.59
18 | ER1L18 | 220kV ARA-KHAGOL I | 48.44 | ER1 |  |  |  |  | 2019-04-01 | 0:00 | 2019-04-01 | 10:13 | 10.2167 | 0 | 0 | 0 | 10.2167 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-01 | 10:32 | 2019-04-02 | 9:31 | 22.98 | 0 | 0 | 0 | 22.98 | LPRD |  |  |  |  | HAND TRIPPED ON POWER REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2019-04-02 | 17:30 | 2019-04-27 | 15:49 | 598.32 | 0 | 0 | 0 | 598.32 | LPRD |  |  |  |  | HAND TRIPPED ON POWER REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2019-04-27 | 18:54 | 2019-05-01 | 0:00 | 77.1 | 0 | 0 | 0 | 77.1 | LPRD |  |  |  |  | HAND TRIPPED ON POWER REGULATION AS PER ERLDC INSTRUCTION
| TOTAL | [11 empty] | 708.6167 | 0 | 0 | 0 | 708.6167
19 | ER1L19 | 220kV ARA-KHAGOL II | 48.44 | ER1 | -- | -- | -- | -- | 2019-04-01 | 0:00 | 2019-04-01 | 10:13 | 10.2167 | 0 | 0 | 0 | 10.2167 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-01 | 10:32 | 2019-04-02 | 9:31 | 22.98 | 0 | 0 | 0 | 22.98 | LPRD |  |  |  |  | HAND TRIPPED ON POWER REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2019-04-02 | 17:30 | 2019-04-27 | 15:50 | 598.33 | 0 | 0 | 0 | 598.33 | LPRD |  |  |  |  | HAND TRIPPED ON POWER REGULATION AS PER ERLDC INSTRUCTION
[9 empty] | 2019-04-27 | 18:54 | 2019-05-01 | 0:00 | 77.1 | 0 | 0 | 0 | 77.1 | LPRD |  |  |  |  | HAND TRIPPED ON POWER REGULATION AS PER ERLDC INSTRUCTION
| TOTAL | [11 empty] | 708.6267 | 0 | 0 | 0 | 708.6267
20 | ER1L20 | 220kV DEHRI-SASARAM |  | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
21 | ER1L21 | 220kV SASARAM-SAHUPURI | 4.88 | ER1 | -- | -- | -- | -- | 2019-04-11 | 10:07 | 2019-04-11 | 19:45 | 9.6333 | 0 | 0 | 0 | 9.6333 | OSPD |  |  |  |  | S/D TAKEN FOR POWER LINE CROSSING OF 220KV SAHUPURI-RAJA KA TALAB( UPPTCL LINE) BY UPPTCL. | ERPC | 100
[9 empty] | 2019-04-12 | 11:57 | 2019-04-12 | 13:33 | 1.6 | 0 | 1.6 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT. FD-52KM FROM SASARAM( UPPTCL JURIDICTION) AND FC-2.974KA.
[9 empty] | 2019-04-25 | 12:03 | 2019-04-25 | 13:14 | 1.1833 | 0 | 1.1833 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON B-N FAULT.F.D.=8.9 KM FROM DALTONGANJ(BSPTCL JURIDISCTION) = ,F.C.=7.9 KAMP.
[9 empty] | 2019-04-25 | 14:02 | 2019-04-25 | 15:42 | 1.6667 | 0 | 1.6667 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON B-N FAULT.F.D.=7.98 KM FROM PUSAULI(BSPTCL JURIDISCTION) = ,F.C.=9.01 KAMP.
| TOTAL | [11 empty] | 14.0833 | 0 | 4.45 | 0 | 9.6333
22 | ER1L22 | 220kV RANCHI-CHANDIL I | 8.06 | ER1 | -- | -- | -- | -- | 2019-04-13 | 16:06 | 2019-04-13 | 16:41 | 0.58 | 0 | 0.58 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT.F.D.=66.6 KM FROM RANCHI (JUSNL JURIDISCTION),F = ,C,=2.41 KAMP. | ERPC | 100
[9 empty] | 2019-04-15 | 10:54 | 2019-04-15 | 11:27 | 0.55 | 0 | 0.55 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO Y-B FAULT.F.D.=44.3 KM FROM RANCHI(JUSNL JURIDISCTION) = ,F.C.=IY=4.24 KAMP,IB=4.07 KAMP.
[9 empty] | 2019-04-16 | 14:49 | 2019-04-16 | 16:20 | 1.52 | 0 | 1.52 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN BY CHANDIL, FOR CUTTING AND TRIMMING OF TREES UNDER THIS SITE.
[9 empty] | 2019-04-23 | 15:08 | 2019-04-23 | 15:29 | 0.35 | 0 | 0.35 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT, F.C=2.24 KA, F.D= 66.3KM (UNDER JUSNL JURISDICTION).
[9 empty] | 2019-04-29 | 11:26 | 2019-04-29 | 12:46 | 1.33 | 0 | 0 | 0 | 1.33 | OSPD |  |  |  |  | S/D TAKEN BY JUSNL FOR ATTENDING HOT SPOT IN Y PHASE CT AT JUSNL END.
[9 empty] | 2019-04-30 | 16:24 | 2019-04-30 | 16:45 | 0.35 | 0 | 0.35 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON B-N FAULT .F.D.=67.1 KM FROM RANCHI(JUSNL JURIDISCTION) = ,F.C.=2.39 KAMP
| TOTAL | [11 empty] | 4.68 | 0 | 3.35 | 0 | 1.33
23 | ER1L23 | 220kV RANCHI-CHANDIL-II (LILO) | 6.92 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
24 | ER1L24 | 220kV RANCHI-HATIA-I (LILO) | 8.06 | ER1 | -- | -- | -- | -- | 2019-04-17 | 9:21 | 2019-04-17 | 11:37 | 2.27 | 0 | 0 | 0 | 2.27 | OSPD |  |  |  |  | S/D TAKEN BY JUSNL FOR POWER LINE CROSSING WORK OF 220KV HATIA-NAMKUM( JUSNL LINE). | ERPC | 100
| TOTAL | [11 empty] | 2.27 | 0 | 0 | 0 | 2.27
25 | ER1L25 | 220kV RANCHI-HATIA-II(LILO) | 6.92 | ER1 | -- | -- | -- | -- | 2019-04-17 | 9:21 | 2019-04-17 | 11:38 | 2.28 | 0 | 0 | 0 | 2.28 | OSPD |  |  |  |  | S/D TAKEN BY JUSNL FOR POWER LINE CROSSING WORK OF 220KV HATIA-NAMKUM( JUSNL LINE). | ERPC | 100
| TOTAL | [11 empty] | 2.28 | 0 | 0 | 0 | 2.28
26 | ER1L26 | 220kV GAYA-DEHRI -I(LILO PART) | 11 | ER1 |  |  |  |  | 2019-04-02 | 12:08 | 2019-04-02 | 15:03 | 2.92 | 0 | 0 | 0 | 2.92 | OSPD |  |  |  |  | S/D TAKEN FOR JUMPER TIGHTENING WORK BY BSPTCL. | ERPC | 100
[9 empty] | 2019-04-09 | 15:09 | 2019-04-09 | 18:00 | 2.85 | 0 | 2.85 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM DEHRI END DUE TO B-N FAULT.F.D.=16.9 KM ( BSPTCL JURISDICTION)FROM GAYA,F.C.=4.987 KAMP
[9 empty] | 2019-04-28 | 15:12 | 2019-04-28 | 17:26 | 2.23 | 0 | 0 | 0 | 2.23 | LVRD |  |  |  |  | HAND TRIPPED ON VOLTAGE REGULATION AS PER ERLDC INSTRUCTION
[13 empty] | 8 | 0 | 2.85 | 0 | 5.15
27 | ER1L27 | 220kV GAYA-BODHGAYA(BSEB) I | 12.7 | ER1 | -- | -- | -- | -- | 2019-04-09 | 15:23 | 2019-04-09 | 18:55 | 3.53 | 0 | 0 | 0 | 3.53 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 99.86
[9 empty] | 2019-04-29 | 11:48 | 2019-04-29 | 12:48 | 1 | 1 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND SF6 LOSS IN ITS CT AT GAYA END.
[9 empty] | 2019-04-30 | 12:35 | 2019-04-30 | 12:51 | 0.27 | 0 | 0.27 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM BODH GAYA END DUE TO UNSUCCESSFUL A/R AT BODHGAYA. A/R SUCCESSFUL FROM GAYA END. F.D.=17.0 KM FROM GAYA (BSPTCL JURISDICTION) FAULT CURRENT 9.23 KA.
| TOTAL | [11 empty] | 4.8 | 1 | 0.27 | 0 | 3.53
28 | ER1L28 | 220kV GAYA-DEHRI-II (LILO PART) | 11 | ER1 | -- | -- | -- | -- | 2019-04-02 | 15:09 | 2019-04-02 | 17:08 | 1.98 | 0 | 0 | 0 | 1.98 | OSPD |  |  |  |  | S/D TAKEN FOR JUMPER TIGHTENING WORK BY BSPTCL. | ERPC | 100
| TOTAL | [11 empty] | 1.98 | 0 | 0 | 0 | 1.98
29 | ER1L29 | 220kV GAYA-BODHGAYA(BSEB) II | 12.7 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
30 | ER1L30 | 400kV FARAKKA-KAHALGAON I | 95 | ER-I |  |  |  |  | 2019-04-01 | 0:00 | 2019-05-01 | 0:00 | 720 | 0 | 0 | 0 | 720 | LCSD |  |  |  |  | S.OFF FOR TAKING UP BAY UPGRADATION WORK AT FARAKKA END BY ER-2. | ERPC | 100
| TOTAL | [11 empty] | 720 | 0 | 0 | 0 | 720
31 | ER1L31 | 400kV FARAKKA-KAHALGAON II | 95 | ER-I |  |  |  |  | 2019-04-12 | 11:51 | 2019-04-12 | 15:54 | 4.05 | 0 | 4.05 | 0 | 0 | OMSU |  |  |  |  | FOR RECTIFICATION OF BENT TOWER MEMBERS AT LOC NO 21 AND 22 BUT PERMIT WAS NOT ISSUED BY NTPC SO LINE CHARGED. | ERPC | 100
[9 empty] | 2019-04-12 | 16:55 | 2019-04-14 | 18:42 | 49.78 | 0 | 49.78 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR RECTIFICATION OF BENT TOWER MEMBERS AT LOC NO 21 AND 22
| TOTAL | [11 empty] | 53.83 | 0 | 53.83 | 0 | 0
32 | ER1L32 | 400kV KAHALGAON-FARAKKA III | 95.25 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
33 | ER1L33 | 400kV KAHALGAON-FARAKKA IV | 95.25 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
34 | ER1L34 | 400kV KAHALGAON-LAKHISARAI I | 145 | ER1 | -- | -- | -- | -- | 2019-04-30 | 19:47 | 2019-04-30 | 20:50 | 1.05 | 0 | 1.05 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO FACILIATATE INSERTION OF 50 MVAR L/R-II AT LAKHISARAI END. | ERPC | 100
[9 empty] | 2019-04-30 | 9:54 | 2019-04-30 | 10:34 | 0.67 | 0 | 0.67 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO FACILIATATE THE S/D OF 50 MVAR L/R-II AT LAKHISARAI END FOR AMP WORK.
| TOTAL | [11 empty] | 1.72 | 0 | 1.72 | 0 | 0
35 | ER1L35 | 400kV BIHARSHARIFF-LAKHISARAI I | 89 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
36 | ER1L36 | 400kV KAHALGAON-LAKHISARAI II | 145 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
37 | ER1L37 | 400kV BIHARSHARIF-LAKHISARAI II | 89 | ER1 | -- | -- | -- | -- | 2019-04-05 | 16:47 | 2019-04-05 | 18:58 | 2.18 | 0 | 2.18 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR SAFE MOVEMENT OF HYDRA FOR ERECTION OF INTERRUPTER OF Y PH MAIN BAY OF LAKHISARAI-II AT BSF JUST BELOW THE JACK BUS. | ERPC | 100
[9 empty] | 2019-04-04 | 11:37 | 2019-04-04 | 12:27 | 0.83 | 0 | 0.83 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR SAFE MOVEMENT OF HYDRA FOR ERECTION OF INTERRUPTER OF Y PH MAIN BAY OF LAKHISARAI-II AT BSF JUST BELOW THE JACK BUS.
| TOTAL | [11 empty] | 3.01 | 0 | 3.01 | 0 | 0
38 | ER1L38 | 400kV KAHALGAON-BANKA-I | 53.745 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
39 | ER1L39 | 400KV BIHARSHARIF-BANKA I | 184.54 | ER1 | -- | -- | -- | -- | 2019-04-09 | 14:55 | 2019-04-09 | 14:55 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO R-N FAULT CAUSED BY SEVERE LIGHTENING AND THUNDERSTROM. F.D.=25.4 KM FROM BSF,F.C.=8.9 KA. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
40 | ER1L40 | 400kV KAHALGAON-BANKA-II | 53.745 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
41 | ER1L41 | 400KV BIHARSHARIF-BANKA II | 184.54 | ER1 | -- | -- | -- | -- | 2019-04-23 | 9:12 | 2019-04-23 | 18:10 | 8.97 | 0 | 0 | 8.97 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR REPLACEMENT OF FLASHED INSULATOR DUE TO THUNDERSTORM AND LIGHTENING AROUND THE FAULT AREA. | ERPC | 100
[9 empty] | 2019-04-09 | 14:55 | 2019-04-09 | 15:33 | 0.63 | 0 | 0 | 0.63 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT CAUSED BY SEVERE LIGHTENING AND THUNDERSTROM F.D.=26.6 KM FROM BSF,F.C.=8.8 KA.
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 9.6 | 0 | 0 | 9.6 | 0
42 | ER1L42 | 400kV JAMSHEDPUR-CHAIBASA I | 46.14 | ER1 | -- | -- | -- | -- | 2019-04-06 | 12:33 | 2019-04-06 | 14:29 | 1.93 | 0 | 0 | 1.93 | 0 | LNCC |  |  |  |  | TRIPPED ON R-N FAULT. F.D.= 10.65 KM FROM JSR WITH F.C.= 19.252 KA.CAUSED DUE TO SEVERE CYCLONE,HEAVY RAIN AND LIGHTENING IN AND AROUND THE FAULT AREA . | ERPC | 97.59
[9 empty] | 2019-04-30 | 15:15 | 2019-04-30 | 19:17 | 4.03 | 4.03 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND HOT SPOT IN ITS LINE ISOLATOR OF R PHASE AT JAMSHEDPUR END.
[9 empty] | 2019-04-16 | 12:30 | 2019-04-16 | 19:32 | 7.03 | 7.03 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR Y-PH CVT REPLACEMENT AT JAMSHEDPUR.
[9 empty] | 2019-04-15 | 18:41 | 2019-04-16 | 0:54 | 6.22 | 6.22 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND PROBLEM IN Y-PH CVT AT JAMSHEDPUR.
| TOTAL | [11 empty] | 19.21 | 17.28 | 0 | 1.93 | 0
43 | ER1L43 | 400kV JAMSHEDPUR-CHAIBASA II | 46.14 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
44 | ER1L44 | 400kV CHAIBASA-ROURKELA I | 131.48 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
45 | ER1L45 | 400kV CHAIBASA-ROURKELA II | 131.48 | ER1 | -- | -- | -- | -- | 2019-04-13 | 9:28 | 2019-04-13 | 19:38 | 10.17 | 10.17 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR RETROFITTING OF OLD RELAYS WITH NUMERICAL BACKUP IMPEDANCE RELAYS IN THE NON-SWITCHABLE LINE REACTOR OF TH | ERPC | 98.58
[9 empty] | 2019-04-21 | 14:26 | 2019-04-21 | 14:26 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTORECLOSED SUCCESSFULLY ON R-N FAULT.F.D.= 89.44 KM FROM CHAIBASA WITH F.C.= 2.60 KA
[9 empty] | 2019-04-21 | 14:27 | 2019-04-21 | 14:27 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTORECLOSED SUCCESSFULLY ON R-N FAULT. F.D.= 89.94 KM FROM CHAIBASA WITH F.C.= 3.55 KA
| TOTAL | [11 empty] | 10.17 | 10.17 | 0 | 0 | 0
46 | ER1L46 | 400kV MAITHON-KAHALGAON I | 172 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
47 | ER1L47 | 400kV MAITHON-KAHALGAON II | 172 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
48 | ER1L48 | 400kV BIHARSHARIF-SASARAM-I | 210 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
49 | ER1L49 | 400kV SASARAM - VARANASI | 143.73 | ER1 | -- | -- | -- | -- | 2019-04-22 | 11:57 | 2019-04-22 | 13:02 | 1.08 | 0 | 0 | 1.08 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT.F.D.=143 KM FROM SASARAM (NR-III JURIDISCTION) = ,F.C.=2.29 KAMP. TRIPPED DUE TO SEVERE THUNDERSTORM | ERPC | 100
| TOTAL | [11 empty] | 1.08 | 0 | 0 | 1.08 | 0
50 | ER1L50 | 400kV SARNATH - ALLAHABAD - I | 136 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
51 | ER1L51 | 400kV SASARAM - ALLAHABAD II | 212 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
52 | ER1L52 | 400kV BIHARSHARIF - BALIA -I | 241.79 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
53 | ER1L53 | 400kV BIHARSHARIF - BALIA -II | 241.79 | ER1 | -- | -- | -- | -- | 2019-04-09 | 14:08 | 2019-04-09 | 14:08 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO Y-N FAULT. FD-119.9KM FROM BIHARSHARIFF AND FC-3.508KA. | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
54 | ER1L54 | 400kV PATNA - BALIA -I | 195 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
55 | ER1L55 | 400kV PATNA - BALIA -II | 195 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
56 | ER1L56 | 400kV PATNA - BALIA -III | 185 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
57 | ER1L57 | 400kV PATNA - BALIA -IV | 185 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
58 | ER1L58 | 400kV BIHARSHARIF-SASARAM-II | 210 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
59 | ER1L59 | 400KV PATNA-BARH III | 68.66 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
60 | ER1L60 | 400KV PATNA-BARH IV | 68.66 | ER1 | -- | -- | -- | -- | 2019-04-09 | 14:18 | 2019-04-09 | 18:32 | 4.23 | 0 | 0 | 4.23 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT CAUSED BY SEVERE LIGHTENING AND THUNDERSTORM AROUND THE FAULT AREA .F.D.=0.1 KM FROM PATNA,F.C.=18.13 KAMP. | ERPC | 100
[13 empty] | 4.23 | 0 | 0 | 4.23 | 0
61 | ER1L61 | 400KV MUZAFFARPUR-BIHARSHARIF I | 133.3 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
62 | ER1L62 | 400KV MUZAFFARPUR-BIHARSHARIF II | 133.3 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
63 | ER1L63 | 400kV KAHALGAON-BARH I | 217.24 | ER1 |  |  |  |  | 2019-04-09 | 12:58 | 2019-04-09 | 14:06 | 1.13 | 0 | 0 | 1.13 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO B-N FAULT, F.D=45 KM FROM KAHALGAON, F.C=8.1KA. TRIPPED DUE TO SEVERE CYCLONIC STORM THUNDERING AROUND FAULT AREA. | ERPC | 100
[9 empty] | 2019-04-13 | 9:00 | 2019-04-13 | 20:08 | 11.13 | 0 | 11.13 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO FACILITATE S/D OF 400 KV PATNA-BARH-II
[9 empty] | 2019-04-25 | 9:20 | 2019-04-26 | 19:52 | 34.53 | 0 | 0 | 0 | 34.53 | OSPD |  |  |  |  | S/D TAKEN FOR AMP WORK BY NTPC BARH
[13 empty] | 46.79 | 0 | 11.13 | 1.13 | 34.53
64 | ER1L64 | 400kV KAHALGAON-BARH II | 217.24 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
65 | ER1L65 | 400kV PATNA-BARH I | 93.04 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
66 | ER1L66 | 400kV PATNA-BARH II | 93.04 | ER1 | -- | -- | -- | -- | 2019-04-12 | 12:42 | 2019-04-13 | 19:25 | 30.72 | 0 | 0 | 30.72 | 0 | LNCC |  |  |  |  | S/D TAKEN REPLACEMENT OF DECAPPED INSULATOR DUE SEVERE CYLONE AND LIGHTINING. | ERPC | 100
[13 empty] | 30.72 | 0 | 0 | 30.72 | 0
67 | ER1L67 | 400kV MAITHON-RANCHI I | 199.81 | ER1 | -- | -- | -- | -- | 2019-04-01 | 0:00 | 2019-04-18 | 2:35 | 410.5833 | 0 | 0 | 0 | 410.5833 | LCSD |  |  |  |  | S/D TAKEN FOR RREALIGNMENT WORK OF LINES AT DVC RTPS COAL FEEDING RAILWAY LINE. | ERPC | 100
| TOTAL | [11 empty] | 410.5833 | 0 | 0 | 0 | 410.5833
68 | ER1L68 | 400kV RAGHUNATHPUR-MAITHON | 44.02 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
69 | ER1L69 | 400kV RANCHI-RAGHUNATHPUR I(LILO of Maithon-Ranch -II at Raghunathpur) | 155.79 | ER1 | -- | -- | -- | -- | 2019-04-01 | 0:00 | 2019-04-18 | 2:11 | 410.1833 | 0 | 0 | 0 | 410.1833 | LCSD |  |  |  |  | S/D TAKEN FOR RREALIGNMENT WORK OF LINES AT DVC RTPS COAL FEEDING RAILWAY LINE. | ERPC | 100
[13 empty] | 410.1833 | 0 | 0 | 0 | 410.1833
70 | ER1L70 | 400kV MAITHON RB-RANCHI I | 187.64 | ER1 | -- | -- | -- | -- | 2019-04-30 | 15:27 | 2019-04-30 | 15:27 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL FROM BOTH END DUE TO Y-N FAULT.F.D.=14.0 KM FROM RANCHI = ,F.C.=14.8 KAMP. | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
71 | ER1L71 | 400kV MAITHON RB-RANCHI II | 187.64 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
72 | ER1L72 | 400kV RANCHI-ROURKELA I | 144.45 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
73 | ER1L73 | 400kV RANCHI-ROURKELA II | 144.45 | ER1 | -- | -- | -- | -- | 2019-04-17 | 9:33 | 2019-04-17 | 19:09 | 9.6 | 0 | 0 | 9.6 | 0 | LMAC |  |  |  |  | S/D TAKEN FOR REPLACEMENT OF INSULATOR DAMAGED BY MISCREANTS | ERPC | 100
| TOTAL | [11 empty] | 9.6 | 0 | 0 | 9.6 | 0
74 | ER1L74 | 400kV BIHARSHARIF-KODERMA I | 110.69 | ER1 | [9 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
75 | ER1L75 | 400kV BIHARSHARIF-KODERMA II | 110.69 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
76 | ER1L76 | 400kV BIHARSHARIF-VARANASI - I | 321 | ER1 | -- | -- | -- | -- | 2019-04-03 | 11:49 | 2019-05-01 | 0:00 | 660.1833 | 0 | 0 | 0 | 660.1833 | LCSD |  |  |  |  | S/D TAKEN FOR REALIGNMENT WORKS OF SAID TR. LINE DUE TO CONSTRUCTION OF NEW RAILWAY LINE. | ERPC | 100
[13 empty] | 660.1833 | 0 | 0 | 0 | 660.1833
77 | ER1L77 | 400kV BIHARSHARIF-VARANASI - II | 321 | ER1 | -- | -- | -- | -- | 2019-04-03 | 11:50 | 2019-05-01 | 0:00 | 660.1667 | 0 | 0 | 0 | 660.1667 | LCSD |  |  |  |  | S/D TAKEN FOR REALIGNMENT WORKS OF SAID TR. LINE DUE TO CONSTRUCTION OF NEW RAILWAY LINE. | ERPC | 100
| TOTAL | [11 empty] | 660.1667 | 0 | 0 | 0 | 660.1667
78 | ER1L78 | 765kV GAYA-BALLIA | 237.7 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
79 | ER1L79 | 400kV JAMSHEDPUR(DVC)-BARIPADA | 108.29 | ER1 | -- | -- | -- | -- |  |  |  |  | NA | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
80 | ER1L80 | 400kV BARIPADA-JAMSHEDPUR II | 140.28 | ER1 | -- | -- | -- | -- | 2019-04-06 | 17:38 | 2019-04-06 | 17:38 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTORECLOSED DUE TO Y-N FAULT, F.D= 141 KM FROM JAMSHEDPUR, F.C=4.2 KA. | ERPC | 100
[9 empty] | 2019-04-19 | 19:17 | 2019-04-19 | 19:17 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL DUE TO Y-N FAULT FROM BOTH END.F.D.=4.6 KM FROM JAMSHEDPUR,F.C.=22.38 KAMP . THERE WERE HEAVY THUNDERSTORM AROUND THE AFFECTED AREA.
[9 empty] | 2019-04-08 | 20:31 | 2019-04-08 | 21:14 | 0.72 | 0 | 0 | 0.72 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO R-N FAULT, F.D=141.1 KM FROM JAMSHEDPUR (100%), F.C=2.397KA. AS REPORTED, THERE WAS HEAVY RAIN AND THUNDERSTORM AT BARIPADA.
[13 empty] | 0.72 | 0 | 0 | 0.72 | 0
81 | ER1L81 | 400kV JAMSHEDPUR-JAMSHEDPUR(DVC) | 108.29 | ER1 | -- | -- | -- | -- | 2019-04-20 | 14:06 | 2019-04-20 | 18:57 | 4.85 | 0 | 0 | 4.85 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR REPLACEMENT OF DAMAGED JUMPER AT LOC NO 01 DURING CYCLONE. | ERPC | 100
| TOTAL | [11 empty] | 4.85 | 0 | 0 | 4.85 | 0
82 | ER1L82 | SASARAM - NABINAGAR I | 81.65 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
83 | ER1L83 | SASARAM - NABINAGAR II | 81.65 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
84 | ER1L84 | 400kV MOTIHARI - GORAKHPUR - I (LILO BARH-GKP-1) | 153.2 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
85 | ER1L85 | 400kV MOTIHARI - GORAKHPUR - II (LILO BARH-GKP-2) | 153.2 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
86 | ER1L86 | 400kV BARH-MOTIHARI- I (LILO BARH-GKP-1) | 199.8 | ER1 | -- | -- | -- | -- | 2019-04-06 | 21:29 | 2019-04-07 | 10:17 | 12.8 | 0 | 12.8 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT, F.D=171.4 KM FROM GORAKHPUR (DMTCL JURISDICTION) WITH F.C=25KA. | ERPC | 100
[9 empty] | 2019-04-08 | 11:13 | 2019-04-08 | 11:38 | 0.42 | 0 | 0.42 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM MOTIHARI END DUE TO B-N FAULT. FD-17.89KM( DMTCL JURISDICTION) AND FC-5.19KA.
[9 empty] | 2019-04-08 | 12:12 | 2019-04-08 | 19:40 | 7.47 | 0 | 7.47 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM MOTIHARI END DUE TO B-N FAULT. FD-19.44KM( DMTCL JURISDICTION) AND FC-5.17KA.
[9 empty] | 2019-04-13 | 11:51 | 2019-04-13 | 18:48 | 6.95 | 0 | 6.95 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO Y-N FAULT.F.D.=26.76 KM FROM MOTIHARI (DMTCL JURIDISCTION),F.C.=4.073 KAMP.
| TOTAL | [11 empty] | 12.8 | 0 | 12.8 | 0 | 0
87 | ER1L87 | 400kV BARH-MOTIHARI- II (LILO BARH-GKP-2) | 199.8 | ER1 | -- | -- | -- | -- | 2019-04-13 | 11:35 | 2019-04-13 | 19:05 | 7.5 | 0 | 7.5 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT.F.D.=22.4 KM FROM MOTIHARI(DMTCL JURIDISCTION) = ,F.C.=2.554 KAMP | ERPC | 100
[9 empty] | 2019-04-14 | 12:42 | 2019-04-14 | 17:25 | 4.72 | 0 | 4.72 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT.F.D.=16.9 KM FROM MOTIHARI(DMTCL JURIDISCTION) = ,F.C.=4.99 KAMP.
[9 empty] | 2019-04-28 | 11:53 | 2019-04-28 | 18:45 | 6.87 | 0 | 6.87 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT. FD-17.2KM FROM MOTIHARI( DMTCL JURISDICTION) AND FC-4.45KA
| TOTAL | [11 empty] | 19.09 | 0 | 19.09 | 0 | 0
88 | ER1L88 | 400KV GAYA - KODERMA - II | 118.2 | ER1 | -- | -- | -- | -- | 2019-04-28 | 9:07 | 2019-05-01 | 0:00 | 62.8833 | 0 | 0 | 62.8833 | 0 | LMAC |  |  |  |  | S/D TAKEN FOR DESTRINGING, ERECTION RE-STRINGING OF MULTI-CIRCUIT TOWER AT LOC. 80, DAMAGED BY MISCRIENTS. | ERPC | 100
[9 empty] | 2019-04-10 | 9:13 | 2019-04-10 | 17:15 | 8.03 | 0 | 0 | 0 | 8.03 | OSPD |  |  |  |  | S/D TAKEN BY DVC FOR PREVENTIVE MAINTINENCE WORK AT THEIR END.
[13 empty] | 70.9133 | 0 | 0 | 62.8833 | 8.03
89 | ER1L89 | 400kV GAYA-MAITHON II | 277 | ER1 | -- | -- | -- | -- | 2019-04-28 | 10:45 | 2019-05-01 | 0:00 | 61.25 | 0 | 0 | 61.25 | 0 | LMAC |  |  |  |  | S/D TAKEN FOR DESTRINGING, ERECTION RE-STRINGING OF MULTI-CIRCUIT TOWER AT LOC. 80, DAMAGED BY MISCRIENTS. | ERPC | 100
[13 empty] | 61.25 | 0 | 0 | 61.25 | 0
90 | ER1L90 | 400kV GAYA-KODERMA-I | 118.2 | ER1 | -- | -- | -- | -- | 2019-04-28 | 9:03 | 2019-05-01 | 0:00 | 62.95 | 0 | 0 | 62.95 | 0 | LMAC |  |  |  |  | S/D TAKEN FOR DESTRINGING, ERECTION RE-STRINGING OF MULTI-CIRCUIT TOWER AT LOC. 80, DAMAGED BY MISCRIENTS. | ERPC | 100
[9 empty] | 2019-04-08 | 9:43 | 2019-04-08 | 18:20 | 8.62 | 0 | 0 | 0 | 8.62 | OSPD |  |  |  |  | SD TAKEN BY DVC, KODERMA FOR PREVENTIVE MAINTINENCE WORK AT THEIR END.
| TOTAL | [11 empty] | 71.57 | 0 | 0 | 62.95 | 8.62
91 | ER1L91 | 400kV GAYA-MAITHON-I | 277 | ER1 |  |  |  |  | 2019-04-22 | 17:14 | 2019-04-22 | 17:14 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTORECLOSED SUCCESSFULLY ON B-N FAULT.F.D.= 175.2 KM FROM GAYA WITH F.C.= 2.02 KA. | ERPC | 100
[9 empty] | 2019-04-28 | 10:43 | 2019-05-01 | 0:00 | 61.2833 | 0 | 0 | 61.2833 | 0 | LMAC |  |  |  |  | S/D TAKEN FOR DESTRINGING, ERECTION RE-STRINGING OF MULTI-CIRCUIT TOWER AT LOC. 80, DAMAGED BY MISCRIENTS.
[13 empty] | 61.2833 | 0 | 0 | 61.2833 | 0
92 | ER1L92 | 400kV RANCHI-NEW RANCHI II | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
93 | ER1L93 | 400kV RANCHI-NEW RANCHI I | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
94 | ER1L94 | 400kV RANCHI-NEW RANCHI III | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
95 | ER1L95 | 400kV RANCHI-NEW RANCHI IV | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
96 | ER1L96 | 400 KV BOKARO-KODERMA-I | 100 | ER1 | -- | -- | -- | -- | 2019-04-06 | 19:35 | 2019-04-06 | 20:54 | 1.32 | 0 | 1.32 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO DT RECEIVED AT KODERMA( DVC) DUE TO PROBLEM AT BOKARO( DVC). | ERPC | 100
[13 empty] | 1.32 | 0 | 1.32 | 0 | 0
97 | ER1L97 | 400 KV BOKARO-KODERMA-II | 100 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
98 | ER1L98 | 400 KVPATNA - KISHANGANJ -I | 346.72 | ER1 | -- | -- | -- | -- | 2019-04-01 | 0:00 | 2019-05-01 | 0:00 | 720 | 0 | 0 | 720 | 0 | LNCC |  |  |  |  | TRIPPED ON B-N FAULT, ONE TOWER BADLY DAMAGED IN GANGA RIVER AT LOC. - 129/0 DUE TO HEAVY FLOOD. | ERPC | 100
[13 empty] | 720 | 0 | 0 | 720 | 0
99 | ER1L99 | 400 KVPATNA - KISHANGANJ -II | 346.72 | ER1 | -- | -- | -- | -- | 2019-04-25 | 22:51 | 2019-04-25 | 22:51 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTORECLOSED DUE TO R-N FAULT, F.D=104 KM FROM KISHENGNAJ, F.C=3.32KA. | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
100 | ER1L100 | 765 KV GAYA - VARANASI - II |  | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
101 | ER1L101 | 400 KV GAYA - CHANDAWA - I | 118 | ER1 | -- | -- | -- | -- | 2019-04-20 | 9:40 | 2019-04-20 | 19:20 | 9.67 | 0 | 0 | 0 | 9.67 | OSPD |  |  |  |  | S/D TAKEN BY JUSNL FOR SHIFTING OF 33KV LINE (JUSNL LINE) CROSSING UNDER SAID 400KV LINES. | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
102 | ER1L104 | 400 KV GAYA - CHANDAWA - II | 118 | ER1 | -- | -- | -- | -- | 2019-04-20 | 9:43 | 2019-04-20 | 19:20 | 9.62 | 0 | 0 | 0 | 9.62 | OSPD |  |  |  |  | S/D TAKEN BY JUSNL FOR SHIFTING OF 33KV LINE (JUSNL LINE) CROSSING UNDER SAID 400KV LINES. | ERPC | 100
| TOTAL | [11 empty] | 9.62 | 0 | 0 | 0 | 9.62
103 | ER1L105 | 400 KV NEW RANCHI - CHANDAWA - I | 68 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
104 | ER1L104 | 400 KV NEW RANCHI - CHANDAWA - II | 68 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
105 | ER1L105 | 765KV SASARAM - FATEHPUR | 354.7 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
106 | ER1L106 | 765KV GAYA - VARANASI -I | 147.81 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
107 | ER1L107 | 400 KVSASARAM - DALTONGANJ - I | 196.186 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
108 | ER1L108 | 400 KV SASARAM - DALTONGANJ - II | 196.186 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
109 | ER1L109 | 400KV GAYA NABINAGAR-1 | 354.7 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
110 | ER1L110 | 400KV GAYA NABINAGAR-2 | [21 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
111 | ER1T1 | 400/220kV ICT1 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2019-04-03 | 12:20 | 2019-04-03 | 13:32 | 1.2 | 0 | 1.2 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR SAFE MOVEMENT OF 400/220KV 500MVA ICT-IV AT BIHARSHARIFF( NEW ICT) FROM GATE TO ITS FOUNDATION. | ERPC | 100
| TOTAL | [11 empty] | 1.2 | 0 | 1.2 | 0 | 0
112 | ER1T2 | 400/220kV ICT2 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2019-04-06 | 12:54 | 2019-04-06 | 13:50 | 0.93 | 0 | 0.93 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR SAFE MOVEMENT OF HYDRA FOR DISMANTLING OF INTERRUPTER OF Y PH MAIN BAY OF 400/220KV 315MVA ICT-II AT BSF JUST BELOW THE JACK BUS. | ERPC | 100
[9 empty] | 2019-04-07 | 13:40 | 2019-04-07 | 17:26 | 3.77 | 0 | 3.77 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR SAFE MOVEMENT OF HYDRA FOR DISMANTLING OF INTERRUPTER OF Y PH MAIN BAY OF 400/220KV 315MVA ICT-II AT BSF JUST BELOW THE JACK BUS.
[9 empty] | 2019-04-17 | 10:16 | 2019-04-17 | 10:48 | 0.53 | 0 | 0.53 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON INTERTRIP DUE TO FAULT FEDED FROM 220 KV SIDE(BSPTCL END).
[9 empty] | 2019-04-03 | 12:20 | 2019-04-03 | 13:34 | 1.23 | 0 | 1.23 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR SAFE MOVEMENT OF 400/220KV 500MVA ICT-IV AT BIHARSHARIFF( NEW ICT) FROM GATE TO ITS FOUNDATION.
| TOTAL | [11 empty] | 6.46 | 0 | 6.46 | 0 | 0
113 | ER1T3 | 400/220kV ICT3 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2019-04-09 | 10:16 | 2019-04-09 | 16:52 | 6.6 | 0 | 0 | 0 | 6.6 | OSPD |  |  |  |  | S/D TAKEN BY BSPTCL FOR 220KV SIDE MAINTENANCE WORK. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 6.6 | 0 | 0 | 0 | 6.6
114 | ER1T4 | 400/220kV ICT1 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2019-04-23 | 17:41 | 2019-04-23 | 18:25 | 0.73 | 0 | 0.73 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON INTERTRIP DUE TO OVER CURRENT OPERATED IN 220 KV SIDE AT JUSNL END. | ERPC | 99.32
[9 empty] | 2019-04-05 | 11:04 | 2019-04-05 | 15:57 | 4.88 | 4.88 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND HOT SPOT IN Y PH T ISOLATOR.
| TOTAL | [11 empty] | 5.61 | 4.88 | 0.73 | 0 | 0
115 | ER1T5 | 400/220kV ICT2 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | 2019-04-24 | 10:44 | 2019-04-24 | 13:29 | 2.75 | 2.75 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND HOT SPOT IN 400KV SIDE B-PH T ISOLATOR. | ERPC | 99.61
| TOTAL | [11 empty] | 2.75 | 2.75 | 0 | 0 | 0
116 | ER1T6 | 400/220kV ICT1 NEW PURNEA | 500 | ER1 | -- | -- | -- | -- | 2019-04-16 | 9:31 | 2019-04-16 | 18:33 | 9.03 | 0 | 0 | 0 | 9.03 | SCSD |  |  |  |  | S/D TAKEN FOR UPGRADATION OF TRNASFORMER ISOLATOR IN 220KV SIDE. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 9.03 | 0 | 0 | 0 | 9.03
117 | ER1T7 | 400/220kV ICT2 NEW PURNEA | 315 | ER1 | -- | -- | -- | -- | 2019-04-15 | 9:08 | 2019-04-15 | 19:20 | 10.2 | 0 | 10.2 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR UPGRADATION OF TRANSFORMER ISOLATOR(220 KV SIDE) | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
118 | ER1T8 | 400/220kV ICT1 SASARAM | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
119 | ER1T9 | 400/220kV ICT2 SASARAM | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
120 | ER1T10 | 400/220kV ICT1 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
121 | ER1T11 | 400/220kV ICT2 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
122 | ER1T12 | 400/220kV ICT1 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
123 | ER1T13 | 400/220kV ICT2 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
124 | ER1T14 | 400/220kV ICT1 RNC | 315 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
125 | ER1T15 | 400/220kV ICT2 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
126 | ER1T16 | 400/220kV ICT1 GAYA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
127 | ER1T17 | 400/220kV ICT2 GAYA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
128 | ER1T17A | 400/220kV ICT3 GAYA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
129 | ER1T18 | 400/132kV ICT1 BANKA | 200 | ER1 | -- | -- | -- | -- | 2019-04-25 | 10:37 | 2019-04-25 | 14:33 | 3.93 | 3.93 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR INSULATING THE DOME AND TERIIARY BUSHING OF ICT | ERPC | 99.54
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 3.93 | 3.93 | 0 | 0 | 0
130 | ER1T19 | 400/132kV ICT 2 BANKA | 200 | ER1 | -- | -- | -- | -- | 2019-04-26 | 10:56 | 2019-04-26 | 13:47 | 2.85 | 2.85 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D FOR INSTALLING INSULATION TAPE ON DOME AND CONNECTOR OF TERTIARY BUSHING. | ERPC | 99.6
[5 empty] | -- | -- | -- | --
[13 empty] | 2.85 | 2.85 | 0 | 0 | 0
131 | ER1T20 | 765/400kV ICT1 GAYA | 1500 | ER1 | -- | -- | -- | -- | 2019-04-12 | 16:05 | 2019-04-12 | 17:18 | 1.22 | 1.22 | 0 | 0 | 0 | OSPT |  |  |  |  | TO ATTEND THE HOT SPOT IN CT TERMINAL OF ITS 220KV SIDE MAIN BAY. | ERPC | 99.83
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 1.22 | 1.22 | 0 | 0 | 0
132 | ER1T21 | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- | 2019-04-27 | 13:51 | 2019-04-27 | 14:49 | 0.97 | 0.97 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D FOR ATENDING OIL LEKAGE FROM R-PH BUSHING TURRET(HV SIDE). | ERPC | 99.86
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0.97 | 0.97 | 0 | 0 | 0
133 | ER1T22 | 765/400kV ICT3 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0.97 | 0.97 | 0 | 0 | 0
134 | ER1T22A | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 1.94 | 1.94 | 0 | 0 | 0
135 | ER1T23 | 220/132kV ICT1 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 2.91 | 2.91 | 0 | 0 | 0
136 | ER1T24 | 220/132kV ICT2 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 2.91 | 0 | 0 | 0
137 | ER1T25 | 220/132kV ICT3 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
138 | ER1T26 | 220/132kV ICT1 ARRAH | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
139 | ER1T27 | 220/132kV ICT2 ARRAH | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
140 | ER1T28 | 765/400/220 kV ICT 1 SASARAM | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
141 | ER1T29 | 765/400kV ICT1 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
142 | ER1T30 | 765/400kV ICT2 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | SUB TOTAL |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
143 | ER1T31 | 400/132kV ICT1 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
144 | ER1T32 | 400/132kV ICT 2 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
145 | ER1T33 | 400/220kV ICT 2 CHAIBASA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
146 | ER1T34 | 400/220kV ICT 1 CHAIBASA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
147 | ER1T35 | 220/132kV ICT3 ARRAH | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
148 | ER1T36 | 400/220kV ICT3 MUZZAFERPUR | 500 | ER1 | -- | -- | -- | -- | 2019-04-18 | 10:16 | 2019-04-18 | 10:59 | 0.72 | 0 | 0.72 | 0 | 0 | OMSU |  |  |  |  | TRIPPED FROM 220 KV SIDE ONLY DUE TO TRIPPING OF 220 KV BUS-2 AT MUZAFFARPUR DUE TO TOUCHING OF BROKEN CAMERA CABLE CAUSED | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0.72 | 0 | 0.72 | 0 | 0
149 | ER1T36 | 400/220kV ICT2 KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
150 | ER1T37 | 400/220 kV ICT1 AT KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
151 | ER1T38 | 400/220kV ICT3 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
152 | ER1T39 | 400/220kV ICT3 PATNA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
153 | ER1T40 | 400/220kV ICT1 DALTONGANJ | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
154 | ER1T41 | 220/132 kV ICT1 DALTONGANJ | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
155 | ER1T42 | 220/132 kV ICT2 DALTONGANJ | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
156 | ER1T43 | 400/220kV ICT2 DALTONGANJ | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
157 | ER1R1 | 50 MVAR B/R-1 AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
158 | ER1R2 | 50 MVAR B/R-1 AT JMASHEDPUR | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
159 | ER1R3 | 50 MVAR BUS REACTOR-II, JAMSHEDPUR II | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
160 | ER1R4 | 400kV BUS REACTOR MUZAFFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
161 | ER1R5 | 80 MVAR B/R AT PATNA | 80 | ER1 | -- | -- | -- | -- | 2019-04-01 | 0:00 | 2019-05-01 | 0:00 | 720 | 0 | 0 | 0 | 720 | SCSD |  |  |  |  | S/D TAKEN FOR CONSTRUCTION ACTIVITY FOR NAVINAGAR BAY UNDER NAVINAGAR-2 PROJECT. | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 720 | 0 | 0 | 0 | 720
162 | ER1R6 | 400kV BUS REACTOR RANCHI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 720
163 | ER1R7 | 80 MVAR B/R AT BIHARSHARIF | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
164 | ER1R8 | 125 MVAR B/R - I AT NEW PURNEA | 125 | ER1 | -- | -- | -- | -- | 2019-04-15 | 21:30 | 2019-04-16 | 7:17 | 9.78 | 0 | 0 | 0 | 9.78 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-21 | 19:52 | 2019-04-23 | 8:54 | 37.03 | 0 | 0 | 0 | 37.03 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-24 | 21:50 | 2019-05-01 | 0:00 | 146.1667 | 0 | 0 | 0 | 146.1667 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-17 | 20:00 | 2019-04-19 | 7:15 | 35.25 | 0 | 0 | 0 | 35.25 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUTION.
| TOTAL | [11 empty] | 228.2267 | 0 | 0 | 0 | 228.2267
165 | ER1R9 | 125 MVAR B/R - I I AT NEW PURNEA | 125 | ER1 | -- | -- | -- | -- | 2019-04-24 | 21:51 | 2019-05-01 | 0:00 | 146.15 | 0 | 0 | 0 | 146.15 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-17 | 20:02 | 2019-04-20 | 7:33 | 59.52 | 0 | 0 | 0 | 59.52 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUTION.
[9 empty] | 2019-04-21 | 20:07 | 2019-04-23 | 8:55 | 36.8 | 0 | 0 | 0 | 36.8 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-15 | 21:37 | 2019-04-16 | 7:18 | 9.68 | 0 | 0 | 0 | 9.68 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 252.15 | 0 | 0 | 0 | 252.15
166 | ER1R10 | 3*80 B/R AT GAYA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
167 | ER1R11 | 3*80 B/R II AT GAYA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
168 | ER1R12 | 50 MVAR MTN RB-2 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
169 | ER1R13 | 50 MVAR GAYA L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
170 | ER1R14 | 50 MVAR SSRM-III L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
171 | ER1R15 | 400kV BUS REACTOR-I, GAYA 125MVAR | 125 | ER1 | -- | -- | -- | -- | 2019-04-29 | 20:18 | 2019-05-01 | 0:00 | 27.7 | 0 | 0 | 0 | 27.7 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 27.7 | 0 | 0 | 0 | 27.7
172 | ER1R16 | 400kV BUS REACTOR II,GAYA | 125 | ER1 | -- | -- | -- | -- | 2019-04-29 | 20:29 | 2019-05-01 | 0:00 | 27.5167 | 0 | 0 | 0 | 27.5167 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
|  | SUB TOTAL |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 27.5167 | 0 | 0 | 0 | 27.5167
173 | ER1R17 | 765kV BUS REACTOR II, GAYA | 240 | ER1 | -- | -- | -- | -- | 2019-04-29 | 20:42 | 2019-05-01 | 0:00 | 27.3 | 0 | 0 | 0 | 27.3 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 54.8167 | 0 | 0 | 0 | 54.8167
174 | ER1R18 | 765kV BUS REACTOR1-GAYA | 240 | ER1 | -- | -- | -- | -- | 2019-04-29 | 20:27 | 2019-05-01 | 0:00 | 27.55 | 0 | 0 | 0 | 27.55 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
| TOTAL | [11 empty] | 27.55 | 0 | 0 | 0 | 27.55
175 | ER1R19 | 125 MVAR B/R - I AT PSL | 125 | ER1 | -- | -- | -- | -- | 2019-04-20 | 21:34 | 2019-04-27 | 14:37 | 161.05 | 0 | 0 | 0 | 161.05 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-01 | 0:00 | 2019-04-06 | 13:35 | 133.5833 | 0 | 0 | 0 | 133.5833 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-28 | 21:05 | 2019-05-01 | 0:00 | 50.9167 | 0 | 0 | 0 | 50.9167 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-08 | 19:24 | 2019-04-17 | 8:06 | 204.7 | 0 | 0 | 0 | 204.7 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 550.25 | 0 | 0 | 0 | 550.25
176 | ER1R20 | 125 MVAR B/R - II AT PASAULI | 125 | ER1 | -- | -- | -- | -- | 2019-04-28 | 21:06 | 2019-05-01 | 0:00 | 50.9 | 0 | 0 | 0 | 50.9 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-03 | 23:16 | 2019-04-06 | 13:28 | 62.2 | 0 | 0 | 0 | 62.2 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 113.1 | 0 | 0 | 0 | 113.1
177 | ER1R21 | 63 MVAR GKP - I L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
178 | ER1R22 | 63 MVAR GKP - II L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
179 | ER1R23 | 63 MVAR NPRN - I L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
180 | ER1R24 | 63 MVAR NPRN - II L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
181 | ER1R25 | 63 MVAR MUZ - I L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
182 | ER1R26 | 63 MVAR MUZ- II L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
183 | ER1R27 | 63 MVAR BSF- I L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
184 | ER1R28 | 63 MVAR BSF- II L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
185 | ER1R29 | 50 MVAR BSF- III L/R AT PSL | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
186 | ER1R30 | 50 MVAR BALIA L/R AT PSL | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
187 | ER1R31 | 63 MVAR ALLAHABAD-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
188 | ER1R32 | 63 MVAR SARNATH-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
189 | ER1R33 | 50 MVAR B/R - I AT GAYA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
190 | ER1R34 | 50 MVAR B/R - II AT GAYA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
191 | ER1R35 | 50 MVAR L/R - I AT BANKA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
192 | ER1R36 | 50 MVAR L/R - 2 AT BANKA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
193 | ER1R37 | 80 MVAR B/R - 1 AT BANKA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
194 | ER1R38 | 125 3Ph B/R I AT SASARAM | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
195 | ER1R39 | 125 3Ph B/R II AT SASARAM | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
196 | ER1R40 | 3*110 MVAR 1 PH B/R - I AT SASARAM | 330 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
197 | ER1R41 | 3*110 MVAR 1 PH L/R - I AT SASARAM (AS B/R) | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
198 | ER1R42 | 125 MVAR BUS REACTOR-1 RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
199 | ER1R43 | 125 MVAR BUS REACTOR-1 PATNA | 125 | ER1 | -- | -- | -- | -- | 2019-04-11 | 19:28 | 2019-04-13 | 15:12 | 43.73 | 0 | 0 | 0 | 43.73 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 43.73 | 0 | 0 | 0 | 43.73
200 | ER1R44 | 80 MVAR PURNEA-1 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
201 | ER1R45 | 80 MVAR PURNEA-2 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
202 | ER1R46 | 125 MVAR BUS REACTOR-2 PATNA | 125 | ER1 | -- | -- | -- | -- | 2019-04-01 | 0:00 | 2019-05-01 | 0:00 | 720 | 0 | 720 | 0 | 0 | OMSU |  |  |  |  | 125MVAR B/R-2 IS UNDER S/D FOR SHIFTING OF THE SAME AS L/R IN 400KV PATNA-BARH-2. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 720 | 0 | 720 | 0 | 0
203 | ER1R47 | 125 MVAR BUS REACTOR-1 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
204 | ER1R48 | 125 MVAR BUS REACTOR-2 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
205 | ER1R49 | 3*80MVAR 1 PH L/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
206 | ER1R50 | 3*80MVAR 1 PH B/R - II AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
207 | ER1R51 | 80 MVAR B/R - 1 AT LAKHISARAI | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
208 | ER1R52 | 3*80MVAR 1 PH B/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
209 | ER1R53 | 63MVAR KISHANGANJ LR-I AT PATNA | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
210 | ER1R54 | 63MVAR KISHANGANJ LR-II AT PATNA | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
211 | ER1R55 | 3*80 MVAR DHRAMJAYGARH LR-II AS BR AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
212 | ER1R56 | 125 MVAR BR-II AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2019-04-28 | 20:36 | 2019-05-01 | 0:00 | 51.4 | 0 | 0 | 0 | 51.4 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-11 | 19:09 | 2019-04-28 | 14:35 | 403.43 | 0 | 0 | 0 | 403.43 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-04 | 19:12 | 2019-04-06 | 13:26 | 42.23 | 0 | 0 | 0 | 42.23 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 497.06 | 0 | 0 | 0 | 497.06
213 | ER1R57 | 125 MVAR BR-I AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2019-04-11 | 19:07 | 2019-04-13 | 14:50 | 43.72 | 0 | 0 | 0 | 43.72 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-04-28 | 20:35 | 2019-05-01 | 0:00 | 51.4167 | 0 | 0 | 0 | 51.4167 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-16 | 0:15 | 2019-04-16 | 6:59 | 6.73 | 0 | 0 | 0 | 6.73 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-04-17 | 19:24 | 2019-04-28 | 14:32 | 259.13 | 0 | 0 | 0 | 259.13 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUTION.
[9 empty] | 2019-04-04 | 19:10 | 2019-04-06 | 13:23 | 42.22 | 0 | 0 | 0 | 42.22 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 403.2167 | 0 | 0 | 0 | 403.2167
214 | ER1R58 | 125 MVAR BR-III AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | 2019-04-28 | 0:07 | 2019-04-28 | 5:52 | 5.75 | 0 | 0 | 0 | 5.75 | SVRD |  |  |  |  | HAND TRIPPED ON VOLTAGE REGULATION AS PER ERLDC INSTRUCTION | ERPC | 100
| TOTAL | [11 empty] | 5.75 | 0 | 0 | 0 | 5.75
215 | ER1R59 | 125 MVAR BR-I AT Kishanganj | 125 | ER1 | -- | -- | -- | -- | 2019-04-11 | 19:14 | 2019-04-16 | 11:18 | 112.07 | 0 | 0 | 0 | 112.07 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
| TOTAL | [11 empty] | 112.07 | 0 | 0 | 0 | 112.07
216 | ER1R60 | 125 MVAR BR-I AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
217 | ER1R61 | 125 MVAR BR-II AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
218 | ER1R62 | 80 MVAR B/R AT CHAIBASA | 80 | ER1 | -- | -- | -- | -- | 2019-04-13 | 9:33 | 2019-04-13 | 12:36 | 3.05 | 3.05 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND HOT SPOT IN Y-PH ISOLATOR. | ERPC | 99.57
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 3.05 | 3.05 | 0 | 0 | 0
219 | ER1R63 | 3*80 1ph VARANASI L/R-II at Gaya | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
220 | ER1R64 | 125 MVAR B/R - I I AT KISHENGANJ | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
221 | ER1R65 | 80 MVAR B/R - I AT KISHENGANJ | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
222 | ER1R66 | 80 MVAR B/R - II AT KISHENGANJ | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
223 | ER1R67 | 80 MVAR L/R OF 400 kV BARH - GORAKHPUR - I AT GORAKHPUR | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
224 | ER1R68 | 80 MVAR L/R OF 400 kV BARH - GORAKHPUR - II AT GORAKHPUR | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
225 | ER1R69 | 240 MVAR L/R OF 765 kV GAYA - BALIA LINE AT BALIA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
226 | ER1R70 | 330 MVAR L/R OF 765 kV SASARAM - FATEHPUR LINE AT SASARAM | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
227 | ER1R71 | 330 MVAR L/R OF 765 kV SASARAM - FATEHPUR LINE AT FATEHPUR | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
228 | ER1R72 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - I LINE AT GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
229 | ER1R73 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - I LINE AT VARANASI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
230 | ER1R74 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - II LINE AT GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
231 | ER1R75 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - II LINE AT VARANASI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
232 | ER1R76 | 125MVAR, 400kV BUS REACTOR-III, AT JAMSHEDPUR | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
233 | ER1R76 | 80 MVAR BUS REACTOR AT DALTONGANJ | 80 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
234 | ER1R77 | 125 MVAR BR-IV AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
TOTAL
235 | ER1R78 | 125 MVAR BR-II AT Lakhisarai | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
236 | ER1R79 | 50 MVAR L/R of 400 kV Biharsarif - Sasaram - I AT Biharsharif | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
237 | ER1R80 | 50 MVAR L/R of 400 kV Biharsarif - Lakhisarai - II AT Biharsharif | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
238 | ER1R80 | 80 MVAR L/R of 400 kV Kishanganj- Darbhanga - II AT Kishanganj | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
239 | ER1 ST01 | STATCOM AT New ranchi | -550/+300 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
240 | ER1 ST02 | STATCOM AT Kishanganj | -450/+200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
241 | ER1 ST02 | BANKA-BUS REACTOR-2 |  | ER1 | -- | -- | -- | -- | 2019-04-25 | 20:23 | 2019-05-01 | 0:00 | 123.6167 | 0 | 0 | 0 | 123.6167 | SVRD |  |  |  |  | S/OFF FOR V/R AS PER ERLDC INSTRUCTION | ERPC | 100
| TOTAL | [11 empty] | 123.6167 | 0 | 0 | 0 | 123.6167

## SOP MAY 2019
Standard of Performance data for the month of May-2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION-I
'ANNEXURE - A
Sr.No. | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | DETAILS OF OUTAGE |  | Total outage in days (1) | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  |  | Category | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | No. of Tower damaged | No.of insulators failed |  | DATE | TIME | DATE | TIME | TOTAL | ISTS Licensee | OTHERS | System constraint/ Natural calmity/ Militancy | Deemed Available
1 | ER1L1 | 132kV ARA-ARA | 1.7 | ER1 | -- | -- | -- | -- | [14 empty] | TRIPPED DUE TO Y-B FAULT FD-4.129 KM FROM ARA(PG) ( BSPTCL JURISDICTION) ,ZONE-3 AND FC- Iy-5.404KA Ib-4.783KA. | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
2 | ER1L2 | 132kV DEHRI - KUDRA | 40 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
3 | ER1L3 | 132kV KUDRA - SASARAM | 17 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
4 | ER1L4 | 132kV Dehri-SASARAM | 62 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
5 | ER1L5 | 132kV SASARAM- KARAMNASA | 29 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
6 | ER1L6 | 132kV SASARAM-MOHANIA | 13 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
7 | ER1L7 | 132kV MOHANIA - KARMASA | 11 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
8 | ER1L8 | 132kV DUMRAON-ARA | 1.7 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
9 | ER1L9 | 132kV PURNEA-DALKHOLA (LILO PART) | 0.5 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
10 | ER1L10 | 132kV PNR-PRN(LILO PART) | 0.5 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
11 | ER1L11 | 220kV DALKHOLA-PURNEA I | 41 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
12 | ER1L12 | 220kV DALKHOLA-PURNEA II | 41 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
13 | ER1L13 | 220 kV PURNEA - NEW PURNEA-I | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
14 | ER1L14 | 220 kV PURNEA - NEW PURNEA-II | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
15 | ER1L15 | 220kV SASARAM-NADOKHAR | 5 | ER1 |  |  |  |  | 2019-05-13 | 21:11 | 2019-05-14 | 0:06 | 2.92 | 0 | 0 | 0 | 2.92 | OSFD |  |  |  |  | EMERGENCY S/D TAKEN BY BSPTCL FOR RECTIFICATION OF OPENED CT JUMPER AT NADOKHAR END . | ERPC | 100
| TOTAL | [11 empty] | 2.92 | 0 | 0 | 0 | 2.92
16 | ER1L16 | 220kV NADOKHAR -ARRAH I | 107 | ER1 |  |  |  |  | 2019-05-21 | 21:09 | 2019-05-26 | 13:00 | 111.85 | 0 | 0 | 0 | 111.85 | LPRD |  |  |  |  | HAND TRIPPED FOR POWER REGULATION AS PER ERLDC INSTRUCTION | ERPC | 100
| TOTAL | [11 empty] | 111.85 | 0 | 0 | 0 | 111.85
17 | ER1L17 | 220kV SASARAM-ARRAH I | 112 | ER1 |  |  |  |  | 2019-05-30 | 20:47 | 2019-05-30 | 22:40 | 1.88 | 0 | 0 | 0 | 1.88 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[9 empty] | 2019-05-03 | 14:13 | 2019-05-03 | 18:50 | 4.62 | 0 | 0 | 0 | 4.62 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-11 | 12:49 | 2019-05-11 | 17:16 | 4.45 | 0 | 0 | 0 | 4.45 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-06 | 13:01 | 2019-05-06 | 20:03 | 7.03 | 0 | 0 | 0 | 7.03 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-09 | 13:32 | 2019-05-09 | 17:08 | 3.6 | 0 | 0 | 0 | 3.6 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-26 | 13:37 | 2019-05-26 | 17:46 | 4.15 | 0 | 0 | 0 | 4.15 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
| TOTAL | [11 empty] | 25.73 | 0 | 0 | 0 | 25.73
18 | ER1L18 | 220kV ARA-KHAGOL I | 48.44 | ER1 |  |  |  |  | 2019-05-01 | 0:00 | 2019-05-03 | 15:13 | 63.2167 | 0 | 0 | 0 | 63.2167 | LPRD |  |  |  |  | HAND TRIPPED FOR POWER REGULATION AS PER ERLDC INSTRUCTION | ERPC | 100
[9 empty] | 2019-05-07 | 8:04 | 2019-06-01 | 0:00 | 591.9333 | 0 | 0 | 0 | 591.9333 | LPRD |  |  |  |  | HAND TRIPPED FOR POWER REGULATION AS PER ERLDC INSTRUCTION
| TOTAL | [11 empty] | 655.15 | 0 | 0 | 0 | 655.15
19 | ER1L19 | 220kV ARA-KHAGOL II | 48.44 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 0 | 744 | LPRD |  |  |  |  | HAND TRIPPED FOR POWER REGULATION AS PER ERLDC INSTRUCTION | ERPC | 100
| TOTAL | [11 empty] | 744 | 0 | 0 | 0 | 744
20 | ER1L20 | 220kV DEHRI-SASARAM |  | ER1 | -- | -- | -- | -- | 2019-05-01 | 12:57 | 2019-05-01 | 13:51 | 0.9 | 0 | 0.9 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT. FD-6.9KM FROM SASARAM(BSPTCL JURISDICTION) AND FC-7.749KA. | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0.9 | 0 | 0.9 | 0 | 0
21 | ER1L21 | 220kV SASARAM-SAHUPURI | 4.88 | ER1 | -- | -- | -- | -- | 2019-05-14 | 12:18 | 2019-05-14 | 13:11 | 0.88 | 0 | 0.88 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON B-N FAULT.F.D.=49.6 KM FROM SASARAM,F.C.=3.13 KAMP. | ERPC | 100
| TOTAL | [11 empty] | 0.88 | 0 | 0.88 | 0 | 0
22 | ER1L22 | 220kV RANCHI-CHANDIL I | 8.06 | ER1 | -- | -- | -- | -- | 2019-05-12 | 16:16 | 2019-05-12 | 18:20 | 2.07 | 0 | 2.07 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM CHANDIL END DUE TO B-N FAULT.A/R SUCCESSFUL AT RANCHI END.F.D.=67.213 KM FROM RANCHI (JUSNL JURIDISCTION) | ERPC | 100
[9 empty] | 2019-05-22 | 16:55 | 2019-05-22 | 17:16 | 0.35 | 0 | 0.35 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM CHANDIL END ON B-N FAULT.A/R SUCCESSFUL AT RANCHI END.F.D.=15.2 KM FROM RANCHI(JUSNL JURIDISCTION), F.C.=
[9 empty] | 2019-05-22 | 17:23 | 2019-05-23 | 11:51 | 18.47 | 0 | 18.47 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON R-N FAULT ONLY FROM CHANDIL END.A/R SUCCESSFUL AT RANCHI END.F.D.=33.3 KM FROM RANCHI(JUSNL JURIDSCTION),F.C.=3.
| TOTAL | [11 empty] | 20.89 | 0 | 20.89 | 0 | 0
23 | ER1L23 | 220kV RANCHI-CHANDIL-II (LILO) | 6.92 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
24 | ER1L24 | 220kV RANCHI-HATIA-I (LILO) | 8.06 | ER1 | -- | -- | -- | -- | 2019-05-11 | 9:39 | 2019-05-11 | 18:45 | 9.1 | 0 | 0 | 0 | 9.1 | OSPD |  |  |  |  | S/D TAKEN BY JUSNL FOR STRINGING WORK OF UNDER CONSTRUCTED 220KV PGCIL(RANCHI) –HATIA(NEW)(JUSNL LINE). | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 9.1 | 0 | 0 | 0 | 9.1
25 | ER1L25 | 220kV RANCHI-HATIA-II(LILO) | 6.92 | ER1 | -- | -- | -- | -- | 2019-05-11 | 9:42 | 2019-05-11 | 18:46 | 9.07 | 0 | 0 | 0 | 9.07 | OSPD |  |  |  |  | S/D TAKEN BY JUSNL FOR STRINGING WORK OF UNDER CONSTRUCTED 220KV PGCIL(RANCHI) –HATIA(NEW)(JUSNL LINE). | ERPC | 100
| TOTAL | [11 empty] | 9.07 | 0 | 0 | 0 | 9.07
26 | ER1L26 | 220kV GAYA-DEHRI -I(LILO PART) | 11 | ER1 | [19 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
27 | ER1L27 | 220kV GAYA-BODHGAYA(BSEB) I | 12.7 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
28 | ER1L28 | 220kV GAYA-DEHRI-II (LILO PART) | 11 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
29 | ER1L29 | 220kV GAYA-BODHGAYA(BSEB) II | 12.7 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
30 | ER1L30 | 400kV FARAKKA-KAHALGAON I | 95 | [5 empty] | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 0 | 744 | LCSD |  |  |  |  | S.OFF FOR TAKING UP BAY UPGRADATION WORK AT FARAKKA END BY ER-2. | ERPC | 100
| TOTAL | [11 empty] | 744 | 0 | 0 | 0 | 744
31 | ER1L31 | 400kV FARAKKA-KAHALGAON II | 95 | [20 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
32 | ER1L32 | 400kV KAHALGAON-FARAKKA III | 95.25 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
33 | ER1L33 | 400kV KAHALGAON-FARAKKA IV | 95.25 | ER1 | -- | -- | -- | -- | 2019-05-03 | 15:37 | 2019-05-03 | 16:27 | 0.83 | 0 | 0.83 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO BUS-II FAULT AT NTPC KAHALGAON END. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0.83 | 0 | 0.83 | 0 | 0
34 | ER1L34 | 400kV KAHALGAON-LAKHISARAI I | 145 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0.83 | 0 | 0.83 | 0 | 0
35 | ER1L35 | 400kV BIHARSHARIFF-LAKHISARAI I | 89 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
36 | ER1L36 | 400kV KAHALGAON-LAKHISARAI II | 145 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
37 | ER1L37 | 400kV BIHARSHARIF-LAKHISARAI II | 89 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
38 | ER1L38 | 400kV KAHALGAON-BANKA-I | 53.745 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
39 | ER1L39 | 400KV BIHARSHARIF-BANKA I | 184.54 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
40 | ER1L40 | 400kV KAHALGAON-BANKA-II | 53.745 | ER1 | -- | -- | -- | -- | 2019-05-30 | 22:51 | 2019-05-30 | 22:51 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO Y-N FAULT. FD-33.15KM FROM BANKA AND FC-4.108KA. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
41 | ER1L41 | 400KV BIHARSHARIF-BANKA II | 184.54 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
42 | ER1L42 | 400kV JAMSHEDPUR-CHAIBASA I | 46.14 | ER1 | -- | -- | -- | -- | 2019-05-16 | 11:05 | 2019-05-16 | 20:12 | 9.12 | 0 | 9.12 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR A/R RETROFITTING WORK. ELECTROMECHANICAL RELAY REPLACED WITH NUMERICAL RELAY FOR SYSTEM IMPROVEMENT. | ERPC | 99.95
[9 empty] | 2019-05-21 | 10:24 | 2019-05-21 | 10:43 | 0.32 | 0.32 | 0 | 0 | 0 | SRMT |  |  |  |  | TRIPPED DUE TO MAL-OPERATION OF TEED RELAY AT JAMSHEDPUR END.
| TOTAL | [11 empty] | 9.44 | 0.32 | 9.12 | 0 | 0
43 | ER1L43 | 400kV JAMSHEDPUR-CHAIBASA II | 46.14 | ER1 | -- | -- | -- | -- | 2019-05-14 | 11:07 | 2019-05-14 | 19:57 | 8.83 | 0 | 8.83 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR A/R RETROFITTING WORK. ELECTROMECHANICAL RELAY REPLACED WITH NUMERICAL RELAY FOR SYSTEM IMPROVEMENT. | ERPC | 100
| TOTAL | [11 empty] | 8.83 | 0 | 8.83 | 0 | 0
44 | ER1L44 | 400kV CHAIBASA-ROURKELA I | 131.48 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 8.83 | 0 | 8.83 | 0 | 0
45 | ER1L45 | 400kV CHAIBASA-ROURKELA II | 131.48 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
46 | ER1L46 | 400kV MAITHON-KAHALGAON I | 172 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
47 | ER1L47 | 400kV MAITHON-KAHALGAON II | 172 | ER1 | -- | -- | -- | -- | 2019-05-25 | 15:34 | 2019-05-25 | 15:34 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTO-RECLOSED SUCCESSFUL FROM BOTH ENDS DUE TO Y-N FAULT. F.D.=20.85 KM FROM MAITHON WITH F.C.=5.83 KA. | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
48 | ER1L48 | 400kV BIHARSHARIF-SASARAM-I | 210 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
49 | ER1L49 | 400kV SASARAM - VARANASI | 143.73 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
50 | ER1L50 | 400kV SARNATH - ALLAHABAD - I | 136 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
51 | ER1L51 | 400kV SASARAM - ALLAHABAD II | 212 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
52 | ER1L52 | 400kV BIHARSHARIF - BALIA -I | 241.79 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
53 | ER1L53 | 400kV BIHARSHARIF - BALIA -II | 241.79 | ER1 | -- | -- | -- | -- | 2019-05-30 | 10:21 | 2019-05-30 | 12:40 | 2.32 | 2.32 | 0 | 0 | 0 | OMST |  |  |  |  | TRIPPED DURING DC SEGREGATION OF TRIP COIL AND LBB RELAY OF 400KV TIE BAY OF SASARAM-II AND BALIA-II AT BIHARSHARIF. | ERPC | 99.68
[13 empty] | 2.32 | 2.32 | 0 | 0 | 0
54 | ER1L54 | 400kV PATNA - BALIA -I | 195 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
55 | ER1L55 | 400kV PATNA - BALIA -II | 195 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
56 | ER1L56 | 400kV PATNA - BALIA -III | 185 | ER1 | -- | -- | -- | -- | 2019-05-08 | 19:23 | 2019-05-08 | 19:23 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULlY OPERATED FROM BOTH END DUE TO Y-N FAULT,F.D.-99KM FROM PATNA,F.C.-3.47KA | ERPC | 100
[9 empty] | 2019-05-10 | 9:42 | 2019-05-10 | 16:29 | 6.78 | 0 | 0 | 6.78 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR REPLACEMENT OF DAMAGED PILOT STRING AT LOC. NO. 429. DAMAGED DURING SEVERE CYCLONE AND LIGHTNING.
| TOTAL | [11 empty] | 6.78 | 0 | 0 | 6.78 | 0
57 | ER1L57 | 400kV PATNA - BALIA -IV | 185 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
58 | ER1L58 | 400kV BIHARSHARIF-SASARAM-II | 210 | ER1 | -- | -- | -- | -- | 2019-05-30 | 10:21 | 2019-05-30 | 12:09 | 1.8 | 1.8 | 0 | 0 | 0 | OMST |  |  |  |  | TRIPPED DURING DC SEGREGATION OF TRIP COIL AND LBB RELAY OF 400KV TIE BAY OF SASARAM-II AND BALIA-II AT BIHARSHARIF. | ERPC | 99.75
| TOTAL | [11 empty] | 1.8 | 1.8 | 0 | 0 | 0
59 | ER1L59 | 400KV PATNA-BARH III | 68.66 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
60 | ER1L60 | 400KV PATNA-BARH IV | 68.66 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
61 | ER1L61 | 400KV MUZAFFARPUR-BIHARSHARIF I | 133.3 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
62 | ER1L62 | 400KV MUZAFFARPUR-BIHARSHARIF II | 133.3 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
63 | ER1L63 | 400kV KAHALGAON-BARH I | 217.24 | ER1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
64 | ER1L64 | 400kV KAHALGAON-BARH II | 217.24 | ER1 | -- | -- | -- | -- | 2019-05-22 | 18:34 | 2019-05-23 | 17:11 | 22.62 | 0 | 22.62 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR ATTENDING DAMAGED LMU DUE TO FIRE IN BARH NTPC SWITCHYARD | ERPC | 100
| TOTAL | [11 empty] | 22.62 | 0 | 22.62 | 0 | 0
65 | ER1L65 | 400kV PATNA-BARH I | 93.04 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
66 | ER1L66 | 400kV PATNA-BARH II | 93.04 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
67 | ER1L67 | 400kV MAITHON-RANCHI I | 199.81 | ER1 | -- | -- | -- | --
[24 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
68 | ER1L68 | 400kV RAGHUNATHPUR-MAITHON | 44.02 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
69 | ER1L69 | 400kV RANCHI-RAGHUNATHPUR I(LILO of Maithon-Ranch -II at Raghunathpur) | 155.79 | ER1 | -- | -- | -- | -- | 2019-05-31 | 18:40 | 2019-05-31 | 18:40 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO Y-N FAULT. FD-117KM FROM RANCHI AND FC-3.2KA. | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
70 | ER1L70 | 400kV MAITHON RB-RANCHI I | 187.64 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
71 | ER1L71 | 400kV MAITHON RB-RANCHI II | 187.64 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
72 | ER1L72 | 400kV RANCHI-ROURKELA I | 144.45 | ER1 | -- | -- | -- | -- | 2019-05-23 | 17:15 | 2019-05-23 | 17:15 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTO-RECLOSED SUCCESSFULLY FROM BOTH ENDS ON R-N FAULT. F.D.=73.8 KM FROM RANCHI WITH F.C.= 4.3 KA. | ERPC | 100
[9 empty] | 2019-05-26 | 8:07 | 2019-05-26 | 21:18 | 13.18 | 0 | 0 | 0 | 13.18 | LCSD |  |  |  |  | S/D TAKEN FOR STRINGING OF 765 KV RANCH- MEDNIPUR TL.
[9 empty] | 2019-05-25 | 8:01 | 2019-05-25 | 20:49 | 12.8 | 0 | 0 | 0 | 12.8 | LCSD |  |  |  |  | S/D TAKEN FOR STRINGING OF 765 KV RANCH- MEDNIPUR TL.
[13 empty] | 25.98 | 0 | 0 | 0 | 25.98
73 | ER1L73 | 400kV RANCHI-ROURKELA II | 144.45 | ER1 | -- | -- | -- | -- | 2019-05-26 | 8:08 | 2019-05-26 | 21:20 | 13.2 | 0 | 0 | 0 | 13.2 | LCSD |  |  |  |  | S/D TAKEN FOR STRINGING OF 765 KV RANCH- MEDNIPUR TL. | ERPC | 100
[9 empty] | 2019-05-23 | 19:46 | 2019-05-23 | 20:21 | 0.58 | 0 | 0 | 0.58 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO R-N FAULT DURING SEVERE CYCLONE, HEAVY RAIN AND LIGHTENING. F.D.= 96.31 KM FROM RANCHI, F.C.= 3.763KA.
[9 empty] | 2019-05-25 | 8:02 | 2019-05-25 | 20:51 | 12.82 | 0 | 0 | 0 | 12.82 | LCSD |  |  |  |  | S/D TAKEN FOR STRINGING OF 765 KV RANCH- MEDNIPUR TL.
| TOTAL | [11 empty] | 26.6 | 0 | 0 | 0.58 | 26.02
74 | ER1L74 | 400kV BIHARSHARIF-KODERMA I | 110.69 | ER1 | [9 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
75 | ER1L75 | 400kV BIHARSHARIF-KODERMA II | 110.69 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
76 | ER1L76 | 400kV BIHARSHARIF-VARANASI - I | 321 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-04 | 21:47 | 93.7833 | 0 | 0 | 0 | 93.7833 | LCSD |  |  |  |  | S/D TAKEN FOR REALIGNMENT WORKS OF SAID TR. LINE DUE TO CONSTRUCTION OF NEW RAILWAY LINE. | ERPC | 100
[13 empty] | 93.7833 | 0 | 0 | 0 | 93.7833
77 | ER1L77 | 400kV BIHARSHARIF-VARANASI - II | 321 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-04 | 21:48 | 93.8 | 0 | 0 | 0 | 93.8 | LCSD |  |  |  |  | S/D TAKEN FOR REALIGNMENT WORKS OF SAID TR. LINE DUE TO CONSTRUCTION OF NEW RAILWAY LINE. | ERPC | 100
[13 empty] | 93.8 | 0 | 0 | 0 | 93.8
78 | ER1L78 | 765kV GAYA-BALLIA | 237.7 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
79 | ER1L79 | 400kV JAMSHEDPUR(DVC)-BARIPADA | 108.29 | ER1 | -- | -- | -- | -- |  |  |  |  | NA | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
80 | ER1L80 | 400kV BARIPADA-JAMSHEDPUR II | 140.28 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
81 | ER1L81 | 400kV JAMSHEDPUR-JAMSHEDPUR(DVC) | 108.29 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
82 | ER1L82 | SASARAM - NABINAGAR I | 81.65 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
83 | ER1L83 | SASARAM - NABINAGAR II | 81.65 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
84 | ER1L84 | 400kV MOTIHARI - GORAKHPUR - I (LILO BARH-GKP-1) | 153.2 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
85 | ER1L85 | 400kV MOTIHARI - GORAKHPUR - II (LILO BARH-GKP-2) | 153.2 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
86 | ER1L86 | 400kV BARH-MOTIHARI- I (LILO BARH-GKP-1) | 199.8 | ER1 | -- | -- | -- | -- | 2019-05-05 | 15:13 | 2019-05-05 | 16:42 | 1.49 | 0 | 1.49 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO Y-N FAULT, FD-202.8KM FROM BARH( DMTCL JURISDICTION) AND FC=2.49KA . | ERPC | 100
| TOTAL | [11 empty] | 1.49 | 0 | 1.49 | 0 | 0
87 | ER1L87 | 400kV BARH-MOTIHARI- II (LILO BARH-GKP-2) | 199.8 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
88 | ER1L88 | 400KV GAYA - KODERMA - II | 118.2 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION & RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONIC STORM | ERPC | 100
[13 empty] | 744 | 0 | 0 | 744 | 0
89 | ER1L89 | 400kV GAYA-MAITHON II | 277 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION & RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONIC STORM | ERPC | 100
[13 empty] | 744 | 0 | 0 | 744 | 0
90 | ER1L90 | 400kV GAYA-KODERMA-I | 118.2 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION & RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONIC STORM | ERPC | 100
| TOTAL | [11 empty] | 744 | 0 | 0 | 744 | 0
91 | ER1L91 | 400kV GAYA-MAITHON-I | 277 | ER1 |  |  |  |  | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION & RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONIC STORM | ERPC | 100
[13 empty] | 744 | 0 | 0 | 744 | 0
92 | ER1L92 | 400kV RANCHI-NEW RANCHI II | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
93 | ER1L93 | 400kV RANCHI-NEW RANCHI I | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
94 | ER1L94 | 400kV RANCHI-NEW RANCHI III | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
95 | ER1L95 | 400kV RANCHI-NEW RANCHI IV | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
96 | ER1L96 | 400 KV BOKARO-KODERMA-I | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
97 | ER1L97 | 400 KV BOKARO-KODERMA-II | 100 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
98 | ER1L98 | 400 KVPATNA - KISHANGANJ -I | 346.72 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 744 | 0 | LNCC |  |  |  |  | TRIPPED ON B-N FAULT, ONE TOWER BADLY DAMAGED IN GANGA RIVER AT LOC. - 129/0 DUE TO HEAVY FLOOD. | ERPC | 100
[13 empty] | 744 | 0 | 0 | 744 | 0
99 | ER1L99 | 400 KVPATNA - KISHANGANJ -II | 346.72 | ER1 | -- | -- | -- | -- | 2019-05-30 | 22:13 | 2019-05-30 | 22:13 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO Y-N FAULT. FD-267.9KM FROM PATNA AND FC-1.6KA. | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
100 | ER1L100 | 765 KV GAYA - VARANASI - II |  | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
101 | ER1L101 | 400 KV GAYA - CHANDAWA - I | 118 | ER1 | -- | -- | -- | -- | 2019-05-29 | 15:35 | 2019-05-29 | 17:10 | 1.58 | 1.58 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND SF6 GAS LEAKAGE IN ITS BAY (Y-PH) AT CHANDWA | ERPC | 99.78
[5 empty] | -- | -- | -- | --
[13 empty] | 1.58 | 1.58 | 0 | 0 | 0
102 | ER1L104 | 400 KV GAYA - CHANDAWA - II | 118 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
103 | ER1L105 | 400 KV NEW RANCHI - CHANDAWA - I | 68 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
104 | ER1L104 | 400 KV NEW RANCHI - CHANDAWA - II | 68 | ER1 | -- | -- | -- | -- | 2019-05-23 | 14:37 | 2019-05-23 | 14:37 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTO RECLOSED SUCCESSFULLY FROM BOTH ENDS ON R-N FAULT. F.D.= 35 KM FROM NEW RANCHI WITH F.C.= 7.65 KA. | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
105 | ER1L105 | 765KV SASARAM - FATEHPUR | 354.7 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
106 | ER1L106 | 765KV GAYA - VARANASI -I | 147.81 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
107 | ER1L107 | 400 KVSASARAM - DALTONGANJ - I | 196.186 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
108 | ER1L108 | 400 KV SASARAM - DALTONGANJ - II | 196.186 | ER1 | -- | -- | -- | -- | 2019-05-01 | 15:02 | 2019-05-01 | 15:48 | 0.77 | 0 | 0 | 0.77 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT CAUSED BY THUNDERSTORM AROUND THE FAULT AREA. FD-73.93KM FROM SASARAM AND FC-2.5994KA | ERPC | 100
[13 empty] | 0.77 | 0 | 0 | 0.77 | 0
109 | ER1L109 | 400KV GAYA NABINAGAR-1 | 354.7 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
110 | ER1L110 | 400KV GAYA NABINAGAR-2 |  | ER1 | [19 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
111 | ER1T1 | 400/220kV ICT1 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
112 | ER1T2 | 400/220kV ICT2 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
113 | ER1T3 | 400/220kV ICT3 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
114 | ER1T4 | 400/220kV ICT1 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
115 | ER1T5 | 400/220kV ICT2 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
116 | ER1T6 | 400/220kV ICT1 NEW PURNEA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
117 | ER1T7 | 400/220kV ICT2 NEW PURNEA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
118 | ER1T8 | 400/220kV ICT1 SASARAM | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
119 | ER1T9 | 400/220kV ICT2 SASARAM | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
120 | ER1T10 | 400/220kV ICT1 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
121 | ER1T11 | 400/220kV ICT2 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
122 | ER1T12 | 400/220kV ICT1 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
123 | ER1T13 | 400/220kV ICT2 PATNA | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
124 | ER1T14 | 400/220kV ICT1 RNC | 315 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
125 | ER1T15 | 400/220kV ICT2 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
126 | ER1T16 | 400/220kV ICT1 GAYA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
127 | ER1T17 | 400/220kV ICT2 GAYA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
128 | ER1T17A | 400/220kV ICT3 GAYA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
129 | ER1T18 | 400/132kV ICT1 BANKA | 200 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
130 | ER1T19 | 400/132kV ICT 2 BANKA | 200 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
131 | ER1T20 | 765/400kV ICT1 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
132 | ER1T21 | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
133 | ER1T22 | 765/400kV ICT3 GAYA | 1500 | ER1 | -- | -- | -- | -- | 2019-05-25 | 12:37 | 2019-05-25 | 19:02 | 6.42 | 6.42 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR WORK RELATED TO CSD. | ERPC | 99.13
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 6.42 | 6.42 | 0 | 0 | 0
134 | ER1T22A | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 12.84 | 12.84 | 0 | 0 | 0
135 | ER1T23 | 220/132kV ICT1 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 19.26 | 19.26 | 0 | 0 | 0
136 | ER1T24 | 220/132kV ICT2 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 19.26 | 0 | 0 | 0
137 | ER1T25 | 220/132kV ICT3 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
138 | ER1T26 | 220/132kV ICT1 ARRAH | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
139 | ER1T27 | 220/132kV ICT2 ARRAH | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
140 | ER1T28 | 765/400/220 kV ICT 1 SASARAM | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
141 | ER1T29 | 765/400kV ICT1 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | 2019-05-21 | 9:18 | 2019-05-21 | 17:57 | 8.65 | 8.65 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR AMP WORK. | ERPC | 97.86
[5 empty] | -- | -- | -- | -- | 2019-05-20 | 10:24 | 2019-05-20 | 17:40 | 7.27 | 7.27 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR AMP WORK.
| TOTAL | [11 empty] | 15.92 | 15.92 | 0 | 0 | 0
142 | ER1T30 | 765/400kV ICT2 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | 2019-05-22 | 9:23 | 2019-05-22 | 18:51 | 9.47 | 9.47 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR AMP WORK. | ERPC | 97.58
|  | SUB TOTAL |  |  | -- | -- | -- | -- | 2019-05-23 | 9:29 | 2019-05-23 | 16:42 | 7.21 | 7.21 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR AMP WORK.
| TOTAL | [11 empty] | 16.68 | 16.68 | 0 | 0 | 0
143 | ER1T31 | 400/132kV ICT1 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | 2019-05-28 | 7:28 | 2019-05-28 | 19:55 | 12.45 | 12.45 | 0 | 0 | 0 | OSPT |  |  |  |  | SHUTDOWN TAKEN FOR AMP WORK. | ERPC | 98.32
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 12.45 | 12.45 | 0 | 0 | 0
144 | ER1T32 | 400/132kV ICT 2 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | 2019-05-29 | 7:35 | 2019-05-29 | 19:43 | 12.13 | 12.13 | 0 | 0 | 0 | OSPT |  |  |  |  | SHUTDOWN TAKEN FOR AMP WORK. | ERPC | 98.36
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 12.13 | 12.13 | 0 | 0 | 0
145 | ER1T33 | 400/220kV ICT 2 CHAIBASA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
146 | ER1T34 | 400/220kV ICT 1 CHAIBASA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
147 | ER1T35 | 220/132kV ICT3 ARRAH | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
148 | ER1T36 | 400/220kV ICT3 MUZZAFERPUR | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
149 | ER1T36 | 400/220kV ICT2 KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | 2019-05-15 | 19:14 | 2019-05-15 | 21:25 | 2.18 | 0 | 2.18 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON OPERATION OF BACK UP OVER CURRENT RELAY DUE TO FAULT IN DOWNSTREAM SYSTEM. | ERPC | 100
| TOTAL | [11 empty] | 2.18 | 0 | 2.18 | 0 | 0
150 | ER1T37 | 400/220 kV ICT1 AT KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 2.18 | 0 | 2.18 | 0 | 0
151 | ER1T38 | 400/220kV ICT3 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
152 | ER1T39 | 400/220kV ICT3 PATNA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
153 | ER1T40 | 400/220kV ICT1 DALTONGANJ | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
154 | ER1T41 | 220/132 kV ICT1 DALTONGANJ | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
155 | ER1T42 | 220/132 kV ICT2 DALTONGANJ | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
156 | ER1T43 | 400/220kV ICT2 DALTONGANJ | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
157 | ER1R1 | 50 MVAR B/R-1 AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
158 | ER1R2 | 50 MVAR B/R-1 AT JMASHEDPUR | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
159 | ER1R3 | 50 MVAR BUS REACTOR-II, JAMSHEDPUR II | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
160 | ER1R4 | 400kV BUS REACTOR MUZAFFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
161 | ER1R5 | 80 MVAR B/R AT PATNA | 80 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 0 | 0 | 744 | SCSD |  |  |  |  | S/D TAKEN FOR CONSTRUCTION ACTIVITY FOR NAVINAGAR BAY UNDER NAVINAGAR-2 PROJECT. | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 744 | 0 | 0 | 0 | 744
162 | ER1R6 | 400kV BUS REACTOR RANCHI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 744
163 | ER1R7 | 80 MVAR B/R AT BIHARSHARIF | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
164 | ER1R8 | 125 MVAR B/R - I AT NEW PURNEA | 125 | ER1 | -- | -- | -- | -- | 2019-05-27 | 20:26 | 2019-06-01 | 0:00 | 99.5667 | 0 | 0 | 0 | 99.5667 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[9 empty] | 2019-05-08 | 20:54 | 2019-05-23 | 6:30 | 345.6 | 0 | 0 | 0 | 345.6 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-01 | 0:00 | 2019-05-03 | 7:26 | 55.4333 | 0 | 0 | 0 | 55.4333 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
| TOTAL | [11 empty] | 500.6 | 0 | 0 | 0 | 500.6
165 | ER1R9 | 125 MVAR B/R - I I AT NEW PURNEA | 125 | ER1 | -- | -- | -- | -- | 2019-05-08 | 21:02 | 2019-05-23 | 6:31 | 345.48 | 0 | 0 | 0 | 345.48 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[9 empty] | 2019-05-01 | 0:00 | 2019-05-03 | 7:29 | 55.4833 | 0 | 0 | 0 | 55.4833 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
| TOTAL | [11 empty] | 345.48 | 0 | 0 | 0 | 345.48
166 | ER1R10 | 3*80 B/R AT GAYA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
167 | ER1R11 | 3*80 B/R II AT GAYA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
168 | ER1R12 | 50 MVAR MTN RB-2 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
169 | ER1R13 | 50 MVAR GAYA L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
170 | ER1R14 | 50 MVAR SSRM-III L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
171 | ER1R15 | 400kV BUS REACTOR-I, GAYA 125MVAR | 125 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-03 | 7:46 | 55.7667 | 0 | 0 | 0 | 55.7667 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 55.7667 | 0 | 0 | 0 | 55.7667
172 | ER1R16 | 400kV BUS REACTOR II,GAYA | 125 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-03 | 7:47 | 55.7833 | 0 | 0 | 0 | 55.7833 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
|  | SUB TOTAL |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 55.7833 | 0 | 0 | 0 | 55.7833
173 | ER1R17 | 765kV BUS REACTOR II, GAYA | 240 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-06 | 13:11 | 133.1833 | 0 | 0 | 0 | 133.1833 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 188.9667 | 0 | 0 | 0 | 188.9667
174 | ER1R18 | 765kV BUS REACTOR1-GAYA | 240 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-06 | 13:07 | 133.1167 | 0 | 0 | 0 | 133.1167 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[9 empty] | 2019-05-22 | 20:42 | 2019-05-26 | 13:29 | 88.78 | 0 | 0 | 0 | 88.78 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-08 | 0:22 | 2019-05-09 | 13:50 | 37.47 | 0 | 0 | 0 | 37.47 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
| TOTAL | [11 empty] | 259.3667 | 0 | 0 | 0 | 259.3667
175 | ER1R19 | 125 MVAR B/R - I AT PSL | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
176 | ER1R20 | 125 MVAR B/R - II AT PASAULI | 125 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
177 | ER1R21 | 63 MVAR GKP - I L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
178 | ER1R22 | 63 MVAR GKP - II L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
179 | ER1R23 | 63 MVAR NPRN - I L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
180 | ER1R24 | 63 MVAR NPRN - II L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
181 | ER1R25 | 63 MVAR MUZ - I L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
182 | ER1R26 | 63 MVAR MUZ- II L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
183 | ER1R27 | 63 MVAR BSF- I L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
184 | ER1R28 | 63 MVAR BSF- II L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
185 | ER1R29 | 50 MVAR BSF- III L/R AT PSL | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
186 | ER1R30 | 50 MVAR BALIA L/R AT PSL | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
187 | ER1R31 | 63 MVAR ALLAHABAD-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
188 | ER1R32 | 63 MVAR SARNATH-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
189 | ER1R33 | 50 MVAR B/R - I AT GAYA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
190 | ER1R34 | 50 MVAR B/R - II AT GAYA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
191 | ER1R35 | 50 MVAR L/R - I AT BANKA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
192 | ER1R36 | 50 MVAR L/R - 2 AT BANKA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
193 | ER1R37 | 80 MVAR B/R - 1 AT BANKA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
194 | ER1R38 | 125 3Ph B/R I AT SASARAM | 125 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-03 | 7:13 | 55.2167 | 0 | 0 | 0 | 55.2167 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 55.2167 | 0 | 0 | 0 | 55.2167
195 | ER1R39 | 125 3Ph B/R II AT SASARAM | 125 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-03 | 7:15 | 55.25 | 0 | 0 | 0 | 55.25 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 110.4667 | 0 | 0 | 0 | 110.4667
196 | ER1R40 | 3*110 MVAR 1 PH B/R - I AT SASARAM | 330 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
197 | ER1R41 | 3*110 MVAR 1 PH L/R - I AT SASARAM (AS B/R) | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
198 | ER1R42 | 125 MVAR BUS REACTOR-1 RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
199 | ER1R43 | 125 MVAR BUS REACTOR-1 PATNA | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
200 | ER1R44 | 80 MVAR PURNEA-1 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
201 | ER1R45 | 80 MVAR PURNEA-2 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
202 | ER1R46 | 125 MVAR BUS REACTOR-2 PATNA | 125 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | 744 | 0 | 744 | 0 | 0 | OMSU |  |  |  |  | 125MVAR B/R-2 IS UNDER S/D FOR SHIFTING OF THE SAME AS L/R IN 400KV PATNA-BARH-2. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 744 | 0 | 744 | 0 | 0
203 | ER1R47 | 125 MVAR BUS REACTOR-1 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
204 | ER1R48 | 125 MVAR BUS REACTOR-2 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
205 | ER1R49 | 3*80MVAR 1 PH L/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
206 | ER1R50 | 3*80MVAR 1 PH B/R - II AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | 2019-05-28 | 15:52 | 2019-05-30 | 9:34 | 41.7 | 0 | 0 | 0 | 41.7 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 41.7 | 0 | 0 | 0 | 41.7
207 | ER1R51 | 80 MVAR B/R - 1 AT LAKHISARAI | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
208 | ER1R52 | 3*80MVAR 1 PH B/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | 2019-05-22 | 16:11 | 2019-05-24 | 13:46 | 45.58 | 0 | 0 | 0 | 45.58 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 45.58 | 0 | 0 | 0 | 45.58
209 | ER1R53 | 63MVAR KISHANGANJ LR-I AT PATNA | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
210 | ER1R54 | 63MVAR KISHANGANJ LR-II AT PATNA | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
211 | ER1R55 | 3*80 MVAR DHRAMJAYGARH LR-II AS BR AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
212 | ER1R56 | 125 MVAR BR-II AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2019-05-07 | 19:54 | 2019-06-01 | 0:00 | 580.1 | 0 | 0 | 0 | 580.1 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[9 empty] | 2019-05-01 | 0:00 | 2019-05-03 | 7:21 | 55.35 | 0 | 0 | 0 | 55.35 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-05 | 22:20 | 2019-05-06 | 14:15 | 15.92 | 0 | 0 | 0 | 15.92 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
| TOTAL | [11 empty] | 651.37 | 0 | 0 | 0 | 651.37
213 | ER1R57 | 125 MVAR BR-I AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2019-05-04 | 9:46 | 2019-05-05 | 13:46 | 28 | 0 | 0 | 0 | 28 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[9 empty] | 2019-05-07 | 19:52 | 2019-06-01 | 0:00 | 580.1333 | 0 | 0 | 0 | 580.1333 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-05 | 22:17 | 2019-05-06 | 14:20 | 16.05 | 0 | 0 | 0 | 16.05 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
[9 empty] | 2019-05-01 | 0:00 | 2019-05-03 | 7:18 | 55.3 | 0 | 0 | 0 | 55.3 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS.
| TOTAL | [11 empty] | 679.4833 | 0 | 0 | 0 | 679.4833
214 | ER1R58 | 125 MVAR BR-III AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
215 | ER1R59 | 125 MVAR BR-I AT Kishanganj | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
216 | ER1R60 | 125 MVAR BR-I AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
217 | ER1R61 | 125 MVAR BR-II AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
218 | ER1R62 | 80 MVAR B/R AT CHAIBASA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
219 | ER1R63 | 3*80 1ph VARANASI L/R-II at Gaya | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
220 | ER1R64 | 125 MVAR B/R - I I AT KISHENGANJ | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
221 | ER1R65 | 80 MVAR B/R - I AT KISHENGANJ | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
222 | ER1R66 | 80 MVAR B/R - II AT KISHENGANJ | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
223 | ER1R67 | 80 MVAR L/R OF 400 kV BARH - GORAKHPUR - I AT GORAKHPUR | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
224 | ER1R68 | 80 MVAR L/R OF 400 kV BARH - GORAKHPUR - II AT GORAKHPUR | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
225 | ER1R69 | 240 MVAR L/R OF 765 kV GAYA - BALIA LINE AT BALIA | 240 | ER1 | -- | -- | -- | --
[5 empty] | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
226 | ER1R70 | 330 MVAR L/R OF 765 kV SASARAM - FATEHPUR LINE AT SASARAM | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
227 | ER1R71 | 330 MVAR L/R OF 765 kV SASARAM - FATEHPUR LINE AT FATEHPUR | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
228 | ER1R72 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - I LINE AT GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
229 | ER1R73 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - I LINE AT VARANASI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
230 | ER1R74 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - II LINE AT GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
231 | ER1R75 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - II LINE AT VARANASI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
232 | ER1R76 | 125MVAR, 400kV BUS REACTOR-III, AT JAMSHEDPUR | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
233 | ER1R76 | 80 MVAR BUS REACTOR AT DALTONGANJ | 80 | ER1 | -- | -- | -- | -- | 2019-05-25 | 20:24 | 2019-06-01 | 0:00 | 147.6 | 0 | 0 | 0 | 147.6 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 147.6 | 0 | 0 | 0 | 147.6
234 | ER1R77 | 125 MVAR BR-IV AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
TOTAL
235 | ER1R78 | 125 MVAR BR-II AT Lakhisarai | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
236 | ER1R79 | 50 MVAR L/R of 400 kV Biharsarif - Sasaram - I AT Biharsharif | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
237 | ER1R80 | 50 MVAR L/R of 400 kV Biharsarif - Lakhisarai - II AT Biharsharif | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
238 | ER1R80 | 80 MVAR L/R of 400 kV Kishanganj- Darbhanga - II AT Kishanganj | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
239 | ER1 ST01 | STATCOM AT New ranchi | -550/+300 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
240 | ER1 ST02 | STATCOM AT Kishanganj | -450/+200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
241 |  | BANKA-BUS REACTOR-2 | -450/+200 | ER1 | -- | -- | -- | -- | 2019-05-01 | 0:00 | 2019-05-03 | 7:50 | 55.8333 | 0 | 0 | 0 | 55.8333 | SVRD |  |  |  |  | HANDT TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
| TOTAL | [11 empty] | 55.8333 | 0 | 0 | 0 | 55.8333

## SOP Jun 2019
Standard of Performance data for the month of June-2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION-I
'ANNEXURE - A
Sr.No. | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | DETAILS OF OUTAGE |  | Total outage in days (1) | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  |  | Category | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | No. of Tower damaged | No.of insulators failed |  | DATE | TIME | DATE | TIME | TOTAL | ISTS Licensee | OTHERS | System constraint/ Natural calmity/ Militancy | Deemed Available
1 | ER1L1 | 132kV ARA-ARA | 1.7 | ER1 | -- | -- | -- | -- | 2019-06-12 | 15:11 | 2019-06-12 | 15:50 | 0.65 | 0 | 0.65 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO B-N FAULT . FD-1.82 KM FROM ARA (BSPTCL JURISDICTION) , FC-3.03KA. | ERPC | 100
[9 empty] | 2019-06-05 | 20:41 | 2019-06-05 | 21:06 | 0.41667 | 0 | 0.41667 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON OPERATION OF OVER CURRENT REALY AT ARA(PG) DUE TO PROBLEM AT BSPTCL END.
[9 empty] | 2019-06-08 | 9:39 | 2019-06-08 | 12:21 | 2.7 | 0 | 2.7 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO CHANGE CT RATIO SETTING AT ARA(PG) END.
| TOTAL | [11 empty] | 3.7667 | 0 | 3.7667 | 0 | 0
2 | ER1L2 | 132kV DEHRI - KUDRA | 40 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
3 | ER1L3 | 132kV KUDRA - SASARAM | 17 | ER1 | -- | -- | -- | -- | 2019-06-13 | 12:24 | 2019-06-13 | 19:01 | 6.6167 | 0 | 6.6167 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR RELAY RETROFITTING WORK AT PUSAULI (UNDER NTAMC PROJECT) | ERPC | 100
| TOTAL | [11 empty] | 6.6167 | 0 | 6.6167 | 0 | 0
4 | ER1L4 | 132kV Dehri-SASARAM | 62 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
5 | ER1L5 | 132kV SASARAM- KARAMNASA | 29 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
6 | ER1L6 | 132kV SASARAM-MOHANIA | 13 | ER1 | -- | -- | -- | -- | 2019-06-14 | 11:05 | 2019-06-14 | 17:23 | 6.3 | 0 | 6.3 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR RELAY RETROFITTING WORK AT PUSAULI (UNDER NTAMC PROJECT). | ERPC | 100
| TOTAL | [11 empty] | 6.3 | 0 | 6.3 | 0 | 0
7 | ER1L7 | 132kV MOHANIA - KARMASA | 11 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
8 | ER1L8 | 132kV DUMRAON-ARA | 1.7 | ER1 | -- | -- | -- | -- | 2019-06-24 | 16:55 | 2019-06-24 | 17:37 | 0.7 | 0 | 0.7 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO R-N FAULT.F.D.=47.57 KM FROM ARA( BSPTCL JURISDICTION) = ,F.C.=1.31KAMP. | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0.7 | 0 | 0.7 | 0 | 0
9 | ER1L9 | 132kV PURNEA-DALKHOLA (LILO PART) | 0.5 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
10 | ER1L10 | 132kV PNR-PRN(LILO PART) | 0.5 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
11 | ER1L11 | 220kV DALKHOLA-PURNEA I | 41 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
12 | ER1L12 | 220kV DALKHOLA-PURNEA II | 41 | ER1 | -- | -- | -- | -- | 2019-06-02 | 4:29 | 2019-06-02 | 4:29 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL FROM BOTH END ON B-N FAULT.F.D.=25.6 KM FROM PURNEA.F.C.=4.34 KAMP.SEVERE CYCLONE AROUND THE AFFECTED AREA. | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
13 | ER1L13 | 220 kV PURNEA - NEW PURNEA-I | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
14 | ER1L14 | 220 kV PURNEA - NEW PURNEA-II | 1 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
15 | ER1L15 | 220kV SASARAM-NADOKHAR | 5 | ER1 |  |  |  |  | 2019-06-11 | 12:08 | 2019-06-11 | 21:18 | 9.1667 | 0 | 0 | 0 | 9.1667 | OSPD |  |  |  |  | S/D TAKEN BY BSPTCL FOR OVER LINE CROSSING WORK | ERPC | 100
| TOTAL | [11 empty] | 9.1667 | 0 | 0 | 0 | 9.1667
16 | ER1L16 | 220kV NADOKHAR -ARRAH I | 107 | ER1 | [19 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
17 | ER1L17 | 220kV SASARAM-ARRAH I | 112 | ER1 |  |  |  |  | 2019-06-12 | 15:10 | 2019-06-12 | 23:00 | 7.8333 | 0 | 0 | 0 | 7.8333 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-26 | 9:33 | 2019-06-26 | 11:26 | 1.8833 | 0 | 0 | 0 | 1.8833 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-22 | 8:58 | 2019-06-22 | 19:43 | 10.75 | 0 | 0 | 0 | 10.75 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-10 | 18:47 | 2019-06-10 | 20:05 | 1.3 | 0 | 0 | 0 | 1.3 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-11 | 11:52 | 2019-06-11 | 21:43 | 9.85 | 0 | 0 | 0 | 9.85 | OSPD |  |  |  |  | S/D TAKEN BY BSPTCL FOR OVER LINE CROSSING WORK
| TOTAL | [11 empty] | 31.6167 | 0 | 0 | 0 | 31.6167
18 | ER1L18 | 220kV ARA-KHAGOL I | 48.44 | ER1 |  |  |  |  | 2019-06-01 | 0:00 | 2019-06-11 | 11:50 | 251.8333 | 0 | 0 | 0 | 251.8333 | LPRD |  |  |  |  | HAND TRIPPED FOR POWER REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-11 | 21:44 | 2019-07-01 | 0:00 | 458.2667 | 0 | 0 | 0 | 458.2667 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 710.1 | 0 | 0 | 0 | 710.1
19 | ER1L19 | 220kV ARA-KHAGOL II | 48.44 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-06-11 | 11:51 | 251.85 | 0 | 0 | 0 | 251.85 | LPRD |  |  |  |  | HAND TRIPPED FOR POWER REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-11 | 21:44 | 2019-07-01 | 0:00 | 458.2667 | 0 | 0 | 0 | 458.2667 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 710.1167 | 0 | 0 | 0 | 710.1167
20 | ER1L20 | 220kV DEHRI-SASARAM | FALSE | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
21 | ER1L21 | 220kV SASARAM-SAHUPURI | 4.88 | ER1 | -- | -- | -- | -- | 2019-06-22 | 5:10 | 2019-06-22 | 9:33 | 4.3833 | 0 | 4.3833 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ON THREE PHASE FAULT.F.D.=110 KM FROM SASARAM (UPPCL JURIDISCTION),F.C.=NA | ERPC | 100
[9 empty] | 2019-06-06 | 10:27 | 2019-06-06 | 16:32 | 6.0833 | 0 | 0 | 0 | 6.0833 | OSFD |  |  |  |  | S/D TAKEN BY UPPCL TO ATTEND HOT SPOT IN LINE CT AT SAHUPURI END.
| TOTAL | [11 empty] | 10.4667 | 0 | 4.3833 | 0 | 6.0833
22 | ER1L22 | 220kV RANCHI-CHANDIL I | 8.06 | ER1 | -- | -- | -- | -- | 2019-06-20 | 14:55 | 2019-06-20 | 16:01 | 1.1 | 0 | 1.1 | 0 | 0 | OMSU |  |  |  |  | TRIPPED IN R-N FAULT.F.D.=93.6 KM FROM RANCHI(JUSNL JURIDISCTION) = ,F.C.=1.969 KAMP. | ERPC | 100
[9 empty] | 2019-06-12 | 19:16 | 2019-06-12 | 19:50 | 0.56667 | 0 | 0.56667 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM CHANDIL END DUE TO B-N FAULT. FD-15.3KM FROM RANCHI , UNDER JUSNL JURISDICTION, AND FC-4.94KA.
| TOTAL | [11 empty] | 1.6667 | 0 | 1.6667 | 0 | 0
23 | ER1L23 | 220kV RANCHI-CHANDIL-II (LILO) | 6.92 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
24 | ER1L24 | 220kV RANCHI-HATIA-I (LILO) | 8.06 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
25 | ER1L25 | 220kV RANCHI-HATIA-II(LILO) | 6.92 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
26 | ER1L26 | 220kV GAYA-DEHRI -I(LILO PART) | 11 | ER1 | [19 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
27 | ER1L27 | 220kV GAYA-BODHGAYA(BSEB) I | 12.7 | ER1 | -- | -- | -- | -- | 2019-06-07 | 11:42 | 2019-06-07 | 13:16 | 1.5667 | 0 | 0 | 0 | 1.5667 | OSPD |  |  |  |  | S/D TAKEN BY BSPTCL FOR MAINTINENCE WORK | ERPC | 100
| TOTAL | [11 empty] | 1.5667 | 0 | 0 | 0 | 1.5667
28 | ER1L28 | 220kV GAYA-DEHRI-II (LILO PART) | 11 | ER1 | -- | -- | -- | -- | 2019-06-29 | 16:00 | 2019-06-29 | 16:25 | 0.41667 | 0 | 0.41667 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM DEHRI END DUE TO B-N FAULT.A/R SUCCESSFUL AT GAYA END.F.D.=48.6 KM FROM GAYA(BSPTCL JURIDISCTION),F.C.=2.501 KA | ERPC | 100
[9 empty] | 2019-06-30 | 12:49 | 2019-06-30 | 12:58 | 0.15 | 0 | 0.15 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM DEHRI END IN R-N FAULT.A/R SUCCESSFUL FROM GAYA END.F.D.=33.3 KM FROM GAYA(BSPTCL JURIDISCTION),F.C.=4.12 KA
| TOTAL | [11 empty] | 0.56667 | 0 | 0.56667 | 0 | 0
29 | ER1L29 | 220kV GAYA-BODHGAYA(BSEB) II | 12.7 | ER1 | -- | -- | -- | -- | 2019-06-12 | 16:34 | 2019-06-12 | 18:40 | 2.1 | 0 | 0 | 0 | 2.1 | LVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[5 empty] | -- | -- | -- | -- | 2019-06-08 | 12:09 | 2019-06-08 | 14:05 | 1.9333 | 0 | 0 | 0 | 1.9333 | OSPD |  |  |  |  | S/D TAKEN BY BSPTCL FOR MAINTENANCE WORK
| TOTAL | [11 empty] | 4.0333 | 0 | 0 | 0 | 4.0333
30 | ER1L30 | 400kV FARAKKA-KAHALGAON I | 95 | [5 empty] | 2019-06-01 | 0:00 | 2019-07-01 | 0:00 | 720 | 0 | 0 | 0 | 720 | LCSD |  |  |  |  | S.OFF FOR TAKING UP BAY UPGRADATION WORK AT FARAKKA END BY ER-2. | ERPC | 100
| TOTAL | [11 empty] | 720 | 0 | 0 | 0 | 720
31 | ER1L31 | 400kV FARAKKA-KAHALGAON II | 95 | [20 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
32 | ER1L32 | 400kV KAHALGAON-FARAKKA III | 95.25 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
33 | ER1L33 | 400kV KAHALGAON-FARAKKA IV | 95.25 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
34 | ER1L34 | 400kV KAHALGAON-LAKHISARAI I | 145 | ER1 | -- | -- | -- | -- | 2019-06-02 | 4:27 | 2019-06-02 | 5:26 | 0.98333 | 0 | 0 | 0.98333 | 0 | LNCC |  |  |  |  | TRIPPED ON B-N FAULT.F.D.=138.4 KM FROM LAKHISARAI,F.C.=2.119 KAMP.OPGW CLIPPING OF 400 KV KAHL-LAKHISARAI-II SNAPPED AT LOC. NO.09 DUE TO SEVERE CYCLONE AROUND THE AFFECTED AREA. | ERPC | 100
| TOTAL | [11 empty] | 0.98333 | 0 | 0 | 0.98333 | 0
35 | ER1L35 | 400kV BIHARSHARIFF-LAKHISARAI I | 89 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
36 | ER1L36 | 400kV KAHALGAON-LAKHISARAI II | 145 | ER1 | -- | -- | -- | -- | 2019-06-25 | 11:28 | 2019-06-25 | 13:17 | 1.8167 | 0 | 0 | 1.8167 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO OPERATION OF ITS L/R PRV TRIP RELAY AT LAKHISARAI DUE TO INGRESS OF MOISTURE IN ITS TERMINAL BOX CAUSED BY CONTINUOUS HEAVY RAIN. | ERPC | 99.85
[9 empty] | 2019-06-02 | 4:10 | 2019-06-02 | 15:24 | 11.2333 | 0 | 0 | 11.2333 | 0 | LNCC |  |  |  |  | TRIPPED ON R-N FAULT. F.D.=117.16 KM FROM LAKHISARAI,F.C.=1.721 KAMP.OPGW CLIPPING OF THE SAID CKT SNAPPED AT LOC NO.09 DUE DUE TO SEVERE CYCLONE AROUND THE AFFECTED AREA.
[9 empty] | 2019-06-26 | 15:26 | 2019-06-26 | 16:26 | 1 | 1 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN FOR CHARGING OF ITS NON SWITCHABLE L/R AT LAKHISARAI.
| TOTAL | [11 empty] | 14.05 | 1 | 0 | 13.05 | 0
37 | ER1L37 | 400kV BIHARSHARIF-LAKHISARAI II | 89 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
38 | ER1L38 | 400kV KAHALGAON-BANKA-I | 53.745 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
39 | ER1L39 | 400KV BIHARSHARIF-BANKA I | 184.54 | ER1 | -- | -- | -- | -- | 2019-06-12 | 16:39 | 2019-06-12 | 17:59 | 1.3333 | 0 | 0 | 1.3333 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO B-N FAULT CAUSED BY SEVERE CYCLONIC STORM AROUND THE FAULT AREA .FD-71.9KM FROM BANKA AND FC-2.4KA. | ERPC | 100
[5 empty] | -- | -- | -- | -- | 2019-06-08 | 17:05 | 2019-06-08 | 19:12 | 2.1167 | 0 | 2.1167 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO CHANGE OLD OBSOLETE RELAY
| TOTAL | [11 empty] | 3.45 | 0 | 2.1167 | 1.3333 | 0
40 | ER1L40 | 400kV KAHALGAON-BANKA-II | 53.745 | ER1 | -- | -- | -- | -- | 2019-06-13 | 11:44 | 2019-06-13 | 18:59 | 7.25 | 0 | 0 | 0 | 7.25 | OSFD |  |  |  |  | HAND TRIPPED BT NTPC KAHALGAON ON EMERGENCY BASIS TO ATTEND HOT SPOT IN ITS R-PH LINE ISOLATOR AT NTPC, KAHALGAON. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
41 | ER1L41 | 400KV BIHARSHARIF-BANKA II | 184.54 | ER1 | -- | -- | -- | -- | 2019-06-12 | 16:39 | 2019-06-12 | 16:52 | 0.21667 | 0 | 0 | 0.21667 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO B-N FAULT CAUSED BY SEVERE CYCLONIC STORM AROUND THE FAULT AREA .FD-184.5KM FROM BANKA AND FC-0.8KA. | ERPC | 100
[9 empty] | 2019-06-14 | 11:33 | 2019-06-14 | 15:00 | 3.45 | 0 | 3.45 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO CHANGE OLD OBSOLETE RELAY
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 3.6667 | 0 | 3.45 | 0.21667 | 0
42 | ER1L42 | 400kV JAMSHEDPUR-CHAIBASA I | 46.14 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 3.6667 | 0 | 3.45 | 0.21667 | 0
43 | ER1L43 | 400kV JAMSHEDPUR-CHAIBASA II | 46.14 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
44 | ER1L44 | 400kV CHAIBASA-ROURKELA I | 131.48 | ER1 | -- | -- | -- | -- | 2019-06-29 | 9:28 | 2019-06-29 | 19:34 | 10.1 | 0 | 10.1 | 0 | 0 | OMSU |  |  |  |  | FOR CRANE MOVEMENT DURING THE ERECTION OF INTERRUPTER AND POLE COLUMN OF NEW CGL MAKE CB OF THE 416R-52CB . S/D TAKEN BY ER-II. | ERPC | 99.57
[9 empty] | 2019-06-12 | 16:59 | 2019-06-12 | 17:26 | 0.45 | 0 | 0 | 0.45 | 0 | LNCC |  |  |  |  | TRIPPED ONLY FROM RKL END DUE TO R-N FAULT CAUSED BY SEVERE THUNDER STORM . FD-50.8KM FROM CHAIBASA AND FC-5.03KA.
[9 empty] | 2019-06-25 | 9:21 | 2019-06-25 | 20:17 | 10.9333 | 0 | 10.9333 | 0 | 0 | OMSU |  |  |  |  | FOR SAFE CRANE MOVEMENT DURING THE DISMANTELING OF INTERRUPTER AND POLE COLUMN OF OLD BHEL MAKE CB OF L/R AT ROURKELA BY ER-II.
[9 empty] | 2019-06-17 | 16:50 | 2019-06-17 | 19:48 | 2.9667 | 2.9667 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND BROKEN JUMPER AT LOC 04.
| TOTAL | [11 empty] | 24.45 | 2.9667 | 21.0333 | 0.45 | 0
45 | ER1L45 | 400kV CHAIBASA-ROURKELA II | 131.48 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
46 | ER1L46 | 400kV MAITHON-KAHALGAON I | 172 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
47 | ER1L47 | 400kV MAITHON-KAHALGAON II | 172 | ER1 | -- | -- | -- | -- | 2019-06-20 | 19:09 | 2019-06-20 | 19:09 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH DUE TO R-N FAULT. FD-46.5KM FROM MAITHONA ND FC-4.29KA | ERPC | 100
[9 empty] | 2019-06-26 | 14:58 | 2019-06-26 | 14:58 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCESSFULLY OPERATED FROM BOTH END DUE TO Y-N FAULT. FD-48KM FROM MAITHON AND FC-4.06 KA.
[9 empty] | 2019-06-28 | 14:10 | 2019-06-28 | 14:10 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO R-N FAULT. FAULT DETAIL FROM MAITHON:-F.D=30.8KM &FC=5.21KA
[9 empty] | 2019-06-02 | 4:44 | 2019-06-02 | 17:53 | 13.15 | 0 | 0 | 13.15 | 0 | LNCC |  |  |  |  | TRIPPED ON Y-N FAULT.F.D.=81.5 KM FROM MAITHON,F.C.=2.76 KAMP.MIDDLE PHASE INSULATOR OF SAID CKT DECAPPED AT LOC NO.37 DUE TO SEVERE CYCLONE,LIGHTNING AND HAEAVY RAIN.
| TOTAL | [11 empty] | 13.15 | 0 | 0 | 13.15 | 0
48 | ER1L48 | 400kV BIHARSHARIF-SASARAM-I | 210 | ER1 | -- | -- | -- | -- | 2019-06-12 | 16:39 | 2019-06-13 | 16:37 | 23.9667 | 0 | 0 | 23.9667 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO R-N FAULT CAUSED BY E/W SNAPPING BETWEEN LOC. NO. 18 & 19 DUE TO SEVERE CYCLONIC STORM AROUND THE FAULT AREA.FD-10.22KM FROM BSF AND FC-14.52KA. | ERPC | 100
| TOTAL | [11 empty] | 37.1167 | 0 | 0 | 37.1167 | 0
49 | ER1L49 | 400kV SASARAM - VARANASI | 143.73 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
50 | ER1L50 | 400kV SARNATH - ALLAHABAD - I | 136 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
51 | ER1L51 | 400kV SASARAM - ALLAHABAD II | 212 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
52 | ER1L52 | 400kV BIHARSHARIF - BALIA -I | 241.79 | ER1 | -- | -- | -- | -- | 2019-06-16 | 10:36 | 2019-06-16 | 20:27 | 9.85 | 0 | 0 | 9.85 | 0 | LNCC |  |  |  |  | S/D TAKEN TO ATTEND E/W DISLOCATION AT LOC NO.210 & REPLACEMENT OF DAMAGED PILOT INSULATOR STRING AT LOC NO.212 CAUSED BY SEVERE CYCLONE,LIGHTNING AND RAIN. | ERPC | 99.88
[9 empty] | 2019-06-12 | 15:24 | 2019-06-12 | 18:18 | 2.9 | 0 | 0 | 2.9 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT CAUSED BY SEVERE CYCLONIC STORM AROUND THE FAULT AREA. FD-101.8KM FROM BSF AND FC-4.24KA.
[9 empty] | 2019-06-05 | 13:30 | 2019-06-05 | 14:21 | 0.85 | 0.85 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND HOT SPOT IN B-PH LINE ISOLATOR AT BIHARSHARIF END.
| TOTAL | [11 empty] | 13.6 | 0.85 | 0 | 12.75 | 0
53 | ER1L53 | 400kV BIHARSHARIF - BALIA -II | 241.79 | ER1 | -- | -- | -- | -- | 2019-06-12 | 15:57 | 2019-06-13 | 19:47 | 27.8333 | 0 | 0 | 27.8333 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO SNAPPING OF E/W BETWEEN LOCATION NO. 211-212 CAUSING BY SEVERE CYCLONIC STORM AROUND THE FAULT AREA. R-N FAULT ,FD-80.03KM FROM BSF. FC-5.4KA. | ERPC | 100
[13 empty] | 27.8333 | 0 | 0 | 27.8333 | 0
54 | ER1L54 | 400kV PATNA - BALIA -I | 195 | ER1 | -- | -- | -- | -- | 2019-06-12 | 15:13 | 2019-06-12 | 17:15 | 2.0333 | 0 | 0 | 2.0333 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO R-N FAULT CAUSED BY SEVERE CYCLONIC STORM AROUND THE FAULT AREA.FD-74.56KM FROM PATNA AND FC-5.559KA. | ERPC | 100
[13 empty] | 2.0333 | 0 | 0 | 2.0333 | 0
55 | ER1L55 | 400kV PATNA - BALIA -II | 195 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
56 | ER1L56 | 400kV PATNA - BALIA -III | 185 | ER1 | -- | -- | -- | -- | 2019-06-21 | 8:04 | 2019-06-21 | 20:40 | 12.6 | 0 | 12.6 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN BY NR-3 FOR REPLACEMENT OF PORCELAIN INSULATORS BY POLYMER INSULATORS. | ERPC | 98.91
[9 empty] | 2019-06-20 | 8:12 | 2019-06-20 | 20:56 | 12.7333 | 0 | 12.7333 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN BY NR-3 FOR REPLACEMENT OF PORCELAIN INSULATORS BY POLYMER INSULATORS.
[9 empty] | 2019-06-22 | 8:26 | 2019-06-22 | 21:14 | 12.8 | 0 | 12.8 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR REPLACEMENT OF PORCELIEN INSULATOR WITH POLYMER INSULATOR.
[9 empty] | 2019-06-24 | 11:35 | 2019-06-24 | 18:59 | 7.4 | 7.4 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN BY NR-3 TO ATTEND HOT SPOT IN LINE ISOILATOR OF THE SAID LINE AT BALLIA END.
| TOTAL | [11 empty] | 45.5333 | 7.4 | 38.1333 | 0 | 0
57 | ER1L57 | 400kV PATNA - BALIA -IV | 185 | ER1 | -- | -- | -- | -- | 2019-06-12 | 15:11 | 2019-06-13 | 13:50 | 22.65 | 0 | 0 | 22.65 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO R-N FAULT CAUSED BY SEVERE CYCLONIC STORM AROUND THE FAULT AREA. FD-86.5KM FROM PATNA AND FC-3.99KA. | ERPC | 100
[9 empty] | 2019-06-18 | 8:03 | 2019-06-18 | 20:52 | 12.8167 | 0 | 12.8167 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER BY NR-3.
[9 empty] | 2019-06-16 | 10:35 | 2019-06-16 | 10:51 | 0.26667 | 0 | 0.26667 | 0 | 0 | OMSU |  |  |  |  | TO FACILITATE S/D OF 400 BSF-BALIA-I DUE TO OUTAGE OF MAIN BAY OF 400 KV PATNA-BALLIA-IV AT BALLIA END. IT IS TO BE NOTED THAT 400 KV PATNA-BALLIA-IV AND 400 KV BIHARSHARIF BALLIA-I ARE IN THE SAME DIA AT BALLIA END.
[9 empty] | 2019-06-16 | 19:05 | 2019-06-16 | 20:36 | 1.5167 | 0 | 1.5167 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO FACILITATE CHARGIN G OF 400 KV BIHARSHARIF-BALLIA-I.
[9 empty] | 2019-06-19 | 8:06 | 2019-06-19 | 18:34 | 10.4667 | 0 | 10.4667 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN BY NR-3 FOR REPLACEMENT OF PORCELAIN INSULATORS BY POLYMER INSULATORS
[9 empty] | 2019-06-17 | 10:01 | 2019-06-17 | 21:02 | 11.0167 | 0 | 11.0167 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER BY NR-3.
[13 empty] | 58.7333 | 0 | 36.0833 | 22.65 | 0
58 | ER1L58 | 400kV BIHARSHARIF-SASARAM-II | 210 | ER1 | -- | -- | -- | -- | 2019-06-21 | 23:03 | 2019-06-22 | 0:39 | 1.6 | 0 | 0 | 1.6 | 0 | GOVC |  |  |  |  | TRIPPED ON O/V PROTECTION AT BSF END. DT RECEIVED AT SASARAM END. | ERPC | 100
| TOTAL | [11 empty] | 1.6 | 0 | 0 | 1.6 | 0
59 | ER1L59 | 400KV PATNA-BARH III | 68.66 | ER1 | -- | -- | -- | -- | 2019-06-16 | 9:04 | 2019-06-18 | 1:18 | 40.2333 | 0 | 0 | 0 | 40.2333 | LCSD |  |  |  |  | S/D TAKEN TO FACILITATE REALIGNMENT WORKS OF 400 KV D/C BARH-MOTIHARI TL DUE TO CONSTRUCTION OF BARH BYPASS NHAI. | ERPC | 100
[9 empty] | 2019-06-27 | 9:50 | 2019-06-27 | 20:53 | 11.05 | 0 | 0 | 0 | 11.05 | OSPD |  |  |  |  | S/D TAKEN BY NTPC BARH FOR SCADA UPGRADATION WORK AT NTPC BARH END.
| TOTAL | [11 empty] | 51.2833 | 0 | 0 | 0 | 51.2833
60 | ER1L60 | 400KV PATNA-BARH IV | 68.66 | ER1 | -- | -- | -- | -- | 2019-06-16 | 9:05 | 2019-06-18 | 1:19 | 40.2333 | 0 | 0 | 0 | 40.2333 | LCSD |  |  |  |  | S/D TAKEN TO FACILITATE REALIGNMENT WORKS OF 400 KV D/C BARH-MOTIHARI TL DUE TO CONSTRUCTION OF BARH BYPASS NHAI. | ERPC | 100
[9 empty] | 2019-06-06 | 12:06 | 2019-06-07 | 20:49 | 32.7167 | 0 | 0 | 0 | 32.7167 | OSFD |  |  |  |  | S/D TAKEN TO ATTEND HOT SPOT IN LINE CT AT NTPC BARH END.S/D TAKEN BY NTPC BARH.
[13 empty] | 72.95 | 0 | 0 | 0 | 72.95
61 | ER1L61 | 400KV MUZAFFARPUR-BIHARSHARIF I | 133.3 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC
[14 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC
[13 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC
62 | ER1L62 | 400KV MUZAFFARPUR-BIHARSHARIF II | 133.3 | ER1 | -- | -- | -- | -- | 2019-06-30 | 12:22 | 2019-06-30 | 12:22 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO R-N FAULT. FD-20.25KM FROM BIHARSHARIF AND FC-11.305KA | ERPC | 100
[9 empty] | 2019-06-12 | 17:12 | 2019-06-13 | 17:07 | 23.9167 | 0 | 0 | 23.9167 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO R-N FAULT (TOP PHASE INSULATOR DE-CAP) CAUSED BY SEVERE THUNDER STORM AROUND THE FAULT AREA. FD-27.42KM FROM BSF AND FC-8.872KA.
[13 empty] | 23.9167 | 0 | 0 | 23.9167 | 0
63 | ER1L63 | 400kV KAHALGAON-BARH I | 217.24 | ER1 |  |  |  |  | 2019-06-11 | 9:39 | 2019-06-11 | 20:53 | 11.2333 | 0 | 0 | 0 | 11.2333 | OSPD |  |  |  |  | S/D TAKEN BY NTPC, BARH FOR UPGRADTION &TESTING OF SCADA AT BARH. | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
[13 empty] | 11.2333 | 0 | 0 | 0 | 11.2333
64 | ER1L64 | 400kV KAHALGAON-BARH II | 217.24 | ER1 | -- | -- | -- | -- | 2019-06-12 | 9:48 | 2019-06-12 | 21:11 | 11.3833 | 0 | 0 | 0 | 11.3833 | OSPD |  |  |  |  | S/D TAKEN BY NTPC BARH FOR UPGRADATION AND TESTING OF SCADA . | ERPC | 100
| TOTAL | [11 empty] | 11.3833 | 0 | 0 | 0 | 11.3833
65 | ER1L65 | 400kV PATNA-BARH I | 93.04 | ER1 | -- | -- | -- | -- | 2019-06-13 | 9:46 | 2019-06-13 | 13:26 | 3.6667 | 0 | 0 | 0 | 3.6667 | OSPD |  |  |  |  | S/D TAKEN BY NTPC/BARH FOR UPGRADATION AND TESTING OF SCADA AT NTPC/BARH. | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0
[13 empty] | 3.6667 | 0 | 0 | 0 | 3.6667
66 | ER1L66 | 400kV PATNA-BARH II | 93.04 | ER1 | -- | -- | -- | -- | 2019-06-14 | 10:10 | 2019-06-14 | 20:07 | 9.95 | 0 | 0 | 0 | 9.95 | OSPD |  |  |  |  | S/D TAKEN BY NTPC/BARH FOR UPGRADATION AND TESTING OF SCADA AT NTPC/BARH. | ERPC | 100
[13 empty] | 9.95 | 0 | 0 | 0 | 9.95
67 | ER1L67 | 400kV MAITHON-RANCHI I | 199.81 | ER1 | -- | -- | -- | -- | 2019-06-12 | 19:51 | 2019-06-12 | 19:51 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO B-N FAULT. FD-50.9KM FROM RANCHI AND FC-6.41KA. | ERPC | 100
[9 empty] | 2019-06-13 | 15:37 | 2019-06-14 | 2:29 | 10.8667 | 0 | 0 | 10.8667 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT, F.D=14.5 KM FROM RANCHI, F.C=11.49 KA. IT WAS TRIPPED DUE TO SNAPPING OF EARTHWIRE OF 400KV RANCHI-RAGHUNATHPUR BETWEEN LOC NO.510-511 WHICH FALLED ON RANCHI-MAITHON CKT-I.
| TOTAL | [11 empty] | 10.8667 | 0 | 0 | 10.8667 | 0
68 | ER1L68 | 400kV RAGHUNATHPUR-MAITHON | 44.02 | ER1 | -- | -- | -- | -- | 2019-06-29 | 1:41 | 2019-06-29 | 1:58 | 0.28333 | 0 | 0.28333 | 0 | 0 | OMSU |  |  |  |  | TRIPPED FROM RAGHUNATHPUR END ONLY DUE TO R-N FAULT , FD-24.1KM FROM MAITHON AND FC-8.12KA. | ERPC | 100
| TOTAL | [11 empty] | 0.28333 | 0 | 0.28333 | 0 | 0
69 | ER1L69 | 400kV RANCHI-RAGHUNATHPUR I(LILO of Maithon-Ranch -II at Raghunathpur) | 155.79 | ER1 | -- | -- | -- | -- | 2019-06-30 | 18:24 | 2019-06-30 | 18:24 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL DUE TO Y-N FAULT.F.D.=129.7 KM FROM RANCHI,F.C.=2.83 KAMP.THERE WAS HEAVY RAIN AND LIGHTINING AROUND THE AFFECTED AREA. | ERPC | 100
[9 empty] | 2019-06-13 | 18:53 | 2019-06-14 | 2:00 | 7.1167 | 0 | 0 | 7.1167 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR RECTIFICATION OF SNAPPED EARTH WIRE BETWEEN LOC NO.510-511 DUE TO SEVER CYCLONE AROUND THE AFFECTED AREA.
[13 empty] | 7.1167 | 0 | 0 | 7.1167 | 0
70 | ER1L70 | 400kV MAITHON RB-RANCHI I | 187.64 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
71 | ER1L71 | 400kV MAITHON RB-RANCHI II | 187.64 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
72 | ER1L72 | 400kV RANCHI-ROURKELA I | 144.45 | ER1 | -- | -- | -- | -- | 2019-06-12 | 20:13 | 2019-06-12 | 20:13 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO B-N FAULT. FD-148KM FROM RANCHI ,AND FC-2.69KA. | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
73 | ER1L73 | 400kV RANCHI-ROURKELA II | 144.45 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
74 | ER1L74 | 400kV BIHARSHARIF-KODERMA I | 110.69 | ER1 |  |  |  |  | 2019-06-30 | 13:21 | 2019-06-30 | 13:21 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH END DUE TO B-N FAULT. FD-123.6KM FROM KODERMA AND FC-7.11KA. | ERPC | 100
[9 empty] | 2019-06-27 | 7:35 | 2019-06-27 | 9:19 | 1.7333 | 0 | 1.7333 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO O/V AT DVC KODERMA END.DT RECEIVED AT BIHARSHARIF END.
[9 empty] | 2019-06-24 | 8:46 | 2019-06-24 | 19:05 | 10.3167 | 0 | 0 | 0 | 10.3167 | OSPD |  |  |  |  | S/D TAKEN FOR PREVENTIVE MAINTINENCE WORK BY DVC AT DVC KODERMA END.
[13 empty] | 12.05 | 0 | 1.7333 | 0 | 10.3167
75 | ER1L75 | 400kV BIHARSHARIF-KODERMA II | 110.69 | ER1 | -- | -- | -- | -- | 2019-06-21 | 8:57 | 2019-06-21 | 19:03 | 10.1 | 0 | 0 | 0 | 10.1 | OSPD |  |  |  |  | S/D TAKEN BY DVC KODERMA FOR PREVENTIVE MAINTENANCE . | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
| TOTAL | [11 empty] | 10.1 | 0 | 0 | 0 | 10.1
76 | ER1L76 | 400kV BIHARSHARIF-VARANASI - I | 321 | ER1 | -- | -- | -- | -- | 2019-06-12 | 16:42 | 2019-06-12 | 18:57 | 2.25 | 0 | 0 | 2.25 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO B-N FAULT CAUSED BY SEVERE THUNDERSTORM. FD-10.00KM FROM BSF AND FC-15.7KA. | ERPC | 100
[13 empty] | 2.25 | 0 | 0 | 2.25 | 0
77 | ER1L77 | 400kV BIHARSHARIF-VARANASI - II | 321 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
78 | ER1L78 | 765kV GAYA-BALLIA | 237.7 | ER1 | -- | -- | -- | -- | 2019-06-04 | 10:35 | 2019-06-04 | 19:41 | 9.1 | 0 | 0 | 9.1 | 0 | LNCC |  |  |  |  | S/D TAKEN TO RECTIFY 02 NOS. BENT TOWER ANGLE MEMBER AT LOC NO.232 CAUSED BY SEVERE CYCLONIC STORM. | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 9.1 | 0 | 0 | 9.1 | 0
79 | ER1L79 | 400kV JAMSHEDPUR(DVC)-BARIPADA | 108.29 | ER1 | -- | -- | -- | -- |  |  |  |  | NA | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
80 | ER1L80 | 400kV BARIPADA-JAMSHEDPUR II | 140.28 | ER1 | -- | -- | -- | -- | 2019-06-29 | 14:52 | 2019-06-29 | 14:52 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL DUE TO B-N FAULT.F.D.=141 KM FROM JSR,F.C.=3.72 KAMP. | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
81 | ER1L81 | 400kV JAMSHEDPUR-JAMSHEDPUR(DVC) | 108.29 | ER1 | -- | -- | -- | -- | 2019-06-07 | 10:27 | 2019-06-07 | 13:58 | 3.5167 | 0 | 0 | 0 | 3.5167 | OSPD |  |  |  |  | S/D TAKEN BY TISCO TO ATTEND HOT SPOT IN LINE ISOLATOR AT TISCO END. | ERPC | 100
| TOTAL | [11 empty] | 3.5167 | 0 | 0 | 0 | 3.5167
82 | ER1L82 | SASARAM - NABINAGAR I | 81.65 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
83 | ER1L83 | SASARAM - NABINAGAR II | 81.65 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
84 | ER1L84 | 400kV MOTIHARI - GORAKHPUR - I (LILO BARH-GKP-1) | 153.2 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
85 | ER1L85 | 400kV MOTIHARI - GORAKHPUR - II (LILO BARH-GKP-2) | 153.2 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
86 | ER1L86 | 400kV BARH-MOTIHARI- I (LILO BARH-GKP-1) | 199.8 | ER1 | -- | -- | -- | -- | 2019-06-13 | 13:30 | 2019-07-01 | 0:00 | 418.5 | 0 | 0 | 0 | 418.5 | LCSD |  |  |  |  | S/D TAKEN FOR REALIGNMENT WORKS OF 400KV D/C BARH- MOTIHARI-D/C TRANSMISSION LINE DUE TO CONSTRUCTION OF BARH BYPASS BY NHAI. | ERPC | 100
| TOTAL | [11 empty] | 418.5 | 0 | 0 | 0 | 418.5
87 | ER1L87 | 400kV BARH-MOTIHARI- II (LILO BARH-GKP-2) | 199.8 | ER1 | -- | -- | -- | -- | 2019-06-13 | 11:55 | 2019-07-01 | 0:00 | 420.0833 | 0 | 0 | 0 | 420.0833 | LCSD |  |  |  |  | S/D TAKEN FOR REALIGNMENT WORKS OF 400KV BARH- MOTIHARI-D/C TRANSMISSION LINE DUE TO CONSTRUCTION OF BARH BYPASS BY NHAI. | ERPC | 100
| TOTAL | [11 empty] | 420.0833 | 0 | 0 | 0 | 420.0833
88 | ER1L88 | 400KV GAYA - KODERMA - II | 118.2 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-06-08 | 21:46 | 189.7667 | 0 | 0 | 189.7667 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION &RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONE. | ERPC | 100
[13 empty] | 189.7667 | 0 | 0 | 189.7667 | 0
89 | ER1L89 | 400kV GAYA-MAITHON II | 277 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-06-08 | 21:49 | 189.8167 | 0 | 0 | 189.8167 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION & RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONE. | ERPC | 100
[13 empty] | 189.8167 | 0 | 0 | 189.8167 | 0
90 | ER1L90 | 400kV GAYA-KODERMA-I | 118.2 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-06-08 | 21:45 | 189.75 | 0 | 0 | 189.75 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION &RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONE. | ERPC | 100
| TOTAL | [11 empty] | 189.75 | 0 | 0 | 189.75 | 0
91 | ER1L91 | 400kV GAYA-MAITHON-I | 277 | ER1 |  |  |  |  | 2019-06-15 | 16:38 | 2019-06-15 | 16:38 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFULLY OPERATED FROM BOTH ENDS DUE Y-N FAULT. FD-6.7KM FROM MAITHON AND FC-13.33KA. | ERPC | 100
[9 empty] | 2019-06-01 | 0:00 | 2019-06-08 | 21:48 | 189.8 | 0 | 0 | 189.8 | 0 | LNCC |  |  |  |  | S/D TAKEN FOR DESTRINGING,ERECTION & RESTRINGING OF BULGED MULTI CKT TOWER AT LOC NO-80,CAUSED BY SEVERE LOCALISED CYCLONE.
[9 empty] | 2019-06-30 | 11:43 | 2019-06-30 | 12:03 | 0.33333 | 0 | 0 | 0.33333 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT.F.D.=114.6 KM FROM GAYA,F.C.=2.76 KAMP.THERE WAS HAEAVY LIGTNING AND RAIN AROUND THE AFFECTED AREA
[9 empty] | 2019-06-11 | 19:19 | 2019-06-11 | 19:45 | 0.43333 | 0 | 0 | 0.43333 | 0 | LNCC |  |  |  |  | TRIPPED ON R-B FAULT DURING SEVERE CYCLONE IN AND AROUND THE FAULT AREA. F.D.= 186.5 KM FROM GAYA WITH F.C.= Ir=3.31 KA AN
[9 empty] | 2019-06-28 | 22:34 | 2019-06-28 | 23:24 | 0.83333 | 0 | 0 | 0.83333 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO Y-N FAULT. FD=68.2 KM FROM GAYA, F.C=4.54KA .THERE WAS HAEAVY LIGTNING AND RAIN AROUND THE AFFECTED AREA
[13 empty] | 191.4 | 0 | 0 | 191.4 | 0
92 | ER1L92 | 400kV RANCHI-NEW RANCHI II | 78.6 | ER1 | -- | -- | -- | -- | 2019-06-25 | 16:40 | 2019-06-25 | 16:40 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCESSFULLY OPERATED FROM BOTH END DUE TO R-N FAULT. FD-2.3KM FROM RANCHI AND FC-17.81KA. | ERPC | 100
[9 empty] | 2019-06-13 | 15:37 | 2019-06-13 | 17:00 | 1.3833 | 0 | 0 | 1.3833 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO B-N FAULT CAUSED BY SEVERE THUNDER STORM AROUND FAULT AREA, F.D=24.8 KM FROM RANCHI, F.C=12 KA.
[9 empty] | 2019-06-28 | 10:39 | 2019-06-29 | 11:02 | 24.3833 | 0 | 24.3833 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO FACILITATE S/D OF BUS-II AT RANCHI
[13 empty] | 25.7667 | 0 | 24.3833 | 1.3833 | 0
93 | ER1L93 | 400kV RANCHI-NEW RANCHI I | 78.6 | ER1 | -- | -- | -- | -- | 2019-06-13 | 15:37 | 2019-06-13 | 16:58 | 1.35 | 0 | 0 | 1.35 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO R-N FAULT CAUSED BY SEVERE THUNDER STORM AROUND THE FAULT AREA, F.D=19.6 KM FROM RANCHI, F.C=11.60 KA. | ERPC | 100
[9 empty] | 2019-06-28 | 10:39 | 2019-06-29 | 3:23 | 16.7333 | 0 | 16.7333 | 0 | 0 | OMSU |  |  |  |  | S/D TAKEN TO FACILITATE S/D OF 400 KV BUS-II AT RANCHI.
[13 empty] | 18.0833 | 0 | 16.7333 | 1.35 | 0
94 | ER1L94 | 400kV RANCHI-NEW RANCHI III | 78.6 | ER1 | -- | -- | -- | -- | 2019-06-03 | 16:49 | 2019-06-03 | 16:49 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL FROM BOTH END ON R-N FAULT.F.D.=49 KM FROM NEW RANCHI = ,F.C.=6.09 KAMP. THERE WAS SEVERE CYCLONE AROUND THE AFFECTED AREA. | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
95 | ER1L95 | 400kV RANCHI-NEW RANCHI IV | 78.6 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
96 | ER1L96 | 400 KV BOKARO-KODERMA-I | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
97 | ER1L97 | 400 KV BOKARO-KODERMA-II | 100 | ER1 | -- | -- | -- | -- | 2019-06-16 | 18:05 | 2019-06-16 | 22:15 | 4.1667 | 4.1667 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TAKEN TO ATTEND HOT SPOT AT LOC. NO. 112 | ERPC | 99.42
[13 empty] | 4.1667 | 4.1667 | 0 | 0 | 0
98 | ER1L98 | 400 KVPATNA - KISHANGANJ -I | 346.72 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-07-01 | 0:00 | 720 | 0 | 0 | 720 | 0 | LNCC |  |  |  |  | TRIPPED ON B-N FAULT, ONE TOWER BADLY DAMAGED IN GANGA RIVER AT LOC. - 129/0 DUE TO HEAVY FLOOD. | ERPC | 100
[13 empty] | 720 | 0 | 0 | 720 | 0
99 | ER1L99 | 400 KVPATNA - KISHANGANJ -II | 346.72 | ER1 | -- | -- | -- | -- | 2019-06-02 | 3:34 | 2019-06-02 | 3:34 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL FROM BOTH END ON R-N FAULT.F.D.=280.1 KM FROM PATNA = ,F.C.=2.002 KAMP.THERE WAS SEVERE CYCLONE AROUND THE AFFECTED AREA. | ERPC | 100
[9 empty] | 2019-06-11 | 2:57 | 2019-06-11 | 2:57 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | A/R SUCCESSFUL FROM BOTH END ON RN FAULT.F.D.=344.4 KM FROM PATNA = ,F.C.=1.63 KAMP.
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
100 | ER1L100 | 765 KV GAYA - VARANASI - II |  | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0
101 | ER1L101 | 400 KV GAYA - CHANDAWA - I | 118 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
102 | ER1L104 | 400 KV GAYA - CHANDAWA - II | 118 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
103 | ER1L105 | 400 KV NEW RANCHI - CHANDAWA - I | 68 | ER1 | -- | -- | -- | -- | 2019-06-02 | 22:59 | 2019-06-02 | 22:59 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTO RECLOSED ON R-N FAULT. F.D.= 47.56 KM FROM NRNC WITH F.C.= 3.644 KA | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
104 | ER1L104 | 400 KV NEW RANCHI - CHANDAWA - II | 68 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
105 | ER1L105 | 765KV SASARAM - FATEHPUR | 354.7 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[14 empty] | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
106 | ER1L106 | 765KV GAYA - VARANASI -I | 147.81 | ER1 | -- | -- | -- | -- | 2019-06-20 | 7:23 | 2019-06-20 | 7:23 | 0 | 0 | 0 | 0 | 0 | LART |  |  |  |  | AUTO RECLOSED ON B-N FAULT. F.D.=203 KM FROM GAYA(NR-3 JURISDICTION) F.C.=2.65 KA | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
107 | ER1L107 | 400 KVSASARAM - DALTONGANJ - I | 196.186 | ER1 | -- | -- | -- | -- | 2019-06-03 | 9:52 | 2019-06-03 | 13:28 | 3.6 | 0 | 0 | 3.6 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO OPERATION OF ITS L/R PRV TRIP RELAY AT DALTONGANJ DUE TO INGRESS OF MOISTURE IN ITS TERMINAL BOX CAUSED BY CONTINUOUS HEAVY RAIN. | ERPC | 100
[13 empty] | 3.6 | 0 | 0 | 3.6 | 0
108 | ER1L108 | 400 KV SASARAM - DALTONGANJ - II | 196.186 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
109 | ER1L109 | 400KV GAYA NABINAGAR-1 | 354.7 | ER1 | -- | -- | -- | -- | 2019-06-15 | 10:58 | 2019-06-15 | 22:23 | 11.4167 | 0 | 0 | 0 | 11.4167 | LCSD |  |  |  |  | FOR UP RATING OF EXITING ISOLATOR OF CURRENT RATING 2000A AS TO BE UP RATED WITH 3000A AT GAYA | ERPC | 100
[9 empty] | 2019-06-22 | 14:18 | 2019-06-22 | 19:58 | 5.6667 | 0 | 0 | 5.6667 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO FAILURE OF R PHASE LA BY SEVERE LIGHTNING &THUNDERSTORM AT GAYA END
| TOTAL | [11 empty] | 17.0833 | 0 | 0 | 5.6667 | 11.4167
110 | ER1L110 | 400KV GAYA NABINAGAR-2 | [6 empty] | 2019-06-22 | 14:18 | 2019-06-22 | 15:32 | 1.2333 | 0 | 0 | 1.2333 | 0 | LNCC |  |  |  |  | TRIPPED DUE TO LA FAIL OF CKT-1 AT GAYA DURING SEVERE LIGHTNING &THUNDER STORM | ERPC | 100
| TOTAL | [11 empty] | 1.2333 | 0 | 0 | 1.2333 | 0
111 | ER1T1 | 400/220kV ICT1 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2019-06-03 | 10:58 | 2019-06-03 | 13:50 | 2.8667 | 0 | 0 | 0 | 2.8667 | OSPD |  |  |  |  | S/D TAKEN BY BSPTCL FOR MAITINENCE WORK IN 220 KV SIDE | ERPC | 100
[13 empty] | 2.8667 | 0 | 0 | 0 | 2.8667
112 | ER1T2 | 400/220kV ICT2 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2019-06-12 | 16:42 | 2019-06-12 | 17:38 | 0.93333 | 0 | 0.93333 | 0 | 0 | OMSU |  |  |  |  | TRIPPED DUE TO INTERTRIP DUE TO PROBLEM IN BSPTCL END. | ERPC | 100
[13 empty] | 0.93333 | 0 | 0.93333 | 0 | 0
113 | ER1T3 | 400/220kV ICT3 BIHARSHARIFF | 315 | ER1 | -- | -- | -- | -- | 2019-06-12 | 16:42 | 2019-06-12 | 17:28 | 0.76667 | 0 | 0.76667 | 0 | 0 | OMSU |  |  |  |  | TRIPPED ONLY FROM BSPTCL END DUE TO PROBLEM IN BSPTCL END. | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0.76667 | 0 | 0.76667 | 0 | 0
114 | ER1T4 |  | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
115 | ER1T5 | 400/220kV ICT2 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
116 | ER1T6 | 400/220kV ICT1 NEW PURNEA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
117 | ER1T7 | 400/220kV ICT2 NEW PURNEA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[13 empty] | 0 | 0 | 0 | 0 | 0
118 | ER1T8 | 400/220kV ICT1 SASARAM | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
119 | ER1T9 | 400/220kV ICT2 SASARAM | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
120 | ER1T10 | 400/220kV ICT1 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
121 | ER1T11 | 400/220kV ICT2 MUZ | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
122 | ER1T12 | 400/220kV ICT1 PATNA | 315 | ER1 | -- | -- | -- | -- | 2019-06-30 | 9:03 | 2019-06-30 | 17:37 | 8.5667 | 0 | 0 | 0 | 8.5667 | SCSD |  |  |  |  | S/D TAEKN FOR WIRING AND STABILITY TEST OF DIFFERNTIAL &OVER CURRENT REALY OF ITS TIE BAY IN ORDER TO COMMISSIONING | ERPC | 100
[13 empty] | 8.5667 | 0 | 0 | 0 | 8.5667
123 | ER1T13 | 400/220kV ICT2 PATNA | 315 | ER1 | -- | -- | -- | -- | 2019-06-28 | 13:05 | 2019-06-28 | 14:58 | 1.8833 | 1.8833 | 0 | 0 | 0 | OSPT |  |  |  |  | S/D TO ATTEND HOT SPOT IN ITS 400KV SIDE T- ISOLATOR (B PHASE). | ERPC | 99.73
[5 empty] | -- | -- | -- | --
[13 empty] | 1.8833 | 1.8833 | 0 | 0 | 0
124 | ER1T14 | 400/220kV ICT1 RNC | 315 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
125 | ER1T15 | 400/220kV ICT2 RNC | 315 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
126 | ER1T16 | 400/220kV ICT1 GAYA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
127 | ER1T17 | 400/220kV ICT2 GAYA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
128 | ER1T17A | 400/220kV ICT3 GAYA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
129 | ER1T18 | 400/132kV ICT1 BANKA | 200 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
130 | ER1T19 | 400/132kV ICT 2 BANKA | 200 | ER1 | -- | -- | -- | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
[13 empty] | 0 | 0 | 0 | 0 | 0
131 | ER1T20 | 765/400kV ICT1 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
132 | ER1T21 | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
133 | ER1T22 | 765/400kV ICT3 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
134 | ER1T22A | 765/400kV ICT2 GAYA | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
135 | ER1T23 | 220/132kV ICT1 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
136 | ER1T24 | 220/132kV ICT2 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
137 | ER1T25 | 220/132kV ICT3 PRN | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
138 | ER1T26 | 220/132kV ICT1 ARRAH | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
139 | ER1T27 | 220/132kV ICT2 ARRAH | 100 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
140 | ER1T28 | 765/400/220 kV ICT 1 SASARAM | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
141 | ER1T29 | 765/400kV ICT1 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
142 | ER1T30 | 765/400kV ICT2 RANCHI(NEW) | 1500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | SUB TOTAL |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
143 | ER1T31 | 400/132kV ICT1 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
144 | ER1T32 | 400/132kV ICT 2 LAKHISARAI | 200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
145 | ER1T33 | 400/220kV ICT 2 CHAIBASA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
146 | ER1T34 | 400/220kV ICT 1 CHAIBASA | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
147 | ER1T35 | 220/132kV ICT3 ARRAH | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
148 | ER1T36 | 400/220kV ICT3 MUZZAFERPUR | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
149 | ER1T36 | 400/220kV ICT2 KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
150 | ER1T37 | 400/220 kV ICT1 AT KISHANGANJ | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
151 | ER1T38 | 400/220kV ICT3 JAMSHEDPUR | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
152 | ER1T39 | 400/220kV ICT3 PATNA | 500 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
153 | ER1T40 | 400/220kV ICT1 DALTONGANJ | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
154 | ER1T41 | 220/132 kV ICT1 DALTONGANJ | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
155 | ER1T42 | 220/132 kV ICT2 DALTONGANJ | 160 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
156 | ER1T43 | 400/220kV ICT2 DALTONGANJ | 315 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
157 | ER1R1 | 50 MVAR B/R-1 AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
158 | ER1R2 | 50 MVAR B/R-1 AT JMASHEDPUR | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
159 | ER1R3 | 50 MVAR BUS REACTOR-II, JAMSHEDPUR II | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
160 | ER1R4 | 400kV BUS REACTOR MUZAFFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
161 | ER1R5 | 80 MVAR B/R AT PATNA | 80 | ER1 | -- | -- | -- | -- | 2019-06-01 | 11:02 | 2019-07-01 | 0:00 | 708.9667 | 0 | 0 | 0 | 708.9667 | SCSD |  |  |  |  | S/D TAKEN FOR CONSTRUCTION ACTIVITY FOR NAVINAGAR BAY UNDER NAVINAGAR-2 PROJECT. | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 708.9667 | 0 | 0 | 0 | 708.9667
162 | ER1R6 | 400kV BUS REACTOR RANCHI | 80 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 708.9667
163 | ER1R7 | 80 MVAR B/R AT BIHARSHARIF | 80 | ER1 | -- | -- | -- | -- | 2019-06-29 | 19:57 | 2019-07-01 | 0:00 | 28.05 | 0 | 0 | 0 | 28.05 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 28.05 | 0 | 0 | 0 | 28.05
164 | ER1R8 | 125 MVAR B/R - I AT NEW PURNEA | 125 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-06-11 | 6:56 | 246.9333 | 0 | 0 | 0 | 246.9333 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-16 | 20:42 | 2019-06-18 | 9:12 | 36.5 | 0 | 0 | 0 | 36.5 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-23 | 20:05 | 2019-07-01 | 0:00 | 171.9167 | 0 | 0 | 0 | 171.9167 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 455.35 | 0 | 0 | 0 | 455.35
165 | ER1R9 | 125 MVAR B/R - I I AT NEW PURNEA | 125 | ER1 | -- | -- | -- | -- | 2019-06-06 | 21:47 | 2019-06-10 | 13:45 | 87.9667 | 0 | 0 | 0 | 87.9667 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-23 | 20:06 | 2019-07-01 | 0:00 | 171.9 | 0 | 0 | 0 | 171.9 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 87.9667 | 0 | 0 | 0 | 87.9667
166 | ER1R10 | 3*80 B/R AT GAYA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
167 | ER1R11 | 3*80 B/R II AT GAYA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
168 | ER1R12 | 50 MVAR MTN RB-2 L/R AT RANCHI | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
169 | ER1R13 | 50 MVAR GAYA L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
170 | ER1R14 | 50 MVAR SSRM-III L/R AT BIHARSHARIF | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
171 | ER1R15 | 400kV BUS REACTOR-I, GAYA 125MVAR | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
172 | ER1R16 | 400kV BUS REACTOR II,GAYA | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | SUB TOTAL |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
173 | ER1R17 | 765kV BUS REACTOR II, GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
174 | ER1R18 | 765kV BUS REACTOR1-GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
175 | ER1R19 | 125 MVAR B/R - I AT PSL | 125 | ER1 | -- | -- | -- | -- | 2019-06-23 | 19:54 | 2019-06-26 | 7:35 | 59.6833 | 0 | 0 | 0 | 59.6833 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-14 | 22:18 | 2019-06-22 | 4:08 | 173.8333 | 0 | 0 | 0 | 173.8333 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-30 | 22:25 | 2019-07-01 | 0:00 | 1.5833 | 0 | 0 | 0 | 1.5833 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 235.1 | 0 | 0 | 0 | 235.1
176 | ER1R20 | 125 MVAR B/R - II AT PASAULI | 125 | ER1 | -- | -- | -- | -- | 2019-06-14 | 22:21 | 2019-06-22 | 4:05 | 173.7333 | 0 | 0 | 0 | 173.7333 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-23 | 19:56 | 2019-06-26 | 8:04 | 60.1333 | 0 | 0 | 0 | 60.1333 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-30 | 22:26 | 2019-07-01 | 0:00 | 1.5667 | 0 | 0 | 0 | 1.5667 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 235.4333 | 0 | 0 | 0 | 235.4333
177 | ER1R21 | 63 MVAR GKP - I L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
178 | ER1R22 | 63 MVAR GKP - II L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
179 | ER1R23 | 63 MVAR NPRN - I L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
180 | ER1R24 | 63 MVAR NPRN - II L/R AT MUZZAFERPUR | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
181 | ER1R25 | 63 MVAR MUZ - I L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
182 | ER1R26 | 63 MVAR MUZ- II L/R AT NPRN | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
183 | ER1R27 | 63 MVAR BSF- I L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
184 | ER1R28 | 63 MVAR BSF- II L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
185 | ER1R29 | 50 MVAR BSF- III L/R AT PSL | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
186 | ER1R30 | 50 MVAR BALIA L/R AT PSL | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
187 | ER1R31 | 63 MVAR ALLAHABAD-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
188 | ER1R32 | 63 MVAR SARNATH-1 L/R AT PSL | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
189 | ER1R33 | 50 MVAR B/R - I AT GAYA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
190 | ER1R34 | 50 MVAR B/R - II AT GAYA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
191 | ER1R35 | 50 MVAR L/R - I AT BANKA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
192 | ER1R36 | 50 MVAR L/R - 2 AT BANKA | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
193 | ER1R37 | 80 MVAR B/R - 1 AT BANKA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
194 | ER1R38 | 125 3Ph B/R I AT SASARAM | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
195 | ER1R39 | 125 3Ph B/R II AT SASARAM | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
196 | ER1R40 | 3*110 MVAR 1 PH B/R - I AT SASARAM | 330 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
197 | ER1R41 | 3*110 MVAR 1 PH L/R - I AT SASARAM (AS B/R) | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
198 | ER1R42 | 125 MVAR BUS REACTOR-1 RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
199 | ER1R43 | 125 MVAR BUS REACTOR-1 PATNA | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
200 | ER1R44 | 80 MVAR PURNEA-1 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
201 | ER1R45 | 80 MVAR PURNEA-2 L/R at Biharsharif | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
202 | ER1R46 | 125 MVAR BUS REACTOR-2 PATNA | 125 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-07-01 | 0:00 | 720 | 0 | 720 | 0 | 0 | OMSU |  |  |  |  | 125MVAR B/R-2 is under S/D for shifting of the same as L/R in 400KV PATNA-BARH-2. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 720 | 0 | 720 | 0 | 0
203 | ER1R47 | 125 MVAR BUS REACTOR-1 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
204 | ER1R48 | 125 MVAR BUS REACTOR-2 NEW RANCHI | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
205 | ER1R49 | 3*80MVAR 1 PH L/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
206 | ER1R50 | 3*80MVAR 1 PH B/R - II AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
207 | ER1R51 | 80 MVAR B/R - 1 AT LAKHISARAI | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
208 | ER1R52 | 3*80MVAR 1 PH B/R - I AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
|  | Sub-Total= |  |  | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
209 | ER1R53 | 63MVAR KISHANGANJ LR-I AT PATNA | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
210 | ER1R54 | 63MVAR KISHANGANJ LR-II AT PATNA | 63 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
211 | ER1R55 | 3*80 MVAR DHRAMJAYGARH LR-II AS BR AT NEW RANCHI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
ERPC
212 | ER1R56 | 125 MVAR BR-II AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-06-12 | 15:53 | 279.8833 | 0 | 0 | 0 | 279.8833 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTIONS. | ERPC | 100
[9 empty] | 2019-06-23 | 19:55 | 2019-06-26 | 10:06 | 62.1833 | 0 | 0 | 0 | 62.1833 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-27 | 19:46 | 2019-07-01 | 0:00 | 76.2333 | 0 | 0 | 0 | 76.2333 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-14 | 20:25 | 2019-06-22 | 17:19 | 188.9 | 0 | 0 | 0 | 188.9 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 607.2 | 0 | 0 | 0 | 607.2
213 | ER1R57 | 125 MVAR BR-I AT MUZAFFERPUR | 125 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-06-12 | 15:52 | 279.8667 | 0 | 0 | 0 | 279.8667 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[9 empty] | 2019-06-27 | 19:43 | 2019-07-01 | 0:00 | 76.2833 | 0 | 0 | 0 | 76.2833 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-23 | 19:42 | 2019-06-26 | 9:46 | 62.0667 | 0 | 0 | 0 | 62.0667 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
[9 empty] | 2019-06-14 | 20:24 | 2019-06-22 | 13:49 | 185.4167 | 0 | 0 | 0 | 185.4167 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION.
| TOTAL | [11 empty] | 603.6333 | 0 | 0 | 0 | 603.6333
214 | ER1R58 | 125 MVAR BR-III AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | 2019-06-28 | 19:39 | 2019-07-01 | 0:00 | 52.35 | 0 | 0 | 0 | 52.35 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
| TOTAL | [11 empty] | 52.35 | 0 | 0 | 0 | 52.35
215 | ER1R59 | 125 MVAR BR-I AT Kishanganj | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
216 | ER1R60 | 125 MVAR BR-I AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
217 | ER1R61 | 125 MVAR BR-II AT Chandawa | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
218 | ER1R62 | 80 MVAR B/R AT CHAIBASA | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
219 | ER1R63 | 3*80 1ph VARANASI L/R-II at Gaya | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
220 | ER1R64 | 125 MVAR B/R - I I AT KISHENGANJ | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
221 | ER1R65 | 80 MVAR B/R - I AT KISHENGANJ | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
222 | ER1R66 | 80 MVAR B/R - II AT KISHENGANJ | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
223 | ER1R67 | 80 MVAR L/R OF 400 kV BARH - GORAKHPUR - I AT GORAKHPUR | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
224 | ER1R68 | 80 MVAR L/R OF 400 kV BARH - GORAKHPUR - II AT GORAKHPUR | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
225 | ER1R69 | 240 MVAR L/R OF 765 kV GAYA - BALIA LINE AT BALIA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
226 | ER1R70 | 330 MVAR L/R OF 765 kV SASARAM - FATEHPUR LINE AT SASARAM | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
227 | ER1R71 | 330 MVAR L/R OF 765 kV SASARAM - FATEHPUR LINE AT FATEHPUR | 330 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
228 | ER1R72 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - I LINE AT GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
229 | ER1R73 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - I LINE AT VARANASI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
230 | ER1R74 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - II LINE AT GAYA | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
231 | ER1R75 | 240 MVAR L/R OF 765 kV GAYA - VARANASI - II LINE AT VARANASI | 240 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
232 | ER1R76 | 125MVAR, 400kV BUS REACTOR-III, AT JAMSHEDPUR | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
233 | ER1R76 | 80 MVAR BUS REACTOR AT DALTONGANJ | 80 | ER1 | -- | -- | -- | -- | 2019-06-01 | 0:00 | 2019-07-01 | 0:00 | 720 | 0 | 0 | 0 | 720 | SVRD |  |  |  |  | HAND TRIPPED FOR VOLTAGE REGULATION AS PER ERLDC INSTRUCTION. | ERPC | 100
[5 empty] | -- | -- | -- | --
| TOTAL | [11 empty] | 720 | 0 | 0 | 0 | 720
234 | ER1R77 | 125 MVAR BR-IV AT Biharsharif | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
TOTAL
235 | ER1R78 | 125 MVAR BR-II AT Lakhisarai | 125 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
236 | ER1R79 | 50 MVAR L/R of 400 kV Biharsarif - Sasaram - I AT Biharsharif | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
237 | ER1R80 | 50 MVAR L/R of 400 kV Biharsarif - Lakhisarai - II AT Biharsharif | 50 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
238 | ER1R80 | 80 MVAR L/R of 400 kV Kishanganj- Darbhanga - II AT Kishanganj | 80 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
239 | ER1 ST01 | STATCOM AT New ranchi | -550/+300 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
240 | ER1 ST02 | STATCOM AT Kishanganj | -450/+200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0
241 |  | BANKA-BUS REACTOR-2 | -450/+200 | ER1 | -- | -- | -- | -- | [15 empty] | ERPC | 100
| TOTAL | [11 empty] | 0 | 0 | 0 | 0 | 0