## ER-II
Sr.No. | Unique ID code | Element | Line Length/MVAR/MVA | Type of failure | DETAILS OF OUTAGE | No.of insulator failed | Total outage in days (1) | Trip date and Time | Restoration Date and Time | Outage Attributable to powergrid(T) | Outage Attributable to Others(U) | Outage Attributable to System Constraints ( C ) | Deemed Available ( D ) | Category | 'Restoration Time as per Regulation 5(b) (2) | 'Whether Restoration Time more than normative (Y/N) | 'Difference between Actual and Norm 1-2 | Reason | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
1 | ET39 | 100 MVA ICT-I OF BIRPARA | 100 | --- | --- | --- | --- | 2015-08-01 05:57 | 2015-08-01 13:37 | 0 | 7.6667 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP. | ERPC
|  | 100 MVA ICT-I OF BIRPARA |  | --- | --- | --- | --- | 2015-08-02 05:40 | 2015-08-02 13:43 | 0 | 8.05 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP.
|  | 100 MVA ICT - I AT BIRPARA |  | --- | --- | --- | --- | 2015-08-04 05:14 | 2015-08-04 13:38 | 0 | 8.4 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP.
|  | 100 MVA ICT - I AT BIRPARA |  | --- | --- | --- | --- | 2015-08-05 05:27 | 2015-08-05 14:45 | 0 | 9.3 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP.
|  | 100 MVA ICT-I OF BIRPARA |  | --- | --- | --- | --- | 2015-08-08 05:38 | 2015-08-08 17:25 | 0 | 11.7833 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP.
|  | 100 MVA ICT-I OF BIRPARA |  | --- | --- | --- | --- | 2015-08-09 05:57 | 2015-08-09 13:45 | 0 | 7.8 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP.
|  | 100 MVA ICT - I AT BIRPARA |  | --- | --- | --- | --- | 2015-08-12 06:15 | 2015-08-12 14:03 | 0 | 7.8 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP.
|  | 100 MVA ICT - I AT BIRPARA |  | --- | --- | --- | --- | 2015-08-13 05:19 | 2015-08-13 14:47 | 0 | 9.4667 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for Isolator retrofitting work, under ADDCAP.
[9 empty] | TOTAL | 0 | 70.2667 | 0 | 0 | [6 empty] | 100
2 | ET37 | 100 MVA ICT - I AT SILIGURI | 100 | --- | --- | --- | --- | 2015-08-23 11:33 | 2015-08-23 14:53 | 0 | 3.3333 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken by SLG for Bus bar protection Implementation work at SLG end under ERSS XII package.
|  | 100 MVA ICT - I AT SILIGURI |  | --- | --- | --- | --- | 2015-08-29 11:10 | 2015-08-29 15:55 | 0 | 4.75 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
[9 empty] | TOTAL | 0 | 8.0833 | 0 | 0 | [6 empty] | 100
3 | ET44 | 100 MVA RANGPO ICT-I | 100 | --- | --- | --- | --- | 2015-08-01 09:03 | 2015-08-01 18:36 | 0 | 0 | 0 | 9.55 | SPRD | N/A | N/A | N/A | H/T as per ERLDC for power regulation.
[9 empty] | TOTAL | 0 | 0 | 0 | 9.55 | [6 empty] | 100
4 | ET45 | 100 MVA RANGPO ICT-II | 100 | --- | --- | --- | --- | 2015-08-01 09:03 | 2015-08-01 18:36 | 0 | 0 | 0 | 9.55 | SPRD | N/A | N/A | N/A | H/T as per ERLDC for power regulation.
[9 empty] | TOTAL | 0 | 0 | 0 | 9.55 | [6 empty] | 100
5 | ET46 | 100 MVA RANGPO ICT-III | 100 | --- | --- | --- | --- | 2015-08-01 09:03 | 2015-08-01 18:36 | 0 | 0 | 0 | 9.55 | SPRD | N/A | N/A | N/A | H/T as per ERLDC for power regulation.
[9 empty] | TOTAL | 0 | 0 | 0 | 9.55 | [6 empty] | 100
6 | E2R33 | 125 MVAR B/R AT INDRAVATI | 125 | --- | --- | --- | --- | 2015-08-07 09:51 | 2015-08-07 17:22 | 0 | 7.5167 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for CSD commissioning work at IVT(PG) end.
|  | 125 MVAR B/R AT INDRAVATI |  | --- | --- | --- | --- | 2015-08-18 15:23 | 2015-08-18 17:08 | 0 | 1.75 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken by IVT for installation & commissioning of CSD in its main bay.
|  | 125 MVAR B/R AT INDRAVATI |  | --- | --- | --- | --- | 2015-08-18 17:12 | 2015-08-18 18:03 | 0 | 0.85 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken by IVT for installation & commissioning of CSD in its main bay.
|  | 125 MVAR B/R AT INDRAVATI |  | --- | --- | --- | --- | 2015-08-19 12:10 | 2015-08-19 17:58 | 0 | 0 | 0 | 5.8 | SCSD | N/A | N/A | N/A | Adjustment of CSD and re-wiring of main bay CT and 'OFF-ON' testing with CSD.
|  | 125 MVAR B/R AT INDRAVATI |  | --- | --- | --- | --- | 2015-08-21 09:33 | 2015-08-21 21:54 | 0 | 0 | 0 | 12.35 | SVRD | N/A | N/A | N/A | H/T or kept open as per ERLDC instruction for voltage regulation
|  | 125MVAR B/R AT INDRAVATI |  | --- | --- | --- | --- | 2015-08-26 06:45 | 2015-08-27 15:56 | 0 | 0 | 0 | 33.18 | SVRD | N/A | N/A | N/A | H/T or kept open as per ERLDC instruction for voltage regulation
[9 empty] | TOTAL | 0 | 10.1167 | 0 | 51.33 | [6 empty] | 100
7 | E2R29 | 125 MVAR B/R AT ROURKELA | 125 | --- | --- | --- | --- | 2015-08-10 10:06 | 2015-08-10 17:52 | 7.7667 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | S/D taken to carry out replacement of defective relay & its testing
[9 empty] | TOTAL | 7.7667 | 0 | 0 | 0 | [6 empty] | 98.9561
8 | ERL76 | 132 KV SILIGURI - KARSIANG | 31.3 | --- | --- | --- | --- | 2015-08-10 17:10 | 2015-08-10 17:31 | 0 | 0 | 0.35 | 0 | LNCC | N/A | N/A | N/A | Tripped on RN fault, FL-20.52km from SLG, F/C-2.819KA due to severe rain/lightening.
[9 empty] | TOTAL | 0 | 0 | 0.35 | 0 | [6 empty] | 100
9 | ERL83 | 132 KV SILIGURI - MELLI | 92 | --- | --- | --- | --- | 2015-08-10 17:10 | 2015-08-10 17:44 | 0 | 0 | 0.56667 | 0 | LNCC | N/A | N/A | N/A | Tripped on RN fault, FL-16.88km from SLG, F/C-2.968KA due to severe rain/lightening.
[9 empty] | TOTAL | 0 | 0 | 0.56667 | 0 | [6 empty] | 100
10 | ET38 | 160 MVA ICT - II AT SILIGURI | 160 | --- | --- | --- | --- | 2015-08-23 07:44 | 2015-08-23 10:47 | 0 | 3.05 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken by SLG for Bus bar protection Implementation work at SLG end under ERSS XII package.
|  | 160 MVA ICT - II AT SILIGURI |  | --- | --- | --- | --- | 2015-08-29 07:04 | 2015-08-29 09:45 | 0 | 2.6833 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
[9 empty] | TOTAL | 0 | 5.7333 | 0 | 0 | [6 empty] | 100
11 | ET42 | 160 MVA ICT-I AT MALDA | 160 | --- | --- | --- | --- | 2015-08-12 08:03 | 2015-08-12 17:33 | 0 | 9.5 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for testing of bushing on variable frequency as recommended by manufacturer.
[9 empty] | TOTAL | 0 | 9.5 | 0 | 0 | [6 empty] | 100
12 | ET41 | 160 MVA ICT-II OF MALDA | 160 | --- | --- | --- | --- | 2015-08-13 09:05 | 2015-08-13 16:30 | 0 | 7.4167 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for testing of bushing on variable frequency as recommended by manufacturer.
[9 empty] | TOTAL | 0 | 7.4167 | 0 | 0 | [6 empty] | 100
13 | ERL62 | 220 KV NSLG - BRP - I | 80 | --- | --- | --- | --- | 2015-08-10 15:25 | 2015-08-10 15:37 | 0 | 0 | 0.2 | 0 | LNCC | N/A | N/A | N/A | Tripped on RN fault only from BRP end & A/R sucessful at NSLG end due to severe rain/lightening.
|  | 220 KV BIRPARA - N.SLG-I |  | --- | --- | --- | --- | 2015-08-30 05:53 | 2015-08-30 06:35 | 0 | 0 | 0.7 | 0 | LNCC | N/A | N/A | N/A | Tripped on ph-ph fault(Y &B),F/D-71.89ka,F/C-2.438ka in Yph,2.670ka in Bph,during heavy rain & lightening
[9 empty] | TOTAL | 0 | 0 | 0.9 | 0 | [6 empty] | 100
14 | ERL65 | 220 KV BIRPARA - SALAKATI - II | 161 | --- | --- | --- | --- | 2015-08-19 21:02 | 2015-08-19 23:04 | 0 | 0 | 2.0333 | 0 | LNCC | N/A | N/A | N/A | Tripped on YB-N fault, FL-144km from BRP end, F/C : IY-1.863KA & IB-1.009KA due to heavy lightening/thundering/rain.
[9 empty] | TOTAL | 0 | 0 | 2.0333 | 0 | [6 empty] | 100
15 | ERL64 | 220 KV BIRPARA - SALAKATI - I | 161 | --- | --- | --- | --- | 2015-08-19 21:05 | 2015-08-19 22:30 | 0 | 0 | 1.4167 | 0 | LNCC | N/A | N/A | N/A | Tripped on BN fault, FL-144.7km from BRP end, F/C : 892.6KA due to heavy lightening/thundering/rain.
[9 empty] | TOTAL | 0 | 0 | 1.4167 | 0 | [6 empty] | 100
16 | ERL60 | 220KV BIRPARA-CHUKHA-I | 36 | --- | --- | --- | --- | 2015-08-02 23:44 | 2015-08-03 00:57 | 0 | 1.2167 | 0 | 0 | OMSU | N/A | N/A | N/A | G- Tripped on Zone-II,fd:139.2km/Birpara,R-Y-B fault,fc: 834.9amp-R-ph,873.9amp=y ph,852.4amp=b ph.. Problem at Bhutan jurisdiction.
|  | 220 KV CHK - BRP - I |  | --- | --- | --- | --- | 2015-08-10 14:55 | 2015-08-10 15:35 | 0 | 0 | 0.66667 | 0 | LNCC | N/A | N/A | N/A | Tripped on RN fault, FL-29.54km from BRP end due to severe rain/lightening.
|  | 220 KV BIRPARA-CHUKHA-I |  | --- | --- | --- | --- | 2015-08-16 23:19 | 2015-08-17 00:12 | 0 | 0.88333 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped on Z1, R-Y-B.. F/L: 48.90 KM (Upto 35 km: Indian area), F/Current: R/Y/B-1.885/3.019/2.254 KA.. Bhutan jurisdiction.
|  | 220KV CHUKHA-BIRPARA-I |  | --- | --- | --- | --- | 2015-08-27 10:00 | 2015-08-27 10:10 | 0 | 0.16667 | 0 | 0 | OMSU | N/A | N/A | N/A | Breaker opened at Chukha end but breaker charged at Birpara end due to problem at CHPC end for both ckts.
[9 empty] | TOTAL | 0 | 2.2667 | 0.66667 | 0 | [6 empty] | 100
17 | ERL61 | 220KV BIRPARA-CHUKHA-II | 36 | --- | --- | --- | --- | 2015-08-02 23:44 | 2015-08-04 16:00 | 0 | 40.27 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped on Zone-II, R-N fault,fd: 64.1km/Birpara,fc:1.564ka, line charged at 00:41hrs tripped immediately on SOTF; R-Y phase, dist from Birpara-60 km.. Problem is at Bhutan area.
|  | 220 KV CHUKHA - BIRPARA - II |  | --- | --- | --- | --- | 2015-08-09 08:07 | 2015-08-09 16:32 | 0 | 8.4167 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped on B-N fault,F/C-1.519ka,F/D-70 km from Birpara ( Bhutan Jurisdiction)/ Flashed insulators detected at Loc no: 197.
|  | 220 KV CHK - BRP - II |  | --- | --- | --- | --- | 2015-08-10 14:55 | 2015-08-10 15:42 | 0 | 0 | 0.78333 | 0 | LNCC | N/A | N/A | N/A | Tripped on RN fault, FL-29.54km from BRP end due to severe rain/lightening.
|  | 220 KV BIRPARA-CHUKHA-II |  | --- | --- | --- | --- | 2015-08-16 23:19 | 2015-08-17 00:21 | 0 | 1.0333 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped on Z1, R-Y-B.. F/L: 52.91 KM (Upto 35 km: Indian area), F/Current: R/Y/B-2.109KA/869A/2.136 KA.. Bhutan jurisdiction.
|  | 220KV CHUKHA-BIRPARA-II |  | --- | --- | --- | --- | 2015-08-27 10:00 | 2015-08-27 13:37 | 0 | 3.6167 | 0 | 0 | OMSU | N/A | N/A | N/A | Breaker opened at Chukha end but breaker charged at Birpara end due to problem at CHPC end for both ckts.
[9 empty] | TOTAL | 0 | 53.3367 | 0.78333 | 0 | [6 empty] | 100
18 | ERL71 | 220 KV NSLG - SLG - II | 9 | --- | --- | --- | --- | 2015-08-26 13:01 | 2015-08-26 19:25 | 0 | 6.4 | 0 | 0 | OMSU | N/A | N/A | N/A | E/S/D taken by SLG/PG for R-phase jumper at gantry rectification work damaged due to exessive over loading in system.
|  | 220 KV SILIGURI - NEW SILIGURI-II |  | --- | --- | --- | --- | 2015-08-28 16:40 | 2015-08-28 20:50 | 0 | 4.1667 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
[9 empty] | TOTAL | 0 | 10.5667 | 0 | 0 | [6 empty] | 100
19 | ERL67 | 220 KV SILIGURI-DALKHOLA-I | 119 | --- | --- | --- | --- | 2015-08-11 09:13 | 2015-08-11 13:57 | 0 | 0 | 0 | 4.7333 | LCSD | N/A | N/A | N/A | S/D taken for related connection work for antitheft charge of part of 800 KV B'chariali-Agra line from 220 KV SLG-DLK-I line between loc 266 & 267 of HVDC line
|  | 220 KV SILIGURI - DALKHOLA - I |  | --- | --- | --- | --- | 2015-08-25 13:50 | 2015-08-25 18:13 | 0 | 4.3833 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for testing & implementation of Bus-Bar protection at SLG s/s
|  | 220KV SILIGURI - DALKHOLA - I |  | --- | --- | --- | --- | 2015-08-26 13:40 | 2015-08-26 18:56 | 0 | 5.2667 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken by ULDC/PG for OPGW work
|  | 220KV SILIGURI - DALKHOLA - I |  | --- | --- | --- | --- | 2015-08-27 10:09 | 2015-08-27 19:46 | 0 | 9.6167 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken by ULDC/PG for OPGW work
|  | 220 KV SILIGURI - DALKHOLA - I |  | --- | --- | --- | --- | 2015-08-28 16:23 | 2015-08-28 21:24 | 0 | 5.0167 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
|  | 220 KV SILIGURI - DALKHOLA - I |  | --- | --- | --- | --- | 2015-08-29 17:47 | 2015-08-29 19:46 | 0 | 1.9833 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
|  | 220 KV SILIGURI - DALKHOLA - I |  | --- | --- | --- | --- | 2015-08-29 19:46 | 2015-08-30 00:12 | 0 | 4.4333 | 0 | 0 | OMSU | N/A | N/A | N/A | Delay charging from ERLDC side
|  | 220 KV SILIGURI - DALKHOLA - I |  | --- | --- | --- | --- | 2015-08-30 15:46 | 2015-08-30 18:26 | 0 | 0 | 0 | 2.6667 | LCSD | N/A | N/A | N/A | Shut down taken for anti- theft charging of HVDC line at Loc no: 247 of HVDC, as part of constructional activities.
[9 empty] | TOTAL | 0 | 30.7 | 0 | 7.4 | [6 empty] | 100
20 | ERL | 220 KV SILIGURI-DALKHOLA-II | 119 | --- | --- | --- | --- | 2015-08-15 22:51 | 2015-08-16 03:29 | 0 | 0 | 4.6333 | 0 | LNCC | N/A | N/A | N/A | Tripped during rain & thunderstorm.. From Siliguri- 12.11 KM, Y-B-N, B-phase Jumper opened at Loc no: 41 (T).
|  | 220 KV SILIGURI - DALKHOLA - II |  | --- | --- | --- | --- | 2015-08-25 10:54 | 2015-08-25 13:37 | 0 | 2.7167 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for testing & implementation of Bus-Bar protection at SLG s/s
|  | 220 KV SILIGURI - DALKHOLA - II |  | --- | --- | --- | --- | 2015-08-31 10:40 | 2015-08-31 13:30 | 0 | 2.8333 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
[9 empty] | TOTAL | 0 | 5.55 | 4.6333 | 0 | [6 empty] | 100
21 | ERL70 | 220 KV SILIGURI - NEW SILIGURI-I | 9 | --- | --- | --- | --- | 2015-08-28 16:40 | 2015-08-28 20:50 | 0 | 4.1667 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
|  | 220 KV SILIGURI - NEW SILIGURI-I |  | --- | --- | --- | --- | 2015-08-29 18:21 | 2015-08-29 23:48 | 0 | 5.45 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for busbar protection implementation and testing at Siliguri
[9 empty] | TOTAL | 0 | 9.6167 | 0 | 0 | [6 empty] | 100
22 | ERL61 | 220KV BIRPARA-MALBASE | 38 | --- | --- | --- | --- | 2015-08-01 | 2015-08-03 11:56 | 0 | 0 | 0 | 59.56 | LPRD | N/A | N/A | N/A | H/T as per ERLDC instruction for power regulation.
|  | 220KV BIRPARA-MALBASE |  | --- | --- | --- | --- | 2015-08-03 17:13 | 2015-09-01 | 0 | 0 | 0 | 678.47 | LPRD | N/A | N/A | N/A | H/T as per ERLDC instruction for power regulation.
[9 empty] | TOTAL | 0 | 0 | 0 | 738.03 | [6 empty] | 100
23 | ERL74 | 220KV RANGPO-MELLI | 26 | --- | --- | --- | --- | 2015-08-31 11:14 | 2015-09-01 | 0 | 0 | 0 | 12.7667 | LCSD | N/A | N/A | N/A | S/D taken by JLHEP for commissioning of LILO of the line.
[9 empty] | TOTAL | 0 | 0 | 0 | 12.7667 | [6 empty] | 100
24 | ET18 | 315MVA ICT-II/INDRAVATI | 315 | --- | --- | --- | --- | 2015-08-22 10:00 | 2015-08-22 19:19 | 9.3167 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | Shut down for attending oil leakage in tan-delta point of R-ph bushing(400kv side).
[9 empty] | TOTAL | 9.3167 | 0 | 0 | 0 | [6 empty] | 98.7478
25 | ET17 | 315 MVA ICT - I AT BARIPADA | 315 | --- | --- | --- | --- | 2015-08-25 09:02 | 2015-09-01 | 0 | 158.97 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for tan-delta measurment with variable frequency
[9 empty] | TOTAL | 0 | 158.97 | 0 | 0 | [6 empty] | 100
26 | ET14 | 315 MVA ICT - III AT MALDA | 315 | --- | --- | --- | --- | 2015-08-26 09:49 | 2015-08-26 13:08 | 0 | 3.3167 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for testing of bushing with variable frequency
[9 empty] | TOTAL | 0 | 3.3167 | 0 | 0 | [6 empty] | 100
27 | ET11 | 315MVA ICT-I AT JEYPUR | 315 | --- | --- | --- | --- | 2015-08-31 08:00 | 2015-08-31 11:46 | 3.7667 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | S/D for unloading of SIEMENS make 125MVAR BR at Jeypore.
|  | 315MVA ICT-I AT JEYPUR |  | --- | --- | --- | --- | 2015-08-31 15:23 | 2015-08-31 16:47 | 1.4 | 0 | 0 | 0 | SICT | N/A | N/A | N/A | ICT Tripped due to PRV operated.
[9 empty] | TOTAL | 5.1667 | 0 | 0 | 0 | [6 empty] | 99.3056
28 | ERL28 | 400 KV ANGUL - BOLANGIR | 196 | --- | --- | --- | --- | 2015-08-08 12:33 | 2015-08-08 12:37 | 0 | 0 | 0.066667 | 0 | LNCC | N/A | N/A | N/A | Tripped on RN fault, FL-160km from Angul end,F/C-2.49KA due to rain/lightening.
|  | 400 KV ANGUL - BOLANGIR |  | --- | --- | --- | --- | 2015-08-08 12:37 | 2015-08-08 15:00 | 0 | 0 | 0 | 2.3833 | LVRD | N/A | N/A | N/A | H/T or kept open as per ERLDC instruction for voltage regulation
[9 empty] | TOTAL | 0 | 0 | 0.066667 | 2.3833 | [6 empty] | 100
29 | ERL57 | 400 JHARSUGDA - IND-BHARAT | 62.6 | --- | --- | --- | --- | 2015-08-08 14:31 | 2015-08-08 14:56 | 0.41667 | 0 | 0 | 0 | LEFT | N/A | N/A | N/A | Tripped on R-N fault,F/C-3.41 ka F/D-78.6 km from Jharsugda
|  | 400 KV SUNDARGARH-IND-BHARAT |  | --- | --- | --- | --- | 2015-08-25 08:10 | 2015-08-25 22:12 | 0 | 14.0333 | 0 | 0 | OMSU | N/A | N/A | N/A | Shut down taken for thorough scheme checking & testing of protection at Sundargarh end by internal auditor.
[9 empty] | TOTAL | 0.41667 | 14.0333 | 0 | 0 | [6 empty] | 99.9429
30 | ERL05 | 400 KV BAHARAMPUR-JEERHAT | 165.27 | --- | --- | --- | --- | 2015-08-21 17:30 | 2015-08-21 18:18 | 0 | 0 | 0.8 | 0 | LNCC | N/A | N/A | N/A | During rain & thunder-storm tripped on R-B; From B'pur: 113 KM, R/B: 3.56/4.09 KA.. From Jeerhat: 47 km.
[9 empty] | TOTAL | 0 | 0 | 0.8 | 0 | [6 empty] | 100
31 | ERL93 | 400 KV BARIPADA-DUBURI | 190.25 | --- | --- | --- | --- | 2015-08-22 15:31 | 2015-08-22 16:16 | 0 | 0.75 | 0 | 0 | OMSU | N/A | N/A | N/A | Mendashall/OPTCL end, isolator opened autometically.. D/T recd at Baripada end.
|  | 400 KV BARIPADA-DUBURI |  | --- | --- | --- | --- | 2015-08-28 09:11 | 2015-08-28 10:03 | 0 | 0.86667 | 0 | 0 | OMSU | N/A | N/A | N/A | Line tripped due to Direct trip recd from remote end of Duburi & Mendashall, both under OPTCL.
[9 empty] | TOTAL | 0 | 1.6167 | 0 | 0 | [6 empty] | 100
32 | ERL31 | 400 KV BARIPADA-KEONJHAR | 28 | --- | --- | --- | --- | 2015-08-24 06:17 | 2015-08-24 18:07 | 0 | 0 | 11.8333 | 0 | LNCC | N/A | N/A | N/A | Shut down taken for replacement of Insulator string at Loc no: 06, damaged during rercent thundering on rain..
[9 empty] | TOTAL | 0 | 0 | 11.8333 | 0 | [6 empty] | 100
33 | ERL41 | 400 KV BARIPADA-MENDASHAL-I | 276.63 | --- | --- | --- | --- | 2015-08-13 10:13 | 2015-08-13 20:01 | 0 | 0 | 0 | 9.8 | LCSD | N/A | N/A | N/A | Completion of balance work of LILO at New Duburi end & PLCC dismantlling at Baripada.
|  | 400 KV BARIPADA-MENDASHALL-I |  | --- | --- | --- | --- | 2015-08-28 09:11 | 2015-08-28 09:51 | 0 | 0.66667 | 0 | 0 | OMSU | N/A | N/A | N/A | Line tripped due to Direct trip recd from remote end of Duburi & Mendashall, both under OPTCL.
[9 empty] | TOTAL | 0 | 0.66667 | 0 | 9.8 | [6 empty] | 100
34 | ERL92 | 400 KV DUBURI-MENDASHALL-I | 115.26 | --- | --- | --- | --- | 2015-08-22 15:31 | 2015-08-22 16:32 | 0 | 1.0167 | 0 | 0 | OMSU | N/A | N/A | N/A | Mendashall/OPTCL end, isolator opened autometically.. D/T recd at Baripada end.
|  | 400 KV DUBURI-MENDASHALL-I |  | --- | --- | --- | --- | 2015-08-28 11:46 | 2015-08-28 18:28 | 0 | 0 | 0 | 6.7 | OSPD | N/A | N/A | N/A | S/D taken for rectification of main bay isolator of line at Mendhasal end
[9 empty] | TOTAL | 0 | 1.0167 | 0 | 6.7 | [6 empty] | 100
35 | ERL42 | 400 KV BARIPADA-MENDASHAL-II | 276.63 | --- | --- | --- | --- | 2015-08-11 10:26 | 2015-08-17 19:01 | 0 | 0 | 0 | 152.58 | LCSD | N/A | N/A | N/A | Completion of balance work of LILO at New Duburi end & PLCC dismantlling at Baripada.
[9 empty] | TOTAL | 0 | 0 | 0 | 152.58 | [6 empty] | 100
36 | ERL37 | 400 KV BINAGURI-RANGPO-I | 109.88 | --- | --- | --- | --- | 2015-08-01 09:13 | 2015-08-01 18:27 | 9.2333 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | B-Ph CVT replacement work at Rangpo
[9 empty] | TOTAL | 9.2333 | 0 | 0 | 0 | [6 empty] | 98.759
37 | ERL39 | 400 KV NSLG - RANGPO - II | 110.42 | --- | --- | --- | --- | 2015-08-07 10:03 | 2015-08-07 15:27 | 0 | 0 | 5.4 | 0 | LNCC | N/A | N/A | N/A | S/D taken for replacement of flashed over insulator & corona rings damaged due to severe lightening at loc.no.222,223,250 & 267.
[9 empty] | TOTAL | 0 | 0 | 5.4 | 0 | [6 empty] | 100
38 | ERL38 | 400KV TEESTA- RANGPO- 1 | 11.83 | --- | --- | --- | --- | 2015-08-29 15:47 | 2015-08-29 16:41 | 0 | 0 | 0.9 | 0 | LNCC | N/A | N/A | N/A | Tripped on R-B ph fault,FD: 5.54km from Rangpo,FC: R ph=1.03ka,Bph=6.36ka,observed heavy rain & lightening in the affected area.
[9 empty] | TOTAL | 0 | 0 | 0.9 | 0 | [6 empty] | 100
39 | ERL18 | 400 KV INDRAVATI - RENGALI | 356 | --- | --- | --- | --- | 2015-08-13 07:21 | 2015-08-13 09:33 | 0 | 2.2 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken by RNG/PG to take Line Reactor into service.
[9 empty] | TOTAL | 0 | 2.2 | 0 | 0 | [6 empty] | 100
40 | ERL19 | 400 KV JEYPORE - INDRAVATI | 71 | --- | --- | --- | --- | 2015-08-25 12:50 | 2015-08-25 13:04 | 0 | 0 | 0.23333 | 0 | LNCC | N/A | N/A | N/A | Tripped on R-N fault,F/C-1`8 ka,F/D-69.03 km from JPR due to heavy lightening/thundering.
[9 empty] | TOTAL | 0 | 0 | 0.23333 | 0 | [6 empty] | 100
41 | ERL45 | 400 KV MTN - DGP -I | 70.71 | --- | --- | --- | --- | 2015-08-28 00:01 | 2015-08-28 21:30 | 0 | 0 | 21.4833 | 0 | LMAC | N/A | N/A | N/A | Tripped due to conductor cutting between loc.no.184 & 185 by miscreants for sabotage.
|  | 400 KV MAITHAN-DURGAPUR-I |  | --- | --- | --- | --- | 2015-08-29 11:07 | 2015-08-29 16:47 | 0 | 5.6667 | 0 | 0 | OMSU | N/A | N/A | N/A | To avoid inductional hazzard, during replacement of Insulator string of Maithan- Mejia both ckt, those are now under shut down.
[9 empty] | TOTAL | 0 | 5.6667 | 21.4833 | 0 | [6 empty] | 100
42 | ERL46 | 400 KV MTN - DGP -II | 70.71 | --- | --- | --- | --- | 2015-08-28 00:01 | 2015-08-28 00:32 | 0 | 0 | 0.51667 | 0 | LMAC | N/A | N/A | N/A | Tripped during cutting of conductor by miscreants.
|  | 400 KV MAITHAN-DURGAPUR-II |  | --- | --- | --- | --- | 2015-08-29 11:07 | 2015-08-29 16:54 | 0 | 5.7833 | 0 | 0 | OMSU | N/A | N/A | N/A | To avoid inductional hazzard, during replacement of Insulator string of Maithan- Mejia both ckt, those are now under shut down.
[9 empty] | TOTAL | 0 | 5.7833 | 0.51667 | 0 | [6 empty] | 100
43 | ERL44 | 400 KV MAITHAN-MEJIA-II | 59.18 | --- | --- | --- | --- | 2015-08-05 20:59 | 2015-08-05 22:51 | 1.8667 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | Shut down taken to attend Hot-spot on R phase line CT connector
|  | 400KV MAITHON-MEJIA- II |  | --- | --- | --- | --- | 2015-08-24 14:22 | 2015-08-29 18:06 | 0 | 0 | 3.7333 | 0 | LMAC | N/A | N/A | N/A | S/D for replacement of defective tower leg at loc. 170(DA+0) on account of heavy theft.
[9 empty] | TOTAL | 1.8667 | 0 | 3.7333 | 0 | [6 empty] | 99.7478
44 | ERL01 | 400 KV MAITHAN-MEJIA-III | 83.74 | --- | --- | --- | --- | 2015-08-20 10:47 | 2015-08-20 16:46 | 0 | 0 | 5.9833 | 0 | LMAC | N/A | N/A | N/A | Shut down taken to replace the 5 nos broken insulators at Loc no: 98, those were damaged by miscreants.
[9 empty] | TOTAL | 0 | 0 | 5.9833 | 0 | [6 empty] | 100
45 | ERL43 | 400KV MAITHON-MEJIA- I | 59.18 | --- | --- | --- | --- | 2015-08-24 13:41 | 2015-08-29 17:55 | 0 | 0 | 124.23 | 0 | LMAC | N/A | N/A | N/A | S/D for replacement of defective tower leg at loc. 170(DA+0) on account of heavy theft.
[9 empty] | TOTAL | 0 | 0 | 124.23 | 0 | [6 empty] | 100
46 | ERL23 | 400 KV MALDA - NEWPURNIA - II | 167 | --- | --- | --- | --- | 2015-08-01 09:05 | 2015-08-01 19:26 | 10.35 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | S/D taken for Bay AMP work at Malda
[9 empty] | TOTAL | 10.35 | 0 | 0 | 0 | [6 empty] | 98.6089
47 | ERL22 | 400 KV MALDA-PURNEA-I | 167 | --- | --- | --- | --- | 2015-08-04 09:00 | 2015-08-04 18:54 | 9.9 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | Shut down taken for L/R testing, & Line Isolator alignment.
[9 empty] | TOTAL | 9.9 | 0 | 0 | 0 | [6 empty] | 98.6694
48 | ERL50 | 400 KV MAITHAN-R/B (MPL)- II | 30 | --- | --- | --- | --- | 2015-08-05 14:22 | 2015-08-05 17:49 | 3.45 | 0 | 0 | 0 | OSFT | N/A | N/A | N/A | E/S/D taken to replace the R-phase Insulator string at Loc no: 18.
[9 empty] | TOTAL | 3.45 | 0 | 0 | 0 | [6 empty] | 99.5363
49 | ERL49 | 400 KV MAITHAN-R/B (MPL)- I | 30 | --- | --- | --- | --- | 2015-08-05 18:05 | 2015-08-05 18:59 | 0 | 0.9 | 0 | 0 | OMSU | N/A | N/A | N/A | E/S/D taken to replace the Insulator string at Loc no: 17, but it has return back by ERLDC, due to system constraint..
|  | 400 KV MAITHAN-R/B (MPL)- I |  | --- | --- | --- | --- | 2015-08-06 12:21 | 2015-08-06 13:52 | 0 | 1.5167 | 0 | 0 | OMSU | N/A | N/A | N/A | E/S/D taken to replace the Insulator string at Loc no: 17
[9 empty] | TOTAL | 0 | 2.4167 | 0 | 0 | [6 empty] | 100
50 | ERL88 | 400 KV NSLG - BNGG - II | 217 | --- | --- | --- | --- | 2015-08-07 12:20 | 2015-08-07 12:25 | 0 | 0 | 0.083333 | 0 | LNCC | N/A | N/A | N/A | Tripped on B-N fault, Z2, FL-180km frm NSLG end, F/C-2.114KA due to rain/lightening.
|  | 401 KV NSLG - BNGG - II |  | --- | --- | --- | --- | 2015-08-07 12:25 | 2015-08-24 21:36 | 0 | 0 | 0 | 417.18 | LVRD | N/A | N/A | N/A | H/T or kept open as per ERLDC instruction for voltage regulation
|  | 400 KV NSLG - BONG - II |  | --- | --- | --- | --- | 2015-08-25 13:27 | 2015-08-26 00:13 | 0 | 0 | 10.7667 | 0 | LNCC | N/A | N/A | N/A | Tripped on R-N fault,F/C-2.063ka,F/D-231.3 km from NSLG & Decapping at loc.no-94 due to rain & thundering.
|  | 400 KV NSLG - BONG - II |  | --- | --- | --- | --- | 2015-08-26 00:13 | 2015-08-26 01:49 | 0 | 0 | 0 | 1.6 | LVRD | N/A | N/A | N/A | H/T or kept open as per ERLDC instruction for voltage regulation
[9 empty] | TOTAL | 0 | 0 | 10.85 | 418.78 | [6 empty] | 100
51 | ERL51 | 400 KV ROURKELA-SUNDARGARH-I | 145.3 | --- | --- | --- | --- | 2015-08-05 17:24 | 2015-08-05 18:18 | 0 | 0.9 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped as D/T recd at RKL end.. CB tripped only at Rourkela.. Remains charged from SNGR.
|  | 400 KV ROURKELA-JHARSUGUDA-I |  | --- | --- | --- | --- | 2015-08-16 07:58 | 2015-08-16 08:33 | 0.58333 | 0 | 0 | 0 | OMST | N/A | N/A | N/A | D/T sent from S'garh to Rourkela, due to SF6 lock-out on main bay CT (SF6 filled) of S'Garh.
|  | 400 KV ROURKELA-SUNDARGARH-I |  | --- | --- | --- | --- | 2015-08-20 12:15 | 2015-08-20 19:00 | 0 | 0 | 0 | 6.75 | SCSD | N/A | N/A | N/A | S/D taken for removal of PIR from the main bay no: 418 at RKL, as part of up-gradation of power system.
|  | 400KV RKL- JHARSUGUDA- I |  | --- | --- | --- | --- | 2015-08-22 09:58 | 2015-08-22 17:34 | 0 | 0 | 0 | 7.6 | SCSD | N/A | N/A | N/A | S/D taken for removal of PIR from the main bay no: 418 at RKL, as part of up-gradation of power system.
|  | 400KV RKL - JHARSUGUDA - I |  | --- | --- | --- | --- | 2015-08-25 19:51 | 2015-08-26 10:48 | 0 | 14.95 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped on group relay operated
[9 empty] | TOTAL | 0.58333 | 15.85 | 0 | 14.35 | [6 empty] | 99.9199
52 | ERL52 | 400KV ROURKELA-SUNDERGARH-II | 145.3 | --- | --- | --- | --- | 2015-08-21 02:24 | 2015-08-21 03:18 | 0 | 0.9 | 0 | 0 | OMSU | N/A | N/A | N/A | E/H/T from Jharsuguda end due to smoke observed from control panel at RKL.
[9 empty] | TOTAL | 0 | 0.9 | 0 | 0 | [6 empty] | 100
53 | ERL12 | 400KV MALDA-FARAKKA- II | 40 | --- | --- | --- | --- | 2015-08-14 09:47 | 2015-08-14 19:19 | 9.5333 | 0 | 0 | 0 | OSPT | N/A | N/A | N/A | Shut down for connection of pipe bus and checking of protection related to 404 main CB at Malda.
[9 empty] | TOTAL | 9.5333 | 0 | 0 | 0 | [6 empty] | 98.7186
54 | ET43 | 50 MVA ICT - IV AT MALDA | 50 | --- | --- | --- | --- | 2015-08-25 09:11 | 2015-08-25 18:17 | 0 | 9.1 | 0 | 0 | OMSU | N/A | N/A | N/A | S/D taken for testing of bushing with variable frequency
[9 empty] | TOTAL | 0 | 9.1 | 0 | 0 | [6 empty] | 100
56 | ERL14 | 400 KV ROURKELA-TALCHER-I | 171 | --- | --- | --- | --- | 2015-08-29 10:10 | 2015-08-29 10:22 | 0 | 0.2 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped due to Direct trip recd from Talcher/NTPC end.Feeder remains charged from Talcher end.
|  | 400 KV ROURKELA-TALCHER-I |  | --- | --- | --- | --- | 2015-08-29 10:28 | 2015-08-29 11:02 | 0 | 0.56667 | 0 | 0 | OMSU | N/A | N/A | N/A | Tripped due to Direct trip recd from Talcher/NTPC end.Feeder remains charged from Talcher end.
|  | 400KV RKL - TALCHER - I |  | --- | --- | --- | --- | 2015-08-25 17:33 | 2015-08-27 16:21 | 0 | 0 | 46.48 | 0 | LNCC | N/A | N/A | N/A | G - Tripped on RB-N fault, FL-171km from RKL end, F/C: Rph-3.421KA, Bph-4.994KA,during heavy rain & thundering
[9 empty] | TOTAL | 0 | 0.76667 | 46.48 | 0 | [6 empty] | 100
57 | ERL24 | 400 KV TALCHER - MERAMUNDALI | 51 | --- | --- | --- | --- | 2015-08-18 12:10 | 2015-08-18 12:54 | 0 | 0 | 0.73333 | 0 | LNCC | N/A | N/A | N/A | Tripped on B-N fault,F/C-9.7 ka due to rain/thundering.
[9 empty] | TOTAL | 0 | 0 | 0.73333 | 0 | [6 empty] | 100
58 | ERL15 | 400KV RKL - TALCHER - II | 171 | --- | --- | --- | --- | 2015-08-25 21:29 | 2015-08-25 21:59 | 0 | 0 | 0 | 0.5 | OSFD | N/A | N/A | N/A | Emergency shut down taken by NTPC/Talcher end.
[9 empty] | TOTAL | 0 | 0 | 0 | 0.5 | [6 empty] | 100
59 | E2R16 | 400kV BUS REACTOR1,BOLANGIR | 80 | --- | --- | --- | --- | 2015-08-01 | 2015-08-08 16:23 | 0 | 0 | 0 | 184.38 | SVRD | N/A | N/A | N/A | HAND TRIPPED AS PER ERLDC INSTRUCTION FOR VOLTAGE REGULATION.
|  | 80 MVAR B/R AT BOLANGIR |  | --- | --- | --- | --- | 2015-08-12 13:30 | 2015-09-01 | 0 | 0 | 0 | 466.5 | SVRD | N/A | N/A | N/A | H/T or kept open as per ERLDC instruction for voltage regulation
[9 empty] | TOTAL | 0 | 0 | 0 | 650.88 | [6 empty] | 100
60 | ERL87 | 400KV NSLG-BONGAIGAON-1 | 217 | --- | --- | --- | --- | 2015-08-05 10:44 | 2015-08-05 14:03 | 3.3167 | 0 | 0 |  | OSPT | N/A | N/A | N/A | Shut down for attending oil leakage ,R-phase CVT at Binaguri/PG end.
[9 empty] | TOTAL | 3.3167 | 0 | 0 | 0 | [6 empty] | 99.5542
61 | ERL04 | 400KV FARAKKA- BEHRAMPUR | 70.73 | --- | --- | --- | --- | 2015-08-27 10:32 | 2015-08-27 17:50 | 0 | 0 | 0 | 7.3 | OSPD | N/A | N/A | N/A | Shut down taken by NTPC/Farakka for relay testing work at their end.
[9 empty] | TOTAL | 0 | 0 | 0 | 7.3 | [6 empty] | 100
62 | ERL58 | 765 KV ANGUL- JHARSUGUDA - II | 274.92 | --- | --- | --- | --- | 2015-08-01 08:20 | 2015-08-01 18:32 | 0 | 10.2 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-02 08:00 | 2015-08-02 18:08 | 0 | 10.1333 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-03 08:09 | 2015-08-03 21:25 | 0 | 13.2667 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-05 08:23 | 2015-08-05 18:27 | 0 | 10.0667 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-06 08:13 | 2015-08-06 18:40 | 0 | 10.45 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-07 08:05 | 2015-08-07 19:43 | 0 | 11.6333 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-08 08:06 | 2015-08-08 18:34 | 0 | 10.4667 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-09 07:51 | 2015-08-09 19:55 | 0 | 12.0667 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-14 08:02 | 2015-08-14 21:54 | 0 | 13.8667 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL- JHARSUGUDA - II |  | --- | --- | --- | --- | 2015-08-16 08:21 | 2015-08-16 18:08 | 0 | 9.7833 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL - JHARSUGDA - II |  | --- | --- | --- | --- | 2015-08-17 09:02 | 2015-08-17 19:02 | 0 | 10 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
|  | 765 KV ANGUL - JHARSUGDA - II |  | --- | --- | --- | --- | 2015-08-18 08:01 | 2015-08-18 18:47 | 0 | 10.7667 | 0 | 0 | OMSU | N/A | N/A | N/A | Sd for stringing of balance OPGW work.
[9 empty] | TOTAL | 0 | 132.7 | 0 | 0 | [6 empty] | 100
63 | E2R24 | 63 MVAR B/R AT JEYPORE | 63 | --- | --- | --- | --- | 2015-08-21 09:16 | 2015-08-21 11:32 | 0 | 0 | 0 | 2.2667 | SVRD | N/A | N/A | N/A | H/T or kept open as per ERLDC instruction for voltage regulation
[9 empty] | TOTAL | 0 | 0 | 0 | 2.2667 | [6 empty] | 100
64 | ERL55 | 400 KV S,DIGHI - BAHARAMPUR - I | 71 | --- | --- | --- | --- | 2015-08-28 11:03 | 2015-08-28 16:50 | 0 | 0 | 0 | 5.7833 | OSPD | N/A | N/A | N/A | S/D taken for details checking of PLCC panels at Sagardighi end
[9 empty] | TOTAL | 0 | 0 | 0 | 5.7833 | [6 empty] | 100
65 | ER89 | Berhampore - Bheramara - I(Indian portion) | 71.51 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
66 | ER90 | Berhampore - Bheramara - II(Indian Portion) | 71.51 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
67 | ERL02 | MEJIA - Jamshedpur - I | 167.74 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
68 | ERL03 | MTN-JSR II | 153 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
69 | ERL06 | JRT-SGM-II | 63 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
70 | ERL07 | FKK-SGDI-II | 55.38 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
71 | ERL08 | SGDI - SGM-II | 245.64 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
72 | ERL09 | FKK-DGP I | 150 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
73 | ERL10 | FKK-DGP II | 146 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
74 | ERL11 | MLD-FKK I | 40 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
75 | ERL13 | DGP-JSR | 177 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
76 | ERL16 | RNG-TAL I | 24 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
77 | ERL17 | RNG-TAL II | 24 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
78 | ERL20 | NSLG - NPRN- I | 168 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
79 | ERL21 | NSLG - NPRN- II | 168 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
80 | ERL25 | TAL-ANGUL # II | 68.35 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
81 | ERL26 | ANGUL-Meramundali # II | 18.61 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
82 | ERL27 | JPR-BOLANGIR# I | 287 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
83 | ERL29 | ANGUL-MERAMUNDALI # I | 25.34 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
84 | ERL30 | RNG-Keonjhar ( LILO Portion) | 9.38 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
85 | ERL31 | Keonjhar-BPD (both LILO Portion) | 28.12 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
86 | ERL32 | BRPD-KGP(LILO) | 18.74 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
87 | ERL33 | TALA-NSILIGURI-I | 98.087 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
88 | ERL34 | TALA-NSILIGURI-II | 98.087 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
89 | ERL35 | TALA-SILIGURI-III | 115.553 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
90 | ERL36 | TALA-SILIGURI-IV | 115.553 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
91 | ERL40 | Rangpo-TSTA-II | 21.42 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
92 | ERL47 | ANDAL - JSR - I | 156.76 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
93 | ERL48 | ANDAL - JSR - II | 156.76 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
94 | ERL53 | Rourkela-SEL I | 139 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
95 | ERL54 | Rourkela-SEL II | 135 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
96 | ERL56 | Berhampore-Sdighi-II | 26.1 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
97 | ERL63 | BRP-NSLG II | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
98 | ERL68 | DLK-MLD I | 116 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
99 | ERL69 | DLK-MLD II | 116 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
100 | ERL72 | BTPS-SLKT-I | 3 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
101 | ERL73 | BTPS-SLKT-II | 3 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
102 | ERL75 | Rangpo-JHEP | 22 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
103 | ERL76 | New Melli-JHEP | 4.1 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
104 | ERL77 | Kurseong-RNGT-I (up to LILO) | 61.2 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
105 | ERL78 | RANGIT-Rangpo | 26.381 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
106 | ERL79 | Rangpo-GANGTOK | 54.08 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
107 | ERL80 | MELLI-Chujachenj(Up to LILO) | 21 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
108 | ERL81 | Chujacheng-Rangpo (LILO) | 1 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
109 | ERL82 | Rangpo-Gangtok (including LILO) | 17 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
110 | ERL84 | RNGT-RMM | 27 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
111 | ERL85 | RNGT-Rabangla(up to LILO) | 1 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
112 | ERL86 | Ravangla - MLI(up to LILO) | 36 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
113 | ET01 | ICT-II Sundergarh | 1500 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
114 | ET02 | ICT-I Sundergarh | 1500 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
115 | ET03 | ICT-I,DGP | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
116 | ET04 | ICT-II,DGP | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
117 | ET05 | ICT-I,MTN | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
118 | ET06 | ICT-II,MTN | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
119 | ET07 | ICT-I,RKL | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
120 | ET08 | ICT-II,RKL | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
121 | ET09 | ICT-I, RNG | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
122 | ET10 | ICT-II, RNG | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
123 | ET12 | ICT-II, JPR | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
124 | ET13 | ICT-I,FKK | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
125 | ET15 | ICT-V,MLD | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
126 | ET16 | ICT-I, NSLG | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
127 | ET19 | ICT-II, NSLG | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
128 | ET20 | ICT-I, SGM | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
129 | ET21 | ICT-II, SGM | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
130 | ET22 | ICT-V, SGM | 500 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
131 | ET23 | ICT-II, BOLANGIR | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
132 | ET24 | ICT-I, BOLANGIR | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
133 | ET25 | ICT-I at Angul | 1500 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
134 | ET26 | ICT-IV at Angul | 1500 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
135 | ET27 | ICT-I, KEONJHAR | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
136 | ET28 | ICT-II, KEONJHAR | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
137 | ET29 | ICT-II BRPD | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
138 | ET30 | ICT-V RANGPO | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
139 | ET31 | ICT-IV RANGPO | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
140 | ET32 | ICT-III RANGPO | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
141 | ET33 | ICT-II RANGPO | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
142 | ET34 | ICT-I RANGPO | 315 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
143 | ET35 | ICT- II, BRPD | 160 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
144 | ET36 | ICT-I, BRPD | 160 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
145 | ET40 | ICT-II,BRP | 160 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
146 | ET47 | ICT-I, GTK | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
147 | ET48 | ICT-II,GTK | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
148 | E2R33 | 3*80, 1 ph BR-II at Sundergarh | 240 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
149 | E2R01 | 125 3ph B/R- II NSLG | 125 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
150 | E2R02 | 125 3ph B/R- I NSLG | 125 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
151 | E2R03 | 125 3ph B/R- III Angul | 125 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
152 | E2R04 | 125 3ph B/R- II Angul | 125 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
153 | E2R05 | 125 3ph B/R- I Angul | 125 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
154 | E2R06 | 110X3 MVAR BR-I at Angul | 330 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
155 | E2R07 | 110X3 MVAR BR-II at Angul | 330 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
156 | E2R08 | 125 3ph B/R- I Sundergarh | 125 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
157 | E2R09 | 125 3ph B/R- II Sundergarh | 125 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
158 | E2R10 | 3X80 3ph B/R- I Sundergarh | 240 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
159 | E2R11 | 80 BONGG-III L/R at Binaguri | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
160 | E2R12 | 80 BONGG-IV L/R at Binaguri | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
161 | E2R13 | 63 Mendhasal L/R at BPD | 63 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
162 | E2R14 | 50 MRL L/R at Bolangir | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
163 | E2R15 | 50 JPR L/R at Bolangir | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
164 | E2R17 | 50 Gaya-I L/R at Maithon | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
165 | E2R18 | 50 Gaya-II L/R at Maithon | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
166 | E2R19 | 80 MVAR B/R at Keonjhar | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
167 | E2R20 | 80 MVAR B/R at Berhampore | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
168 | E2R21 | 80 MVAR B/R -I at Rangpo | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
169 | E2R22 | 80 MVAR B/R -II at Rangpo | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
170 | E2R23 | 50 1ph B/R-I ,DGP | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
171 | E2R25 | 50 3ph B/R ,MTN | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
172 | E2R26 | 50 3ph B/R ,RKL | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
173 | E2R27 | 50 1ph B/R ,JRT | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
174 | E2R28 | 50 JSR -I L/R at RKL | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
175 | E2R30 | 50 BPD L/R at RNG | 50 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
176 | E2R31 | 80 JPR L/R at Meramundli | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
177 | E2R32 | 80 MVAR B/R at DUBRI | 80 | --- | --- | --- | --- |  |  | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A |  |  | 100
Note on C193: D.O.C.O - w.e.f 01.09.13
Note on C194: D.O.C.O - w.e.f 01.09.13
Note on C195: Author: made LILO on 20.01.10 & DOCO wef 01.02.10
Note on C198: Author: made LILO on 07.07.08
Note on C199: Author: made LILO on 07.07.08
Note on C208: Author: LILOed on 08.06.14
Note on C209: Author: LILOed at 10.06.14
Note on C210: Author: DOCO WEF - 01.09.12
Note on C211: Author: LILO at Angul, Charged on 29.03.13 and DOCO wef 01.04.13
Note on C212: Author: Keonjhar DOCO 01.02.2013
Note on C213: Author: Keonjhar DOCO 01.02.2013
Note on C219: 50084 doco 1.6.08 LILO 29.11.14
Note on C220: 50084 Charged Ckt-I on 30.04.12 DOCO on 01.05.2012
Note on C221: 50084 Charged Ckt-I on 30.04.12 DOCO on 01.05.2012
Note on C233: Author: LILO on 29.11.14
Note on C234: Author: LILO on 29.11.14
Note on C239: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C240: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C241: Author: DOCO : 31.07.14
Note on C242: Author: DOCO 2.11.2014
Note on C259: Author: DOCO 01.09.2012
Note on C260: Author: DOCO 01.11.2012
Note on C263: Author: DOCO 01.02.2013
Note on C264: Author: DOCO 01.03.2013
Note on C265: Author: doco 01.05.08
Note on C266: Author: DOCO 24.04.14 3 X 105 MVA
Note on C267: Author: DOCO 22.05.14 3 X 105 MVA
Note on C268: Author: DOCO 09.06.2014 3 X 105 MVA
Note on C269: Author: DOCO 30.06.2014 3 X 105 MVA
Note on C270: Author: DOCO 03.07.2014 3 X 105 MVA
Note on C271: Author: Charged on 22.03.11 at 15:00hrs and loaded on 23.03.11 at 16:10 hrs DOCO - 01.04.2011
Note on C273: Author: DOCO wef - 01.02.2013 under ERSS-IV
Note on C276: Author: DOCO 31.07.14
Note on C277: Author: DOCO w.e.f 01.11.2011
Note on C278: Author: DOCO w.e.f 01.04.2012
Note on C279: Author: DOCO w.e.f 01.05.2013
Note on C280: Author: DOCO w.e.f 01.06.2013
Note on C281: Author: DOCO w.e.f 01.11.2013
Note on C284: Author: DOCO w.e.f 01.05.2013
Note on C285: Author: DOCO w.e.f 01.06.2013
Note on C286: Author: DOCO w.e.f 01.05.2013
Note on C287: Author: DOCO wef 01.05.2013
Note on C288: Author: DOCO wef 01.06.2013
Note on C289: Author: DOCO 01.09.11
Note on C290: Author: DOCO 01.09.12
Note on C291: Author: DOCO 01.09.12
Note on C292: Author: D.O.C.O w.e.f 01.04.2012
Note on C293: Author: D.O.C.O w.e.f 01.04.2012
Note on C294: Author: Charged on 31.01.13 DOCO : 01.02.2013
Note on C295: Author: DOCO : w.e.f - 01.09.2013
Note on C296: Author: DOCO : w.e.f - 22.05.14
Note on C297: Author: DOCO : w.e.f - 09.06.2014
Note on C305: Author: 01.04.2014