## ODISHA
Standard of Performance data for the month of NOVEMBER 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD.,Odisha
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | Outage Attributable to |  |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Date | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | Detailed Reason(s) for Outage
1 | ODL1 | ROURKELA-TALCHER I | 171 | Odisha | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- | ERPC | 100
2 | ODL2 | ROURKELA-TALCHER II | 171 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
3 | ODL3 | RENGALI-TALCHER-I | 24 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
4 | ODL4 | RENGALI-TALCHER-II | 24 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
5 | ODL5 | RENGALI-INDRAVATI I | 356 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
6 | ODL6 | INDRAVATI-JEYPORE | 71 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
7 | ODL7 | TAL-MEERAMUNDALI | 51 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
8 | ODL8 | TALCHER-ANGUL | 68.35 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
9 | ODL9 | ANGUL-Meramundali # II | 18.61 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
10 | ODL10 | JEYPORE-BOLANGIR# I | 287 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
11 | ODL11 | BOLANGIR-ANGUL | 196.12 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
12 | ODL12 | ANGUL-MERAMUNDALI # I | 25.34 |  | --- | 2016-11-11 15:47 | 2016-11-11 18:24 | --- | --- | --- | 2.6167 | 0 | 0 | 0 | Shut down taken for rectification of B- phase jumper at Loc no: 03 as one of the conductor of jumper disconnected from one end. | --- | --- | --- |  | 99.645
[5 empty] | --- | 2016-11-12 23:11 | 2016-11-13 05:14 | --- | --- | --- | 0 | 6.05 | 0 | 0 | A/R was successful at Angul end.Tripped on B-N fault due to failure of B-phase Bushing & fire Hazard occured in ICT - I at Meramundali end,which is owned by OPTCL. | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 2.6167 | 6.05 | 0 | 0 |  | --- | --- | ---
13 | ODL13 | RNG-Keonjhar ( LILO Portion) | 9.38 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
14 | ODL14 | Keonjhar-BPD (both LILO Portion) | 28.12 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
15 | ODL15 | BARIPADA-KHARAGPUR(LILO) | 18.74 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | --- | --- | --- |  | 100
16 | ODL17 | BARIPADA-DUBURI | 190.247 |  | --- | 2016-11-23 15:23 | 2016-11-23 17:41 | --- | --- | --- | 2.3 | 0 | 0 | 0 | S/D taken for attending hot-spot at jumper at loc no 13 by replacing new bolts | --- | --- | --- |  | 99.6909
[5 empty] | --- |  | TOTAL | --- | --- | --- | 2.3 | 0 | 0 | 0 |  | --- | --- | ---
17 | ODL18A | DUBRI-PANDIABALLI | 143.3 |  | --- | 2016-11-10 16:49 | 2016-11-10 18:36 | --- | --- | --- | 0 | 0 | 1.7833 | 18.8 | S/d taken for rectification of jumper/ replacement of insulators at Loc: 7A/0 which was damaged by miscreants. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 1.7833 | 18.8 |  | --- | --- | --- |  | 100
18 | ODL18B | PANDIABALLI-MENDHASAL-II | 28 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
19 | ODL19 | Rourkela-Sundergarh I | 145.3 |  | --- | 2016-11-07 08:23 | 2016-11-07 19:35 | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-08 08:19 | 2016-11-08 19:13 | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | --- |  | 100
20 | ODL20 | Rourkela-Sundergarh II | 145.3 |  | --- | 2016-11-09 08:25 | 2016-11-09 19:53 | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | --- |  | 100
21 | ODL21 | Rourkela-Raigarh-II | 188 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
22 | ODL22 | Rourkela-SEL II | 135 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
23 | ODL23 | Sundargarh-Inbharat | 62.6 |  | --- | 2016-11-11 08:10 | 2016-11-12 18:31 | --- | --- | --- | 0 | 0 | 0 | 34 | S/d for modification in scheme of mechanical interlock in 400kv isolators at Sundergarh (constructional activity) in bay extension package | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-12 09:06 | 2016-11-12 17:21 | --- | --- | --- | 0 | 0 | 0 | 0 | S/d for modification in scheme of mechanical interlock in 400kv isolators at Sundergarh (constructional activity) in bay extension package | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 42 |  | --- | --- | --- |  | 100
24 | ODL24 | Angul-Sundargarh-II | 274.92 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
25 | ODL25 | Angul-Sundargarh-I | 272 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
26 | ODL26 | STERLITE-RAIGARH-II | 106 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
27 | ODL27 | IND-BHARAT-RAIGARH | 43 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
28 | ODL28 | SUNDERGARH-RAIGARH | 86 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
29 | ODL16A | BARIPADA-PANDIABALLI | 301.5 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
30 | ODL16B | PANDIABALLI-MENDHASHAL-I | 28 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
31 | ODT1 | ICT-II Sundergarh | 1500 | Odisha | --- | 2016-11-17 17:50 | 2016-11-17 18:25 | --- | --- | --- | 0 | 0.58333 | 0 | 0 |  | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-29 09:00 | 2016-11-29 19:05 | --- | --- | --- | 0 | 0 | 0 | 10.0833 | Spurious tripping generated from Bus Bar protection. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0.58333 | 0 | 10.0833 | For rectification of mechanical inter-lock of 400 KV Isolators & for RTV coating in 765 KV Bushing, as part of the punch point of constructional activities.. | --- | --- | --- |  | 100
32 | ODT2 | ICT-I Sundergarh | 1500 |  | --- | 2016-11-17 17:50 | 2016-11-17 18:24 | --- | --- | --- | 0 | 0.56667 | 0 | 0 |  | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-25 09:01 | 2016-11-25 18:52 | --- | --- | --- | 0 | 0 | 0 | 9.85 | For rectification of mechanical inter-lock of 400 KV Isolators & for RTV coating in 765 KV Bushing, as part of the punch point of constructional activities.. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-26 09:08 | 2016-11-26 17:54 | --- | --- | --- | 0 | 0 | 0 | 8.7667 | For rectification of mechanical inter-lock of 400 KV Isolators & for RTV coating in 765 KV Bushing, as part of the punch point of constructional activities.. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0.56667 | 0 | 18.6167 |  | --- | --- | --- |  | 100
33 | ODT3 | ICT-I,RKL | 315 |  | --- | 2016-11-01 | 2016-11-23 18:56 | --- | --- | --- | 0 | 0 | 0 | 546.9333 | Said ICT is 23 years old & require complete overhauling alongwith replacement of gasket to arrest oil leakage &thorough maintenance work for better performance & system improvement under ADDCAP | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 546.9333 |  | --- | --- | --- |  | 100
34 | ODT4 | ICT-II,RKL | 315 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
35 | ODT5 | ICT-I, RNG | 315 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
36 | ODT6 | ICT-II, RNG | 315 |  | --- | 2016-11-01 | 2016-11-03 19:13 | --- | --- | --- | 0 | 0 | 0 | 67.2167 | Said ICT is 26 years old & s/d taken to replace 220 KV Y-phase bushing & 400 KV Y-Phase bushing due to violation of Ten-delta & oil leakage for better performance & system improvement under ADDCAP | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 67.2167 |  | --- | --- | --- |  | 100
37 | ODT7 | ICT-I, JEYPORE | 315 |  | --- | 2016-11-18 12:35 | 2016-11-18 13:38 | --- | --- | --- | 1.05 | 0 | 0 | 0 | To replace R-phase unit of ICT:I with spare phase ICT, for oil replacement. | --- | --- | --- |  | 99.86
[5 empty] | --- |  | TOTAL | --- | --- | --- | 1.05 | 0 | 0 | 0 |  | --- | --- | ---
38 | ODT8 | ICT-II, JEYPORE | 315 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
39 | ODT9 | ICT-I BRPD | 315 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
40 | ODT10 | ICT- II, INDRAVATI | 315 |  | --- | 2016-11-10 09:45 | 2016-11-19 17:05 | --- | --- | --- | 0 | 0 | 0 | 223.3333 | For replacement of defective 400 KV R-phase Bushing of ICT:II at GRIDCO S/Y, for system improvement as pro-active action.. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 223.3333 |  | --- | --- | --- |  | 100
41 | ODT11 | ICT-II, BOLANGIR | 315 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
42 | ODT12 | ICT-I, BOLANGIR | 315 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
43 | ODT13 | ICT-I at Angul | 1500 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
44 | ODT14 | ICT-2 at Angul | 1500 |  | --- | --- | --- | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
45 | ODT15 | ICT-3 at Angul | 1500 |  | --- | 2016-11-15 12:00 | 2016-11-16 11:38 | --- | --- | --- | 0 | 0 | 0 | 23.6333 | S/D taken for commissioning of Spare ICT unit in place of B-Phase of said bank under construction head | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 23.6333 |  | --- | --- | --- |  | 100
46 | ODT16 | ICT-IV at Angul | 1500 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
47 | ODT17 | ICT-I, KEONJHAR | 315 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
48 | ODT18 | ICT-II, KEONJHAR | 315 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
49 | ODT19 | ICT-II BRPD | 315 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
47 | ODT20 | ICT- II, BRPD | 160 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
48 | ODT21 | ICT-I, BRPD | 160 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
49 | ODT22 | ICT-I,PANDIABALLI | 500 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
50 | ODT23 | ICT-II,PANDIABALLI | 500 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
51 | ODT24 | ICT-III BARIPADA | 500 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
52 | ODR1 | 240, 1 ph BR-II at Sundergarh | 240 | Odisha | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
53 | ODR2 | 125 3ph B/R- III Angul | 125 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
54 | ODR3 | 125 3ph B/R- II Angul | 125 |  | --- | [10 empty] | --- | --- | --- |  | 100
55 | ODR4 | 125 3ph B/R- I Angul | 125 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
56 | ODR5 | 330 MVAR BR-I at Angul | 330 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
57 | ODR6 | 330 MVAR BR-II at Angul | 330 |  | --- | [10 empty] | --- | --- | --- |  | 100
58 | ODR7 | 240 MVAR SLR-1 at Angul | 240 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
59 | ODR8 | 240 MVAR SLR-2 at Angul | 240 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
60 | ODR9 | 125 3ph B/R- I Sundergarh | 125 |  | --- | 2016-11-03 08:21 | 2016-11-03 19:55 | --- | --- | --- | 0 | 0 | 0 | 11.5667 | S/D taken by Sundergarh for facilitating testing of new 400KV isolators under bay extension construction work at Sundergarh end. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL |  |  |  | 0 | 0 | 0 | 11.5667 |  | --- | --- | --- |  | 100
61 | ODR10 | 125 3ph B/R- II Sundergarh | 125 |  | --- | 2016-11-05 09:18 | 2016-11-05 18:36 | --- | --- | --- | 0 | 0 | 0 | 9.3 | S/D taken by Sundergarh for facilitating testing of new 400KV isolators under bay extension construction work at Sundergarh end. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 9.3 |  | --- | --- | --- |  | 100
[5 empty] | --- | [10 empty] | --- | --- | --- |  | 100
63 | ODR11 | 240 3ph B/R- I Sundergarh | 240 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
64 | ODR12 | 63 Mendhasal L/R at BPD | 63 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
65 | ODR13 | 50 MRL L/R at Bolangir | 50 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
66 | ODR14 | 50 JPR L/R at Bolangir | 50 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
67 | ODR15 | 80 MVAR B/R at Bolangir | 80 |  | --- | 2016-11-01 | 2016-12-01 | --- | --- | --- | 0 | 0 | 0 | 720 | H/T or kept open as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 720 | [5 empty] | 100
68 | ODR16 | 80 MVAR B/R at Keonjhar | 80 |  | --- |  |  | --- | --- | --- | [9 empty] | 100
69 | ODR17 | 63 3ph B/R ,JEYPORE | 63 |  | --- | 2016-11-17 08:34 | 2016-11-18 09:15 | --- | --- | --- | 0 | 0 | 0 | 24.6833 | Hand tripped as per ERLDC instruction for voltage regulation. |  |  |  |  | 100
[5 empty] | --- | 2016-11-19 07:33 | 2016-11-19 21:11 | --- | --- | --- | 0 | 0 | 0 | 13.6333 | Hand tripped as per ERLDC instruction for voltage regulation. |  |  |  |  | 100
[5 empty] | --- | 2016-11-20 05:20 | 2016-11-21 07:06 | --- | --- | --- | 0 | 0 | 0 | 25.7667 | Hand tripped as per ERLDC instruction for voltage regulation. |  |  |  |  | 100
[5 empty] | --- | 2016-11-22 10:45 | 2016-11-23 02:28 | --- | --- | --- | 0 | 0 | 0 | 15.7167 | H/T or kept open as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-23 07:51 | 2016-11-23 12:32 | --- | --- | --- | 0 | 0 | 0 | 4.6833 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-23 16:49 | 2016-11-27 21:27 | --- | --- | --- | 0 | 0 | 0 | 100.6333 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-29 10:18 | 2016-11-29 22:44 | --- | --- | --- | 0 | 0 | 0 | 12.4333 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-15 06:02 | 2016-11-15 06:13 | --- | --- | --- | 0 | 0 | 0 | 0.18333 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-15 21:58 | 2016-11-16 07:47 | --- | --- | --- | 0 | 0 | 0 | 9.8167 | H/T as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 207.55 |  | --- | --- | --- |  | 100
70 | ODR18 | 50 3ph B/R ,RKL | 50 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
71 | ODR19 | 50 1ph B/R ,JRT | 0 |  | --- | 2016-11-04 17:20 | 2016-11-04 22:01 | --- | --- | --- | 0 | 0 | 0 | 4.6833 |  | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 4.6833 |  | --- | --- | --- |  | 100
72 | ODR20 | 50 JSR -I L/R at RKL | 50 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
73 | ODR21 | 125MVAR BR-I at RKL | 125 |  | --- | 2016-11-26 13:00 | 2016-11-26 14:19 | --- | --- | --- | 0 | 0 | 0 | 1.3167 | For final commissioning of PSD (Phaseor sequencing device), as part of the incorporated this new element for system stability. | --- | --- | --- |  | 99.33
[5 empty] | --- | 2016-11-08 12:35 | 2016-11-08 17:32 | --- | --- | --- | 4.95 | 0 | 0 | 0 | S/D taken for verifying the setting & fine tuning of PSD at Rourkela. | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 4.95 | 0 | 0 | 1.3167 |  | --- | --- | ---
74 | ODR22 | 50 BPD L/R at RNG | 50 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
75 | ODR23 | 80 JPR L/R at Meramundli | 80 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
76 | ODR24 | 80 MVAR B/R at DUBRI | 80 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
77 | ODR25 | 125 MVAR B/R at IVT | 125 |  | --- | 2016-11-18 09:10 | 2016-11-18 12:00 | --- | --- | --- | 0 | 0 | 0 | 2.8333 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 2.8333 |  | --- | --- | --- |  | 100
78 | ODR26 | 125 MVAR B/R at JPR | 125 |  | --- | 2016-11-15 06:05 | 2016-11-15 08:30 | --- | --- | --- | 0 | 0 | 0 | 2.4167 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 2.4167 |  | --- | --- | --- |  | 100
79 | ODR27 | 50MVAR Keonjhar LR at Baripada | 50 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
80 | ODR28 | 63MVAR BARIPADA L/R AT PANDIABALLI | 63 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
81 | ODR29 | 80MVAR B/R AT PANDIABALLI | 80 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
[5 empty] | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
82 | ODR30 | 125MVAR B/R AT BARIPADA | 125 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
[5 empty] | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
Note on C14: Author: LILOed on 08.06.14
Note on C15: Author: LILOed at 10.06.14
Note on C16: Author: DOCO WEF - 01.09.12
Note on C17: Author: LILO at Angul, Charged on 29.03.13 and DOCO wef 01.04.13
Note on C18: Author: LILO at Angul, Charged on 29.03.13 and DOCO wef 01.04.13
Note on C21: Author: Keonjhar DOCO 01.02.2013
Note on C22: Author: Keonjhar DOCO 01.02.2013
Note on C24: 50084 Charged both Ckt on 29.08.11 DOCO on 01.09.2011
Note on C40: Author: 25.01.2016
Note on C46: Author: DOCO : 31.07.14
Note on C49: Author: DOCO 2.11.2014
Note on C65: Author: DOCO 01.09.2012
Note on C66: Author: DOCO 01.11.2012
Note on C68: Author: 04.05.2015
Note on C69: Author: 25.01.2016
Note on C72: Author: DOCO 01.02.2013
Note on C73: Author: DOCO 01.03.2013
Note on C74: Author: doco 01.05.08
Note on C75: Author: Charged on 22.03.11 at 15:00hrs and loaded on 23.03.11 at 16:10 hrs DOCO - 01.04.2011

## ER-II
Standard of Performance data for the month of NOVEMBER 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION - II
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | Outage Attributable to |  |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Date | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | Detailed Reason(s) for Outage
1 | ER2L1 | Maithon -MEJIA - III | 83.74 | ER-II | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- | ERPC | 100
2 | ER2L2 | MEJIA - Jamshedpur - I | 167.74 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
3 | ER2L3 | Maithon-Jamshedpur | 153 |  | --- | 2016-11-19 13:55 | 2016-11-19 16:34 | --- | --- | --- | 0 | 2.65 | 0 | 0 | Line tripped due to a bamboo fallen on top phase of the line (R-ph),the stem of the said bamboo tree was far away from Powergrid's line corridor . However,as huge flashing occured on that instant, local people got agitated.Charging of line took time to make the situation under control by concerened TL personnel with the help of local authority . Tripped on R-N; R/I at Maithon end: M1: Dist: 33.7 km; F/current: 8.6 KA; M:II- 32.5 km; 6.5 KA; Jamshedpur end: Dist: 123.1 km; 2.6 KA; | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 2.65 | 0 | 0 |  | --- | --- | ---
4 | ER2L4 | Farakka-Baharampore - I(upto LILO) | 70.725 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
5 | ER2L5 | Berhampore - Jeerat - I(upto LILO) | 165.266 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
6 | ER2L6 | Jeerat-Subhasgram | 63 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
7 | ER2L7 | Farakka-Sagardighi | 55.38 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
8 | ER2L8 | Sagardighi- Subhasgram | 245.64 |  | --- | 2016-11-29 09:12 | 2016-11-29 10:08 | --- | --- | --- | 0 | 0.93333 | 0 | 0 | S/D for taking 50 MVAR L/R of 400 KV S,Gram-S,Dighi line at S,Gram end into service | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0.93333 | 0 | 0 |  | --- | --- | ---
9 | ER2L9 | Farakka-Durgapur-I | 150 |  | --- | 2016-11-06 09:43 | 2016-11-06 09:43 | --- | --- | --- | 0 | 0 | 0 | 0 | Auto Reclose operated successfully. R/I at DGP: M1- B-N fault, F/D-55.4kms, F/C- 5.53kA;M2- B-N fault, F/D-56.84kms., F/C- 5.4KA | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-24 10:26 | 2016-11-24 16:26 | --- | --- | --- | 0 | 0 | 0 | 6 | S/D taken by NTPC/FKK for breaker CRM & timing testing at NTPC/Farakka end. | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 6 |  | --- | --- | ---
10 | ER2L10 | Farakka-Durgapur-II | 146 |  | --- | 2016-11-06 10:35 | 2016-11-06 10:35 | --- | --- | --- | 0 | 0 | 0 | 0 | Auto Reclose operated successfully.R/I at DGP: M1- B-N fault, F/D-72.50kms, F/C- 3.92kA;M2- B-N fault, F/D-73.86kms., F/C- 3.96 KA | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-09 10:46 | 2016-11-09 10:46 | --- | --- | --- | 0 | 0 | 0 | 0 | A/R operated at both end. R/I at DGP: M1: Y-N; Z1; 7.22 KM, F/Current: 14.318 KA; M2: Y-N; Z1; 6.91 KM; 15.11 KA; | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | ---
11 | ER2L11 | Malda-Farakka-I | 40 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
12 | ER2L12 | Malda-Farakka-II | 40 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
13 | ER2L13 | Durgapur-Jamshedpur | 177 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
14 | ER2L14 | Binaguri-New Purnea-I | 168 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
15 | ER2L16 | Malda-New Purnea-I | 167 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
16 | ER2L17 | Malda-New Purnea-II | 167 |  | --- | 2016-11-17 05:51 | 2016-11-17 08:45 | --- | --- | --- | 2.9 | 0 | 0 | 0 | Due to operation of Buccholz relay of Neutral Grounding Reactor (NGR) at Malda end, 400kv Malda-NewPurnea -II tripped. | --- | --- | --- |  | 99.6102
[5 empty] | --- |  | TOTAL | --- | --- | --- | 2.9 | 0 | 0 | 0 |  | --- | --- | ---
17 | ER2L18 | TALA-BINAGURI-I | 98.087 |  | --- | 2016-11-14 22:43 | 2016-11-21 08:50 | --- | --- | --- | 0 | 0 | 0 | 154 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 154 |  | --- | --- | ---
18 | ER2L19 | TALA-BINAGURI-II | 98.087 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
19 | ER2L20 | TALA-BINAGURI-III | 115.553 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
20 | ER2L21 | TALA-BINAGURI-IV | 115.553 |  | --- | 2016-11-01 13:29 | 2016-12-01 | --- | --- | --- | 0 | 0 | 0 | 706 | H/T as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 706 |  | --- | --- | ---
21 | ER2L22 | BINAGURI-Rangpo-I | 109.88 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
22 | ER2L23 | Rangpo-TEESTA-I | 11.83 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
23 | ER2L24 | BINAGURI-Rangpo- II | 110.42 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
24 | ER2L25 | Rangpo-Teesta-II | 21.42 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
25 | ER2L26 | MAITHON - MEJIA - I | 59.182 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
26 | ER2L27 | MAITHON - MEJIA - II | 59.182 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
27 | ER2L28 | MAITHON - Durgapur - I | 70.77 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
28 | ER2L29 | MAITHON - Durgapur - II | 70.77 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
29 | ER2L30 | ANDAL - Jamshedpur - I | 156.76 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
[5 empty] | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
30 | ER2L31 | ANDAL - Jamshedpur - II | 156.76 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
[5 empty] | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
31 | ER2L32 | Maithon - MaithonRB- I | 31.5 |  | --- | 2016-11-17 12:31 | 2016-11-17 14:32 | --- | --- | --- | 2.0167 | 0 | 0 | 0 | To attend misalignment problem on Y-phase line isolator at Maithon end. | --- | --- | --- |  | 99.7289
[5 empty] | --- |  | TOTAL | --- | --- | --- | 2.0167 | 0 | 0 | 0 |  | --- | --- | ---
32 | ER2L33 | Maithon - MaithonRB- II | 31.5 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
33 | ER2L33 | Baharampore-Sagardighi-I | 26.1 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
34 | ER2L34 | Baharampore-Sagardighi-II | 26.1 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
35 | ER2L37 | Chukha-Birpara-I | 36 |  | --- | 2016-11-27 08:55 | 2016-11-27 18:54 | --- | --- | --- | 0 | 0 | 0 | 9.9833 | S/D taken for installation of polymer insulator in place of existing porcelain insulator for system improvement under construction head. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-27 18:54 | 2016-11-28 08:55 | --- | --- | --- | 0 | 14.0167 | 0 | 0 | Line has been charged from Birpara end but could not Syncronised due to some technical problem at chukha end under Bhutan jurisdiction | --- | --- | ---
[5 empty] | --- | 2016-11-28 08:55 | 2016-11-28 17:14 | --- | --- | --- | 0 | 0 | 0 | 8.3167 | S/D taken for installing polymer insulator in place of existing porcelain insulator under construction head for system improvement | --- | --- | ---
[5 empty] | --- | 2016-11-28 17:14 | 2016-12-01 | --- | --- | --- | 0 | 54.7667 | 0 | 0 | Line has been charged from Birpara end but could not Syncronised due to some technical problem at chukha end under Bhutan jurisdiction | --- | --- | ---
[5 empty] | --- | 2016-11-26 09:43 | 2016-11-26 18:08 | --- | --- | --- | 0 | 0 | 0 | 8.4167 | S/D taken for installing polymer insulator in place of existing porcelain insulator under construction head ,for system improvement | --- | --- | ---
[5 empty] | --- | 2016-11-26 18:08 | 2016-11-27 08:55 | --- | --- | --- | 0 | 14.7833 | 0 | 0 | Line has been charged from Birpara end but could not Syncronised due to some technical problem at chukha end under Bhutan jurisdiction | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 83.5667 | 0 | 2.7167 |  | --- | --- | ---
36 | ER2L38 | Chukha-Birpara-II | 36 |  | --- | 2016-11-21 14:40 | 2016-11-22 09:50 | --- | --- | --- | 0 | 0 | 0 | 19.1667 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-22 09:50 | 2016-11-22 18:32 | --- | --- | --- | 0 | 0 | 0 | 8.7 | S/D taken for installing polymer insulator in place of existing porcelain insulator under construction head for system improvement | --- | --- | ---
[5 empty] | --- | 2016-11-23 03:20 | 2016-11-23 08:30 | --- | --- | --- | 0 | 0 | 0 | 5.1667 | Hand tripped as per ERLDC instruction for voltage regulation. | --- | --- | ---
[5 empty] | --- | 2016-11-23 08:30 | 2016-11-23 18:02 | --- | --- | --- | 0 | 0 | 0 | 9.5333 | S/D taken for installing polymer insulator in place of existing porcelain insulator under construction head for system improvement . The line is ready for charging at 18:02hrs on 23.11.16 from Powergrid Birpara end but kept open as per ERLDC instruction | --- | --- | ---
[5 empty] | --- | 2016-11-23 18:02 | 2016-11-24 09:20 | --- | --- | --- | 0 | 0 | 0 | 15.3 | Kept open as per ERLDC instruction . The line is ready for charging at 18:02hrs on 23.11.16 from Powergrid Birpara end but kept open as per ERLDC instruction. | --- | --- | ---
[5 empty] | --- | 2016-11-24 09:20 | 2016-11-24 18:37 | --- | --- | --- | 0 | 0 | 0 | 9.2833 | S/D taken for installing polymer insulator in place of existing porcelain insulator under construction head for system improvement | --- | --- | ---
[5 empty] | --- | 2016-11-24 18:37 | 2016-11-25 12:55 | --- | --- | --- | 0 | 18.3 | 0 | 0 | Line has been charged from Birpara end but could not Syncronised due to some technical problem at chukha end | --- | --- | ---
[5 empty] | --- | 2016-11-25 12:55 | 2016-11-25 18:47 | --- | --- | --- | 0 | 0 | 0 | 5.8667 | S/D taken for installing polymer insulator in place of existing porcelain insulator under construction head for system improvement | --- | --- | ---
[5 empty] | --- | 2016-11-25 18:47 | 2016-11-26 09:33 | --- | --- | --- | 0 | 14.7667 | 0 | 0 | Line has been charged from Birpara end but could not Syncronised due to some technical problem at chukha end which is under Bhutan jurisdiction | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 33.0667 | 0 | 73.0167 |  | --- | --- | ---
37 | ER2L39 | MALBASE-Birpara(CHUKHA III) | 38 |  | --- | 2016-11-03 17:19 | 2016-11-03 19:23 | --- | --- | --- | 2.0667 | 0 | 0 | 0 | To attend hot spot at R-Ph CT connector | --- | --- | --- |  | 99.72
[5 empty] | --- |  | TOTAL | --- | --- | --- | 2.0667 | 0 | 0 | 0 |  | --- | --- | ---
38 | ER2L40 | Birpara-Binaguri-I | 80 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
39 | ER2L41 | Birpara-Binaguri-II | 80 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
40 | ER2L42 | Birpara-Salakati-I | 161 |  | --- | 2016-11-16 09:09 | 2016-11-19 12:23 | --- | --- | --- | 0 | 0 | 0 | 75.23 | S/D taken for energisation of 220kv Alipurduar switch yard by LILO of existing 220kv Birpara-Salakati -D/C lines at Alipurduar under construction head under NE-NW project | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 75.23 |  | --- | --- | ---
41 | ER2L43 | Birpara-Salakati-II | 161 |  | --- | 2016-11-16 09:09 | 2016-11-19 13:06 | --- | --- | --- | 0 | 0 | 0 | 75.95 | S/D taken for energisation of 220kv Alipurduar switch yard by LILO of existing 220kv Birpara-Salakati -D/C lines at Alipurduar under construction head under NE-NW project | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 75.95 |  | --- | --- | ---
42 | ER2L44 | Siliguri-Kishengunj-I | 108 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
43 | ER2L45 | Siliguri-Kishengunj-II | 108 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
44 | ER2L46 | Dalkhola-Kishengunj-I | 30.9 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
45 | ER2L47 | Dalkhola-Kishengunj-II | 30.9 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
46 | ER2L48 | Dalkhola-Malda-I | 116 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
47 | ER2L49 | Dalkhola-Malda-II | 116 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
48 | ER2L50 | Binaguri-Siliguri-I | 9 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
49 | ER2L51 | Binaguri-Siliguri-II | 9 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
50 | ER2L52 | Rangpo-New Melli | 26.1 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
51 | ER2L53 | Rangpo-JHEP | 22 |  | --- | 2016-11-11 10:08 | 2016-11-12 18:37 | --- | --- | --- | 0 | 32.4833 | 0 | 0 | S/D taken by JLHEP for charging of 220kv Jorethang-New Melli dedicated feeder-I by withdrawing present LILO arrangement through Bay No-206 at New Melli & restoration of 220kv Rangpo-New Melli - I feeder after withdrawing LILO.It was under construction head activity | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 32.4833 | 0 | 0 |  | --- | --- | ---
52 | ER2L54 | New Melli-JHEP | 4.1 |  | --- | 2016-11-07 14:30 | 2016-11-12 18:37 | --- | --- | --- | 0 | 124.1167 | 0 | 0 | S/D taken for removal of present LILO arrangement by DANS Energy at New-Melli S/S which is under construction head | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 124.1167 | 0 | 0 |  | --- | --- | ---
53 | ER2L55 | Siliguri-Kurseong-I (up to LILO) | 31.3 |  | --- | 2016-11-28 07:47 | 2016-11-28 12:45 | --- | --- | --- | 0 | 0 | 0 | 0 | Shut down taken for final GIS commissioning activivites of the said line bay, at Siliguri S/S end under construction head ERSS-XII | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | ---
54 | ER2L56 | Kurseong-Rangit-I (up to LILO) | 61.2 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
55 | ER2L57 | RANGIT-Rangpo | 54.17 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
56 | ER2L58 | Rangpo-GANGTOK-1 | 26.36 |  | --- |  |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
57 | ER2L59 | Chujacheng-Rangpo (LILO) | 1 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
58 | ER2L60 | Chuzacheng-Gangtok | 28.06 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
59 | ER2L61 | MELLI-SILIGURI | 92.45 |  | --- | 2016-11-20 11:04 | 2016-11-20 12:56 | --- | --- | --- | 0 | 0 | 0 | 0 | S/D taken for construction work of conversion of 132 KV AIS to GIS at Siliguri S/s under ERSS-XII | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-26 07:12 | 2016-11-26 19:17 | --- | --- | --- | 0 | 0 | 0 | 0 | Shut down taken for final GIS commissioning activivites of the said line bay, at Siliguri S/S end under construction head under ERSS-XII | --- | --- | ---
[5 empty] | --- | 2016-11-27 20:24 | 2016-11-28 02:27 | --- | --- | --- | 0 | 0 | 0 | 0 | Shut down taken for final GIS commissioning activivites of the said line bay, at Siliguri S/S end under construction head under ERSS-XII | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | ---
60 | ER2L62 | RANGPO-MELLI | 16.61 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
61 | ER2L63 | Rangit-Rammam | 27.15 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
62 | ER2L64 | Rangit-Rabangla(up to LILO) | 1 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
63 | ER2L65 | Rabangla - Melli(up to LILO) | 36 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
64 | ER2L66 | Binaguri-Bongaigaon-I | 217.275 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
65 | ER2L67 | Binaguri-Bongaigaon-II | 217.275 |  | --- | 2016-11-09 23:28 | 2016-11-10 16:51 | --- | --- | --- | 0 | 0 | 0 | 0 | H/T as per ERLDC instruction for voltage regulation. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | ---
66 | ER2L68 | Farakka-Baharampore - I (LILO portion) | 2.54 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
67 | ER2L69 | Baharampore-Jeerat - I(LILO portion) | 2.634 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
68 | ER2L70 | Baharampore - Bheramara - I(Indian portion) | 71.51 |  | --- | 2016-11-25 07:41 | 2016-11-25 15:51 | --- | --- | --- | 0 | 0 | 0 | 0 | Planned Shut down taken by Bheramara, Bangladesh for planned work of transmission system at there end | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | ---
69 | ER2L71 | Baharampore - Bheramara - II(Indian Portion) | 71.51 |  | --- | 2016-11-26 07:25 | 2016-11-26 15:23 | --- | --- | --- | 0 | 0 | 0 | 0 | Planned Shut down taken by Bheramara, Bangladesh for planned work of transmission system at there end | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 0 |  | --- | --- | ---
70 | ER2L42A | BIRPARA-ALIPURDUAR-I | 57.49 |  | --- | [14 empty] | 100
71 | ER2L42B | SALAKATI-ALIPURDUAR-I | 100.57 |  | --- | [14 empty] | 100
72 | ER2L43A | BIRPARA-ALIPURDUAR-II | 57.49 |  | --- | [14 empty] | 100
73 | ER2L43B | SALAKATI-ALIPURDUAR-I | 100.57 |  | --- | [14 empty] | 100
74 | ER2L53A | RANGPO-NEW-MELLI-II | 26.1 |  | ---
75 | ER2T1 | ICT-I,DGP | 315 | ER-II | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
76 | ER2T2 | ICT-II,DGP | 315 |  | --- | 2016-11-13 13:07 | 2016-11-13 14:04 | --- | --- | --- | 0 | 0.95 | 0 | 0 | 220KV DGP-DVC-I (line belongs to DVC) tripped at 13:07hrs. on 13.11.2016. Y-phase LA got blast at DVC end. Fault sensed in Zone-2 & F/C-8.16 KA at Durgapur end. Back up earth fault operated with F/C-6.4 KA at 220KV side of ICT-II . | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0.95 | 0 | 0 |  | --- | --- | ---
77 | ER2T3 | ICT-I,MTN | 500 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
78 | ER2T4 | ICT-II,MTN | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
79 | ER2T5 | ICT-I,FKK | 315 |  | --- | 2016-11-09 11:39 | 2016-11-09 17:23 | --- | --- | --- | 0 | 0 | 0 | 5.7333 | S/D for constructional activities under ERSS-13 pkg. | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-08 11:22 | 2016-11-08 16:35 | --- | --- | --- | 0 | 0 | 0 | 5.2167 | S/D for constructional activities under ERSS-13 pkg. | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 10.95 |  | --- | --- | ---
80 | ER2T6 | ICT-III,MLD | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
81 | ER2T7 | ICT-V,MLD | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
82 | ER2T8 | ICT-I, NSLG | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
83 | ER2T9 | ICT-II, NSLG | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
84 | ER2T10 | ICT-I, SGM | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
85 | ER2T11 | ICT-II, SGM | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
86 | ER2T12 | ICT-V, SGM | 500 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
87 | ER2T13 | ICT-V RANGPO | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
88 | ER2T14 | ICT-IV RANGPO | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
89 | ER2T15 | ICT-III RANGPO | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
90 | ER2T16 | ICT-II RANGPO | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
91 | ER2T17 | ICT-I RANGPO | 315 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
92 | ER2T18 | ICT-I,SLG | 160 |  | --- | 2016-11-28 15:53 | 2016-11-28 23:51 | --- | --- | --- | 0 | 0 | 0 | 7.9667 | Shut down taken for final GIS commissioning activivites of the said line bay, at Siliguri S/S end under construction head. | --- | --- | --- |  | 100
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 7.9667 |  | --- | --- | ---
93 | ER2T19 | ICT-II,SLG | 160 |  | --- | 2016-11-26 07:13 | 2016-11-26 19:03 | --- | --- | --- | 0 | 0 | 0 | 11.8333 | Shut down taken for final GIS commissioning activivites | --- | --- | --- |  | 100
[5 empty] | --- | 2016-11-27 20:27 | 2016-11-28 02:24 | --- | --- | --- | 0 | 0 | 0 | 5.95 | Shut down taken for final GIS commissioning activivites under construction head. | --- | --- | ---
[5 empty] | --- | 2016-11-08 10:25 | 2016-11-08 11:38 | --- | --- | --- | 0 | 0 | 0 | 1.2167 | S/D for GIS work under constructional activities dismantalling of the CTs foundations of ICT-II(AIS BAY) for erection of bus duct support at Siliguri . | --- | --- | ---
[5 empty] | --- |  | TOTAL | --- | --- | --- | 0 | 0 | 0 | 19 |  | --- | --- | ---
94 | ER2T20 | ICT-I,BRP | 160 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
95 | ER2T21 | ICT-II,BRP | 160 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
96 | ER2T22 | ICT-II, Malda | 160 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
97 | ER2T23 | ICT-I, Malda | 160 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
98 | ER2T24 | ICT-IV, MLD | 50 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
99 | ER2T25 | ICT-I, RANGPO | 100 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
100 | ER2T26 | ICT-II, RANGPO | 100 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
101 | ER2T27 | ICT-III, RANGPO | 100 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
102 | ER2T28 | ICT-I, GTK | 50 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
103 | ER2T29 | ICT-II,GTK | 50 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
103 | ER2R1 | 125 3ph B/R- II NSLG | 125 | ER-II | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
104 | ER2R2 | 125 3ph B/R- I NSLG | 125 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
105 | ER2R3 | 80 BONGG-III L/R at Binaguri | 80 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
106 | ER2R4 | 80 BONGG-IV L/R at Binaguri | 80 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
107 | ER2R5 | 50 Gaya-I L/R at Maithon | 50 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
108 | ER2R6 | 50 Gaya-II L/R at Maithon | 50 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
109 | ER2R7 | 80 MVAR B/R at Berhampore | 80 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
110 | ER2R8 | 80 MVAR B/R -I at Rangpo | 80 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
111 | ER2R9 | 80 MVAR B/R -II at Rangpo | 80 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
112 | ER2R10 | 50+125 MVAR B/R-I ,DGP | 175 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
113 | ER2R11 | 50 3ph B/R ,MTN | 50 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
114 | ER2R12 | 2*50 1ph B/R ,JRT | 100 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
115 | ER2R13 | 31.5MVAR B/R-I at New Melli | 31.5 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
116 | ER2R14 | 31.5MVAR B/R-II at New Melli | 31.5 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
117 | ER2R15 | 125MVAR B/R-I at Maithan | 125 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
118 | ER2R16 | 125MVAR B/R-II at Maithan | 125 |  | --- | --- |  | --- | --- | --- | [5 empty] | --- | --- | --- |  | 100
Note on C6: Author: made LILO on 20.01.10 & DOCO wef 01.02.10 Made further LILO at Andal on 22.01.11 & LILO on 01.02.11 LILO at Andal Removed in April'13
Note on C7: Author: made LILO on 20.01.10 & DOCO wef 01.02.10
Note on C10: Author: Made LILO w.e.f 01.09.13
Note on C11: Author: Made LILO w.e.f 01.09.13
Note on C13: Author: made LILO on 07.07.08
Note on C14: Author: made LILO on 07.07.08
Note on C37: 50084 doco 1.6.08 LILO on 29.11.14
Note on C39: 50084 Charged Ckt-I on 03.12.11 DOCO on 01.12.2011
Note on C40: 50084 Charged Ckt-II on 30.11.11 DOCO on 01.12.2011
Note on C41: 50084 Charged Ckt-I on 22.02.12 DOCO on 01.03.2012
Note on C42: 50084 Charged Ckt-I on 22.02.12 DOCO on 01.03.2012
Note on C43: 50084 Charged Ckt-I on 30.04.12 DOCO on 01.05.2012
Note on C45: 50084 Charged Ckt-I on 30.04.12 DOCO on 01.05.2012
Note on C47: 50084 doco 01.10.2010
Note on C93: Author: LILO on 29.11.14
Note on C103: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C104: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C108: Author: Made LILO w.e.f 01.09.13
Note on C109: Author: Made LILO w.e.f 01.09.13
Note on C110: D.O.C.O - w.e.f 01.09.13
Note on C134: Author: DOCO 24.04.14 3 X 105 MVA
Note on C135: Author: DOCO 22.05.14 3 X 105 MVA
Note on C136: Author: DOCO 09.06.2014 3 X 105 MVA
Note on C137: Author: DOCO 30.06.2014 3 X 105 MVA
Note on C138: Author: DOCO 03.07.2014 3 X 105 MVA
Note on C141: Author: DOCO 01.01.2013, ERSS-IV
Note on C146: Author: DOCO wef - 01.02.2013 under ERSS-IV
Note on C147: Author: DOCO wef - 01.02.2013 under ERSS-IV
Note on C148: Author: DOCO wef - 01.03.2013 under ERSS-IV
Note on C150: Author: DOCO 24.04.14
Note on C151: Author: DOCO 24.04.14
Note on C152: Author: DOCO 30.06.2014
Note on C155: Author: DOCO w.e.f 01.11.2011
Note on C156: Author: DOCO w.e.f 01.04.2012
Note on C157: Author: DOCO wef 01.05.2013
Note on C158: Author: DOCO wef 01.06.2013
Note on C159: Author: D.O.C.O w.e.f 01.04.2012
Note on C160: Author: D.O.C.O w.e.f 01.04.2012
Note on C161: Author: DOCO : w.e.f - 01.09.2013
Note on C163: Author: DOCO : w.e.f - 09.06.2014

## Sheet1
Standard of Performance data for the month of NOVEMBER 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., ODISHA TRANSMISSION SYSTEM
ANNEXURE - A