## Odisha SOP
Standard of Performance data for the month of DECEMBER 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., ODISHA
ANNEXTURE-A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | No. of towers damaged | no. of insulator failed | Total outage in days (1) | Outage Attributable to |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date Time | Date Time |  |  |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | ODL1 | ROURKELA-TALCHER I | 171 | Odisha | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ERPC 'ERPC/MS/TAC/2018/209 | 100
2 | ODL2 | ROURKELA-TALCHER II | 171 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
3 | ODL3 | RENGALI-TALCHER-I | 24 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
4 | ODL4 | RENGALI-TALCHER-II | 24 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
5 | ODL5 | RENGALI-INDRAVATI I | 356 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
6 | ODL6 | INDRAVATI-JEYPORE | 71 | ---- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
7 | ODL7 | TAL-MEERAMUNDALI | 51 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
8 | ODL8 | TALCHER-ANGUL | 68.35 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
9 | ODL9 | ANGUL-Meramundali # II | 18.61 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
10 | ODL10 | JEYPORE-BOLANGIR# I | 287 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
11 | ODL11 | BOLANGIR-ANGUL | 196.12 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
12 | ODL12 | ANGUL-MERAMUNDALI # I | 25.34 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
13 | ODL13 | RNG-Keonjhar ( LILO Portion) | 9.38 | ---- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
14 | ODL14 | Keonjhar-BPD (both LILO Portion) | 28.12 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
15 | ODL15 | BARIPADA-KHARAGPUR(LILO) | 18.74 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
16 | ODL17 | BARIPADA-DUBURI | 190.247 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
17 | ODL18A | DUBURI-PANDIABALLI | 143.3 | ----- | ----- | 2018-12-11 10:10 | 2018-12-11 18:18 | ----- | ----- | ----- | 8:08 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for rectification of accumulated defects in cuttack section |  | 98.91
[6 empty] | TOTAL |  | ----- | ----- | ----- | 8:08 | 0:00 | 0:00 | 0:00 |  |  |  | ---
18 | ODL18B | PANDIABALLI-MENDHASAL-I | 28 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
19 | ODL24 | Angul-Sundargarh-II | 274.92 | ----- | ----- | 2018-12-01 | 2018-12-03 13:46 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 61:46 | ----- | ----- | ----- | H/T as per ERLDC instruction for Voltage Regulation. |  | 100
|  |  |  | ---- | --- | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 61:46 | ----- | ----- | ----- | ---
20 | ODL25 | Angul-Sundargarh-I | 272 | ---- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
21 | ODL16A | BARIPADA-PANDIABALLI | 301.5 | ---- | --- | 2018-12-10 10:06 | 2018-12-10 18:50 | ----- | ----- | ----- | 8:44 | 0:00 | 0:00 | 0:00 |  |  | ----- | For rectification of accumulated defects. |  | 98.34
[6 empty] | 2018-12-01 11:25 | 2018-12-01 15:01 | ----- | ----- | ----- | 3:36 | 0:00 | 0:00 | 0:00 |  |  |  | S/D taken for attending Hot Spot of Bottom-Phase Jumper at Loc no 628
[6 empty] | TOTAL |  | ----- | ----- | ----- | 12:20 | 0:00 | 0:00 | 0:00 |  |  |  | ---
22 | ODL16B | 400KV-MENDHASAL-PANDIABILI-2 | 28 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
23 | ODL28 | DARLIPALLI-JHARSUGURA-1 | 20.54 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ---- | ----- | ----- | --- |  | 100
24 | ODL29 | DARLIPALLI-JHARSUGURA-2 | 20.54 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ---- | ----- | ----- | --- |  | 100
25 | ODL30 | 765 KV ANGUL-JHARSUGURA-3 | 295.06 |  |  | 2018-12-17 01:58 | 2018-12-17 01:58 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  | A/R successful at both end. R/I at Angul: Y-N fault,F/D:111.9kms,F/C:5.29KA. R/I at Sundargarh: M1:Y-N fault, F/D:233.9Kms, F/C: 3.17KA; M2: Y-N, F/D: 212.6Kms, F/C: 3.3KA |  | 100
[6 empty] | 2018-12-17 03:22 | 2018-12-17 04:05 | ----- | ----- | ----- | 0:00 | 0:00 | 0:43 | 0:00 |  |  |  | During heavy rain & cyclonic weather named 'PHETAI', line Tripped on Over voltage protection & DT received at Sundargarh
[6 empty] | 2018-12-21 13:04 | 2019-01-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 250:56:00 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:43 | 250:56:00 |  |  |  | ---
26 | ODL31 | 765 KV ANGUL-JHARSUGURA-4 | 295.06 |  |  | 2018-12-03 11:45 | 2018-12-20 10:44 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 406:59:00 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. |  | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 406:59:00 |  |  |  | ---
27 | ODT1 | ICT-II Sundergarh | 1500 | Odisha | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
28 | ODT2 | ICT-I Sundergarh | 1500 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
29 | ODT3 | ICT-I,RKL | 315 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
30 | ODT4 | ICT-II,RKL | 315 |  | ----- | 2018-12-27 11:26 | 2018-12-27 18:39 | ----- | ----- | ----- | 7:13 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for AMP work |  | 99.03
[6 empty] | TOTAL |  | ----- | ----- | ----- | 7:13 | 0:00 | 0:00 | 0:00 |  |  |  | ---
31 | ODT5 | ICT-I, RNG | 315 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
32 | ODT6 | ICT-II, RNG | 315 |  | --- | 2018-12-10 10:59 | 2018-12-10 18:28 | ----- | ----- | ----- | 0:00 | 7:29 | 0:00 | 0:00 | ----- | ----- | ----- | Shut down taken for health assesment and AMP work for system improvement as it is too old ICT. |  | 100
[6 empty] | 2018-12-11 09:36 | 2018-12-11 20:34 | ----- | ----- | ----- | 0:00 | 10:58 | 0:00 | 0:00 |  |  |  | Shut down taken for health assesment and AMP work for system improvement as it is too old ICT.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 18:27 | 0:00 | 0:00 |  |  |  | ---
33 | ODT7 | ICT-I, JEYPORE | 315 |  | ----- | 2018-12-17 05:29 | 2018-12-17 09:09 | ----- | ----- | ----- | 0:00 | 0:00 | 3:40 | 0:00 | ----- | ----- | ----- | During heavy rain & cyclonic weather named 'PHETAI', ICT got tripped. |  | 99.66
[6 empty] | 2018-12-18 15:54 | 2018-12-18 18:24 | ----- | ----- | ----- | 2:30 | 0:00 | 0:00 | 0:00 |  |  |  | S/D taken to top up oil in conservator in ICT-I unit-III (B phase)
[6 empty] | TOTAL |  | ----- | ----- | ----- | 2:30 | 0:00 | 3:40 | 0:00 |  |  |  | ---
34 | ODT8 | ICT-II, JEYPORE | 315 |  | ----- | 2018-12-17 05:29 | 2018-12-17 15:17 | ----- | ----- | ----- | 0:00 | 0:00 | 9:48 | 0:00 | ----- | ----- | ----- | During heavy rain & cyclonic weather named 'PHETAI', ICT got tripped. |  | 100
[6 empty] | 2018-12-06 13:27 | 2018-12-06 13:50 | ----- | ----- | ----- | 0:00 | 0:23 | 0:00 | 0:00 |  |  |  | During RAS integration of 125 MVAR B/R-2, LBB relay operated resulting Bus-I Bus Bar protection operated & Bus I got tripped.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:23 | 9:48 | 0:00 |  |  |  | ---
35 | ODT9 | ICT-I BRPD | 315 |  | --- | 2018-12-27 08:55 | 2018-12-27 19:15 | ----- | ----- | ----- | 10:20 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for AMP work |  | 98.61
[6 empty] | TOTAL |  | ----- | ----- | ----- | 10:20 | 0:00 | 0:00 | 0:00 |  |  |  | ---
36 | ODT10 | ICT- II, IVT | 315 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
37 | ODT11 | ICT-II, BOLANGIR | 315 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
38 | ODT12 | ICT-I, BOLANGIR | 315 |  | --- | 2018-12-11 09:40 | 2018-12-11 17:08 | ----- | ----- | ----- | 7:28 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for AMP work |  | 99
[5 empty] | ----- | TOTAL |  | ----- | ----- | ----- | 7:28 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | ---
39 | ODT13 | ICT-I at Angul | 1500 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
40 | ODT14 | ICT-2 at Angul | 1500 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
41 | ODT15 | ICT-3 at Angul | 1500 |  | --- | 2018-12-19 09:38 | 2018-12-19 18:59 | ----- | ----- | ----- | 9:21 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | To carry out AMP work. |  | 98.75
[6 empty] | TOTAL |  | ----- | ----- | ----- | 9:21 | 0:00 | 0:00 | 0:00 |  |  |  | ---
42 | ODT16 | ICT-IV at Angul | 1500 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
43 | ODT17 | ICT-I, KEONJHAR | 315 |  | ----- | 2018-12-12 09:31 | 2018-12-12 19:29 | ----- | ----- | ----- | 9:58 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for AMP work |  | 98.66
[5 empty] | ----- | TOTAL |  | ----- | ----- | ----- | 9:58 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | ---
44 | ODT18 | ICT-II, KEONJHAR | 315 |  | ----- | 2018-12-07 09:25 | 2018-12-07 19:03 | ----- | ----- | ----- | 9:38 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | Shut-down taken for timing & CRM of Breaker. |  | 98.71
[6 empty] | TOTAL |  | ----- | ----- | ----- | 9:38 | 0:00 | 0:00 | 0:00 |  |  |  | ---
45 | ODT19 | ICT-II BRPD | 315 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
46 | ODT20 | ICT- II, BRPD | 160 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
45 | ODT21 | ICT-I, BRPD | 160 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
47 | ODT22 | ICT-I,PANDIABALLI | 500 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
48 | ODT23 | ICT-II,PANDIABALLI | 500 |  | ----- | 2018-12-14 00:01 | 2018-12-29 20:22 | ----- | ----- | ----- | 0:00 | 380:21 | 0:00 | 0:00 | ----- | ----- | ----- | Shut down taken to attend the issue of sudden rise of faulty gases (Hydrozen & Acitiline) detected through DGA test.Rise of fault gases may happen due to system parameter i.e voltage stress,load,fault in downstream etc. ICT was thoroughly inspected by OEM and necessary action taken.Hence,s/d was taken as a pro-active action to minimize/avoid future downtime i.e to ensure maximum system reliability. |  | 100
[5 empty] | ----- | TOTAL |  | ----- | ----- | ----- | 0:00 | 380:21 | 0:00 | 0:00 | ----- | ----- | ----- | ---
49 | ODT24 | ICT-III BARIPADA | 500 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
50 | ODR1 | 240, 1 ph BR-II at Sundergarh | 240 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
51 | ODR2 | 125 3ph B/R- III Angul | 125 | ----- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
52 | ODR3 | 125 3ph B/R- II Angul | 125 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
53 | ODR4 | 125 3ph B/R- I Angul | 125 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
54 | ODR5 | 330 MVAR BR-I at Angul | 330 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
54 | ODR6 | 330 MVAR BR-II at Angul | 330 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
55 | ODR7 | 240 MVAR SLR-1 at Angul | 240 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
56 | ODR8 | 240 MVAR SLR-2 at Angul | 240 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
57 | ODR9 | 125 3ph B/R- I Sundergarh | 125 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
58 | ODR10 | 125 3ph B/R- II Sundergarh | 125 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
59 | ODR11 | 240 3ph B/R- I Sundergarh | 240 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
60 | ODR12 | 63 Duburi L/R at Baripada | 63 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
61 | ODR13 | 50 MRL L/R at Bolangir | 50 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
62 | ODR14 | 50 JPR L/R at Bolangir | 50 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
63 | ODR15 | 80 MVAR B/R at Bolangir | 80 |  | --- | 2018-12-01 | 2019-01-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 744:00 | ----- | ----- | ----- | H/T as per ERLDC instruction for Voltage Regulation. |  | 100
[5 empty] | --- | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 744:00 | ----- | ----- | ----- | ---
64 | ODR16 | 80 MVAR B/R at Keonjhar | 80 |  | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
65 | ODR17 | 63 3ph B/R ,JEYPORE | 63 |  | --- | 2018-12-01 | 2018-12-06 14:14 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 134:14 | ----- | ----- | ----- | H/T as per ERLDC instruction for Voltage Regulation. |  | 100
[6 empty] | 2018-12-08 09:33 | 2018-12-08 17:42 | ----- | ----- | ----- | 0:00 | 8:09 | 0:00 | 0:00 |  |  |  | S/D taken for conditioning assessment for life acceptancy of Reactor through testing by FDS Kit.
[5 empty] | ----- | TOTAL |  | ----- | ----- | ----- | 0:00 | 8:09 | 0:00 | 134:14 | ----- | ----- | ----- | ---
66 | ODR20 | 50 CHAIBASA -I L/R at RKL | 50 |  | ---- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
67 | ODR21 | 125MVAR BR-I at RKL | 125 |  | ---- | 2018-12-22 09:40 | 2018-12-22 18:26 | ----- | ----- | ----- | 8:46 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for AMP work. |  | 98.82
[6 empty] | TOTAL |  | ----- | ----- | ----- | 8:46 | 0:00 | 0:00 | 0:00 |  |  |  | ---
68 | ODR23 | 80 JPR L/R at Meramundli | 80 |  | ---- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
69 | ODR24 | 80 MVAR B/R at DUBRI | 80 |  | ---- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
70 | ODR25 | 125 MVAR B/R at IVT | 125 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
71 | ODR26 | 125 MVAR B/R at JPR | 125 |  | ---- | 2018-12-06 13:27 | 2018-12-06 14:48 | ----- | ----- | ----- | 0:00 | 1:21 | 0:00 | 0:00 | ----- | ----- | ----- | During RAS integration of 125 MVAR B/R-2 under NTAMC integration work, LBB relay operated resulting Bus-I Bus Bar protection operated & Bus I got tripped. |  | 100
[5 empty] | ----- | TOTAL |  | ----- | ----- | ----- | 0:00 | 1:21 | 0:00 | 0:00 | ----- | ----- | ----- | ---
72 | ODR27 | 50MVAR Keonjhar LR at Baripada | 50 |  | ---- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
73 | ODR28 | 63MVAR BARIPADA L/R AT PANDIABALLI | 63 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
74 | ODR29 | 80MVAR B/R AT PANDIABALLI | 80 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
75 | ODR30 | 125MVAR B/R AT BARIPADA | 125 |  | ---- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- |  | 100
76 | ODR31 | 63 MVAR NEW DUBURI L/R AT PANDIABILI END | 63 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
77 | ODR32 | RENGALI-BUS REACTOR-1_125MVAR | 125 |  | ---- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
78 | ODR33 | RENGALI-BUS REACTOR-2_125MVAR | 126 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ---- | 100
79 | ODR34 | ROURKELA BUS REACTOR-2_125 MVAR | 125 |  | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
|  |  |  | ----- | ----- | --- |  | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | -----
80 | ODR35 | STATCOM AT ROURKELA | 850 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
81 | ODR36 | BOLANGIR-BUS REACTOR-2_125MVAR | 125 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
82 | ODR37 | BARIPADA BUS REACTOR-2_125 MVAR | 125 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
83 | ODR38 | STATCOM AT JEYPORE | 900 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
84 | ODR39 | 125MVAR B/R-II AT KEONJHAR | 125 | ----- | ----- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | ----- | ----- | ----- | --- | ----- | 100
85 | ODR40 | ANGUL-SUNDERGARH LINE-3_240MVAR | 330 | --- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 100
86 | ODR41 | ANGUL-SUNDERGARH LINE-4_240MVAR | 330 | --- | --- | --- | --- | ----- | ----- | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 100
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
Note on C71: Author: Charged on 22.03.11 at 15:00hrs and loaded on 23.03.11 at 16:10 hrs DOCO - 01.04.2011

## ER-II SOP
Standard of Performance data for the month of DECEMBER 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION-II
Annexure-A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | Outage Attributable to |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date Time | Date Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | ER2L1 | Maithon -MEJIA - III | 83.74 | ER-II | ----- | 2018-12-10 10:22 | 2018-12-10 18:09 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 7:47 | --- | --- | --- | Shut down taken by Mejia/DVC to attend Hot-spot of B-phase isolator at Mejia end. | --- | 100
[6 empty] | 2018-12-11 09:54 | 2018-12-11 17:47 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 7:53 | --- | --- | --- | Shut down taken by Mejia/DVC to attend Hot-spot of B-phase isolator at Mejia end. | ---
[6 empty] | 2018-12-21 10:45 | 2018-12-21 18:33 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 7:48 | --- | --- | --- | S/D taken by DVC for replacement of connector of line side isolator & arm of the said isolator's B-ph. | ---
[5 empty] | ----- | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 23:28 | --- | --- | --- | --- | ---
2 | ER2L2 | MEJIA - Jamshedpur | 167.74 |  | ----- | --- | --- |  |  |  | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
3 | ER2L3 | Maithon-Jamshedpur | 153 |  | ----- | --- | --- |  |  |  | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
4 | ER2L6 | Jeerat-Subhasgram | 63 |  |  | 2018-12-19 10:03 | 2018-12-19 15:15 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 5:12 | --- | --- | --- | For hoisting of Insulator in Rajarhat-Purnea line multicircuit tower no: 1/0. |  | 100
[6 empty] | 2018-12-22 09:32 | 2018-12-22 16:08 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 6:36 | --- | --- | --- | S/D taken for completion of power line crossing work of under construction 400 KV Rajarhat-New Purnea D/C
[6 empty] | 2018-12-23 07:12 | 2018-12-23 17:38 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 10:26 | --- | --- | --- | S/D taken for completion of power line crossing work of under construction 400 KV Rajarhat-New Purnea D/C
[6 empty] | 2018-12-30 08:54 | 2018-12-30 08:54 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 0:00 | --- | --- | --- | A/R successful from both ends. R/I at Subhasgram:M1-B-N,Z1, F/D-51.85 KM, F/C-3.256 kA.M2-B-N,Z1, F/D-51.70 KM, F/C-3.2 kA.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 22:14 | --- | --- | --- | ---
5 | ER2L7 | Farakka-Sagardighi-I | 55.38 |  | --- | --- | --- |  |  |  | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
6 | ER2L8 | Sagardighi- Subhasgram | 245.64 |  | ----- | 2018-12-22 09:22 | 2018-12-22 16:11 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 6:49 | --- | --- | --- | S/D taken for completion of power line crossing work of under construction 400 KV Rajarhat-New Purnea D/C |  | 100
[6 empty] | 2018-12-23 07:08 | 2018-12-23 17:40 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 10:32 | --- | --- | --- | S/D taken for completion of power line crossing work of under construction 400 KV Rajarhat-New Purnea D/C
[5 empty] | ----- | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 17:21 | --- | --- | --- | ---
7 | ER2L9 | Farakka-Durgapur-I | 150 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
8 | ER2L10 | Farakka-Durgapur-II | 146 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
9 | ER2L11 | Malda-Farakka-I | 40 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
10 | ER2L12 | Malda-Farakka-II | 40 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
11 | ER2L13 | Durgapur-Jamshedpur | 177 |  | ----- | 2018-12-08 13:20 | 2018-12-08 15:51 | --- | --- | --- | 2:31 | 0:00 | 0:00 | 0:00 | --- | --- | --- | Shutdown for rectification of OPGW suspension clamp at Loc.- 257 |  | 99.66
[6 empty] | TOTAL |  |  |  |  | 2:31 | 0:00 | 0:00 | 0:00 | --- | --- | --- | ---
12 | ER2L14 | Binaguri-New Purnea-I | 168 |  | ----- | 2018-12-07 09:51 | 2018-12-07 18:47 | --- | --- | --- | 0:00 | 8:56 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement. |  | 100
[5 empty] | ----- | 2018-12-09 09:00 | 2018-12-09 18:11 | --- | --- | --- | 0:00 | 9:11 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-11 08:56 | 2018-12-11 18:37 | --- | --- | --- | 0:00 | 9:41 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-13 09:00 | 2018-12-13 19:40 | --- | --- | --- | 0:00 | 10:40 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-15 08:42 | 2018-12-15 18:23 | --- | --- | --- | 0:00 | 9:41 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-17 09:03 | 2018-12-17 18:28 | --- | --- | --- | 0:00 | 9:25 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-20 08:50 | 2018-12-20 17:49 | --- | --- | --- | 0:00 | 8:59 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[5 empty] | ----- | TOTAL |  |  |  |  | 0:00 | 66:33 | 0:00 | 0:00 | --- | --- | --- | ---
13 | ER2L15 | Binaguri-New Purnea-II | 168 |  |  | 2018-12-08 08:44 | 2018-12-08 18:04 | --- | --- | --- | 0:00 | 9:20 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement. |  | 100
[6 empty] | 2018-12-10 09:02 | 2018-12-10 18:14 | --- | --- | --- | 0:00 | 9:12 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-12 08:35 | 2018-12-12 18:36 | --- | --- | --- | 0:00 | 10:01 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-14 08:31 | 2018-12-14 19:30 | --- | --- | --- | 0:00 | 10:59 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-16 08:31 | 2018-12-16 17:42 | --- | --- | --- | 0:00 | 9:11 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-19 09:44 | 2018-12-19 18:20 | --- | --- | --- | 0:00 | 8:36 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | 2018-12-21 09:06 | 2018-12-21 17:50 | --- | --- | --- | 0:00 | 8:44 | 0:00 | 0:00 | --- | --- | --- | Shut-down for insulator replacement with CLR insulator for system improvement.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 66:03 | 0:00 | 0:00 | --- | --- | --- | ---
14 | ER2L16 | Malda-New Purnea-I | 167 |  | ---- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
15 | ER2L17 | Malda-New Purnea-II | 167 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
16 | ER2L18 | TALA-BINAGURI-I | 98.087 |  | ----- | 2018-12-01 | 2018-12-11 10:54 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 250:54 | --- | --- | --- | H/T as per ERLDC instruction for Voltage Regulation. |  | 100
[5 empty] | ----- | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 250:54 | --- | --- | --- | ---
17 | ER2L19 | TALA-BINAGURI-II | 98.087 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
18 | ER2L20 | TALA-BINAGURI-III | 115.553 |  | ----- | 2018-12-11 10:59 | 2018-12-28 14:46 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 411:47 | --- | --- | --- | S/D taken by Malbase/Bhutan for general maintenance of broken disc insulators replacement at tower loc no TPS-89,99,100,73,74 |  | 100
[6 empty] | 2018-12-29 07:40 | 2018-12-29 15:39 | --- | --- | --- | 0:00 | 7:59 | 0:00 | 0:00 | --- | --- | --- | Line tripped due to LA blast at Malbase end.Relay indication at Binaguri end : M1 : Y-N,Z-2,F/D-115.3 km,F/C-2.111kA.M2 : Y-N,Z-2, F/D-126.2 km,F/C-2.111kA. Fault is under Bhutan jurisdiction.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 7:59 | 0:00 | 411:47 | --- | --- | --- | ---
19 | ER2L21 | TALA-BINAGURI-IV | 115.553 |  | ----- | 2018-12-05 17:28 | 2018-12-20 12:39 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 355:11 | --- | --- | --- | H/T as per ERLDC instruction for Voltage Regulation. |  | 100
[6 empty] | 2018-12-20 12:39 | 2019-01-01 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 275:21 | --- | --- | --- | S/D taken by Tala. Line presently in idle charged condition from binaguri up to Loc.102 for anti-theft measure.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 275:21 | --- | --- | --- | ---
20 | ER2L22 | BINAGURI-Rangpo-I | 109.88 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  |  | 100
21 | ER2L23 | Rangpo-TEESTA-I | 11.83 |  | ----- | 2018-12-21 09:10 | 2018-12-21 13:55 | --- | --- | --- | 0:00 | 4:45 | 0:00 | 0:00 | --- | --- | --- | S/D taken for PD inspection work (as a special activity for GIS) at GIS Rangpo site by OEM,M/s Hyosung |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 4:45 | 0:00 | 0:00
22 | ER2L24 | BINAGURI-Rangpo- II | 110.42 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  |  | 100
23 | ER2L25 | Rangpo-Teesta-II | 21.42 |  | ----- | 2018-12-22 09:02 | 2018-12-22 12:51 | --- | --- | --- | 0:00 | 3:49 | 0:00 | 0:00 | --- | --- | --- | S/D taken for PD inspection work (as a special activity for GIS)at GIS Rangpo site by OEM,M/s Hyosung |  | 100
[6 empty] | \ |  |  |  |  | 0:00 | 3:49 | 0:00 | 0:00
24 | ER2L26 | MAITHON - MEJIA - I | 59.182 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
25 | ER2L27 | MAITHON - MEJIA - II | 59.182 |  | ----- | 2018-12-04 10:15 | 2018-12-04 12:51 | --- | --- | --- | 2:36 | 0:00 | 0:00 | 0:00 | --- | --- | --- | S/D taken to attend hot-spot of R-Phase line isolator of 400 KV MTN-Mejia-2 line at Maithan s/s |  | 99.65
[6 empty] | 2018-12-05 09:45 | 2018-12-05 17:47 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 8:02 | --- | --- | --- | S/D taken by DVC for preventive maintenance of bay and time test of breaker at their end.
[6 empty] | TOTAL |  |  |  |  | 2:36 | 0:00 | 0:00 | 8:02 | --- | --- | --- | ---
26 | ER2L28 | MAITHON - Durgapur - I | 70.77 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
27 | ER2L29 | MAITHON - Durgapur - II | 70.77 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
28 | ER2L30 | ANDAL - Jamshedpur - I | 156.76 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
29 | ER2L31 | ANDAL - Jamshedpur - II | 156.76 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
30 | ER2L32 | Maithon - MaithonRB- I | 31.5 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
31 | ER2L33 | Maithon - MaithonRB- II | 31.5 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
32 | ER2L34 | Baharampore-Sagardighi-I | 26.1 |  | ----- | 2018-12-06 10:22 | 2018-12-06 17:05 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 6:43 | --- | --- | --- | S/D taken by WBSETCL for maintenance work at their end. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 6:43 | --- | --- | --- | ---
33 | ER2L35 | Baharampore-Sagardighi-II | 26.1 |  | ----- | 2018-12-07 07:19 | 2018-12-07 16:27 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 9:08 | --- | --- | --- | Shut-down taken by WBSETCL, for maintenance work. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 9:08 | --- | --- | --- | ---
34 | ER2L36 | Chukha-Birpara-II | 36 |  | ----- | 2018-12-01 | 2019-01-01 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 744:00 | --- | --- | --- | S/D taken by CHPC/Bhutan for retrofitting of 220KV-BIRPARA -CHUKHA-2 with new panels and protection system(replacement of single strand control cable with multi-strand) and replacing exsisting CBs with new SF6 breakers. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 744:00 | --- | --- | --- | ---
35 | ER2L37 | Chukha-Birpara-I | 36 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
36 | ER2L39 | MALBASE-Birpara(CHUKHA III) | 38 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
37 | ER2L40 | Birpara-Binaguri-I | 80 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
38 | ER2L41 | Birpara-Binaguri-II | 80 |  | ---- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
39 | ER2L42A | BIRPARA-ALIPURDUAR-I | 57.49 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
40 | ER2L42B | ALIPURDUAR-SALAKATI-I | 100.57 |  | ----- | 2018-12-26 08:36 | 2018-12-26 19:42 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 11:06 | --- | --- | --- | Shut-down taken by NER for power line crossing of 400 KV Jigmlling Alipurduar under Mangdechu Power evacuation, at Loc no: 121/0- 122/0. |  | 100
[6 empty] | 2018-12-27 08:31 | 2018-12-27 19:43 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 11:12 | --- | --- | --- | Shut-down taken by NER for power line crossing of 400 KV Jigmlling Alipurduar under Mangdechu Power evacuation, at Loc no: 121/0- 122/0.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 22:18 | --- | --- | --- | ---
41 | ER2L43A | BIRPARA-ALIPURDUAR-II | 57.49 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
42 | ER2L43B | ALIPURDUAR-SALAKATI-II | 100.57 |  | ----- | 2018-12-26 08:37 | 2018-12-26 19:43 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 11:06 | --- | --- | --- | Shut-down taken by NER for power line crossing of 400 KV Jigmlling Alipurduar under Mangdechu Power evacuation, at Loc no: 121/0- 122/0. |  | 100
[6 empty] | 2018-12-27 08:32 | 2018-12-27 18:40 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 10:08 | --- | --- | --- | Shut-down taken by NER for power line crossing of 400 KV Jigmlling Alipurduar under Mangdechu Power evacuation, at Loc no: 121/0- 122/0.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 21:14 | --- | --- | --- | ---
43 | ER2L44 | Siliguri-Kishengunj-I | 108 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
44 | ER2L45 | Siliguri-Kishengunj-II | 108 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
45 | ER2L46 | Dalkhola-Kishengunj-I | 30.9 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
46 | ER2L47 | Dalkhola-Kishengunj-II | 30.9 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
47 | ER2L48 | Dalkhola-Malda-I | 116 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
48 | ER2L49 | Dalkhola-Malda-II | 116 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
49 | ER2L50 | Binaguri-Siliguri-I | 9 |  | ----- | 2018-12-06 21:43 | 2018-12-06 22:15 | --- | --- | --- | 0:00 | 0:32 | 0:00 | 0:00 | --- | --- | --- | Emergency hand -tripped to save the live of a person who climed on the tower top at Loc no: 240, as information recd from NJP police stn. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:32 | 0:00 | 0:00 | --- | --- | --- | ---
50 | ER2L51 | Binaguri-Siliguri-II | 9 |  | ----- | 2018-12-06 21:44 | 2018-12-06 22:17 | --- | --- | --- | 0:00 | 0:33 | 0:00 | 0:00 | --- | --- | --- | Emergency hand -tripped to save the live of a person who climed on the tower top at Loc no: 240, as information recd from NJP police stn. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:33 | 0:00 | 0:00 | --- | --- | --- | ---
51 | ER2L52 | Rangpo-New Melli-I | 26.1 |  | ----- | 2018-12-11 09:12 | 2018-12-11 17:33 | --- | --- | --- | 8:21 | 0:00 | 0:00 | 0:00 | --- | --- | --- | S/D taken for AMP work |  | 98.88
[6 empty] | TOTAL |  |  |  |  | 8:21 | 0:00 | 0:00 | 0:00 | --- | --- | --- | ---
52 | ER2L53 | Rangpo-Tashiding | 26.1 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
53 | ER2L55 | Siliguri-Kurseong-I (up to LILO) | 31.3 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
54 | ER2L56 | Kurseong-Rangit-I (up to LILO) | 61.2 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
55 | ER2L57 | RANGIT-Rangpo | 54.17 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
56 | ER2L58 | Rangpo-GANGTOK-II | 26.36 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
57 | ER2L59 | Chujacheng-Rangpo (LILO) | 1 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
58 | ER2L60 | 132KV-GANGTOK -CHUZACHEN-1 | 28.06 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
59 | ER2L61 | MELLI-SILIGURI | 92.45 |  | --- | 2018-12-28 15:11 | 2018-12-28 15:44 | --- | --- | --- | 0:00 | 0:33 | 0:00 | 0:00 | --- | --- | --- | Tripped on R-Y fault; Siliguri end R/I: Z2, F/D: 104.7 KM (Line length 92 km), F/C: Ir: 1.1 KA, Iy: 1.28 KA.Actual fault area is under Sikkim jurisdiction Fault cleared by Siliguri end as CB at Melli (Sikkim power depart)end did not able to clear the fault of 132 KV Rangpo-Melli line, occurred on the same instant. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:33 | 0:00 | 0:00 | --- | --- | --- | ---
60 | ER2L62 | RANGPO-MELLI | 16.61 |  | ---- | 2018-12-28 15:11 | 2018-12-28 15:37 | --- | --- | --- | 0:00 | 0:26 | 0:00 | 0:00 | --- | --- | --- | Tripped on R-Y fault; Rangpo end R/I: Z1, F/D: 2.493 km (Sikkim jurisdiction), F/C: Ir: 1.39 KA, Iy: 1.37 KA. CB at Melli (Sikkim power depart) end did not opened on subject fault. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:26 | 0:00 | 0:00 | --- | --- | --- | ---
61 | ER2L63 | Rangit-Rammam | 27.15 |  | ----- | 2018-12-26 12:47 | 2018-12-26 15:35 | --- | --- | --- | 2:48 | 0:00 | 0:00 | 0:00 | --- | --- | --- | Shut down taken for rectification of damaged earth wire. |  | 99.62
[6 empty] | 2018-12-31 14:48 | 2018-12-31 15:07 | --- | --- | --- | 0:00 | 0:19 | 0:00 | 0:00 | --- | --- | --- | R/I at Rangit end: B-N, F/D: 30.2 kM, F/C-1.348 kA. Fault distance is beyond the actual line length,which is beyond Powergrid's jurisdiction
[6 empty] | TOTAL |  |  |  |  | 2:48 | 0:19 | 0:00 | 0:00 | --- | --- | --- | ---
62 | ER2L64 | Rangit-Rabangla(up to LILO) | 1 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
63 | ER2L65 | Rabangla - Melli(up to LILO) | 36 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
64 | ER2L66 | Binaguri-Bongaigaon-I | 217.275 |  | ----- | 2018-12-05 10:19 | 2018-12-05 11:42 | --- | --- | --- | 0:00 | 1:23 | 0:00 | 0:00 | --- | --- | --- | Tripped due to fault at Bongaigaon for external severity (Monkey). R/I at Binaguri : RN, FL-216 Km, F/C-1.313 KA. |  | 100
[6 empty] | 2018-12-20 10:22 | 2018-12-20 17:07 | --- | --- | --- | 0:00 | 6:45 | 0:00 | 0:00 | --- | --- | --- | S/D taken by NER as because of the constructional feature of the reactor, it is difficult to replace at the bushing as it is coming under the vicinity of induction zone. Keeping considering the safety aspect, here is no any other option, except switch-off the related line.This issue will be resolved after commissioning of the new reactor.
[6 empty] | 2018-12-21 09:47 | 2018-12-21 16:36 | --- | --- | --- | 0:00 | 6:49 | 0:00 | 0:00 | --- | --- | --- | S/D taken by NER as because of the constructional feature of the reactor, it is difficult to replace at the bushing as it is coming under the vicinity of induction zone. Considering the safety aspect, there was not any other option, except switching-off the line.This issue will be resolved after commissioning of the new reactor.
[5 empty] | --- | TOTAL |  | --- | --- | --- | 0:00 | 14:57 | 0:00 | 0:00 | --- | --- | --- | ---
65 | ER2L67 | Binaguri-Bongaigaon-II | 217.275 |  | ----- | 2018-12-05 10:19 | 2018-12-05 11:50 | --- | --- | --- | 0:00 | 1:31 | 0:00 | 0:00 | --- | --- | --- | Tripped due to fault at Bongaigaon for external severity (Monkey). R/I at Binaguri : RN, FL-216 Km, F/C-1.272 KA. |  | 100
[5 empty] | ----- | TOTAL |  | --- | --- | --- | 0:00 | 1:31 | 0:00 | 0:00 | --- | --- | --- | ---
66 | ER2L70 | Baharampore - Bheramara - I(Indian portion) | 71.51 |  | ----- | 2018-12-07 06:29 | 2018-12-07 16:50 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 10:21 | --- | --- | --- | For DFDR commissioning at Bheramara ( Bangladesh) end. |  | 100
[6 empty] | 2018-12-01 08:21 | 2018-12-01 15:54 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 7:33 | --- | --- | --- | S/D taken for maintenance work by Bheramara/Bangladesh at their end.
[5 empty] | --- | TOTAL |  | --- | --- | --- | 0:00 | 0:00 | 0:00 | 17:54 | --- | --- | --- | ---
67 | ER2L71 | Baharampore - Bheramara - II(Indian Portion) | 71.51 |  | ----- | 2018-12-08 06:23 | 2018-12-08 15:58 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 9:35 | --- | --- | --- | For DFDR commissioning at Bheramara ( Bangladesh) end. |  | 100
[6 empty] | 2018-12-02 07:24 | 2018-12-02 16:45 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 9:21 | --- | --- | --- | S/D taken for maintenance work by Bheramara/Bangladesh at their end.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 18:56 | --- | --- | --- | ---
68 | ER2L74 | Rangpo-Teesta-III(LILO) | 10.78 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
69 | ER2L75 | Rangpo_Kishengunj(LILO) | 10.78 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
70 | ER2L72 | Farakka-Gokarna-I | 120 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
71 | ER2L73 | Farakka-Gokarna-II | 120 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
72 | ER2L74 | BINAGURI-KISUNGANJ-1-LILO | 5 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
73 | ER2L75 | BINAGURI-KISUNGANJ-2-LILO | 5 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
74 | ER2L76 | 400KV-KISHANGANJ-PURNEA-1 LILO | ----- |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
75 | ER2L77 | 400KV-KISHANGANJ-PURNEA-2 LILO | ----- |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
76 | ER2L78 | 400KV FARAKKA-SAGARDIGHI-II | 76 |  | ----- | 2018-12-08 07:11 | 2018-12-08 16:33 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 9:22 | --- | --- | --- | Shut-down taken by WBSETCL, for maintenance work. |  | 100
[6 empty] | 2018-12-28 09:51 | 2018-12-28 15:27 | --- | --- | --- | 0:00 | 5:36 | 0:00 | 0:00 | --- | --- | --- | S/D taken for for SAS configuration work at Sagardighi end(WBPDCL).
[6 empty] | TOTAL |  |  |  |  | 0:00 | 5:36 | 0:00 | 9:22 | --- | --- | --- | ---
77 | ER2L79 | 400 KV SAGARDIGHI-JEERAT | 199.5 |  | ----- | 2018-12-10 07:49 | 2018-12-10 17:24 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 9:35 | --- | --- | --- | Shut down taken by WBSETCL for maintenance work. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 9:35 | --- | --- | --- | ---
78 | ER2L80 | LILO OF BINAGURI-BONGAIGAION-III AT ALIPURDUAR | 12.89 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
79 | ER2L81 | LILO OF BINAGURI-BONGAIGAION-IV AT ALIPURDUAR | 12.89 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
80 | ER2L82 | 400KV FARAKKA-BAHARAMPORE-I | 83 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
81 | ER2L83 | 400KV FARAKKA-BAHARAMPORE-II | 83 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
82 | ER2L84 | 400 KV ALIPURDUAR-PUNATSANGHCUN -I | 64.152 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
83 | ER2L85 | 400 KV ALIPURDUAR-PUNATSANGHCUN -II | 64.152 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
84 | ER2T1 | ICT-I,DGP | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
85 | ER2T2 | ICT-II,DGP | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
86 | ER2T3 | ICT-I,MTN | 500 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
87 | ER2T4 | ICT-II,MTN | 500 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
88 | ER2T5 | ICT-I,FKK | 315 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
89 | ER2T6 | ICT-III,MLD | 315 |  | --- | 2018-12-08 09:00 | 2018-12-08 16:01 | --- | --- | --- | 7:01 | 0:00 | 0:00 | 0:00 | --- | --- | --- | Shutdown taken for AMP work. |  | 99.06
[6 empty] | TOTAL |  |  |  |  | 7:01 | 0:00 | 0:00 | 0:00 | --- | --- | --- | ---
89 | ER2T7 | ICT-V,MLD | 315 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
90 | ER2T8 | ICT-I, NSLG | 315 |  | ----- | 2018-12-29 16:47 | 2018-12-29 18:13 | --- | --- | --- | 1:26 | 0:00 | 0:00 | 0:00 | --- | --- | --- | S/D taken to attend 220 KV Y Phase CT leakage. |  | 99.81
[6 empty] | TOTAL |  |  |  |  | 1:26 | 0:00 | 0:00 | 0:00 | --- | --- | --- | ---
91 | ER2T9 | ICT-II, NSLG | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
92 | ER2T10 | ICT-I, SGM | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
93 | ER2T11 | ICT-II, SGM | 315 |  | ---- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
94 | ER2T12 | ICT-V, SGM | 500 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
95 | ER2T13 | ICT-V RANGPO | 315 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
96 | ER2T14 | ICT-IV RANGPO | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
97 | ER2T15 | ICT-III RANGPO | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
98 | ER2T16 | ICT-II RANGPO | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
99 | ER2T17 | ICT-I RANGPO | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
100 | ER2T18 | ICT-I,SLG | 160 |  | --- | 2018-12-06 09:19 | 2018-12-06 17:16 | --- | --- | --- | 0:00 | 7:57 | 0:00 | 0:00 | --- | --- | --- | S/D taken for modification in NIFS of ICT-I |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 7:57 | 0:00 | 0:00 | --- | --- | --- | ---
101 | ER2T19 | ICT-II,SLG | 160 |  | --- | 2018-12-11 10:13 | 2018-12-11 17:27 | --- | --- | --- | 0:00 | 7:14 | 0:00 | 0:00 | --- | --- | --- | S/D taken for modification in NIFS of ICT-II |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 7:14 | 0:00 | 0:00 | --- | --- | --- | ---
102 | ER2T20 | ICT-I,BRP | 160 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
103 | ER2T21 | ICT-II,BRP | 160 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
104 | ER2T22 | ICT-II, Malda | 160 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
105 | ER2T23 | ICT-I, Malda | 160 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
106 | ER2T24 | ICT-IV, MLD | 50 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
107 | ER2T25 | ICT-I, RANGPO | 100 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
108 | ER2T26 | ICT-II, RANGPO | 100 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
109 | ER2T27 | ICT-III, RANGPO | 100 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
110 | ER2T28 | ICT-I, GTK | 50 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
111 | ER2T29 | ICT-II,GTK | 50 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
112 | ER2T30 | ALIPURDUAR-ICT-I | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
113 | ER2T31 | ALIPURDUAR-ICT-II | 315 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
114 | ER2R1 | 125 3ph B/R- II NSLG | 125 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
115 | ER2R2 | 125 3ph B/R- I NSLG | 125 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
116 | ER2R3 | 80 BONGG-III L/R at Binaguri | 80 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
117 | ER2R4 | 80 BONGG-IV L/R at Binaguri | 80 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
118 | ER2R5 | 50 Gaya-I L/R at Maithon | 50 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
119 | ER2R6 | 50 Gaya-II L/R at Maithon | 50 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
120 | ER2R7 | 80 MVAR B/R at Berhampore | 80 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
121 | ER2R8 | 80 MVAR B/R -I at Rangpo | 80 |  | ----- | 2018-12-22 08:58 | 2018-12-30 01:04 | --- | --- | --- | 0:00 | 0:00 | 0:00 | 184:06 | --- | --- | --- | H/T as per ERLDC instruction for Voltage Regulation. |  | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 184:06 | --- | --- | --- | ---
122 | ER2R9 | 80 MVAR B/R -II at Rangpo | 80 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
123 | ER2R10 | 50 MVAR B/R-I ,DGP | 50 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
124 | ER2R11 | 125 MVAR B/R-II ,DGP | 51 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
125 | ER2R11 | MAITHAN-MEJIA-I LR | 50 |  | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
126 | ER2R12 | 2*50 1ph B/R ,JRT | 100 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
127 | ER2R13 | 31.5MVAR B/R-I at New Melli | 31.5 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
128 | ER2R14 | 31.5MVAR B/R-II at New Melli | 31.5 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
129 | ER2R15 | 125MVAR B/R-I at Maithan | 125 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
130 | ER2R16 | 125MVAR B/R-II at Maithan | 125 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
131 | ER2R17 | 125MVAR B/R-III AT DURGAPUR | 125 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
132 | ER2R18 | 80MVAR B/R AT GOKARNA | 80 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
133 | ER2R19 | ALIPURDUAR-125MVAR BUS REACTOR-I | 125 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
134 | ER2R20 | ALIPURDUAR-125MVAR BUS REACTOR-II | 125 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
135 | ER2R21 | FARAKKA -GOKARNA-I L/R | 80 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
136 | ER2R22 | 125MVAR BAHARAMPORE B/R | 125 |  | ----- | 2018-12-05 20:07 | 2018-12-05 20:47 | --- | --- | --- | 0:40 | 0:00 | 0:00 | 0:00 | --- | --- | --- | S/D taken for isolation of defective WTI of 125 MVAR B/R-2 at Baharampur |  | 99.57
[6 empty] | 2018-12-06 11:24 | 2018-12-06 12:17 | --- | --- | --- | 0:53 | 0:00 | 0:00 | 0:00 | --- | --- | --- | S/D taken for restoration of Bus Reactor alongwith WTI at Baharampur.
[6 empty] | 2018-12-13 16:18 | 2018-12-13 17:59 | --- | --- | --- | 1:41 | 0:00 | 0:00 | 0:00 | --- | --- | --- | S/D taken for re-location of WTI & OTI due to repeated failure of the same for avoiding any unwanted tripping on mal-operation.
[6 empty] | TOTAL |  |  |  |  | 3:14 | 0:00 | 0:00 | 0:00 | --- | --- | --- | ---
137 | ER2R23 | SUBHASGRAM SAGARDIGHI LR | 50 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
138 | ER2R24 | 125MVAR B/R-IV AT DURGAPUR | 125 |  | ----- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 100
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
----- | ----- | ----- | ----- | ----- | ---- | --- | --- | [7 empty] | --- | --- | --- | --- | ---
Note on C114: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C115: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C163: Author: DOCO 09.06.2014 3 X 105 MVA
Note on C176: Author: DOCO 24.04.14
Note on C177: Author: DOCO 30.06.2014