## ER-II SOP
Standard of Performance data for the month of JULY 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., ER-II TRANSMISSION SYSTEM
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | No. of towers damaged | no. of insulator failed | Total outage in days (1) | Outage Attributable to |  |  |  | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date Time | Date Time |  |  |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available |  |  | ----- | -----
1 | ER2L1 | Maithon -MEJIA - III | 83.74 | ER-II |  | 2018-07-07 12:54 | 2018-07-09 12:58 | ---- | ---- | ---- | 0:00 | 48:04 | 0:00 | 0:00 | Tripped due to Bus Fault at Mejia/DVC end. R/I at Maithon end : Main-I : BN, FL-74.6 Km, F/C-4.2KA, DT received. Main-II : BN, FL-66.4 Km, F/C-4.3 KA. As per communication received from Mejia/DVC: During physical inspection of Transfer B/C at Mejia/DVC end, it has been found that some problems are there in B/C breaker which is /are yet to be rectified. Later on line anti-theft charged at 22:00 hrs of 07.07.18 from Maithon upto line isolator Mejia/DVC end. | ---- | ---- | ---- | ERPC ERPC/MS/TAC/2018/4148 dtd:17.09.18 | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 48:04 | 0:00 | 0:00 |  | ---- | ---- | ----
2 | ER2L2 | MEJIA - Jamshedpur | 167.74 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
3 | ER2L3 | Maithon-Jamshedpur | 153 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
4 | ER2L4 | Farakka-Baharampore - I(upto LILO) | 70.725 |  | --- | 2018-07-19 07:04 | 2018-07-28 21:23 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 230:19 | Shut down for completion of LILO connectivity at Sagardighi, under construction head.. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 230:19 |  | ---- | ---- | ----
5 | ER2L5 | Berhampore - Jeerat - I | 165.266 |  |  | 2018-07-03 06:28 | 2018-07-03 19:08 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 12:40 | Shut down taken BY WBSETCL, for maintenance activities at their own end. | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-17 15:27 | 2018-07-17 16:20 | ---- | ---- | ---- | 0:00 | 0:53 | 0:00 | 0:00 | Tripped only from Jeerat(WBSETCL) end. R/I at Baharampur: B-N,FD: 13.98KM,FC: 10.3KA. A/R successful at Baharampur end. | ---- | ---- | ----
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:53 | 0:00 | 12:40 |  | ----- | ----- | -----
6 | ER2L6 | Jeerat-Subhasgram | 63 |  |  | 2018-07-02 06:19 | 2018-07-02 16:23 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:04 | Shut down taken BY WBSETCL, for maintenance activities at their own end. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:04 |  | ----- | ----- | -----
7 | ER2L7 | Farakka-Sagardighi | 55.38 |  | --- | 2018-07-10 07:25 | 2018-07-10 17:28 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:03 | S/D for stringing of 400 KV Farakka-Berhampore D/C transmission line between section 13/0-14/0 | ----- | ----- | ----- |  | 100
[5 empty] | ---- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:03 |  | ---- | ---- | ----
8 | ER2L8 | Sagardighi- Subhasgram | 245.64 |  | ----- | 2018-07-05 12:27 | 2018-07-06 01:41 | ---- | 1 | 0.55 | 0:00 | 0:00 | 13:14 | 0:00 | During rain and thunder-storm on the affected area, Tripped on B-N fault. R/I at Subhasgram end: Z1, F/D: 21.51 KM, F/C:6.448 KA; R/I at Sagardhighi end: Z1, F/D: 214.4 KM, F/C: 2.2 KA; Charging attempt taken at 13:12 hrs but triped on SOTF. R/I at Subhasgram: Z1, B-N, 21.06 KM. During emergency patrolling suspension insulator string de-capping found at Loc no: 85 (B-phase/Top). | ----- | ----- | ----- |  | 100
[6 empty] | 2018-07-08 08:03 | 2018-07-08 16:20 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 8:17 | S/D taken by WBSETCL for testing of Direct trip and permissive signal. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 13:14 | 8:17 |  | ---- | ---- | ----
9 | ER2L9 | Farakka-Durgapur-I | 150 |  |  | 2018-07-25 08:23 | 2018-07-25 19:52 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 11:29 | Shutdown for powerline crossing work between section 10/0- 11/0 of 400KV Farakka- Baharampur D/C TL. | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-26 10:29 | 2018-07-26 15:48 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 5:19 | Shutdown for powerline crossing work between section 10/0- 11/0 of 400KV Farakka- Baharampur D/C TL. | ---- | ---- | ----
[6 empty] | 2018-07-28 18:20 | 2018-07-28 21:28 | ---- | ---- | ---- | 0:00 | 3:08 | 0:00 | 0:00 | Line opened to facilitate the first time charging of 400 KV Farakka-sagardighi-II as per the sequence of operation circulated by ERLDC | ---- | ---- | ----
[5 empty] | --- |  | TOTAL | ---- | ---- | ---- | 0:00 | 3:08 | 0:00 | 16:48 |  | ----- | ----- | -----
10 | ER2L10 | Farakka-Durgapur-II | 146 |  | --- | 2018-07-11 09:32 | 2018-07-11 17:53 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 8:21 | Shut down taken by Farakka/ NTPC, for relay testing at Farakka / NTPC end. | ----- | ----- | ----- |  | 100
[6 empty] | 2018-07-18 08:19 | 2018-07-18 20:02 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 11:43 | For stringing of 400 KV Farakka-Baharampur D/C transmission line between section 8/0 - 9/0, under const head.. | ---- | ---- | ----
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 20:04 |  | ----- | ----- | -----
11 | ER2L11 | Malda-Farakka-I | 40 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
12 | ER2L12 | Malda-Farakka-II | 40 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
13 | ER2L13 | Durgapur-Jamshedpur | 177 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
14 | ER2L14 | Binaguri-New Purnea-I | 168 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
15 | ER2L15 | Binaguri-New Purnea-II | 168 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
16 | ER2L16 | Malda-New Purnea-I | 167 |  | ---- | 2018-07-11 09:50 | 2018-07-11 10:53 | ---- | ---- | ---- | 0:00 | 1:03 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR of non-switchable Line Reactor, to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability . | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 1:03 | 0:00 | 0:00 |  | ---- | ---- | ----
17 | ER2L17 | Malda-New Purnea-II | 167 |  | --- | 2018-07-11 11:09 | 2018-07-11 11:34 | ---- | ---- | ---- | 0:00 | 0:25 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR of non-switchable Line Reactor, to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability . | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:25 | 0:00 | 0:00 |  | ---- | ---- | ----
18 | ER2L18 | TALA-BINAGURI-I | 98.087 |  | ----- | 2018-07-01 | 2018-07-07 16:31 | ---- | ---- | ---- | 0:00 | 160:31 | 0:00 | 0:00 | Tripped on Y-N fault: R/I at Binaguri:Main-I: Y-N, Z-2, F/D-195KM,F/C-3.282 KA;Main-II:Y-N, Z-2, F/D-140.3 KM[100%], F/C-2.171KA.Fault is under Tala[Bhutan] jurisdiction. Now Tala is not ready to charge & they will give clearance after detail investigation. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 160:31 | 0:00 | 0:00 |  | ---- | ---- | ----
19 | ER2L19 | TALA-BINAGURI-II | 98.087 |  | --- | 2018-07-20 17:41 | 2018-07-20 17:47 | ---- | ---- | ---- | 0:00 | 0:06 | 0:00 | 0:00 | A/R successful at Binaguri end only. R/I at Binaguri: Y-N, Z2, M1: F/D: 167.7 KM, F/C: 3.312 KA. M2: F/D: 135.9 KM, F/C: 2.369 KA. | ----- | ----- | ----- |  | 100
[5 empty] | ---- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:06 | 0:00 | 0:00 |  | ---- | ---- | ----
20 | ER2L20 | TALA-BINAGURI-III | 115.553 |  |  | 2018-07-20 17:54 | 2018-07-20 18:57 | ---- | ---- | ---- | 0:00 | 1:03 | 0:00 | 0:00 | Line tripped from both end. R/I at Binaguri: R-N, F/D: 120.20 KM (Fault is under Bhutan jurisdiction) , F/C: 2.97 KA. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 1:03 | 0:00 | 0:00 |  | ---- | ---- | ----
21 | ER2L21 | TALA-BINAGURI-IV | 115.553 |  |  | 2018-07-05 01:18 | 2018-07-05 01:43 | ---- | ---- | ---- | 0:00 | 0:00 | 0:25 | 0:00 | Tripped during heavy rain/lightening / thunderstorm in the effected area . R/I at Binaguri end: Y-N,FD: 44.50KM,FC: 6.096KA. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:25 | 0:00 |  | ---- | ---- | ----
22 | ER2L22 | BINAGURI-Rangpo-I | 109.88 |  | --- | 2018-07-10 08:14 | 2018-07-10 19:43 | ---- | ---- | ---- | 0:00 | 0:00 | 11:29 | 0:00 | During rain and thunder-storm line tripped on R-B fault. R/I at Rangpo: F/D: 48.11 KM, F/C: R- 2.075 KA, B- 4.674 KA; R/I at Binaguri: M1: F/D: 61.61 KM, F/C: R- 6.949KA, B- 5.629 KA; M2: F/D: 61.54 KM, F/C: R- 7360 Amps, B- 5549 Amps; As per patrolling fault detected as top phase conductor snapped due to dead end failure at Loc no: 147 towards 148. | ----- | ----- | ----- |  | 100
[6 empty] | 2018-07-23 14:56 | 2018-07-23 17:06 | ---- | ---- | ---- | 0:00 | 0:00 | 2:10 | 0:00 | S/D taken to attend the Hot Spot in R-Ph web trap & Tie bay Y-Ph Isolator at Binaguri S/S. | ---- | ---- | ----
[5 empty] | ----- |  | TOTAL | ---- | ---- | ---- | 2:10 | 0:00 | 13:39 | 0:00 |  | ----- | ----- | -----
23 | ER2L23 | Rangpo-TEESTA-I | 11.83 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ----
24 | ER2L24 | BINAGURI-Rangpo- II | 110.42 |  | --- | 2018-07-30 20:42 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 0:00 | 27:18 | 0:00 | During rain and thunder-storm, Tripped on Y-B fault. R/I at Rangpo: Y-B-N, Z1, F/D: 26.86 KM, F/C: Y: 5.38 KA, B: 3.429 KA. R/I at Binaguri: Y-B-N, Z1, F/D: 84 KM, F/C: 4.198 KA, B: 5.225 KA. Charging attempt taken at 21:11 hrs but tripped on SOTF. | ----- | ----- | ----- |  | 100
[5 empty] | ----- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 27:18 | 0:00 |  | ----- | ----- | -----
25 | ER2L25 | Rangpo-Teesta-II | 21.42 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
26 | ER2L26 | MAITHON - MEJIA - I | 59.182 |  |  | 2018-07-07 12:54 | 2018-07-07 15:41 | ---- | ---- | ---- | 0:00 | 2:47 | 0:00 | 0:00 | Tripped due to Bus Fault at Mejia/DVC end. R/I at Maithon end : Main-I : BN, FL-59.7 Km, F/C-3 KA, DT received. Main-II : BN, FL-Not shwon, F/C-3 KA, | ---- | ---- | ---- |  | 100
[5 empty] | --- | 2018-07-31 11:41 | 2018-07-31 19:15 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 7:34 | S/D taken by DVC for attending hot spot at their end. | ----- | ----- | -----
[5 empty] | ---- | TOTAL |  | ---- | ---- | ---- | 0:00 | 2:47 | 0:00 | 0:00 |  | ---- | ---- | ----
27 | ER2L27 | MAITHON - MEJIA - II | 59.182 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
28 | ER2L28 | MAITHON - Durgapur - I | 70.77 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
29 | ER2L29 | MAITHON - Durgapur - II | 70.77 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
30 | ER2L30 | ANDAL - Jamshedpur - I | 156.76 |  | --- | 2018-07-28 21:06 | 2018-07-29 02:20 | ---- | ---- | ---- | 0:00 | 0:00 | 5:14 | 0:00 |  | ----- | ----- | ----- |  | 100
[6 empty] | 2018-07-30 15:10 | 2018-07-30 15:10 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 0:00 |  | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 5:14 | 0:00 |  | ---- | ---- | ----
31 | ER2L31 | ANDAL - Jamshedpur - II | 156.76 |  |  | 2018-07-28 21:06 | 2018-07-28 22:46 | ---- | ---- | ---- | 0:00 | 0:00 | 1:40 | 0:00 |  | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-29 01:55 | 2018-07-29 02:11 | ---- | ---- | ---- | 0:00 | 0:16 | 0:00 | 0:00 |  | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:16 | 1:40 | 0:00 |  | ---- | ---- | ----
32 | ER2L32 | Maithon - MaithonRB- I | 31.5 |  | --- | 2018-07-01 | 2018-07-11 03:02 | ---- | ---- | ---- | 0:00 | 0:00 | 243:02 | 0:00 | Tripped during heavy thunderstrom/lightning/rain in the affected area .R/I at Maithon : R-N, FD-19.13 KM, F/C-1.96KA , charging attempt taken from Maithon end at 05:51hrs but tripped on SOTF. Later on it is found that, 03 (three) nos D+25 towers collapsed at Loc no: 63-64-65. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 243:02 | 0:00 |  | ---- | ---- | ----
33 | ER2L33 | Maithon - MaithonRB- II | 31.5 |  | --- | 2018-07-01 | 2018-07-11 02:52 | 3 | ---- | 45 | 0:00 | 0:00 | 242:52 | 0:00 | Tripped during heavy thunderstrom/lightning/rain in the affected area .R/I at Maithon : b-N, FD-18.67 KM, F/C-8.5KA , charging attempt taken from Maithon end at 06:07hrs but tripped on SOTF. Later on it is found that, 03 (three) nos D+25 towers collapsed at Loc no: 63-64-65. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 242:52 | 0:00 |  | ---- | ---- | ----
34 | ER2L34 | Baharampore-Sagardighi-I | 26.1 |  |  | 2018-07-17 07:49 | 2018-07-17 20:16 | 3 | ---- | 45 | 0:00 | 0:00 | 0:00 | 12:27 | Tie bay of 400KV-BAHARAMPUR-SAGARDIGHI-1 at Sagadighi end was already under S/D for new Pipe-pass connection, scheme checking , A/R , SAS intigration etc. at SgTPP end. Now Main bay of the same at Sagardighi has taken under S/D for Stability & SAS checking work. These all are to facilitate the LILO connectivity at Sagardighi of 400 KV Farakka-Berhampore D/C line. | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-30 12:47 | 2018-07-30 13:04 | ---- | ---- | ---- | 0:00 | 0:17 | 0:00 | 0:00 | Tripped due to DT received at Baharampur from Sagardighi/WBSETCL end. | ---- | ---- | ----
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:17 | 0:00 | 12:27 |  | ----- | ----- | -----
35 | ER2L35 | Baharampore-Sagardighi-II | 26.1 |  |  | 2018-07-29 07:50 | 2018-07-29 08:15 | ---- | ---- | ---- | 0:00 | 0:25 | 0:00 | 0:00 | Tripped from sagardighi end.Breaker remain closed from Baharampur end. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:25 | 0:00 | 0:00 |  | ----- | ----- | -----
36 | ER2L36 | Chukha-Birpara-II | 36 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
37 | ER2L37 | Chukha-Birpara-I | 36 |  | --- | 2018-07-30 14:36 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 33:24 | 0:00 | 0:00 | Tripped on R-N fault, R/I at Birpara: M1: F/C-3.265KA, F/D:34.28kms, Z1; M2:F/C-3.278 KA,F/D-37.16 KM, Z1.A Charging attempt taken at 15:01 hrs on 30.07.18 but immidiatly tripped on SOTF,R/I at Birpara:R-Y-N fault, Ir:5.776KA, Iy: 4.737KA, F/D: 30.49kms. As per information received from NLDC, fault is between tower loc. 113-114(under Bhutan jurisdiction). | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 33:24 | 0:00 | 0:00 |  | ---- | ---- | ----
38 | ER2L39 | MALBASE-Birpara(CHUKHA III) | 38 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
39 | ER2L40 | Birpara-Binaguri-I | 80 |  | --- | 2018-07-03 21:46 | 2018-07-03 21:46 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end. R/I at Birpara:Y-N fault,F/C: 2.27 kA,F/D: 44.27km. Binaguri:F/C: 2.133 kA,F/D: 41.082km. Heavy rain & lightning reported from both end. | ----- | ----- | ----- |  | 100
[6 empty] | 2018-07-20 17:56 | 2018-07-20 17:56 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end. R/I at Birpara: R-N, Z1, F/D: 21.66 KM, F/C: 4.086 KA; R/I at Binaguri: R-N, Z1, F/D: 49.50 KM, F/C: 2.910 KA. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 0:00 |  | ---- | ---- | ----
40 | ER2L41 | Birpara-Binaguri-II | 80 |  | ---- | 2018-07-03 21:46 | 2018-07-03 22:58 | ---- | ---- | ---- | 0:00 | 0:00 | 1:12 | 0:00 | A/R successful at Birpara end but CB got OPENED at Binaguri end.R/I at Birpara:Y-N fault,F/C: 2.065kA,F/D: 44.20km. R/I at Binaguri:F/C: 2.123 kA,F/D: 41.22km. Heavy rain & lightning reported from both end. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 1:12 | 0:00 |  | ---- | ---- | ----
41 | ER2L42A | BIRPARA-ALIPURDUAR-I | 57.49 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
42 | ER2L42B | ALIPURDUAR-SALAKATI-I | 100.57 |  | ----- | 2018-07-04 04:17 | 2018-07-04 05:06 | ---- | ---- | ---- | 0:00 | 0:00 | 0:49 | 0:00 | Ttripped during heavy rain & lightning reported from both end. R/I at APD:Y-B (Ph.-Ph.), Z1, FL-35.3 Km, F/C: Yph-3.6KA & Bph-3.4KA.R/I at SLKT:Y-B (Ph.-Ph.), Z1, FL-59.3 Km, F/C: Yph-2.3KA & Bph-2.3KA | ----- | ----- | ----- |  | 98.78
[6 empty] | 2018-07-25 08:44 | 2018-07-25 17:50 | ---- | ---- | ---- | 9:06 | 0:00 | 0:00 | 0:00 | Shutdown for AMP work. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 9:06 | 0:00 | 0:49 | 0:00 |  | ---- | ---- | ----
43 | ER2L43A | BIRPARA-ALIPURDUAR-II | 57.49 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ----
44 | ER2L43B | ALIPURDUAR-SALAKATI-II | 100.57 |  | ----- | 2018-07-26 08:15 | 2018-07-26 18:45 | ---- | ---- | ---- | 10:30 | 0:00 | 0:00 | 0:00 | Shutdown for AMP work. | ----- | ----- | ----- |  | 98.59
[6 empty] | 2018-07-04 04:17 | 2018-07-04 05:14 | ---- | ---- | ---- | 0:00 | 0:00 | 0:57 | 0:00 | Ttripped during heavy rain & lightning reported from both end. R/I at APD:Y-B (Ph.-Ph.), Z1, FL-33.2 Km, F/C: Yph-3.2KA & Bph-3.4KA. R/I at SLKT:Y-B (Ph.-Ph.), Z1, FL-62.1 Km, F/C: Yph-2.3KA & Bph-2.2KA. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 10:30 | 0:00 | 0:57 | 0:00 |  | ---- | ---- | ----
45 | ER2L44 | Siliguri-Kishengunj-I | 108 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
46 | ER2L45 | Siliguri-Kishengunj-II | 108 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
47 | ER2L46 | Dalkhola-Kishengunj-I | 30.9 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
48 | ER2L47 | Dalkhola-Kishengunj-II | 30.9 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
49 | ER2L48 | Dalkhola-Malda-I | 116 |  | --- | 2018-07-04 09:38 | 2018-07-04 20:15 | ---- | ---- | ---- | 0:00 | 10:37 | 0:00 | 0:00 | Shut down taken for A/R retrofitting work. | ----- | ----- | ----- |  | 100
[6 empty] | 2018-07-05 09:38 | 2018-07-05 19:41 | ---- | ---- | ---- | 0:00 | 10:03 | 0:00 | 0:00 | Shut down taken for A/R retrofitting work. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 20:40 | 0:00 | 0:00 |  | ---- | ---- | ----
50 | ER2L49 | Dalkhola-Malda-II | 116 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
51 | ER2L50 | Binaguri-Siliguri-I | 9 |  | ----- | 2018-07-11 12:13 | 2018-07-11 16:22 | ---- | ---- | ---- | 4:09 | 0:00 | 0:00 | 0:00 | Shut down taken to carry out AMP work. | ----- | ----- | ----- |  | 99.44
[6 empty] | TOTAL |  | ---- | ---- | ---- | 4:09 | 0:00 | 0:00 | 0:00 |  | ---- | ---- | ----
52 | ER2L51 | Binaguri-Siliguri-II | 9 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
53 | ER2L52 | Rangpo-New Melli-I | 26.1 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
54 | ER2L53 | Rangpo-Tashiding | 26.1 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
55 | ER2L55 | Siliguri-Kurseong-I (up to LILO) | 31.3 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
56 | ER2L56 | Kurseong-Rangit-I (up to LILO) | 61.2 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
57 | ER2L57 | RANGIT-Rangpo | 54.17 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
58 | ER2L58 | Rangpo-GANGTOK-II | 26.36 |  |  | 2018-07-04 13:59 | 2018-07-04 15:45 | ---- | ---- | ---- | 0:00 | 1:46 | 0:00 | 0:00 | S/D taken for replacement of faulty P442 distance relay at Gantok. | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-22 09:16 | 2018-07-22 13:36 | ---- | ---- | ---- | 0:00 | 4:20 | 0:00 | 0:00 | Shut down for O/C and E/F relay replacement work, for IEC upgradation to make compatible with NTAMC adaptation work. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 6:06 | 0:00 | 0:00 |  | ---- | ---- | ----
59 | ER2L59 | Chujacheng-Rangpo (LILO) | 1 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | -----
60 | ER2L60 | 132KV-GANGTOK -CHUZACHEN-1 | 28.06 |  | ----- | 2018-07-21 09:36 | 2018-07-21 16:33 | ---- | ---- | ---- | 0:00 | 6:57 | 0:00 | 0:00 | Shut down for O/C and E/F relay replacement work, for IEC upgradation to make compatible with NTAMC adaptation work. | Tripped on R-Y Fault. R/I at Gangtok end: F/D: 29.77 KM,(fault is under Sikkim jurisdiction) F/C: R-1.8 KA, Y-1.7 KA; Weather condition : extreme rain,lightening and thunder storm, surrounding affected area.. | ----- | ----- |  | 100
[5 empty] | ---- | TOTAL |  | ---- | ---- | ---- | 0:00 | 6:57 | 0:00 | 0:00 |  | During rain and thunder-storm, tripped from both end. R/I at Gangtok: R-N, F/D: 2.56 KM; F/C: Ir:2.7 KA; FAULT JURISDICTION UNDER SIKIM. | ---- | ----
61 | ER2L61 | MELLI-SILIGURI | 92.45 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
62 | ER2L62 | RANGPO-MELLI | 16.61 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
63 | ER2L63 | Rangit-Rammam | 27.15 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
64 | ER2L64 | Rangit-Rabangla(up to LILO) | 1 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
65 | ER2L65 | Rabangla - Melli(up to LILO) | 36 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
66 | ER2L66 | Binaguri-Bongaigaon-I | 217.275 |  |  | 2018-07-04 07:43 | 2018-07-04 09:13 | ---- | ---- | ---- | 0:00 | 1:30 | 0:00 | 0:00 | Tripped on DT received at Binaguri end.Due to Buccloz & PRV operated in 63 MVAR Line reactor at Bongaigoan end line got tripped. | ---- | ---- | ---- |  | 99.53
[5 empty] | --- | 2018-07-24 09:33 | 2018-07-24 14:30 | ---- | ---- | ---- | 4:57 | 0:00 | 0:00 | 0:00 | Shutdown taken by NER/Bongaigaon for general maintenance for testing of Line Reactor at their end. | ----- | ----- | -----
[5 empty] | ---- | TOTAL |  | ---- | ---- | ---- | 4:57 | 1:30 | 0:00 | 0:00 |  | ---- | ---- | ----
67 | ER2L67 | Binaguri-Bongaigaon-II | 217.275 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
68 | ER2L68 | Farakka-Baharampore - I (LILO portion) | 2.54 |  |  | 2018-07-19 07:04 | 2018-07-28 21:23 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 230:19 | * Shut down for completion of LILO connectivity at Sagardighi, under construction head.. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- |  |  |  | 230:19 |  | ----- | ----- | -----
69 | ER2L69 | Baharampore-Jeerat - I(LILO portion) | 2.634 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
70 | ER2L70 | Baharampore - Bheramara - I(Indian portion) | 71.51 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
71 | ER2L71 | Baharampore - Bheramara - II(Indian Portion) | 71.51 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
72 | ER2L74 | Rangpo-Teesta-III(LILO) | 10.78 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
73 | ER2L75 | Rangpo_Kishengunj(LILO) | 10.78 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
74 | ER2L72 | Farakka-Gokarna-I | 120 |  |  | 2018-07-14 08:23 | 2018-07-14 12:35 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 4:12 | S/D taken by WBSETCL for for attending jumper bolt loose & missing at their end. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 4:12 |  | ----- | ----- | -----
75 | ER2L73 | Farakka-Gokarna-II | 120 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
76 | ER2L74 | BINAGURI-KISUNGANJ-1-LILO | 5
77 | ER2L75 | BINAGURI-KISUNGANJ-2-LILO | 5
77 | ER2L76 | 400KV-KISHANGANJ-PURNEA-1 LILO | 5 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ----
77 | ER2L77 | 400KV-KISHANGANJ-PURNEA-2 LILO | 5 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ----
75 | ER2T1 | ICT-I,DGP | 315 |  |  | 2018-07-14 09:10 | 2018-07-14 11:15 | ---- | ---- | ---- | 0:00 | 2:05 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 2:05 | 0:00 | 0:00 |  | ----- | ----- | -----
76 | ER2T2 | ICT-II,DGP | 315 |  |  | 2018-07-14 12:02 | 2018-07-14 13:25 | ---- | ---- | ---- | 0:00 | 1:23 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 1:23 | 0:00 | 0:00 |  | ----- | ----- | -----
77 | ER2T3 | ICT-I,MTN | 500 |  |  | 2018-07-23 11:20 | 2018-07-23 13:41 | ---- | ---- | ---- | 0:00 | 2:21 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability. | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-27 01:04 | 2018-07-27 03:16 | ---- | ---- | ---- | 0:00 | 2:12 | 0:00 | 0:00 | Tripped on Directional Earth fault protection relay . | ---- | ---- | ----
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 4:33 | 0:00 | 0:00 |  | ----- | ----- | -----
78 | ER2T4 | ICT-II,MTN | 315 |  |  | 2018-07-24 10:47 | 2018-07-24 13:26 | ---- | ---- | ---- | 0:00 | 2:39 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 2:39 | 0:00 | 0:00 |  | ----- | ----- | -----
79 | ER2T5 | ICT-I,FKK | 315 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
80 | ER2T6 | ICT-III,MLD | 315 |  | --- | 2018-07-09 09:20 | 2018-07-09 14:22 | ---- | ---- | ---- | 0:00 | 5:02 | 0:00 | 0:00 | S/D taken for provoding rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture inggress i.e as a preventive action to ensure maximum system availability and retrofitting of A/R relay at Malda. | ----- | ----- | ----- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 5:02 | 0:00 | 0:00 |  | ----- | ----- | -----
81 | ER2T7 | ICT-V,MLD | 315 |  |  | 2018-07-07 08:02 | 2018-07-07 17:49 | ---- | ---- | ---- | 0:00 | 9:47 | 0:00 | 0:00 | S/D taken for provoding rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture inggress i.e as a preventive action to ensure maximum system availability and upgradation of relay to make it compatible with NTAMC | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 9:47 | 0:00 | 0:00 |  | ---- | ---- | ----
82 | ER2T8 | ICT-I, NSLG | 315 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
83 | ER2T9 | ICT-II, NSLG | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
84 | ER2T10 | ICT-I, SGM | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
85 | ER2T11 | ICT-II, SGM | 315 |  | ---- | 2018-07-27 10:08 | 2018-07-27 12:28 | ---- | ---- | ---- | 0:00 | 2:20 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 2:20 | 0:00 | 0:00 |  | ---- | ---- | ----
86 | ER2T12 | ICT-V, SGM | 500 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
87 | ER2T13 | ICT-V RANGPO | 315 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
88 | ER2T14 | ICT-IV RANGPO | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
89 | ER2T15 | ICT-III RANGPO | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
90 | ER2T16 | ICT-II RANGPO | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
91 | ER2T17 | ICT-I RANGPO | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
92 | ER2T18 | ICT-I,SLG | 160 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
93 | ER2T19 | ICT-II,SLG | 160 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
94 | ER2T20 | ICT-I,BRP | 160 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
95 | ER2T21 | ICT-II,BRP | 160 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
96 | ER2T22 | ICT-II, Malda | 160 |  | --- | 2018-07-10 11:56 | 2018-07-10 13:59 | ---- | ---- | ---- | 0:00 | 2:03 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability . | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 2:03 | 0:00 | 0:00 |  | ---- | ---- | ----
97 | ER2T23 | ICT-I, Malda | 160 |  |  | 2018-07-10 09:37 | 2018-07-10 11:36 | ---- | ---- | ---- | 0:00 | 1:59 | 0:00 | 0:00 | S/D taken for providing rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture ingress i.e as a preventive action to ensure maximum system availability. | ---- | ---- | ---- |  | 100
[7 empty] | TOTAL | ---- | ---- | ---- | 0:00 | 1:59 | 0:00 | 0:00 |  | ---- | ---- | ----
98 | ER2T24 | ICT-IV, MLD | 50 |  |  | 2018-07-06 08:00 | 2018-07-06 14:07 | ---- | ---- | ---- | 0:00 | 6:07 | 0:00 | 0:00 | S/D taken for provoding rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture inggress i.e as a preventive action to ensure maximum system availability and upgradation of relay to make it compatible with NTAMC | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 6:07 | 0:00 | 0:00 |  | ---- | ---- | ----
99 | ER2T25 | ICT-I, RANGPO | 100 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
100 | ER2T26 | ICT-II, RANGPO | 100 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
101 | ER2T27 | ICT-III, RANGPO | 100 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
102 | ER2T28 | ICT-I, GTK | 50 |  |  | 2018-07-06 09:26 | 2018-07-06 11:08 | ---- | ---- | ---- | 0:00 | 1:42 | 0:00 | 0:00 | S/D taken for provoding rain canopy on bucholz,PRD,OSR to prevent any spurious tripping due to moisture inggress i.e as a preventive action to ensure maximum system availability and upgradation of relay to make it compatible with NTAMC | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-19 09:33 | 2018-07-19 19:04 | ---- | ---- | ---- | 0:00 | 9:31 | 0:00 | 0:00 | For O/C and E/F relay replacement work, for IEC upgradation.. | ---- | ---- | ----
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 11:13 | 0:00 | 0:00 |  | ----- | ----- | -----
103 | ER2T29 | ICT-II,GTK | 50 |  | ----- | 2018-07-20 09:18 | 2018-07-20 18:29 | ---- | ---- | ---- | 0:00 | 9:11 | 0:00 | 0:00 | For O/C and E/F relay replacement work, for IEC upgradation.. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 9:11 | 0:00 | 0:00 |  | ---- | ---- | ----
104 | ER2T30 | ALIPURDUAR-ICT-I | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
105 | ER2T31 | ALIPURDUAR-ICT-II | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
106 | ER2R1 | 125 3ph B/R- II NSLG | 125 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
107 | ER2R2 | 125 3ph B/R- I NSLG | 125 |  |  | 2018-07-21 11:00 | 2018-07-21 14:16 | ---- | ---- | ---- | 3:16 | 0:00 | 0:00 | 0:00 | S/D taken for AMP work | ---- | ---- | ---- |  | 99.56
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 3:16 | 0:00 | 0:00 | 0:00 |  | ----- | ----- | -----
108 | ER2R3 | 80 BONGG-III L/R at Binaguri | 80 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
109 | ER2R4 | 80 BONGG-IV L/R at Binaguri | 80 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
110 | ER2R5 | 50 Gaya-I L/R at Maithon | 50 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
111 | ER2R6 | 50 Gaya-II L/R at Maithon | 50 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
112 | ER2R7 | 80 MVAR B/R at Berhampore | 80 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
113 | ER2R8 | 80 MVAR B/R -I at Rangpo | 80 |  | ----- | 2018-07-01 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 744:00 | H/T as per ERLDC instruction for Voltage Regulation. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 744:00 |  | ---- | ---- | ----
114 | ER2R9 | 80 MVAR B/R -II at Rangpo | 80 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
115 | ER2R10 | 50 MVAR B/R-I ,DGP | 50 |  | ----- | 2018-07-01 | 2018-07-29 06:26 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 678:26 | H/T as per ERLDC instruction for Voltage Regulation. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 678:26 |  | ---- | ---- | ----
116 | ER2R11 | 125 MVAR B/R-II ,DGP | 51 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
117 | ER2R12 | 2*50 1ph B/R ,JRT | 100 |  |  | 2018-07-18 21:01 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 314:59 | H/T as per ERLDC instruction for Voltage Regulation. | ---- | ---- | ---- |  | 100
[5 empty] | ----- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 314:59 |  | ----- | ----- | -----
118 | ER2R13 | 31.5MVAR B/R-I at New Melli | 31.5 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
119 | ER2R14 | 31.5MVAR B/R-II at New Melli | 31.5 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
| ER2R15 | 125MVAR B/R-I at Maithan | 125 |  |  | 2018-07-01 | 2018-07-18 13:40 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 421:40 | H/T as per ERLDC instruction for Voltage Regulation. | ---- | ---- | ---- |  | 100
120 |  |  |  |  | ----- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 421:40 |  | ----- | ----- | -----
121 | ER2R16 | 125MVAR B/R-II at Maithan | 125 |  |  | 2018-07-18 13:48 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 322:12 | H/T as per ERLDC instruction for Voltage Regulation. | ---- | ---- | ---- |  | 100
[5 empty] | ----- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 322:12 |  | ----- | ----- | -----
122 | ER2R17 | 125MVAR B/R-III AT DURGAPUR | 125 |  | ----- | 2018-07-01 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 744:00 | H/T as per ERLDC instruction for Voltage Regulation. | ----- | ----- | ----- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 744:00 |  | ---- | ---- | ----
123 | ER2R18 | 80MVAR B/R AT GOKARNA | 80 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ----- | ----- | ----- |  | 100
124 | ER2R19 | ALIPURDUAR-125MVAR BUS REACTOR-I | 125 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
125 | ER2R20 | ALIPURDUAR-125MVAR BUS REACTOR-II | 125 |  |  | 2018-07-14 09:36 | 2018-07-14 14:17 | ---- | ---- | ---- | 4:41 | 0:00 | 0:00 | 0:00 | S/D taken for bushing Tan-Delta measurment. | ---- | ---- | ---- |  | 99.37
[5 empty] | ----- | TOTAL |  | ---- | ---- | ---- | 4:41 | 0:00 | 0:00 | 0:00 |  | ----- | ----- | -----
126 | ER2R21 | FARAKKA -GOKARNA-I L/R | 80 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
127 | ER2R22 | 125MVAR BAHARAMPORE B/R | 125 |  |  | 2018-07-06 10:01 | 2018-07-06 18:56 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 8:55 | Shut down taken for completion of pending construction work under ERSS-XV. | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-07 09:46 | 2018-07-07 18:20 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 8:34 | Shut down taken for completion of pending construction work under ERSS-XV. | ---- | ---- | ----
[6 empty] | 2018-07-05 09:57 | 2018-07-05 17:38 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 7:41 | Shut down taken for completion of pending construction work under ERSS-XV. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 25:10 |  | ---- | ---- | ----
128 | ER2R23 | SUBHASGRAM SAGARDIGHI LR | 50 |  |  | 2018-07-01 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 744:00 | H/T as per ERLDC instruction for Voltage Regulation. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 744:00 |  | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | [10 empty] | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | [10 empty] | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | [10 empty] | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | [10 empty] | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | [10 empty] | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ---- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Note on C115: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C116: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C123: Author: Made LILO w.e.f 01.09.13
Note on C156: Author: DOCO 22.05.14 3 X 105 MVA
Note on C157: Author: DOCO 09.06.2014 3 X 105 MVA
Note on C171: Author: DOCO 24.04.14
Note on C172: Author: DOCO 30.06.2014
Note on C183: Author: DOCO wef 01.05.2013
Note on C184: Author: DOCO wef 01.06.2013
Note on C185: Author: D.O.C.O w.e.f 01.04.2012
Note on C186: Author: D.O.C.O w.e.f 01.04.2012

## Odisha SOP
Standard of Performance data for the month of JULY 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., ODISHA TRANSMISSION SYSTEM
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | No. of towers damaged | no. of insulator failed | Total outage in days (1) | Outage Attributable to |  |  |  | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date Time | Date Time |  |  |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | ODL1 | ROURKELA-TALCHER I | 171 | Odisha | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- | ERPC ERPC/MS/TAC/2018/4148 dtd:17.09.18 | 100
2 | ODL2 | ROURKELA-TALCHER II | 171 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
3 | ODL3 | RENGALI-TALCHER-I | 24 |  | --- | 2018-07-04 16:17 | 2018-07-04 18:42 | ---- | ---- | ---- | 0:00 | 2:25 | 0:00 | 0:00 | Tripped from Talcher/NTPC end only. CB remains charged from Rengali(PG) end. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 2:25 | 0:00 | 0:00 |  | ---- | ---- | ----
4 | ODL4 | RENGALI-TALCHER-II | 24 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
5 | ODL5 | RENGALI-INDRAVATI I | 356 |  |  | 2018-07-24 10:58 | 2018-07-24 12:07 | ---- | ---- | ---- | 1:09 | 0:00 | 0:00 | 0:00 | Shutdown for attending oil leakage from R-ph Bushing of 50MVAR L/R at Indravati. | ---- | ---- | ---- |  | 99.85
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 1:09 | 0:00 | 0:00 | 0:00 |  | ---- | ---- | ----
6 | ODL6 | INDRAVATI-JEYPORE | 71 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
7 | ODL7 | TALCHER -MERAMUNDALI-2 | 51 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
8 | ODL8 | TALCHER-ANGUL | 68.35 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
9 | ODL9 | ANGUL-Meramundali # II | 18.61 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
10 | ODL10 | JEYPORE-BOLANGIR# I | 287 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
11 | ODL11 | BOLANGIR-ANGUL | 196.12 |  | --- | 2018-07-02 10:24 | 2018-07-02 19:39 | ---- | ---- | ---- | 0:00 | 9:15 | 0:00 | 0:00 | For replacement of defective Isulators with Polimer insulators at different locations for System improvement. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 9:15 | 0:00 | 0:00 |  | ---- | ---- | ----
12 | ODL12 | ANGUL-MERAMUNDALI # I | 25.34 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
13 | ODL13 | RENGALI -KEONJHAR-1(LILO Portion) | 9.38 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
14 | ODL14 | BARIPADA -KEONJHAR-1 (both LILO Portion) | 28.12 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
15 | ODL15 | BARIPADA-KHARAGPUR(LILO) | 18.74 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
16 | ODL17 | BARIPADA-DUBURI | 190.247 |  |  | 2018-07-18 11:11 | 2018-07-18 14:47 | ---- | ---- | ---- | 3:36 | 0:00 | 0:00 | 0:00 | To attend hot-spot on R-Y phase Wave trap jumpers , at Baripada end. | ---- | ---- | ---- |  | 99.52
[5 empty] | ----- | TOTAL |  | ---- | ---- | ---- | 3:36 | 0:00 | 0:00 | 0:00 |  | ---- | ---- | ----
17 | ODL18A | DUBURI-PANDIABALLI | 143.3 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
18 | ODL18B | PANDIABALLI-MENDHASAL-I | 28 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
19 | ODL24 | Angul-Sundargarh-II | 274.92 |  | --- | 2018-07-04 22:40 | 2018-07-05 01:49 | ---- | ---- | ---- | 3:09 | 0:00 | 0:00 | 0:00 | Tripped due to mal operation of PRV(Y-Phase) of L/R of said line at Jharsuguda end , DT received at Angul end. After replacement of defective micro switch in PRD , the said line charged alongwith L/R. | ---- | ---- | ---- |  | 99.58
[6 empty] | 2018-07-10 12:49 | 2018-07-10 12:49 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end. R/I at Angul end: M1: R-N, Z2, F/D: 262.8 KM, F/C: 2.42 KA; M2: R-N, Z2, F/D: 262.6 KM, F/C: 2.35 KA; | ---- | ---- | ----
[6 empty] | 2018-07-26 08:51 | 2018-07-26 19:56 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 11:05 | Shut down for strengthening of A type delta tower. | ---- | ---- | ----
[6 empty] | 2018-07-27 09:18 | 2018-07-27 20:01 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:43 | Shut down for strengthening of A type delta tower. | ---- | ---- | ----
[6 empty] | 2018-07-28 08:48 | 2018-07-28 19:50 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 11:02 | Shut down for strengthening of A type delta tower. | ---- | ---- | ----
[6 empty] | 2018-07-29 09:11 | 2018-07-30 19:41 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 34:30 | Shut down for strengthening of A type delta tower. | ---- | ---- | ----
[6 empty] | 2018-07-30 08:52 | 2018-07-30 19:41 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:49 | Shut down for strengthening of A type delta tower. | ---- | ---- | ----
[6 empty] | 2018-07-31 09:14 | 01/08/18 00:00 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 14:46 | Shut down for strengthening of A type delta tower. | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 3:09 | 0:00 | 0:00 | 92:55 |  | ---- | ---- | ----
20 | ODL25 | Angul-Sundargarh-I | 272 |  | --- | 2018-07-20 09:27 | 2018-07-20 20:20 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:53 | Shut down for strinthening works of 765 S/C delta tower(WZ-IV) | ---- | ---- | ---- |  | 100
[6 empty] | 2018-07-21 16:33 | 2018-07-21 16:33 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end. R/I at Sundargarh: B-N, F/C: 3.95 KA; F/D: 153.6 KM; R/I at Angul end: B-N, F/C: 4.13 KA, F/D: 130.8 KM; | ---- | ---- | ----
[6 empty] | 2018-07-07 07:34 | 2018-07-07 21:35 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 14:01 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-08 07:19 | 2018-07-08 20:27 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 13:08 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-09 07:19 | 2018-07-09 20:07 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 12:48 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-10 07:15 | 2018-07-10 20:54 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 13:39 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-11 07:44 | 2018-07-11 19:40 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 11:56 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-16 09:02 | 2018-07-16 20:02 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 11:00 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-17 09:50 | 2018-07-17 20:18 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:28 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-18 10:12 | 2018-07-18 20:04 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 9:52 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | 2018-07-19 09:18 | 2018-07-19 20:11 | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 10:53 | For strenthening work of 765 KV S/C Delta tower ( WZ-IV). | ---- | ---- | ----
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 0:00 | 118:38 |  | ---- | ---- | ----
21 | ODL26 | BARIPADA-PANDIABALLI | 301.5 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
22 | ODL27 | PANDIABALLI-MENDHASHAL-II | 28 |  |  | 2018-07-02 10:48 | 2018-07-02 19:21 | ---- | ---- | ---- | 0:00 | 8:33 | 0:00 | 0:00 | Shut down taken for RTV coating of Insulators for system improvements. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 8:33 | 0:00 | 0:00 |  | ---- | ---- | ----
23 | ODL28 | DARLIPALLI-JHARSUGURA-1 | 20.54 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ----
24 | ODL29 | DARLIPALLI-JHARSUGURA-2 | 20.54 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ----
25 | ODT1 | ICT-II Sundergarh | 1500 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
26 | ODT2 | ICT-I Sundergarh | 1500 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
27 | ODT3 | ICT-I,RKL | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
28 | ODT4 | ICT-II,RKL | 315 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
29 | ODT5 | ICT-I, RNG | 315 |  |  | 2018-07-19 10:12 | 2018-07-19 15:39 | ---- | ---- | ---- | 0:00 | 5:27 | 0:00 | 0:00 | For additional neutral earthing related work, for system improvement. | ---- | ---- | ---- |  | 100
[5 empty] | ---- | TOTAL |  | ---- | ---- | ---- | 0:00 | 5:27 | 0:00 | 0:00 |  | ---- | ---- | ----
30 | ODT6 | ICT-II, RNG | 315 |  |  | 2018-07-20 09:48 | 2018-07-20 16:06 | ---- | ---- | ---- | 0:00 | 6:18 | 0:00 | 0:00 | For additional neutral earthing related work, for system improvement. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 6:18 | 0:00 | 0:00 |  | ---- | ---- | ----
31 | ODT8 | ICT-II, JEYPORE | 315 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
32 | ODT7 | ICT-I, JEYPORE | 315 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
33 | ODT9 | ICT-I BRPD | 315 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
34 | ODT10 | ICT- II, IVT | 315 |  |  | 2018-07-18 18:15 | 2018-07-18 19:23 | ---- | ---- | ---- | 1:08 | 0:00 | 0:00 | 0:00 | Shutdown for attending rectification work of jumper conductor from neutral CT to Earth. | ---- | ---- | ---- |  | 99.85
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 1:08 | 0:00 | 0:00 | 0:00 |  | ---- | ---- | ----
35 | ODT11 | ICT-II, BOLANGIR | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
36 | ODT12 | ICT-I, BOLANGIR | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
37 | ODT13 | ICT-I at Angul | 1500 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
38 | ODT14 | ICT-2 at Angul | 1500 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
39 | ODT15 | ICT-3 at Angul | 1500 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
40 | ODT16 | ICT-IV at Angul | 1500 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
41 | ODT17 | ICT-I, KEONJHAR | 315 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
42 | ODT18 | ICT-II, KEONJHAR | 315 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
42 | ODT19 | ICT-II BRPD | 315 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
43 | ODT20 | ICT- II, BRPD | 160 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
44 | ODT21 | ICT-I, BRPD | 160 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
45 | ODT22 | ICT-I,PANDIABALLI | 500 |  |  | 2018-07-28 18:10 | 2018-08-01 | ---- | ---- | ---- | 0:00 | 0:00 | 77:50 | 0:00 | Tripped due to OLTC operation during heavy rain & lightning. Investigation is being carried out by BHEL team. | ---- | ---- | ---- |  | 100
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 77:50 | 0:00 |  | ---- | ---- | ----
46 | ODT23 | ICT-II,PANDIABALLI | 500 |  |  | 2018-07-16 08:30 | 2018-07-16 14:17 | ---- | ---- | ---- | 0:00 | 0:00 | 5:47 | 0:00 | During heavy rain moisture ingressed in Buchholz contacts resulting tripping of the ICT. | ---- | ---- | ---- |  | 100
[5 empty] | ---- | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 5:47 | 0:00 |  | ---- | ---- | ----
47 | ODT24 | ICT-III BARIPADA | 500 |  |  | 2018-07-05 13:20 | 2018-07-05 15:17 | ---- | ---- | ---- | 1:57 | 0:00 | 0:00 | 0:00 | To attend Oil leakage from PRD. | ---- | ---- | ---- |  | 99.74
[6 empty] | 2018-07-31 10:22 | 2018-07-31 19:30 | ---- | ---- | ---- | 9:08 | 0:00 | 0:00 | 0:00 | * To attend Oil leakage from PRD of 500 MVA ICT-3. | ---- | ---- | ----
[5 empty] | --- | TOTAL |  | ---- | ---- | ---- | 1:57 | 0:00 | 0:00 | 0:00 |  | ---- | ---- | ----
48 | ODR1 | 240, 1 ph BR-II at Sundergarh | 240 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
49 | ODR2 | 125 3ph B/R- III Angul | 125 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
50 | ODR3 | 125 3ph B/R- II Angul | 125 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
51 | ODR4 | 125 3ph B/R- I Angul | 125 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
52 | ODR5 | 330 MVAR BR-I at Angul | 330 |  |  | 2018-07-05 10:47 | 2018-07-05 19:00 | ---- | ---- | ---- | 0:00 | 8:13 | 0:00 | 0:00 | Shut down taken for routine operational change over of spare B/Reactor with B/R-1. | ---- | ---- | ---- |  | 100
[5 empty] | ----- | TOTAL |  | ---- | ---- | ---- | 0:00 | 8:13 | 0:00 | 0:00 |  | ---- | ---- | ----
53 | ODR6 | 330 MVAR BR-II at Angul | 330 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
54 | ODR7 | 240 MVAR SLR-1 at Angul | 240 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
55 | ODR8 | 240 MVAR SLR-2 at Angul | 240 |  |  | 2018-07-12 12:07 | 2018-07-12 13:25 | ---- | ---- | ---- | 0:00 | 1:18 | 0:00 | 0:00 | S/D taken for replacement of PRD with modified PRD to prevent mal-operation for System improvement at Jharsugda end. | ---- | ---- | ---- |  | 99.58
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 1:18 | 0:00 | 0:00 |  | ---- | ---- | ----
56 | ODR9 | 125 3ph B/R- I Sundergarh | 125 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
57 | ODR10 | 125 3ph B/R- II Sundergarh | 125 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
58 | ODR11 | 240 3ph B/R- I Sundergarh | 240 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
59 | ODR12 | 63 Duburi L/R at Baripada | 63 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
60 | ODR13 | 50 ANGUL L/R at Bolangir | 50 |  | ----- | 2018-07-07 18:47 | 2018-07-07 20:23 | ---- | ---- | ---- | 0:00 | 0:00 | 1:36 | 0:00 | During heavy rain & thunderstorm moisture ingressed in bucholz relay contact resulting triiping of the L/R. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 0:00 | 1:36 | 0:00 |  | ---- | ---- | ----
61 | ODR14 | 50 JPR L/R at Bolangir | 50 |  | ----- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
62 | ODR15 | 80 MVAR B/R at Bolangir | 80 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
63 | ODR16 | 80 MVAR B/R at Keonjhar | 80 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
64 | ODR17 | 63 3ph B/R ,JEYPORE | 63 |  | --- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
65 | ODR20 | 50 CHAIBASA -I L/R at RKL | 50 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
66 | ODR21 | 125MVAR BR-I at RKL | 125 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
67 | ODR23 | 80 JPR L/R at Meramundli | 80 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
68 | ODR24 | 80 MVAR B/R at DUBRI | 80 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
69 | ODR25 | 125 MVAR B/R at IVT | 125 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
70 | ODR26 | 125 MVAR B/R at JPR | 125 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
71 | ODR27 | 50MVAR Keonjhar LR at Baripada | 50 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
72 | ODR28 | 63MVAR BARIPADA L/R AT PANDIABALLI | 63 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
73 | ODR29 | 80MVAR B/R AT PANDIABALLI | 80 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
74 | ODR30 | 125MVAR B/R AT BARIPADA | 125 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
[5 empty] | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
75 | ODR31 | 63 MVAR NEW DUBURI L/R AT PANDIABILI END | 63 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
76 | ODR32 | RENGALI-BUS REACTOR-1_125MVAR | 125 |  | ---- |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
77 | ODR33 | RENGALI-BUS REACTOR-2_125MVAR | 125 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ----
78 | ODR33 | ROURKELA BUS REACTOR-2_125 MVAR | 125 |  | ----- | 2018-07-25 10:31 | 2018-07-25 17:49 | ---- | ---- | ---- | 0:00 | 7:18 | 0:00 | 0:00 | Shutdown for overhauling of isolator & canopy erection work for system improvement. | ---- | ---- | ---- |  | 100
[6 empty] | TOTAL |  | ---- | ---- | ---- | 0:00 | 7:18 | 0:00 | 0:00 |  | ---- | ---- | ----
79 | ODR34 | STATCOM AT ROURKELA | 850 |  |  |  |  | ---- | ---- | ---- | [5 empty] | ---- | ---- | ---- |  | 100
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----
[8 empty] | ---- | ---- | ----