## ODISHA
Standard of Performance data for the month of August 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION - II
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) |  |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Date | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | ODL1 | ROURKELA-TALCHER I | 171 | Odisha | --- | 2016-08-15 13:50 | 2016-08-15 14:38 | --- | --- | --- | 0 | 0.8 | 0 | 0 | --- | --- | --- | CB tripped at Talcher end only. No any relay initiation at RKL end. At talcher end - only B-phase start. Problem at NTPC-Talcher end. | ERPC | 100
2 | ODL2 | ROURKELA-TALCHER II | 171 |  | --- | 2016-08-15 13:50 | 2016-08-15 13:50 | --- | --- | --- | 0 | 0 | 0 | 0 | --- | --- | --- | A/R optd successful at both end. R/I: RKL : B-N, Z-1, 15.94 KM; F/C: 11.0 KA; Talcher end: B-N; Z2, 128 km; 2.806 KA. |  | 100
[5 empty] | --- | 2016-08-07 20:38 | 2016-08-08 07:08 | --- | --- | --- | 0 | 0 | 10.5 | 0 | --- | --- | --- | During rain & thunderstorm feeder tripped on R-B phase. R/I at Rourkela: FD : 56.22KM , FC: 8.026KA .
[5 empty] | --- | 2016-08-12 10:54 | 2016-08-12 19:34 | --- | --- | --- | 0 | 8.6667 | 0 | 0 | --- | --- | --- | Emergency S/D taken for replacement of defective B-Phase CT of its main bay ( Bay no-407). Line S/d required for clearance issue due to crane movement.
[5 empty] | --- | TOTAL |  | --- | --- | --- | 0 | 8.6667 | 10.5 | 0 | --- | --- | ---
3 | ODL3 | RENGALI-TALCHER-I | 24 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
4 | ODL4 | RENGALI-TALCHER-II | 24 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
5 | ODL5 | RENGALI-INDRAVATI I | 356 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
6 | ODL6 | INDRAVATI-JEYPORE | 71 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
7 | ODL7 | TALCHER-MEERAMUNDALI | 51 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
8 | ODL8 | TALCHER-ANGUL | 68.35 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
9 | ODL9 | ANGUL-Meramundali # II | 18.61 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
10 | ODL10 | JEYPORE-BOLANGIR# I | 287 |  | --- | 2016-08-27 13:25 | 2016-08-27 13:25 | --- | --- | --- | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at both ends, R/I at JPR : R-N fault, FD- 237KM,F/C-1.0KA , R/I at Bolangir : R-N fault, FD- 28.9KM,F/C-3.2KA. |  | 100
[5 empty] | --- | 2016-08-27 13:38 | 2016-08-27 13:38 | --- | --- | --- | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at both ends, R/I at JPR : R-N fault, FD- 241KM,F/C-1.16KA , R/I at Bolangir : R-N fault, FD- 24.5KM,F/C-2.93KA
[5 empty] | --- | TOTAL |  | --- | --- | --- | 0 | 0 | 0 | 0 | --- | --- | ---
11 | ODL11 | BOLANGIR-ANGUL | 196.12 |  | --- | 2016-08-08 09:43 | 2016-08-08 10:02 | --- | --- | --- | 0 | 0 | 0.31667 | 0 | --- | --- | --- | Tripped due to rain/lightening. R.I at Angil: B-N fault,Fc: 9.23ka,FD: 30.3km frm Angul. R.I. at Bolangir: B-N fault, Fc: 1.12ka, Fd: 175.3km from Bolangir, Zone-2 |  | 98.9781
[5 empty] | --- | 2016-08-17 19:32 | 2016-08-17 22:12 | --- | --- | --- | 2.6667 | 0 | 0 | 0 | --- | --- | --- | Shut down taken To remove the pilot string , which was hanged during OPGW stringing.
[5 empty] | --- | 2016-08-24 11:10 | 2016-08-24 16:06 | --- | --- | --- | 4.9333 | 0 | 0 | 0 | --- | --- | --- | E/S/D taken by Angul for attending hot spot in B-phase jumper at Tower Loc.No-55.
[5 empty] | --- | TOTAL |  | --- | --- | --- | 7.6 | 0 | 0.31667 | 0 | --- | --- | ---
12 | ODL12 | ANGUL-MERAMUNDALI # I | 25.34 |  | --- | 2016-08-31 16:40 | 2016-08-31 18:28 | --- | --- | --- | 0 | 0 | 0 | 1.8 | --- | --- | --- | Emergrecyv shut down taken by Meramundali/ OPTCL , to attend HOT-SPOT on R-Phase isolator at Meramundali end. |  | 100
13 | ODL13 | RNG-Keonjhar ( LILO Portion) | 9.38 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
14 | ODL14 | Keonjhar-BPD (both LILO Portion) | 28.12 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
15 | ODL15 | BARIPADA-KHARAGPUR(LILO) | 18.74 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
16 | ODL17 | BARIPADA-DUBURI | 190.247 |  | --- | 2016-08-21 07:11 | 2016-08-28 21:06 | --- | --- | --- | 0 | 0 | 0 | 181.9167 | --- | --- | --- | S/D taken by Baripada for erection of Tower at new pile foundation at Loc.No-8 under construction head. |  | 100
17 | ODL18A | DUBRI-PANDIABALLI | 143.3 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
18 | ODL18B | PANDIABALLI-MENDHASAL-II | 28 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
19 | ODL19 | Rourkela-Sundergarh I | 145.3 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
20 | ODL20 | Rourkela-Sundergarh II | 145.3 |  | --- | 2016-08-30 08:17 | 2016-08-30 18:50 | --- | --- | --- | 0 | 0 | 10.55 | 0 | --- | --- | --- | Shut down taken to replaced the damaged insulator string by long rod polymer string, after damaged on recent lightning and thunder storm. |  | 100
21 | ODL21 | Rourkela-Raigarh-II | 188 |  | --- | 2016-08-27 10:17 | 2016-08-27 20:47 | --- | --- | --- | 0 | 10.5 | 0 | 0 | --- | --- | --- | S/D taken for replacement of disc porcelain insulators by Polimer insulators , due to high polution and occational A/R operation during rain & lightning. |  | 100
22 | ODL22 | Rourkela-SEL II | 135 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
23 | ODL23 | Sundargarh-Inbharat | 62.6 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
24 | ODL24 | Angul-Sundargarh-II | 274.92 |  | --- | 2016-08-13 13:45 | 2016-08-13 18:30 | --- | --- | --- | 4.75 | 0 | 0 | 0 | --- | --- | --- | To attend HOT-SPOT at Angul end. |  | 99.3616
25 | ODL25 | Angul-Sundargarh-I | 272 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
26 | ODL16A | BARIPADA-PANDIABALLI | 301.5 |  | --- | 2016-08-26 07:21 | 2016-08-29 21:18 | --- | --- | --- | 0 | 0 | 0 | 85.95 | --- | --- | --- | S/D taken for De-stringing & dismantling of existing tower at Loc no: 8 and erection & stringing of new tower at pile foundation loc no: 8. |  | 100
27 | ODL16B | PANDIABALLI-MENDHASHAL-I | 28 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
28 | ODT1 | ICT-II Sundergarh | 1500 | Odisha | --- | 2016-08-07 07:18 | 2016-08-07 09:00 | --- | --- | --- | 0 | 0 | 1.7 | 0 | --- | --- | --- | Tripped on CT SF6 lockout suspected moisture might have been ingress in the micro switch in 705 CT during heavy rain at Sundargarh at that time. |  | 100
29 | ODT2 | ICT-I Sundergarh | 1500 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
30 | ODT3 | ICT-I,RKL | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
31 | ODT4 | ICT-II,RKL | 315 |  | --- | 2016-08-11 08:31 | 2016-08-11 09:44 | --- | --- | --- | 0 | 1.2167 | 0 | 0 | --- | --- | --- | Tripped on Back up O/C and Back up E/F.Tripped due to OPTCL line fault. |  | 100
[5 empty] | --- | 2016-08-12 06:37 | 2016-08-12 08:18 | --- | --- | --- | 0 | 0 | 1.6833 | 0 | --- | --- | --- | Tripped on OLTC B-phase Buchollze relay operated due to moisture/rain water ingress in control box of OLTC during heavy rain.
[5 empty] | --- | TOTAL |  | --- | --- | --- | 0 | 1.2167 | 1.6833 | 0 | --- | --- | ---
32 | ODT5 | ICT-I, RNG | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
33 | ODT6 | ICT-II, RNG | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
34 | ODT7 | ICT-I, JEYPORE | 315 |  | --- | 2016-08-31 09:44 | 2016-08-31 18:28 | --- | --- | --- | 8.7333 | 0 | 0 | 0 | --- | --- | --- | S/D taken by JeyporeL for AMP work at their end. |  | 98.53
35 | ODT8 | ICT-II, JEYPORE | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
36 | ODT9 | ICT-I BRPD | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
37 | ODT10 | ICT- II, IVT | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
38 | ODT11 | ICT-II, BOLANGIR | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
39 | ODT12 | ICT-I, BOLANGIR | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
40 | ODT13 | ICT-I at Angul | 1500 |  | --- | 2016-08-23 09:27 | 2016-08-23 19:22 | --- | --- | --- | 9.9167 | 0 | 0 | 0 | --- | --- | --- | S/D taken by Angul for AMP work at Angul end. |  | 98.67
41 | ODT14 | ICT-2 at Angul | 1500 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
42 | ODT15 | ICT-3 at Angul | 1500 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
43 | ODT16 | ICT-IV at Angul | 1500 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
44 | ODT17 | ICT-I, KEONJHAR | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
45 | ODT18 | ICT-II, KEONJHAR | 315 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
46 | ODT19 | ICT-II BRPD | 315 |  | --- | 2016-08-18 09:18 | 2016-08-18 19:10 | --- | --- | --- | 0 | 0 | 0 | 9.8667 | --- | --- | --- | S/D taken for Main Bus-I and ICT: II GIB erection work under construction head |  | 100
[5 empty] | --- | 2016-08-19 09:00 | 2016-08-19 18:26 | --- | --- | --- | 0 | 0 | 0 | 9.4333 | --- | --- | --- | S/D taken for Main Bus-I and ICT - II for GIB erection work under construction head.
[5 empty] | --- | 2016-08-24 10:08 | 2016-08-24 17:07 | --- | --- | --- | 0 | 0 | 0 | 6.9833 | --- | --- | --- | S/D taken by Baripada for erection of Main Bus-II at Baripada under construction head.
[5 empty] | --- | TOTAL |  | --- | --- | --- | 0 | 0 | 0 | 26.2833 | --- | --- | ---
47 | ODT20 | ICT- II, BRPD | 160 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
48 | ODT21 | ICT-I, BRPD | 160 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
49 | ODT22 | ICT-I,PANDIABALLI | 500 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
50 | ODT23 | ICT-II,PANDIABALLI | 500 |  | --- | 2016-08-08 16:19 | 2016-08-08 18:12 | --- | --- | --- | 0 | 0 | 0 | 1.8833 | --- | --- | --- | To attend Oil leakage of this new ICT under construction head. |  | 100
51 | ODR1 | 240, 1 ph BR-II at Sundergarh | 240 | Odisha | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
52 | ODR2 | 125 3ph B/R- III Angul | 125 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
53 | ODR3 | 125 3ph B/R- II Angul | 125 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
54 | ODR4 | 125 3ph B/R- I Angul | 125 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
55 | ODR5 | 330 MVAR BR-I at Angul | 330 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
56 | ODR6 | 330 MVAR BR-II at Angul | 330 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
57 | ODR7 | 240 MVAR SLR-1 at Angul | 240 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
58 | ODR8 | 240 MVAR SLR-2 at Angul | 240 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
59 | ODR9 | 125 3ph B/R- I Sundergarh | 125 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
60 | ODR10 | 125 3ph B/R- II Sundergarh | 125 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
61 | ODR11 | 240 3ph B/R- I Sundergarh | 240 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
62 | ODR12 | 63 Mendhasal L/R at BPD | 63 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
63 | ODR13 | 50 MRL L/R at Bolangir | 50 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
64 | ODR14 | 50 JPR L/R at Bolangir | 50 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
65 | ODR15 | 80 MVAR B/R at Bolangir | 80 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
66 | ODR16 | 80 MVAR B/R at Keonjhar | 80 |  | --- | 2016-08-17 09:35 | 2016-08-17 18:48 | --- | --- | --- | 0 | 9.2167 | 0 | 0 | --- | --- | --- | S/D taken for CSD commissioning work |  | 100
67 | ODR17 | 63 3ph B/R ,JEYPORE | 63 |  | --- | 2016-08-06 20:54 | 2016-08-07 00:26 | --- | --- | --- | 0 | 0 | 0 | 3.5333 | --- | --- | --- | H/T or kept open as per ERLDC instruction for voltage regulation. |  | 100
[5 empty] | --- | 2016-08-27 16:15 | 2016-09-01 | --- | --- | --- | 0 | 0 | 0 | 103.75 | --- | --- | --- | H/T as per ERLDC instruction for voltage regulation.
[5 empty] | --- | TOTAL |  | --- | --- | --- | 0 | 0 | 0 | 107.2833 | --- | --- | ---
68 | ODR18 | 50 3ph B/R ,RKL | 50 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
69 | ODR19 | 50 JSR -I L/R at RKL | 50 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
70 | ODR20 | 125MVAR BR-I at RKL | 125 |  | --- | 2016-08-07 20:38 | 2016-08-08 03:30 | --- | --- | --- | 0 | 0 | 6.8667 | 0 | --- | --- | --- | Tripped due to operation of B/U impedance relay (R, Y & B ph) during rain & thunder storm/tripping of 400kv Rourkela-Talcher-II line. |  | 100
71 | ODR21 | 50 BPD L/R at RNG | 50 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
72 | ODR22 | 80 JPR L/R at Meramundli | 80 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
73 | ODR23 | 80 MVAR B/R at DUBRI | 80 |  | --- | 2016-08-10 12:40 | 2016-08-10 19:09 | --- | --- | --- | 0 | 0 | 0 | 6.4833 | --- | --- | --- | S/D taken for CSD installation work for system improvement under construction activity work at New Duburi end. |  | 100
74 | ODR24 | 125 MVAR B/R at IVT | 125 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
75 | ODR25 | 125 MVAR B/R at JPR | 125 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
76 | ODR26 | 50MVAR Keonjhar LR at Baripada | 50 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
77 | ODR27 | 63MVAR BARIPADA L/R AT PANDIABALLI | 63 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
78 | ODR28 | 80MVAR B/R AT PANDIABALLI | 80 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
79 | ODR29 | 63MVAR DUBURI L/R AT PANDIABALLI | 63 |  | --- |  |  | --- | --- | --- |  |  |  |  | --- | --- | --- |  |  | 100
Note on C16: Author: LILOed on 08.06.14
Note on C17: Author: LILOed at 10.06.14
Note on C18: Author: DOCO WEF - 01.09.12
Note on C21: Author: LILO at Angul, Charged on 29.03.13 and DOCO wef 01.04.13
Note on C25: Author: LILO at Angul, Charged on 29.03.13 and DOCO wef 01.04.13
Note on C26: Author: Keonjhar DOCO 01.02.2013
Note on C27: Author: Keonjhar DOCO 01.02.2013
Note on C29: 50084 Charged both Ckt on 29.08.11 DOCO on 01.09.2011
Note on C38: Author: 25.01.2016
Note on C41: Author: DOCO : 31.07.14
Note on C53: Author: DOCO 01.09.2012
Note on C54: Author: DOCO 01.11.2012
Note on C56: Author: 04.05.2015
Note on C57: Author: 25.01.2016
Note on C59: Author: DOCO 01.02.2013
Note on C60: Author: DOCO 01.03.2013
Note on C61: Author: doco 01.05.08
Note on C65: Author: Charged on 22.03.11 at 15:00hrs and loaded on 23.03.11 at 16:10 hrs DOCO - 01.04.2011
Note on C69: Author: DOCO 31.07.14
Note on C70: Author: DOCO w.e.f 01.05.2013
Note on C71: Author: DOCO w.e.f 01.06.2013
Note on C72: Author: DOCO w.e.f 01.11.2013
Note on C77: Author: DOCO w.e.f 01.05.2013
Note on C78: Author: DOCO w.e.f 01.06.2013
Note on C79: Author: DOCO w.e.f 01.05.2013
Note on C80: Author: DOCO 01.09.11
Note on C84: Author: Charged on 31.01.13 DOCO : 01.02.2013
Note on C93: Author: 01.04.2014
Note on C94: Shabbir Ahamad Ansari {शब्बीर अहमद अंसारी}: DOCO 01.08.2015
Note on C95: Author: Charged on 31.12.2015

## ER-II
Standard of Performance data for the month of August 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION - II
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Date | No. of towers damaged | no. of insulator failed |  |  | ISTS Licensee |  | OTHERS |  | System Constraints/ Natural calamity / Militancy |  | Deemed Available
1 | ER2L1 | Maithon -MEJIA - III | 83.74 | ER-II | --- |  |  | --- | --- | --- | [8 empty] | --- | --- | --- |  | ERPC | 100
2 | ER2L2 | MEJIA - Jamshedpur - I | 167.74 |  | --- | 2016-08-24 09:57 | 2016-08-24 12:39 | --- | --- | --- | 0:00 | 0 | 0.1125 | 2.7 | 0 | 0 | 0 | 0 | --- | --- | --- | S/D taken by ER-I/Jamshedpur for CT oil sampling work at Jamshedpur end under instruction of CC/OS. |  | 100
[5 empty] | --- | 2016-08-26 09:28 | 2016-08-26 20:35 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.46319 | 11.1167 | --- | --- | --- | S/D taken by Mejia/DVC for maintenance work at their end.
[5 empty] | --- | 2016-08-29 13:39 | 2016-08-29 14:52 | --- | --- | --- | 0:00 | 0 | 0.050694 | 1.2 | 0 | 0 | 0 | 0 | --- | --- | --- | Tripped due to 400KV Bus fault at Jamshedpur end, DT received at Mejia end.
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0 | 0.16319 | 3.9167 | 0 | 0 | 0.46319 | 11.1167 | --- | --- | ---
3 | ER2L3 | Maithon-Jamshedpur | 153 |  | --- | 2016-08-26 10:14 | 2016-08-26 11:21 | --- | --- | --- | 0:00 | 0 | 0.046528 | 1.1 | 0 | 0 | 0 | 0 | --- | --- | --- | Tripped only from Jamshedpur end due to problem at 400kv Bus at Jamshedpur end. |  | 100
4 | ER2L4 | Farakka-Baharampore - I(upto LILO) | 70.725 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
5 | ER2L5 | Berhampore - Jeerat - I(upto LILO) | 165.266 |  | --- | 2016-08-03 07:19 | 2016-08-03 16:40 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.38958 | 9.35 | --- | --- | --- |  |  | 100
[5 empty] | --- | 2016-08-04 07:21 | 2016-08-04 17:34 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.42569 | 10.2 | --- | --- | ---
[5 empty] | --- | 2016-08-04 18:06 | 2016-08-04 19:02 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.038889 | 0.93333 | 0 | 0 | --- | --- | ---
[5 empty] | --- | 2016-08-11 07:25 | 2016-08-11 15:15 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.32639 | 7.8167 | --- | --- | ---
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0.038889 | 0.93333 | 1899-12-31 03:24 | 27.3833 | --- | --- | ---
6 | ER2L6 | Jeerat-Subhasgram | 63 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
7 | ER2L7 | Farakka-Sagardighi | 55.38 |  | --- | 2016-08-02 03:26 | 2016-08-02 14:07 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.44514 | 10.6667 | 0 | 0 | --- | --- | --- | Tripped due to severe storm in the effected area R.I at Sagordighi: R-N fault F/C-4.11ka,F/D- 47.5km. R.I at Farraka: Z-1, R-ph,Fc: M1=23.23ka,M2=23ka, FD: 5.82km from Farakka. |  | 100
[5 empty] | --- | 2016-08-13 11:30 | 2016-08-13 14:37 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.12986 | 3.1167 | --- | --- | --- | S/D taken for bay up-gradation work at Farakka end under ERSS-XIII pkg.
[5 empty] | --- | 2016-08-22 04:48 | 2016-08-22 15:23 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.44097 | 10.5833 | 0 | 0 | --- | --- | --- | Tripped due to heavy rain/lightening in the effected area. R.I at Farakka: R-N fault,zone-1,FD:5.5km,fc: 23.65ka. R.I at Sagordighi: R_N fault,FD: 48.4km, fc: 2.08ka
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0.88611 | 21.25 | 0.12986 | 3.1167 | --- | --- | ---
8 | ER2L8 | Sagardighi- Subhasgram | 245.64 |  | --- | 2016-08-02 07:30 | 2016-08-02 07:50 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.013889 | 0.33333 | --- | --- | --- | E/S/D taken by Sagardighi for maintenance work at their end. |  | 100
9 | ER2L9 | Farakka-Durgapur-I | 150 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
10 | ER2L10 | Farakka-Durgapur-II | 146 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
11 | ER2L11 | Malda-Farakka-I | 40 |  | --- | 2016-08-29 12:22 | 2016-08-29 13:20 | --- | --- | --- | 0:00 | 0 | 0.040278 | 0.96667 | 0 | 0 | 0 | 0 | --- | --- | --- | Power flow interrupted as 400 KV Bus: I is dead at Farakka / NTPC end only. CB remains charged from Malda end. |  | 100
12 | ER2L12 | Malda-Farakka-II | 40 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
13 | ER2L13 | Durgapur-Jamshedpur | 177 |  | --- | 2016-08-19 03:51 | 2016-08-19 03:51 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at both end.Relay indication:Durgapur: MAIN-I:B-N,Z1,F/C:10.07KA,FD:18.6KM MAIN-II:B-N,Z1,F/C:11.23KA,F/D:18KM Jamshedpur:B-N FAULT, F.D.=151.44KM FROM JSR,F.C.=2.56KA. |  | 100
[5 empty] | --- | 2016-08-26 10:14 | 2016-08-26 11:33 | --- | --- | --- | 0:00 | 0 | 0.054861 | 1.3 | 0 | 0 | 0 | 0 | --- | --- | --- | Tripped on RN fault, FL-148.9km from DGP end, F/C-2.17KA due to sub-station fault at Jamshedpur end.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0.054861 | 1.3 | 0 | 0 | 0 | 0 | --- | --- | ---
14 | ER2L14 | Binaguri-New Purnea-I | 168 |  | --- | 2016-08-22 15:50 | 2016-08-22 16:46 | --- | --- | --- | 0:56 | 0.93333 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | Emergency S/D taken by ER-1, Purnea for Oil Sampling of Y Phase busing of 63MVAR Line Reactor |  | 99.8745
[5 empty] | --- | 2016-08-23 23:02 | 2016-08-23 23:07 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.0034722 | 0.066667 | 0 | 0 | --- | --- | --- | Tripped on O/V at New Purnea end, DT received at Binaguri end.
[5 empty] | --- | 2016-08-23 23:07 | 2016-08-23 23:25 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.0125 | 0.3 | --- | --- | --- | Kept open as per ERLDC instruction for voltage regulation.
[5 empty] | --- | 2016-08-31 08:32 | 2016-08-31 19:49 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.47014 | 11.2667 | --- | --- | --- | Modifying the earth wire configuration for increasing the clearance between said line & HVDC-BNC-Agra Bi-Pole under line construction head.
[5 empty] | --- | TOTAL |  |  |  |  | 0:56 | 0.93333 | 0 | 0 | 0.0034722 | 0.066667 | 0.48264 | 11.5833 | --- | --- | ---
15 | ER2L15 | Binaguri-New Purnea-II | 168 |  | --- | 2016-08-30 09:49 | 2016-08-30 18:03 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.34306 | 8.2167 | --- | --- | --- | Modifying the earth wire configuration for increasing the clearance between said line & HVDC-BNC-Agra Bi-Pole. |  | 100
16 | ER2L16 | Malda-New Purnea-I | 167 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
17 | ER2L17 | Malda-New Purnea-II | 167 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
18 | ER2L18 | TALA-BINAGURI-I | 98.087 |  | --- | 2016-08-14 13:05 | 2016-08-14 13:35 | --- | --- | --- | 0:00 | 0 | 0.020833 | 0.48333 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at Binaguri end only.. CB opened at Tala end. R/I at Binaguri: Start: Y-Ph; Z2 aided; 1.746 KA; Dist: 188.9 km; |  | 100
19 | ER2L19 | TALA-BINAGURI-II | 98.087 |  | --- | 2016-08-14 13:05 | 2016-08-17 21:33 | --- | --- | --- | 0:00 | 0 | 1900-01-02 08:28 | 8.4667 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R optd but unsuccessful. Y-N; Zone: 2; F/Distance: 129.2 km; F/current: 1.273 KA.. Fault under Bhutan Jurisdiction.Charging attempt from Tala end taken at 13:57hrs but did not hold. |  | 100
20 | ER2L20 | TALA-BINAGURI-III | 115.553 |  | --- | 2016-08-16 12:18 | 2016-08-16 12:18 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at both end. Y-N; Z2; F/D: 164.04 KM, which is beyond Powergrid jurisdiction.; F/C: 2.232 KA; |  | 100
[5 empty] | --- | 2016-08-17 15:54 | 2016-08-17 15:54 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at both end at 15:54 hrs on 17.08.2016. R/I at Binaguri: M1: Z1, Y-N fault, F/C- 3.213kA, F/D- 98.44kms; M2: Z1, Y-N fault, F/C- 3.186kA, F/D- 96.99kms.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | ---
21 | ER2L21 | TALA-BINAGURI-IV | 115.553 |  | --- | 2016-01-08 10:43 | 2016-01-08 17:52 | --- | --- | --- | 0:00 | 0 | 0.29792 | 7.1333 | 0 | 0 | 0 | 0 | --- | --- | --- | S/D taken for testing of L/R & putting the L/R into service after oil filtr ation |  | 100
[5 empty] | --- | 2016-08-16 12:18 | 2016-08-16 12:35 | --- | --- | --- | 0:00 | 0 | 0.011806 | 0.28333 | 0 | 0 | 0 | 0 | --- | --- | --- | Due to rain and lightning, tripped on Y-N; F/Dist: 163.3 km which is beyond Powergrid jurisdiction; F/C: 2.334 KA; Z2.
[5 empty] | --- | 2016-08-17 15:58 | 2016-08-17 16:15 | --- | --- | --- | 0:00 | 0 | 0.011806 | 0.28333 | 0 | 0 | 0 | 0 | --- | --- | --- | At 15:58 hrs. on 17.08.16 CB opened at TALA end, line was in hanging condition from Binaguri as A/R operated successfully. R/I at Binaguri: M1: Z1, B-N fault, F/D-93.52kms, F/C-3.705kA; M2: Z1, B-N fault, F/D-89.70kms, F/C-3.468kA.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0.32153 | 7.7167 | 0 | 0 | 0 | 0 | --- | --- | ---
22 | ER2L22 | BINAGURI-Rangpo-I | 109.88 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
23 | ER2L23 | Rangpo-TEESTA-I | 11.83 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
24 | ER2L24 | BINAGURI-Rangpo- II | 110.42 |  | --- | 2016-08-12 08:32 | 2016-08-12 10:07 | --- | --- | --- | 1:35 | 1.5833 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | Emergency S/D taken for attending Hot Spot/replacement of dropper conductor at Binaguri S/S in Rangpo- II line bay. |  | 99.7872
25 | ER2L25 | Rangpo-Teesta-II | 21.42 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
26 | ER2L26 | MAITHON - MEJIA - I | 59.182 |  | --- | 2016-08-09 13:52 | 2016-08-09 13:52 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful from both end,R/I at Maithan ,R-N fault,F/C-5.24 KA,F/D-46.4KM |  | 100
27 | ER2L27 | MAITHON - MEJIA - II | 59.182 |  | --- | 2016-08-03 14:53 | 2016-08-03 14:53 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R operated Successfully,R/I at Maithan: R-N fault,F/C-10.97KA,F/D-19.5 Km |  | 100
28 | ER2L28 | MAITHON - Durgapur - I | 70.77 |  | --- | 2016-08-30 10:59 | 2016-08-30 11:03 | --- | --- | --- | 0:00 | 0 | 0.0027778 | 0.066667 | 0 | 0 | 0 | 0 | --- | --- | --- | It remains out of service for few mins, to provide shut down on 400 KV Maithon-MPL: I as it is on the same dia of Maithon-MPL at Maithon end. |  | 100
29 | ER2L29 | MAITHON - Durgapur - II | 70.77 |  | --- | 2016-08-27 10:39 | 2016-08-27 10:42 | --- | --- | --- | 0:00 | 0 | 0.0020833 | 0.033333 | 0 | 0 | 0 | 0 | --- | --- | --- | H/T as per ERLDC instruction to facilitate S/D of 400KV Maithan - Ranchi line taken by DVC. |  | 100
[5 empty] | --- | 2016-08-27 21:25 | 2016-08-27 21:30 | --- | --- | --- | 0:00 | 0 | 0.0034722 | 0.083333 | 0 | 0 | 0 | 0 | --- | --- | --- | H/T as per ERLDC instruction to facilitate S/D of 400KV Maithan - Ranchi line taken by DVC.
[5 empty] | --- | 2016-08-28 08:13 | 2016-08-28 08:21 | --- | --- | --- | 0:00 | 0 | 0.0055556 | 0.11667 | 0 | 0 | 0 | 0 | --- | --- | --- | H/T as per ERLDC instruction to facilitate S/D of 400KV Maithan - Ranchi line taken by DVC.
[5 empty] | --- | 2016-08-28 19:26 | 2016-08-28 19:35 | --- | --- | --- | 0:00 | 0 | 0.00625 | 0.13333 | 0 | 0 | 0 | 0 | --- | --- | --- | H/T as per ERLDC instruction to facilitate S/D of 400KV Maithan - Ranchi line taken by DVC.
[5 empty] | --- | 2016-08-29 20:22 | 2016-08-29 20:46 | --- | --- | --- | 0:00 | 0 | 0.016667 | 0.38333 | 0 | 0 | 0 | 0 | --- | --- | --- | H/T as per ERLDC instruction to facilitate S/D of 400KV Maithan - Ranchi line taken by DVC.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0.034028 | 0.8 | 0 | 0 | 0 | 0 | --- | --- | ---
30 | ER2L30 | ANDAL - Jamshedpur - I | 156.76 |  | --- | 2016-08-29 13:39 | 2016-08-29 15:52 | --- | --- | --- | 0:00 | 0 | 0.092361 | 2.2167 | 0 | 0 | 0 | 0 | --- | --- | --- | Tripped due to 400KV Bus fault at Jamshedpur end, CB remained charged from Andal end. |  | 100
31 | ER2L31 | ANDAL - Jamshedpur - II | 156.76 |  | --- | 2016-08-09 16:42 | 2016-08-09 16:42 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful from both end,R/I at JSR end :YN fault, Z1, F/C-2.47 KA,F/D-114.9KM. R/I at Andal end: YN fault, Z1, F/C-8.83 KA,F/D-21.63 KM |  | 100
[5 empty] | --- | 2016-08-09 17:45 | 2016-08-09 17:45 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful from both end,R/I at JSR end :YN fault, Z1, F/C-3.45 KA,F/D-80 KM. R/I at Andal end: YN fault, Z1, F/C-4.238 KA,F/D-71.8 KM
[5 empty] | --- | 2016-08-17 12:31 | 2016-08-17 12:31 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R operated successful ,R/I at Jamshedpur,B-N fault,F/D-122.6Km, F/C-3.09KA
[5 empty] | --- | 2016-08-29 13:39 | 2016-08-29 13:44 | --- | --- | --- | 0:00 | 0 | 0.0034722 | 0.083333 | 0 | 0 | 0 | 0 | --- | --- | --- | Tripped due to 400KV Bus fault at Jamshedpur end, CB remained charged from Andal end.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0.0034722 | 0.083333 | 0 | 0 | 0 | 0 | --- | --- | ---
32 | ER2L32 | Maithon - MaithonRB- I | 31.5 |  | --- | 2016-08-07 11:46 | 2016-08-07 19:00 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.30139 | 7.2333 | --- | --- | --- | E/S/D taken by MPL for maintenance work at their end. |  | 100
[5 empty] | --- | 2016-08-08 11:13 | 2016-08-08 18:03 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.28472 | 6.8167 | --- | --- | --- | S/d takenby MPL for maintenance work at their end.
[5 empty] | --- | 2016-08-30 10:59 | 2016-08-30 19:52 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.37014 | 8.8667 | --- | --- | --- | S/D taken by MPL to attend annual maintenance at their end.
[5 empty] | --- | 2016-08-31 09:37 | 2016-08-31 18:58 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.38958 | 9.35 | --- | --- | --- | S/D taken by MPL to attend annual maintenance at their end.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 08:18 | 8.2833 | --- | --- | ---
33 | ER2L33 | Maithon - MaithonRB- II | 31.5 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
34 | ER2L33 | Baharampore-Sagardighi-I | 26.1 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
35 | ER2L34 | Baharampore-Sagardighi-II | 26.1 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
36 | ER2L35 | Dalkhola-Purnea-I | 41 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
37 | ER2L36 | Dalkhola-Purnea-I | 41 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
38 | ER2L37 | Chukha-Birpara-I | 36 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
39 | ER2L38 | Chukha-Birpara-II | 36 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
40 | ER2L39 | MALBASE-Birpara(CHUKHA III) | 38 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
41 | ER2L40 | Birpara-Binaguri-I | 80 |  | --- | 2016-08-07 14:26 | 2016-08-07 14:44 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.0125 | 0.28333 | 0 | 0 | --- | --- | --- | Tripped from Birpara end only.. Feeder remains in service from Binaguri as successful A/R at this end. R/I: Binaguri: R-N; 8.093 KA; 11.85 KM; At Birpara: R-N; 1.63 KA; 44.26 KM; Rain & thunder-storm weather condition. |  | 100
[5 empty] | --- | 2016-08-08 14:12 | 2016-08-08 16:14 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.084722 | 2.0167 | 0 | 0 | --- | --- | --- | S/d taken for insulator replacement work damaged due to heavy lightening.
[5 empty] | --- | 2016-08-17 14:38 | 2016-08-17 15:17 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.027083 | 0.65 | 0 | 0 | --- | --- | --- | CB opened at Birpara end, line was in hanging condition from Biguri as A/R operated successfully. R/I at Binaguri: M1: Z1, Y-N fault, F/C- 7.791kA, F/D- 16.49kms; Weather condition: rain and lightning. R/I at Birpara:M1: Z1,Y-N fault, F/C:2.445kA, F/D:38.34kms, M2: Z1, Y-N fault, F/C- 2.568kA, F/D- 37.82kms.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0.12431 | 2.9667 | 0 | 0 | --- | --- | ---
42 | ER2L41 | Birpara-Binaguri-II | 80 |  | --- | 2016-08-07 14:26 | 2016-08-07 17:08 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.1125 | 2.6833 | 0 | 0 | --- | --- | --- | During rain & thunderstorm feeder tripped on R-Y phase. R/I at Binaguri: R: 5.987 KA; Y: 8.745 KA; 15.44 KM; At Birpara: R: 1.77 KA; Y: 2.234 KA; Dist: 64.76 km. |  | 100
[5 empty] | --- | 2016-08-08 10:41 | 2016-08-08 13:20 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.11042 | 2.6333 | 0 | 0 | --- | --- | --- | S/d taken for insulator replacement work damaged due to heavy lightening.
[5 empty] | --- | 2016-08-17 14:38 | 2016-08-17 14:38 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at both end at 14:38 hrs. on 17.08.16. R/I at Binaguri: M1: Z1, B-N fault, F/C- 7.116kA, F/D- 20.10kms. R/I at Birpara: M1: Z1,B-N fault, F/C:2.307kA, F/D:51.31kms, M2: Z1, B-N fault, F/C: 2.607kA, F/D: 50.89kms.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0.22292 | 5.3333 | 0 | 0 | --- | --- | ---
43 | ER2L42 | Birpara-Salakati-I | 161 |  | --- | 2016-08-29 04:20 | 2016-08-29 04:53 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.022917 | 0.55 | 0 | 0 | --- | --- | --- | During rain and lightning, A/R successful at Birpara end only. CB tripped at Salakati end. R/I at Birpara: R-N;3.219 KA; F/D: 60 KM; Salakati end R/I: R-N, 1.29 KA; 121.6 KM; |  | 100
[5 empty] | --- | 2016-08-31 18:02 | 2016-08-31 19:14 | --- | --- | --- | 0:00 | 0 | 0.05 | 1.2 | 0 | 0 | 0 | 0 | --- | --- | --- | Tripped at Birpara end on Directional earth-fault .
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0.05 | 1.2 | 0.022917 | 0.55 | 0 | 0 | --- | --- | ---
44 | ER2L43 | Birpara-Salakati-II | 161 |  | --- | 2016-08-26 05:18 | 2016-08-26 05:45 | --- | --- | --- | 0:27 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R successful at Birpara end only. R/I at Birpara : Z1, B-N; 1.483 KA,97.84 KM; Salakati end: 109.3 Km; B-N; 2.429 KA; |  | 99.9395
45 | ER2L44 | Siliguri-Kishengunj-I | 108 |  | --- | 2016-08-24 11:34 | 2016-08-24 13:26 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.077778 | 1.85 | --- | --- | --- | H/T as per ERLDC instruction for power regulation. |  | 100
[5 empty] | --- | 2016-08-25 11:15 | 2016-08-25 19:35 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.34722 | 8.3167 | --- | --- | --- | Shutdown for bay extension work at Kishanganj
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.425 | 10.1833 | --- | --- | ---
46 | ER2L45 | Siliguri-Kishengunj-II | 108 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
47 | ER2L46 | Dalkhola-Kishengunj-I | 30.9 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
48 | ER2L47 | Dalkhola-Kishengunj-II | 30.9 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
49 | ER2L48 | Dalkhola-Malda-I | 116 |  | --- | 2016-08-11 08:31 | 2016-08-11 13:51 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.22222 | 5.3167 | --- | --- | --- | For Bus bar augmentation work at Dalkhola & Malda end., as part of S/S upgradation work. |  | 100
50 | ER2L49 | Dalkhola-Malda-II | 116 |  | --- | 2016-08-17 13:03 | 2016-08-17 19:06 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.25208 | 6.0333 | --- | --- | --- | E/S/D for retrofitting of new bus bar at 220 kV level of Malda SS |  | 100
51 | ER2L50 | Binaguri-Siliguri-I | 9 |  | --- | 2016-08-24 08:50 | 2016-08-24 13:18 | --- | --- | --- | 0:00 | 0 | 0.18611 | 4.4667 | 0 | 0 | 0 | 0 | --- | --- | --- | S/D taken by Siliguri for replacement of damaged 03 nos. dropping jumpers of R,Y & B-phase CTs of 220kv Binaguri bay at SLG S/s due over loading from down stream. |  | 100
52 | ER2L51 | Binaguri-Siliguri-II | 9 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
53 | ER2L52 | Rangpo-New Melli-I | 26.1 |  | --- | 2016-08-01 11:43 | 2016-08-01 12:41 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.040278 | 0.96667 | 0 | 0 | --- | --- | --- | Tripped on B-N fault during rain & lightening, F.C= 1.11KA |  | 100
54 | ER2L53 | Rangpo-JHEP | 22 |  | --- | 2016-08-07 09:14 | 2016-08-10 19:12 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 1900-01-02 09:58 | 9.9667 | --- | --- | --- | S/D by JLHEP for diversion of double circuit between tower loc. 13 & 14 to new tower loc. 13A of both the circuits. |  | 100
55 | ER2L54 | New Melli-JHEP | 4.1 |  | --- | 2016-08-04 08:48 | 2016-08-06 17:37 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 08:49 | 8.8 | --- | --- | --- | S/D by JLHEP for diversion of double circuit between tower loc. 13 & 14 to new tower loc. 13A of both the circuits. |  | 100
56 | ER2L55 | Siliguri-Kurseong-I (up to LILO) | 31.3 |  | --- | 2016-08-11 07:46 | 2016-08-11 10:01 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.09375 | 2.25 | --- | --- | --- | Shut down for erection of Beam, under GIS work at Siliguri |  | 99.9418
[5 empty] | --- | 2016-08-17 17:50 | 2016-08-17 18:16 | --- | --- | --- | 0:26 | 0.43333 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | R/I at SLG: B-N fault, F/D: 10kms, F/C: 8kA
[5 empty] | --- | TOTAL |  |  |  |  | 0:26 | 0.43333 | 0 | 0 | 0 | 0 | 0.09375 | 2.25 | --- | --- | ---
57 | ER2L56 | Kurseong-Rangit-I (up to LILO) | 61.2 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
58 | ER2L57 | RANGIT-Rangpo | 54.17 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
59 | ER2L58 | Rangpo-GANGTOK-1 | 26.36 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
60 | ER2L59 | Chujacheng-Rangpo (LILO) | 1 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
61 | ER2L60 | Chuzacheng-Gangtok | 28.06 |  | --- | 2016-08-08 11:37 | 2016-08-08 16:26 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.20069 | 4.8 | --- | --- | --- | S/d taken by Chuzachen for emergency purpose. |  | 100
62 | ER2L61 | MELLI-SILIGURI | 92.45 |  | --- | 2016-08-11 13:15 | 2016-08-11 16:22 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.12986 | 3.1 | --- | --- | --- | Shut down for erection of Beam, under GIS work at Siliguri
[5 empty] | --- | 2016-08-17 17:48 | 2016-08-17 18:52 | --- | --- | --- | 1:04 | 1.05 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | R/I at SLG: Y-N fault, F/D: 3.12kms, F/C: 8kA |  | 99.8566
[5 empty] | --- | TOTAL |  |  |  |  | 1:04 | 1.05 | 0 | 0 | 0 | 0 | 0.12986 | 3.1 | --- | --- | ---
63 | ER2L62 | RANGPO-MELLI | 16.61 |  | --- | 2016-08-08 11:45 | 2016-08-08 16:47 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.20972 | 5.0167 | --- | --- | --- | S/d taken by Chuzachen for emergency purpose. |  | 100
64 | ER2L63 | Rangit-Rammam | 27.15 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
65 | ER2L64 | Rangit-Rabangla(up to LILO) | 1 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
66 | ER2L65 | Rabangla - Melli(up to LILO) | 36 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
67 | ER2L66 | Binaguri-Bongaigaon-I | 217.275 |  | --- | 2016-08-02 13:55 | 2016-08-02 13:55 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | A/R succesfully operated from both end. R/I at Binaguri end: RN fault,FL-216km, F/C-2.031KA. BNGG end: RN fault, FL-19.89km, F/C-7.3KA during rain/lightning. |  | 100
[5 empty] | Insulator decapping | 2016-08-02 13:56 | 2016-08-02 21:20 | --- | --- | 0.30833 | 0:00 | 0 | 0 | 0 | 0.30833 | 7.4 | 0 | 0 | 1 | N | -0.69167 | Tripped from both end. R/I at Binaguri end: YN fault,FL-216km, F/C-2.054KA. BNGG end: YN fault, FL-18.93km, F/C-7.54KA during rain/lightning & de-capping in insulator loc.No-53 (Y-phase) & at loc.No-58 (R-phase).
[5 empty] | --- | 2016-08-02 21:20 | 2016-08-06 15:51 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 1900-01-02 18:31 | 90.5 | --- | --- | --- | Line kept opened as per ERLDC instruction
[5 empty] | --- | 2016-08-11 12:45 | 2016-08-11 21:20 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0.35764 | 8.5833 | 0 | 0 | --- | --- | --- | Durring heavy rain and lightening, line tripped on B-N fault , Relay indiacation FD 204.4 KM, FC 1.59 kA at Binaguri end.
[5 empty] | --- | 2016-08-13 11:20 | 2016-08-13 13:58 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.10972 | 2.6333 | --- | --- | --- | Hand tripped as per ERLDC instruction to control the system voltage.
[5 empty] | --- | 2016-08-26 17:15 | 2016-08-26 19:35 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.097222 | 2.3167 | --- | --- | --- | S/D taken by Bongaigaon to take the line reactor of BNG-NSLG-I in service.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0.66597 | 15.9833 | 1900-01-02 23:29 | 95.4667 | --- | --- | ---
68 | ER2L67 | Binaguri-Bongaigaon-II | 217.275 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
69 | ER2L68 | Farakka-Baharampore - I (LILO portion) | 2.54 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
70 | ER2L69 | Baharampore-Jeerat - I(LILO portion) | 2.634 |  | --- | 2016-08-03 07:19 | 2016-08-03 16:40 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.38958 | 9.35 | --- | --- | --- | Shut down taken for Reactor paralleling work at Jeerhat end, taken by PG, as a part of construction activities. |  | 100
71 | ER2L70 | Baharampore - Bheramara - I(Indian portion) | 71.51 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
72 | ER2L71 | Baharampore - Bheramara - II(Indian Portion) | 71.51 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
73 | ER2T1 | ICT-I,DGP | 315 | ER-II | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
74 | ER2T2 | ICT-II,DGP | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
75 | ER2T3 | ICT-I,MTN | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
76 | ER2T4 | ICT-II,MTN | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
77 | ER2T5 | ICT-I,FKK | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
78 | ER2T6 | ICT-III,MLD | 315 |  | --- | 2016-08-26 07:36 | 2016-08-26 11:58 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.18194 | 4.3667 | --- | --- | --- | S/D taken by Malda for Bus Bar commissioning work under construction head. |  | 100
79 | ER2T7 | ICT-V,MLD | 315 |  | --- | 2016-08-18 07:36 | 2016-08-18 17:03 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.39375 | 9.45 | --- | --- | --- | For commissioning of new 220 KV Bus-Bar protection at Malda.
[5 empty] | --- | 2016-08-20 10:45 | 2016-08-20 14:11 | --- | --- | --- | 3:26 | 3.4333 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- | Emergency S/D taken for rectification of hotsopt at Y-Ph Isolator (HV Side) at Malda. |  | 99.54
[5 empty] | --- | TOTAL |  |  |  |  | 3:26 | 3.4333 | 0 | 0 | 0 | 0 | 0.39375 | 9.45 | --- | --- | ---
80 | ER2T8 | ICT-I, NSLG | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
81 | ER2T9 | ICT-II, NSLG | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
82 | ER2T10 | ICT-I, SGM | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
83 | ER2T11 | ICT-II, SGM | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
84 | ER2T12 | ICT-V, SGM | 500 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
85 | ER2T13 | ICT-V RANGPO | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
86 | ER2T14 | ICT-IV RANGPO | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
87 | ER2T15 | ICT-III RANGPO | 315 |  | --- | 2016-08-12 11:55 | 2016-08-12 12:16 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.014583 | 0.33333 | --- | --- | --- | S/D taken in order to comply with punch points for rectification of minimum clearance of Firefighting system pipeline from the tertiary conductor of the same ICT. |  | 100
[5 empty] | --- | 2016-08-26 09:59 | 2016-08-26 17:54 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.32986 | 7.9 | --- | --- | --- | S/D taken by Rangpo to attend clearance problem in the Fire Fighting System of ICT under construction head.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.34444 | 8.25 | --- | --- | ---
88 | ER2T16 | ICT-II RANGPO | 315 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
89 | ER2T17 | ICT-I RANGPO | 315 |  | --- | 2016-08-10 16:07 | 2016-08-10 16:53 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.031944 | 0.76667 | --- | --- | --- | S/D taken by Rangpo for modification for 4-clamp assembly as per modified design under construction activity work at Rangpo end. |  | 100
90 | ER2T18 | ICT-I,SLG | 160 |  | --- | 2016-08-13 06:50 | 2016-08-13 16:54 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.41944 | 10.0667 | --- | --- | --- | S/D taken by Siliguri for modification in bay under GIS work under construction activities. |  | 100
91 | ER2T19 | ICT-II,SLG | 160 |  | --- | 2016-08-18 07:06 | 2016-08-18 18:45 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.48542 | 11.65 | --- | --- | --- | Modification of Bay under GIS Work. |  | 100
92 | ER2T20 | ICT-I,BRP | 160 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
93 | ER2T21 | ICT-II,BRP | 160 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
94 | ER2T22 | ICT-II, Malda | 160 |  | --- | 2016-08-24 10:28 | 2016-08-24 12:58 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.10417 | 2.4833 | --- | --- | --- | S/D taken for Bus Bar Protection commissioning work under construction head. |  | 100
95 | ER2T23 | ICT-I, Malda | 160 |  | --- | 2016-08-24 07:14 | 2016-08-24 10:16 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.12639 | 3.0167 | --- | --- | --- | S/D taken for Bus Bar Protection commissioning work. |  | 100
96 | ER2T24 | ICT-IV, MLD | 50 |  | --- | 2016-08-19 07:34 | 2016-08-19 12:08 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.19028 | 4.5667 | --- | --- | --- | For commissioning of new 220 KV Bus-Bar protection at Malda. |  | 100
[5 empty] | --- | 2016-08-02 08:49 | 2016-08-02 15:56 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.29653 | 7.1167 | --- | --- | --- | S/D taken for proposed up-gradation of transformation capacity at Malda from existing 50 MVA to up-coming 160 MVA measurement & protection checking work at Malda end.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.48681 | 11.6833 | --- | --- | ---
97 | ER2T25 | ICT-I, RANGPO | 100 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
98 | ER2T26 | ICT-II, RANGPO | 100 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
99 | ER2T27 | ICT-III, RANGPO | 100 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
100 | ER2T28 | ICT-I, GTK | 50 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
101 | ER2T29 | ICT-II,GTK | 50 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
102 | ER2L1 | 125 3ph B/R- II NSLG | 125 | ER-II | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
103 | ER2L2 | 125 3ph B/R- I NSLG | 125 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
104 | ER2L3 | 80 BONGG-III L/R at Binaguri | 80 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
105 | ER2L4 | 80 BONGG-IV L/R at Binaguri | 80 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
106 | ER2L5 | 50 Gaya-I L/R at Maithon | 50 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
107 | ER2L6 | 50 Gaya-II L/R at Maithon | 50 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
108 | ER2L7 | 80 MVAR B/R at Berhampore | 80 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
109 | ER2L8 | 80 MVAR B/R -I at Rangpo | 80 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
110 | ER2L9 | 80 MVAR B/R -II at Rangpo | 80 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
111 | ER2L10 | 50 1ph B/R-I ,DGP | 50 |  | --- | 2016-08-18 19:20 | 2016-08-18 21:16 | --- | --- | --- | 0:00 | 0 | 0.080556 | 1.9333 | 0 | 0 | 0 | 0 | --- | --- | --- |  |  | 100
[5 empty] | --- | 2016-08-20 10:07 | 2016-08-29 16:10 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 06:03 | 222.0333 | --- | --- | ---
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0.080556 | 1.9333 | 0 | 0 | 1900-01-08 06:03 | 222.0333 | --- | --- | ---
112 | ER2L11 | 50 3ph B/R ,MTN | 50 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
113 | ER2L12 | 50 1ph B/R ,JRT | 50 |  | --- | 2016-08-01 | 2016-08-26 21:20 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 1900-01-24 21:20 | 21.3333 | --- | --- | --- | S/D taken by PG for dismantling of equipment erection & testing, Gantry erection, stringing work for reactor paralleling work under construction head ERSS-XII |  | 100
114 | ER2L13 | 2x50MVAR 1ph B/R ,JRT | 100 |  | --- | 2016-08-26 21:35 | 2016-08-27 06:07 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 0.35556 | 8.5333 | --- | --- | --- | 1st time charged 2x50 MVAR B/R successfully and thereafter taken out of service, as per given code by ERLDC, for system constraint. |  | 100
[5 empty] | --- | 2016-08-27 18:21 | 2016-09-01 | --- | --- | --- | 0:00 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 05:39 | 101.65 | --- | --- | --- | H/T as per ERLDC instruction for voltage regulation.
[5 empty] | --- | TOTAL |  |  |  |  | 0:00 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 14:11 | 110.1833 | --- | --- | ---
115 | ER2L14 | 31.5MVAR B/R-I at New Melli | 31.5 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
116 | ER2L15 | 31.5MVAR B/R-II at New Melli | 31.5 |  | --- |  |  | --- | --- | --- |  | 0 |  | 0 |  | 0 |  | 0 | --- | --- | --- |  |  | 100
Note on C6: Author: made LILO on 20.01.10 & DOCO wef 01.02.10 Made further LILO at Andal on 22.01.11 & LILO on 01.02.11 LILO at Andal Removed in April'13
Note on C7: Author: made LILO on 20.01.10 & DOCO wef 01.02.10
Note on C12: Author: Made LILO w.e.f 01.09.13
Note on C13: Author: Made LILO w.e.f 01.09.13
Note on C19: Author: made LILO on 07.07.08
Note on C23: Author: made LILO on 07.07.08
Note on C48: 50084: doco 1.2.08
Note on C50: 50084 doco 1.6.08 LILO on 29.11.14
Note on C51: 50084 doco 1.6.08 LILO 29.11.14
Note on C52: 50084 Charged Ckt-I on 03.12.11 DOCO on 01.12.2011
Note on C53: 50084 Charged Ckt-II on 30.11.11 DOCO on 01.12.2011
Note on C54: 50084 Charged Ckt-I on 22.02.12 DOCO on 01.03.2012
Note on C55: 50084 Charged Ckt-I on 22.02.12 DOCO on 01.03.2012
Note on C61: 50084 Charged Ckt-I on 30.04.12 DOCO on 01.05.2012
Note on C62: 50084 Charged Ckt-I on 30.04.12 DOCO on 01.05.2012
Note on C67: 50084 doco 01.10.2010
Note on C75: Author: DOCO : 01.12.1986
Note on C76: Author: DOCO : 01.12.1986
Note on C109: Author: LILO on 29.11.14
Note on C110: Author: LILO on 29.11.14
Note on C118: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C119: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C128: Author: Made LILO w.e.f 01.09.13
Note on C129: Author: Made LILO w.e.f 01.09.13
Note on C130: D.O.C.O - w.e.f 01.09.13
Note on C146: Author: DOCO 24.04.14 3 X 105 MVA
Note on C147: Author: DOCO 22.05.14 3 X 105 MVA
Note on C148: Author: DOCO 09.06.2014 3 X 105 MVA
Note on C151: Author: DOCO 30.06.2014 3 X 105 MVA
Note on C152: Author: DOCO 03.07.2014 3 X 105 MVA
Note on C154: Author: DOCO 01.01.2013, ERSS-IV
Note on C156: Author: DOCO wef - 01.02.2013 under ERSS-IV
Note on C157: Author: DOCO wef - 01.02.2013 under ERSS-IV
Note on C158: Author: DOCO wef - 01.03.2013 under ERSS-IV
Note on C162: Author: DOCO 24.04.14
Note on C163: Author: DOCO 24.04.14
Note on C164: Author: DOCO 30.06.2014
Note on C167: Author: DOCO w.e.f 01.11.2011
Note on C168: Author: DOCO w.e.f 01.04.2012
Note on C169: Author: DOCO wef 01.05.2013
Note on C173: Author: DOCO : w.e.f - 01.09.2013
Note on C174: Author: DOCO : w.e.f - 22.05.14
Note on C175: Author: DOCO : w.e.f - 09.06.2014