## Odisha SOP
Standard of Performance data for the month of MAY- 2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD.,ODISHA
ANNEXURE-A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | No. of towers damaged | no. of insulator failed | Total outage in days (1) | Outage Attributable to |  |  |  | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date Time | Date Time |  |  |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | ODL1 | ROURKELA-TALCHER I | 171 | Odisha |  | 2019-05-31 17:43 | 2019-05-31 18:27 | ----- | ----- | ----- | 0:44 | 0:00 | 0:00 | 0:00 | Tripped due to D/T received from Talcher/NTPC at Rourkela end. | --- | --- | --- | ERPC | 99.9
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:44 | 0:00 | 0:00 | 0:00
2 | ODL2 | ROURKELA-TALCHER II | 171 | Odisha |  |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
3 | ODL3 | RENGALI-TALCHER-I | 24 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
4 | ODL4 | RENGALI-TALCHER-II | 24 | Odisha |  |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
5 | ODL5 | RENGALI-INDRAVATI I | 356 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
6 | ODL6 | INDRAVATI-JEYPORE | 71 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
7 | ODL7 | TAL-MEERAMUNDALI | 51 | Odisha |  |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
8 | ODL8 | TALCHER-ANGUL | 68.35 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
9 | ODL9 | ANGUL-Meramundali # II | 18.61 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
10 | ODL10 | JEYPORE-BOLANGIR# I | 287 | Odisha | ----- | 2019-05-28 21:33 | 2019-05-28 21:33 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | A/R Successful at both end.R/I at Bolangir: Y-N fault,FD: 279KM,FC: 1.368KA .R/I at Jeypore: Y-N,FD: 1.21KM,FC: 5.7KA. | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00
11 | ODL11 | BOLANGIR-ANGUL | 196.12 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
12 | ODL12 | ANGUL-MERAMUNDALI # I | 25.34 | Odisha |  | 2019-05-19 19:23 | 2019-05-19 19:58 | ----- | ----- | ----- | 0:00 | 0:35 | 0:00 | 0:00 | Tripped on DT received from Meramundali end. |  |  |  | ERPC | 100
[5 empty] | ----- | 2019-05-22 09:30 | 2019-05-22 13:30 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 4:00 | S/D taken by GRIDCO for relay testing work at MERAMUNDALIl end. | --- | --- | ---
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:35 | 0:00 | 4:00
13 | ODL13 | RNG-Keonjhar ( LILO Portion) | 9.38 | Odisha | --- | 2019-05-06 11:30 | 2019-05-06 11:30 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end.R/I at Keonjhar: B-N Fault, F/C-1.848 KA,F/D-92.87 KM, R/I at Rengali end : B-N Fault,F/C-1.716 KA,F/D-36.86 KM, Z1. | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00
14 | ODL14 | Keonjhar-BPD (both LILO Portion) | 28.12 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
15 | ODL15 | BARIPADA-KHARAGPUR(LILO) | 18.74 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
16 | ODL17 | BARIPADA-DUBURI | 190.247 | Odisha | ----- | 2019-05-15 17:45 | 2019-05-15 17:45 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end. R/I at Baripada end: R-N fault, F/D: 135.523KM, F/C: 2.739KA | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-31 19:44 | 2019-05-31 19:44 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both ends. R/I at Baripada end:-Z1, B-N fault, F/D:-60.9KM, F/C:-4.10KA
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00
17 | ODL18A | DUBURI-PANDIABALLI | 143.3 | Odisha | ----- | 2019-05-03 10:52 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 685:08 | 0:00 | Line tripped during heavy cyclonic(FANI) weather.R/I at Pandiabily : B-N,FD-9.8 km,FC-2.3 kA. | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 685:08 | 0:00 |  |  |  |  | ERPC
18 | ODL18B | PANDIABALLI-MENDHASAL-I | 28 | Odisha | --- | 2019-05-03 10:01 | 07/05/19 22:40 | ----- | ----- | ----- | 0:00 | 0:00 | 108:39 | 0:00 | Line tripped during heavy cyclonic(FANI) weather.R/I at Pandiabily : B-N,FD-2.7 km,FC-7.77 kA. |  |  |  | ERPC | 100
[6 empty] | 08/05/19 13:05 | 08/05/19 13:54 | ----- | ----- | ----- | 0:00 | 0:49 | 0:00 | 0:00 | Due to 315 MVA ICT-2 HV side B-ph LA blast at Mendhasal(OPTCL) end, 400 KV Pandiabily Sub Station becomes no voltage(Both 400 KV & 220 KV) condition.
[6 empty] | 2019-05-09 07:48 | 2019-05-09 07:53 | ----- | ----- | ----- | 0:00 | 0:00 | 0:05 | 0:00 | Tripped on operation of Over Voltage Protection.
[6 empty] | 2019-05-09 07:53 | 2019-05-09 22:24 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 14:31 | Kept open for Voltage regulation as per ERLDC instruction.
[6 empty] | 2019-05-09 23:02 | 2019-05-10 22:25 | ----- | ----- | ----- | 0:00 | 23:23 | 0:00 | 0:00 | Tripped on DT received(at Pandiabilli), as over voltage protection operated at Mendhasal end and 400KV Bus-I got dead at Mendhasal.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 24:12 | 108:44 | 14:31 |  |  |  |  | ERPC
19 | ODL24 | Angul-Sundargarh-II | 274.92 | Odisha | ----- | 2019-05-16 19:06 | 2019-05-16 19:13 | ----- | ----- | ----- | 0:07 | 0:00 | 0:00 | 0:00 | Line tripped from Angul end only on DT received from Jharsuguda end. |  | --- | --- | ERPC | 100
[6 empty] | 2019-05-19 19:38 | 2019-05-19 19:38 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end. R/I at Angul: Y-N fault,FD: 36.567KM,FC: 9.508KA. R/I at Jharsuguda: Y-N,FD: 238.725KM, FC: 3.98KA.
[6 empty] | 2019-05-28 15:03 | 2019-05-28 15:34 | ----- | ----- | ----- | 0:31 | 0:00 | 0:00 | 0:00 | Tripped at Angul end only due to D/T received from remote end.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:38 | 0:00 | 0:00 | 0:00 |  |  |  |  | ERPC
20 | ODL25 | Angul-Sundargarh-I | 272 | Odisha |  |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
21 | ODL26 | Angul-Sundargarh-III | 295.06 | Odisha |  | 2019-05-02 01:08 | 2019-05-11 22:35 | ----- | ----- | ----- | 237:27 | 0:00 | 0:00 | 0:00 | Tripped due to R Phase Oil CT of Tie bay(722) Blast at Angul end. DT received at Jharsugura end.One specific lot of ARTECHE make CTs failed consecutively at Angul s/s. Also the CTs were under warranty period at the time of failure.The case of failure has been referred to the manufacturer who are also investgating the case. If the ckt would have been charged with the other already installed ARTECHE CTs, it would have a threat to personnel working in the field as well as to other adjacent equipments .Hence to avoid further damage to system i.e to minimizing down time of the power system,ckt was not charged immediately.As failure of specific CTs are totally out of control of Powergrid,it may not be attributed to Powergrid | --- | --- | --- | ERPC | 68.08
[6 empty] | 2019-05-11 22:35 | 2019-05-13 07:59 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 33:24 | Kept open for Voltage regulation as per ERLDC instruction.(Angul S/s has given readiness to charge the line through main bay vide mail dated May 11, 2019 10:35 PM)
[6 empty] | TOTAL |  | ----- | ----- | ----- | 237:27 | 0:00 | 0:00 | 33:24
22 | ODL27 | Angul-Sundargarh-IV | 295.06 | Odisha |  | 2019-04-30 02:15 | 08/05/19 01:36 | ----- | ----- | ----- | 191:21 | 0:00 | 0:00 | 0:00 | Tripped due to B Phase CT of Tie bay(719) Blast at Angul end. DT received at Jharsugura end.One specific lot of ARTECHE make CTs failed consecutively at Angul s/s. Also the CTs were under warranty period at the time of failure.The case of failure has been referred to the manufacturer who are also investgating the case. If the ckt would have been charged with the other already installed ARTECHE CTs, it would have a threat to personnel working in the field as well as to other adjacent equipments .Hence to avoid further damage to system i.e to minimizing down time of the power system,ckt was not charged immediately.As failure of specific CTs are totally out of control of Powergrid,it may not be attributed to Powergrid | --- | --- | --- | ERPC | 72.67
[6 empty] | 2019-05-28 11:08 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 84:52 | H/T as per ERLDC instruction for Voltage Regulation.
[6 empty] | 2019-05-13 07:11 | 2019-05-23 12:08 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 244:57 | H/T as per ERLDC/NLDC instruction for Voltage Regulation.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 191:21 | 0:00 | 0:00 | 329:49
23 | ODL16A | BARIPADA-PANDIABALLI | 301.5 | Odisha | --- | 2019-05-03 09:31 | 2019-05-03 09:31 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successfully at both end during heavy cyclonic weather.R/I at Bripada : B-N,Z2,FC-1.327 kA,FD-300 km.R/I at Pandiabily : B-N,Z1,FC-8.8 kA,FD-3.2 km. | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-03 09:55 | 2019-05-10 23:27 | ----- | ----- | ----- | 0:00 | 0:00 | 181:32 | 0:00 | Line tripped during heavy cyclonic(FANI) weather.R/I at Pandiabily : R-B-N,FD-3.7 km.R/I at Bripada : R-B-N,Z2,FC-Ir-1.756,Ib-1.825 kA,FD-296.21 km.
[6 empty] | 2019-05-25 06:01 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 161:59 | 0:00 | 0:00 | S/D taken for erection of new tower, stringing of 400 KV Baripada-Pandiabilli & 400 KV New Dubri-Pandiabilli line after damaged done during super cyclone fani.
[6 empty] | 2019-05-15 17:59 | 2019-05-15 17:59 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both end. R/I at Baripada end: B-N fault, F/D: 132KM, F/C: 2.79KA.R/I at Pandiabili end: B-N fault, F/D: 131KM, F/C: 0.8KA
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 161:59 | 181:32 | 0:00 |  |  |  |  | ERPC
24 | ODL16B | 400KV-MENDHASAL-PANDIABILI-2 | 28 | Odisha | ----- | 2019-05-03 10:37 | 07/05/19 23:39 | ----- | ----- | ----- | 0:00 | 0:00 | 109:02 | 0:00 | Line tripped during heavy cyclonic(FANI) weather.R/I at Pandiabily : R-N,FD-8 km,FC-4 kA. | --- | --- | --- | ERPC | 100
[6 empty] | 08/05/19 13:05 | 08/05/19 20:56 | ----- | ----- | ----- | 0:00 | 7:51 | 0:00 | 0:00 | Due to 315 MVA ICT-2 HV side B-ph LA blast at Mendhasal(OPTCL) end, 400 KV Pandiabily Sub Station becomes no voltage(Both 400 KV & 220 KV) condition.
[6 empty] | 2019-05-09 07:48 | 2019-05-09 07:53 | ----- | ----- | ----- | 0:00 | 0:00 | 0:05 | 0:00 | Tripped on operation of Over Voltage Protection.
[6 empty] | 2019-05-09 07:53 | 2019-05-10 23:05 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 39:12 | Kept open for Voltage regulation as per ERLDC instruction.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 7:51 | 109:07 | 39:12 |  |  |  |  | ERPC
25 | ODL28 | DARLIPALLI-JHARSUGURA-1 | 20.54 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
26 | ODL29 | DARLIPALLI-JHARSUGURA-2 | 20.54 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
26 | ODT1 | ICT-II Sundergarh | 1500 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
27 | ODT2 | ICT-I Sundergarh | 1500 | Odisha | ----- | 2019-05-22 17:10 | 2019-05-22 19:09 | ----- | ----- | ----- | 1:59 | 0:00 | 0:00 | 0:00 | Tripped due to earth fault occured in control cable. | --- | --- | --- | ERPC | 99.73
[6 empty] | TOTAL |  | ----- | ----- | ----- | 1:59 | 0:00 | 0:00 | 0:00
28 | ODT3 | ICT-I,RKL | 315 | Odisha | --- | 2019-05-28 15:29 | 2019-05-28 16:19 | ----- | ----- | ----- | 0:00 | 0:50 | 0:00 | 0:00 | Tripped on directional earth fault due to problem in down stream system. | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:50 | 0:00 | 0:00 |  |  |  |  | ERPC
29 | ODT4 | ICT-II,RKL | 315 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
30 | ODT5 | ICT-I, RNG | 315 | Odisha | ----- | 2019-05-21 08:19 | 2019-05-21 18:32 | ----- | ----- | ----- | 0:00 | 10:13 | 0:00 | 0:00 | Shutdown for backup impedence relay retrofitting work. | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 10:13 | 0:00 | 0:00 |  |  |  |  | ERPC
31 | ODT6 | ICT-II, RNG | 315 | Odisha | --- | 2019-05-16 10:37 | 2019-05-17 01:27 | ----- | ----- | ----- | 0:00 | 14:50 | 0:00 | 0:00 | S/d taken for Retrofitting of Backup impedance relay | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 14:50 | 0:00 | 0:00 |  |  |  |  | ERPC
32 | ODT8 | ICT-II, JEYPORE | 315 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
33 | ODT7 | ICT-I, JEYPORE | 315 | Odisha | ----- | 2019-05-27 11:24 | 2019-05-28 02:09 | ----- | ----- | ----- | 0:00 | 14:45 | 0:00 | 0:00 | S/D taken for retrofitting work of 30 years old 220KV ICT-I TBC Isolator & Line Isolator of 315MVA ICT-I bay | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-29 08:18 | 2019-05-29 14:25 | ----- | ----- | ----- | 0:00 | 6:07 | 0:00 | 0:00 | S/D taken for change over of ICT-I, from TBC CB to ICT-I Bay(201 CB) after isolator retrofitting works of 30 years old 201 89C (ICT-I Isolator).
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 20:52 | 0:00 | 0:00 |  |  |  |  | ERPC
34 | ODT9 | ICT-I BRPD | 315 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
35 | ODT10 | ICT- II, IVT | 315 | Odisha |  |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
36 | ODT11 | ICT-II, BOLANGIR | 315 | Odisha | --- | 2019-05-26 07:46 | 2019-05-26 13:12 | ----- | ----- | ----- | 0:00 | 5:26 | 0:00 | 0:00 | S/D taken for Back up Impedance Relay retrofitting work | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 5:26 | 0:00 | 0:00 |  |  |  |  | ERPC
37 | ODT12 | ICT-I, BOLANGIR | 315 | Odisha | --- | 2019-05-21 07:40 | 2019-05-21 22:37 | ----- | ----- | ----- | 0:00 | 14:57 | 0:00 | 0:00 | Shutdown for backup impedence relay retrofitting work. | --- | --- | --- | ERPC | 99.91
[6 empty] | 2019-05-26 12:42 | 2019-05-26 13:21 | ----- | ----- | ----- | 0:39 | 0:00 | 0:00 | 0:00 | Tripped due to DC Earth Fault.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:39 | 14:57 | 0:00 | 0:00
38 | ODT13 | ICT-I at Angul | 1500 | Odisha | --- | 2019-05-17 14:00 | 2019-05-17 20:05 | ----- | ----- | ----- | 0:00 | 6:05 | 0:00 | 0:00 | S/D taken for change over of Spare Transformer from ICT-I to ICT-3. | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-31 19:47 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 4:13 | 0:00 | ICT tripped during heavy cyclonic storm & rain due to IPS separated from Y -Ph of 401 89 TA isolator of ICT
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 6:05 | 4:13 | 0:00
39 | ODT14 | ICT-2 at Angul | 1500 | Odisha |  | 2019-05-28 10:11 | 2019-05-28 11:47 | ----- | ----- | ----- | 1:36 | 0:00 | 0:00 | 0:00 | Tripped due to maloperation of B-Ph Buchholz relay. Already planned for replacement of the same. | --- | --- | --- | ERPC | 99.78
[6 empty] | TOTAL |  | ----- | ----- | ----- | 1:36 | 0:00 | 0:00 | 0:00
40 | ODT15 | ICT-3 at Angul | 1500 | Odisha | --- | 2019-05-18 11:27 | 2019-05-18 15:16 | ----- | ----- | ----- | 0:00 | 3:49 | 0:00 | 0:00 | S/D taken for change over of Spare Transformer(B-Phase) from ICT-I to ICT-3. | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-31 22:44 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 1:16 | 0:00 | 0:00 | S/D taken to faciliate normalization of 765/400Kv ICT-I
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 5:05 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
41 | ODT16 | ICT-IV at Angul | 1500 | Odisha | --- | 2019-05-03 00:52 | 2019-05-03 02:34 | ----- | ----- | ----- | 0:00 | 0:00 | 1:42 | 0:00 | Tripped due to mal-operation of buchholz relayl. | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 1:42 | 0:00 |  |  |  |  | ERPC
42 | ODT17 | ICT-I, KEONJHAR | 315 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
43 | ODT18 | ICT-II, KEONJHAR | 315 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
44 | ODT19 | ICT-II BRPD | 315 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
45 | ODT20 | ICT- II, BRPD | 160 | Odisha | --- | 2019-05-22 11:46 | 2019-05-22 13:54 | ----- | ----- | ----- | 2:08 | 0:00 | 0:00 | 0:00 | S/D taken to attend stuck 20489C isolator. | --- | --- | --- | ERPC | 99.71
[6 empty] | TOTAL |  | ----- | ----- | ----- | 2:08 | 0:00 | 0:00 | 0:00
46 | ODT21 | ICT-I, BRPD | 160 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
47 | ODT22 | ICT-I,PANDIABALLI | 500 | Odisha | ----- | 08/05/19 13:05 | 2019-05-08 14:50 | ----- | ----- | ----- | 0:00 | 1:45 | 0:00 | 0:00 | Due to 315 MVA ICT-2 HV side B-ph LA blast at Mendhasal(OPTCL) end, 400 KV Pandiabily Sub Station becomes no voltage(Both 400 KV & 220 KV) condition. | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-09 07:48 | 2019-05-10 10:51 | ----- | ----- | ----- | 0:00 | 0:00 | 27:03 | 0:00 | Tripped on Over Flux.
[6 empty] | TOTAL |  | ----- | ----- | ----- | [8 empty] | ERPC
48 | ODT23 | ICT-II,PANDIABALLI | 500 | Odisha | ----- | 08/05/19 13:05 | 08/05/19 14:28 | ----- | ----- | ----- | 0:00 | 1:23 | 0:00 | 0:00 | Due to 315 MVA ICT-2 HV side B-ph LA blast at Mendhasal(OPTCL) end, 400 KV Pandiabily Sub Station becomes no voltage(Both 400 KV & 220 KV) condition. | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-09 07:48 | 2019-05-09 08:51 | ----- | ----- | ----- | 0:00 | 0:00 | 1:03 | 0:00 | Tripped on Over Flux.
[6 empty] | 2019-05-09 23:02 | 2019-05-10 01:24 | ----- | ----- | ----- | 0:00 | 2:22 | 0:00 | 0:00 | Due to over voltage protection operated at Medhasal, 400 KV Mendhasal-Pandiabilli-I tripped on DT received at Pandiabilli and also Atri(OPTCL) S/stn got dead. As a result 220 KV Pandiabilli-Atri D/C lines tripped from Atri end only. Hence, both 400KV & 220KV buses at Pandiabilli got dead. Now, to nullify the voltage injection risk in a GIS bus [i.e. Pandiabilli] from far end & considering the safety of the element, ICT-II at Pandiabilli hand tripped locally.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 3:45 | 1:03 | 0:00 |  |  |  |  | ERPC
49 | ODT24 | ICT-III BARIPADA | 500 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
50 | ODR1 | 240, 1 ph BR-II at Sundergarh | 240 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
51 | ODR2 | 125 3ph B/R- III Angul | 125 | Odisha | --- | 2019-05-31 19:47 | 2019-05-31 21:09 | ----- | ----- | ----- | 0:00 | 0:00 | 1:22 | 0:00 | Tripping due to WTI opertate during heavy storm & Cyclonic weather | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 1:22 | 0:00 |  |  |  |  | ERPC
52 | ODR3 | 125 3ph B/R- II Angul | 125 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
53 | ODR4 | 125 3ph B/R- I Angul | 125 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
54 | ODR5 | 330 MVAR BR-I at Angul | 330 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
55 | ODR6 | 330 MVAR BR-II at Angul | 330 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
56 | ODR7 | 240 MVAR SLR-1 at Angul | 240 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
57 | ODR8 | 240 MVAR SLR-2 at Angul | 240 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
58 | ODR9 | 125 3ph B/R- I Sundergarh | 125 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
59 | ODR10 | 125 3ph B/R- II Sundergarh | 125 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
60 | ODR11 | 240 3ph B/R- I Sundergarh | 240 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
61 | ODR12 | 63 Duburi L/R at Baripada | 63 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
62 | ODR13 | 50 MRL L/R at Bolangir | 50 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
63 | ODR14 | 50 JPR L/R at Bolangir | 50 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
64 | ODR15 | 80 MVAR B/R at Bolangir | 80 | Odisha | --- | 2019-05-31 18:15 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 5:45 | H/T as per ERLDC instruction for Voltage Regulation. | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 5:45 |  |  |  |  | ERPC
65 | ODR16 | 80 MVAR B/R at Keonjhar | 80 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
66 | ODR17 | 63 3ph B/R ,JEYPORE | 63 | Odisha | --- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
67 | ODR20 | 50 CHAIBASA -I L/R at RKL | 50 | Odisha |  |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
68 | ODR21 | 125MVAR BR-I at RKL | 125 | Odisha | ---- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
69 | ODR23 | 80 JPR L/R at Meramundli | 80 | Odisha | ---- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
70 | ODR24 | 80 MVAR B/R at DUBRI | 80 | Odisha | ---- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
71 | ODR25 | 125 MVAR B/R at IVT | 125 | Odisha |  |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
72 | ODR26 | 125 MVAR B/R at JPR | 125 | Odisha | ---- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
73 | ODR27 | 50MVAR Keonjhar LR at Baripada | 50 | Odisha | ---- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
74 | ODR28 | 63MVAR BARIPADA L/R AT PANDIABALLI | 63 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
75 | ODR29 | 80MVAR B/R AT PANDIABALLI | 80 | Odisha | ----- | 08/05/19 13:05 | 2019-05-08 14:48 | ----- | ----- | ----- | 0:00 | 1:43 | 0:00 | 0:00 | Due to 315 MVA ICT-2 HV side B-ph LA blast at Mendhasal(OPTCL) end, 400 KV Pandiabily Sub Station becomes no voltage(Both 400 KV & 220 KV) condition. | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-09 07:48 | 2019-05-15 19:01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 155:13 | H/T as per ERLDC instruction for Voltage Regulation.
[6 empty] | 2019-05-21 14:28 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 249:32 | H/T as per ERLDC instruction for Voltage Regulation.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 1:43 | 0:00 | 404:45 |  |  |  |  | ERPC
76 | ODR30 | 125MVAR B/R AT BARIPADA | 125 | Odisha | ---- | 2019-05-22 15:42 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 224:18 | H/T as per ERLDC instruction for Voltage Regulation | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 224:18 |  |  |  |  | ERPC
77 | ODR31 | 63 MVAR NEW DUBURI L/R AT PANDIABILI END | 63 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
78 | ODR32 | RENGALI-BUS REACTOR-1_125MVAR | 125 | Odisha | ---- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
79 | ODR33 | RENGALI-BUS REACTOR-2_125MVAR | 126 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
80 | ODR34 | ROURKELA BUS REACTOR-2_125 MVAR | 125 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
81 | ODR35 | STATCOM AT ROURKELA | 850 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
82 | ODR36 | BOLANGIR-BUS REACTOR-2_125MVAR | 125 | Odisha | ----- | 2019-05-01 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 744:00 | H/T as per ERLDC instruction for Voltage Regulation | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 744:00 |  | --- | --- | --- | ERPC
83 | ODR37 | BARIPADA BUS REACTOR-2_125 MVAR | 125 | Odisha | ----- | 2019-05-22 15:22 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 224:38 | H/T as per ERLDC instruction for Voltage Regulation | --- | --- | --- | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 224:38 |  |  |  |  | ERPC
84 | ODR38 | STATCOM AT JEYPORE | 900 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
85 | ODR39 | 125MVAR B/R-II AT KEONJHAR | 125 | Odisha | ----- | 2019-05-14 11:38 | 2019-05-14 18:02 | ----- | ----- | ----- | 0:00 | 6:24 | 0:00 | 0:00 | For completion of balance pending radiator replacement works. | --- | --- | --- | ERPC | 100
[6 empty] | 2019-05-30 10:20 | 2019-05-30 18:37 | ----- | ----- | ----- | 0:00 | 8:17 | 0:00 | 0:00 | S/D taken for NTAMC remote configuration and Signal Validation purpose (DPC Signal,Command checking).
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 14:41 | 0:00 | 0:00 |  |  |  |  | ERPC
86 | ODR40 | L/R OF 765 KV ANGUL-JHARSUGURA-3 at ANGUL | 240 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
87 | ODR41 | L/R OF 765 KV ANGUL-JHARSUGURA-4 at ANGUL | 240 | Odisha | ----- |  |  | ----- | ----- | ----- | [5 empty] | --- | --- | --- | ERPC | 100
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ----- | ----- | ----- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | ----- | ----- | -----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
[6 empty] | ---- | ---- |  |  |  | ---- | ---- | ---- | ----
Note on C95: Author: Charged on 22.03.11 at 15:00hrs and loaded on 23.03.11 at 16:10 hrs DOCO - 01.04.2011
Note on L144: Saswati Sarkar(Kundu) {सास्‍वती कुंडू}:
Note on L145: Saswati Sarkar(Kundu) {सास्‍वती कुंडू}:

## ER-II SOP
Standard of Performance data for the month of MAY- 2019 | [20 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., EASTERN REGION -II | [20 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
ANNEXURE-A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | No. of towers damaged | no. of insulator failed | Total outage in days (1) | Outage Attributable to |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | Date Time | Date Time |  |  |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | [6 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
1 | ER2L1 | Maithon -MEJIA - III | 83.74 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
2 | ER2L2 | MEJIA - Jamshedpur | 167.74 | ER-II | ----- | 2019-05-09 12:27 | 2019-05-09 13:00 | ----- | ----- | ----- | 0:00 | 0:33 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped on R-N fault. R/I at Jamshedpur end: R-N,FD: 98.9KM,FC: 4.15KA. R/I at Mejia end: R-N,FD: 82.4KM,FC: 3.29KA.Local villagers are making pandel for campaigning of upcoming election and during local wind flow Pandel material (clothes, bamboo etc) comes nearer to bottom conductor causing fault. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-10 11:03 | 2019-05-10 19:12 | ----- | ----- | ----- | 0:00 | 8:09 | 0:00 | 0:00 |  |  |  | S/D taken for testing & Commissioning of New A/R relay at Jamshedpur end(ER-I) for system improvement.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 8:42 | 0:00 | 0:00 |  |  |  |  | ERPC
3 | ER2L3 | Maithon-Jamshedpur | 153 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
4 | ER2L7 | Farakka-Sagardighi-I | 55.38 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
5 | ER2L8 | Sagardighi- Subhasgram | 245.64 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
6 | ER2L9 | Farakka-Durgapur-I | 150 | ER-II | ----- | 2019-05-15 21:12 | 2019-05-15 21:12 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | A/R operated successfully both end. R/I at Durgapur end: R-N fault, F/C:12.164KA, F/D: 15.968KM; | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  |  | ERPC
7 | ER2L10 | Farakka-Durgapur-II | 146 | ER-II | --- | 07/05/19 11:50 | 2019-05-07 18:35 | ----- | ----- | ----- | 0:00 | 6:45 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for upgradation of new numerical Auto reclose relay in place of old static type A/R relay for system improvement. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-24 21:06 | 2019-05-24 21:18 | ----- | ----- | ----- | 0:00 | 0:00 | 0:12 | 0:00 |  |  |  | Tripped on B-N fault only from Jamshedpur end. R/I at Jamshedpur end: Z-2, F/D:159.09kms, F/C: 2.586KA. A/R successful at Durgapur end. R/I at Durgapur: F/D: 22.1kms, F/C: 9.83KA. Line synchronised from Jamshedpur end. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 6:45 | 0:12 | 0:00 |  |  |  |  | ERPC | 100
8 | ER2L11 | Malda-Farakka-I | 40 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
9 | ER2L12 | Malda-Farakka-II | 40 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
10 | ER2L13 | Durgapur-Jamshedpur | 177 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
11 | ER2L14 | Binaguri-New Purnea-I | 168 | ER-II |  |  |  | ----- | ----- | ----- | [8 empty] | ERPC | 100
12 | ER2L15 | Binaguri-New Purnea-II | 168 | ER-II |  | 2019-05-22 23:14 | 2019-05-22 23:14 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  | A/R Successful at both end at 23:14 hrs on 22.05.19. R/I at Purnia end:- M-II,Z1,B-N fault,F/D-6.5 KM,F/C-12.47 KA, R/I at Binaguri end:- M-II-F/D-100% only. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
13 | ER2L16 | Malda-New Purnea-I | 167 | ER-II | ---- | 2019-05-16 07:50 | 2019-05-16 08:08 | ----- | ----- | ----- | 0:00 | 0:00 | 0:18 | 0:00 | ----- | ----- | ----- | Tripped at Malda end and A/R successful at New Purnea end.Relay indication at Malda end: Y-N,135.6KM,2.3KA;Purnea end: Y-N,19.5KM,8.218KA;Heavy rain with lightning/thunderstorm observed during tripping near the affected area. | ERPC | 99.16 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-17 14:34 | 2019-05-17 14:49 | ----- | ----- | ----- | 0:00 | 0:00 | 0:15 | 0:00 |  |  |  | Tripped only from Malda end.AR successfully operated at Purnea end.R/I at Malda : Z1,R-N,FC-13.03 kA,FD-3.9 km.The weather condition during fault was heavy lightning with thunderstorm.
[6 empty] | 2019-05-27 12:50 | 2019-05-27 19:04 | ----- | ----- | ----- | 6:14 | 0:00 | 0:00 | 0:00 |  |  |  | S/D taken to attend Hotspot in Y-Ph Line Isolator at New Purnea end
[6 empty] | TOTAL |  | ----- | ----- | ----- | 6:14 | 0:00 | 0:33 | 0:00
14 | ER2L17 | Malda-New Purnea-II | 167 | ER-II | ----- | 2019-05-05 08:54 | 2019-05-05 17:22 | ----- | 1 | 0.35 | 0:00 | 0:00 | 8:28 | 0:00 | ----- | ----- | ----- | Tripped during heavy rain and thunder storm. R/I at Malda: R-N fault,Zone-1, F/D: 52.24KM, F/C: 5.24KA. R/I at Purnea end: R-N fault, Zone-1, F/D: 76.6KM, F/C: 3.49KA. Insulator decapping at tower loc no 992(Suspension type). | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 8:28 | 0:00 |  |  |  |  | ERPC | 100
15 | ER2L18 | TALA-BINAGURI-I | 98.087 | ER-II | ----- | 2019-05-11 08:57 | 21/05/19 15:41 | ----- | ----- | ----- | 0:00 | 246:44 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped on R-N fault.R/I at Binaguri end:- F/D-146.2 KM(Bhutan Jurisdiction),F/C-3.60 KA,Z2.R/I at Tala end:R-N fault,F/D-8.5 KM,F/C-8.44 KA,Z1. Charging attempt taken from Binaguri end at 09:38 hrs of 11.05.19 but line tripped on SOTF. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-25 14:12 | 2019-05-26 08:08 | ----- | ----- | ----- | 0:00 | 17:56 | 0:00 | 0:00 |  |  |  | Tripped on DT received from Tala(Bhutan end). | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 264:40 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
16 | ER2L19 | TALA-BINAGURI-II | 98.087 | ER-II | --- | 2019-05-11 10:34 | 2019-05-28 18:46 | ----- | ----- | ----- | 0:00 | 416:12 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped on Y-N fault.R/I at Binaguri end ,Y-N Fault,F/D-142.5 KM(Bhutan Jurisdiction), F/C-3.153 KA,Z2. Charging attempt taken from Binaguri end at 16:54hrs on 11.05.19 but tripped immediately on SOTF. R/I at Binaguri: Y-B fault,FD: 137.9KM, FC: Iy=4.063KA,Ib==3.483KA. Fault is under Tala/Bhutan jurisdiction. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 416:12 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
17 | ER2L20 | TALA-BINAGURI-III | 115.553 | ER-II |  | 2019-05-01 12:43 | 2019-05-01 15:28 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 2:45 |  |  |  | S/D taken by Tala/Bhutan for checking of energy meter. | ERPC | 100
[6 empty] | 2019-05-03 10:40 | 2019-05-03 14:50 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 4:10 |  |  |  | S/D taken by Chukha Bhutan for Energy Meter replacement work. | ERPC | 100
[6 empty] | 2019-05-11 10:07 | 2019-05-11 10:24 | ----- | ----- | ----- | 0:00 | 0:17 | 0:00 | 0:00 |  |  |  | A/R sucessfull at Binaguri end 10:07 hrs of 11.05.19,but tripped from Malbase end only. R/I at Binaguri end: R-N Fault,F/D-121.1 KM(Bhutan Jurisdiction),F/C-1.513KA,Z2. R/I at Malbase end:R-N fault,F/D-8.1 KM,F/C-5.377KA. The line syncronised at 10:24 hrs of 11.05.19 at Malbase end | ERPC | 100
[6 empty] | 12/05/2019 16:37 | 12/05/2019 16:59 | ----- | ----- | ----- | 0:00 | 0:22 | 0:00 | 0:00 |  |  |  | Tripped on R-N fault under Bhutan Jurisdiction.R/I at Binaguri end: R-N Fault,F/D-126.20 KM(Bhutan Jurisdiction),F/C-1.947KA | ERPC | 100
[6 empty] | 12/05/2019 17:08 | 12/05/2019 17:37 | ----- | ----- | ----- | 0:00 | 0:29 | 0:00 | 0:00 |  |  |  | A/R sucessfull at Binaguri end but tripped from Malbase end only,R/I at Binaguri end: B-N Fault,F/D-122.52 KM(Bhutan Jurisdiction),F/C-1.863KA. The line syncronised at 17:37 hrs of 12.05.19 at Malbase end | ERPC | 100
[6 empty] | 2019-05-13 10:44 | 2019-05-13 11:07 | ----- | ----- | ----- | 0:00 | 0:23 | 0:00 | 0:00 |  |  |  | Line tripped on R-N fault during heavy thunderstorm and lightning weather condition.R/I at Binaguri: M1: R-N,FC-3.629 kA,FD-108.43 km. M2: R-N,FC-3.587 kA,FD-105.1 km.Fault is under Bhutan jurisdiction. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 1:31 | 0:00 | 6:55 |  |  |  |  | ERPC | 100
18 | ER2L21 | TALA-BINAGURI-IV | 115.553 | ER-II | ----- | 2019-04-13 09:00 | 2019-05-04 16:33 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 511:33 | ----- | ----- | ----- | S/D taken by Tala/Bhutan upto 18:00 hrs of 04.05.19[OCB] for maintenance work at their end. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 08/05/19 08:55 | 08/05/19 15:49 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 6:54 |  |  |  | Shutdown taken by Tala/Bhutan for testing of XLPE cable at their end. | ERPC | 100
[6 empty] | 08/05/19 15:49 | 2019-05-11 11:58 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 68:09 |  |  |  | Kept open for Voltage regulation as per ERLDC instruction. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 586:36 |  |  |  |  | ERPC | 100
19 | ER2L22 | BINAGURI-Rangpo-I | 109.88 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
20 | ER2L23 | Rangpo-TEESTA-I | 11.83 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
21 | ER2L24 | BINAGURI-Rangpo- II | 110.42 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
22 | ER2L25 | Rangpo-Teesta-II | 21.42 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
23 | ER2L26 | MAITHON - MEJIA - I | 59.182 | ER-II | ----- | 2019-05-25 15:28 | 2019-05-25 15:52 | ----- | ----- | ----- | 0:00 | 0:24 | 0:00 | 0:00 | ----- | ----- | ----- | A/R successful at Maithon end ,however line tripped at Mejia end due to some problem at DVC end. R/I at maithon end:R-N fault, FD:13.49KM, FC:9.94 kA. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:24 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
24 | ER2L27 | MAITHON - MEJIA - II | 59.182 | ER-II |  | 2019-05-26 10:25 | 2019-05-26 13:15 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 2:50 |  |  |  | Emergency S/D taken by Mejia/DVC to attend lockout of CB at their end. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 2:50 |  |  |  |  | ERPC | 100
25 | ER2L28 | MAITHON - Durgapur - I | 70.77 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
26 | ER2L29 | MAITHON - Durgapur - II | 70.77 | ER-II | ----- | 2019-05-02 11:21 | 2019-05-02 19:11 | ----- | ----- | ----- | 7:50 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for Flash Jumper Rectification at Loc No: 149 | ERPC | 98.95 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 7:50 | 0:00 | 0:00 | 0:00
27 | ER2L30 | ANDAL - Jamshedpur - I | 156.76 | ER-II |  | 2019-05-30 19:00 | 2019-05-30 19:55 | ----- | ----- | ----- | 0:00 | 0:55 | 0:00 | 0:00 |  |  |  | During rain and thunder storm the line tripped. R/I at Jamshedpur end:RN,FD:155.00 KM,F.C:4.12KA.R/I At Andal end: RN,Z1,FD:3.09 KM,F.C:5.958 KA. Fault is under DVC Jurisdiction.(Total line length 158 KM & 3.6KM under DVC jurisdiction) | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:55 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
28 | ER2L31 | ANDAL - Jamshedpur - II | 156.76 | ER-II | ----- | 2019-05-16 12:55 | 2019-05-16 13:15 | ----- | ----- | ----- | 0:00 | 0:20 | 0:00 | 0:00 | ----- | ----- | ----- | Line tripped due to spurious DT received at Jamshedpur end from DTPS,Andal.DT generated at Andal end due to some problem at their end. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-22 19:14 | 2019-05-22 19:14 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  | A/R successful at both end.R/I at Jamsedpur end: B-N fault,F/C: Ib: 6.6kA, F/D: 32.8KM | ERPC | 100
[6 empty] | 2019-05-22 19:26 | 2019-05-22 20:12 | ----- | ----- | ----- | 0:00 | 0:00 | 0:46 | 0:00 |  |  |  | Tripped on R-B-N fault. R/I at Andal end: F/D: 105.4KM, F/C : Ir: 2.944KA, Ib: 6.078kA, F/D at Jamsedpur end: F/D: 100.7KM, F/C : Ir: 6.2KA, Ib: 3.2kA, | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:20 | 0:46 | 0:00 |  |  |  |  | ERPC | 100
29 | ER2L32 | Maithon - MaithonRB- I | 31.5 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
30 | ER2L33 | Maithon - MaithonRB- II | 31.5 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
31 | ER2L34 | Baharampore-Sagardighi-I | 26.1 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
32 | ER2L35 | Baharampore-Sagardighi-II | 26.1 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
33 | ER2L36 | Chukha-Birpara-II | 36 | ER-II | ----- | 2019-05-02 15:19 | 2019-05-02 18:13 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 2:54 | ----- | ----- | ----- | S/D taken by Chukha Bhutan for Energy Meter replacement work. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-11 17:21 | 2019-05-11 17:49 | ----- | ----- | ----- | 0:00 | 0:28 | 0:00 | 0:00 |  |  |  | Tripped due to fault under Bhutan jurisdiction. R/I at Birpara end : Y-N Fault,F/D- 53.91 KM, F/C-2.05 KA. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:28 | 0:00 | 2:54 |  |  |  |  | ERPC | 100
34 | ER2L37 | Chukha-Birpara-I | 36 | ER-II | --- | 2019-05-02 09:22 | 2019-05-02 15:01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 5:39 | ----- | ----- | ----- | S/D taken by Chukha Bhutan for Energy Meter replacement work. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-11 17:21 | 2019-05-11 17:42 | ----- | ----- | ----- | 0:00 | 0:21 | 0:00 | 0:00 |  |  |  | Tripped due to fault under Bhutan jurisdiction. R/I at Birpara end : Y-N Fault,F/D- 57.59 KM, F/C-1.8 KA. | ERPC | 100
[6 empty] | 2019-05-11 19:18 | 2019-05-11 19:38 | ----- | ----- | ----- | 0:00 | 0:20 | 0:00 | 0:00 |  |  |  | Tripped due to fault under Bhutan jurisdiction. R/I at Birpara end : R-N Fault,F/D- 39.7 KM, F/C-3.039 KA. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:41 | 0:00 | 5:39 |  |  |  |  | ERPC | 100
35 | ER2L39 | MALBASE-Birpara(CHUKHA III) | 38 | ER-II | ----- | 2019-05-04 09:41 | 2019-05-04 13:38 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 3:57 | ----- | ----- | ----- | S/D taken by Chukha Bhutan for Energy Meter checking & testing work. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-13 10:26 | 2019-05-13 10:49 | ----- | ----- | ----- | 0:00 | 0:23 | 0:00 | 0:00 |  |  |  | Line tripped from Malbase end only.A/R successful at Birpara end during heavy thunderstorm and lightning weather condition.R/I at Birpara:M1 : B-N,FC-4.15 kA,FD-38.6. M2 : B-N,FC-4.001 kA,FD-39.69.Fault is under Bhutan jurisdiction. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:23 | 0:00 | 3:57 |  |  |  |  | ERPC | 100
36 | ER2L40 | Birpara-Binaguri-I | 80 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
37 | ER2L41 | Birpara-Binaguri-II | 80 | ER-II | ---- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
38 | ER2L42A | BIRPARA-ALIPURDUAR-I | 57.49 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
39 | ER2L42B | ALIPURDUAR-SALAKATI-I | 100.57 | ER-II | ----- | 2019-05-02 06:58 | 2019-05-02 19:10 | ----- | ----- | ----- | 0:00 | 12:12 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-06 07:07 | 2019-05-06 19:56 | ----- | ----- | ----- | 0:00 | 12:49 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 08/05/19 07:28 | 08/05/19 19:30 | ----- | ----- | ----- | 0:00 | 12:02 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-10 07:16 | 2019-05-10 20:12 | ----- | ----- | ----- | 0:00 | 12:56 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-12 07:25 | 2019-05-12 18:13 | ----- | ----- | ----- | 0:00 | 10:48 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 12/05/2019 18:46 | 12/05/2019 19:25 | ----- | ----- | ----- | 0:39 | 0:00 | 0:00 | 0:00 |  |  |  | A/R operated at Alipurduar end but tripped during reclaiming time on Y-N fault during heay rain & thunderstorm. R/I at Alipurduar end:-Y-N fault,Z1,F/D-71.4KM,F/C-2.13KA and R/I at Salakati end:- Y-N fault,F/D-32KM | ERPC | 100
[6 empty] | 2019-05-14 07:11 | 2019-05-14 18:58 | ----- | ----- | ----- | 0:00 | 11:47 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-16 06:57 | 2019-05-16 19:41 | ----- | ----- | ----- | 0:00 | 12:44 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-18 07:20 | 2019-05-18 18:13 | ----- | ----- | ----- | 0:00 | 10:53 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-19 09:25 | 2019-05-19 09:56 | ----- | ----- | ----- | 0:31 | 0:00 | 0:00 | 0:00 |  |  |  | Tripped on B-N Fault during heavy lightning & thunder strom, R/I at Alipurduar end: B-N Fault, F/D-52.2KM, F/C-1.93KA. R/I at Salakati end:Z1,B-N Fault, F/D-49.9Km, F/C-2.6KA | ERPC | 100
[6 empty] | 2019-05-20 07:14 | 2019-05-20 18:22 | ----- | ----- | ----- | 0:00 | 11:08 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-22 07:23 | 2019-05-22 18:12 | ----- | ----- | ----- | 0:00 | 10:49 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-26 07:23 | 2019-05-26 17:11 | ----- | ----- | ----- | 0:00 | 9:48 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement. | ERPC | 100
[6 empty] | 2019-05-28 07:25 | 28/05/19 19:13 | ----- | ----- | ----- | 0:00 | 11:48 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement. | ERPC | 100
[6 empty] | 2019-05-30 07:13 | 2019-05-30 17:35 | ----- | ----- | ----- | 0:00 | 10:22 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 1:10 | 150:06 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
40 | ER2L43A | BIRPARA-ALIPURDUAR-II | 57.49 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
41 | ER2L43B | ALIPURDUAR-SALAKATI-II | 100.57 | ER-II | ----- | 2019-05-01 06:42 | 2019-05-01 19:33 | ----- | ----- | ----- | 0:00 | 12:51 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-03 06:57 | 2019-05-03 18:36 | ----- | ----- | ----- | 0:00 | 11:39 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-05 07:37 | 2019-05-05 18:56 | ----- | ----- | ----- | 0:00 | 11:19 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 07/05/19 07:30 | 2019-05-07 20:14 | ----- | ----- | ----- | 0:00 | 12:44 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-09 06:52 | 2019-05-09 19:29 | ----- | ----- | ----- | 0:00 | 12:37 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-11 07:59 | 2019-05-11 18:16 | ----- | ----- | ----- | 0:00 | 10:17 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-13 06:59 | 13/05/2019 18:44 | ----- | ----- | ----- | 0:00 | 11:45 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-15 07:05 | 2019-05-15 19:00 | ----- | ----- | ----- | 0:00 | 11:55 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-17 07:09 | 2019-05-17 18:26 | ----- | ----- | ----- | 0:00 | 11:17 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-19 07:12 | 2019-05-19 17:08 | ----- | ----- | ----- | 0:00 | 9:56 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-21 07:29 | 2019-05-21 18:45 | ----- | ----- | ----- | 0:00 | 11:16 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement | ERPC | 100
[6 empty] | 2019-05-25 07:07 | 2019-05-25 17:37 | ----- | ----- | ----- | 0:00 | 10:30 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement. | ERPC | 100
[6 empty] | 2019-05-27 07:09 | 2019-05-27 18:27 | ----- | ----- | ----- | 0:00 | 11:18 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement. | ERPC | 100
[6 empty] | 2019-05-29 07:08 | 2019-05-29 19:09 | ----- | ----- | ----- | 0:00 | 12:01 | 0:00 | 0:00 |  |  |  | S/D taken for Installation of transmission line Lighting Arrestor first time for system improvement. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 161:25 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
42 | ER2L44 | Siliguri-Kishengunj-I | 108 | ER-II | ----- | 2019-05-11 09:19 | 2019-05-12 11:13 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 25:54 | ----- | ----- | ----- | S/D taken for Erection & stringing of new Anchor- 2 and Loc-35 which needs to be shifted due to change in course of river Mahananda upto 18:00hrs of 12.05.19. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 25:54 |  |  |  |  | ERPC | 100
43 | ER2L45 | Siliguri-Kishengunj-II | 108 | ER-II | ----- | 2019-05-11 09:20 | 2019-05-12 11:59 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 26:39 | ----- | ----- | ----- | S/D taken for Erection & stringing of new Anchor- 2 and Loc-35 which needs to be shifted due to change in course of river Mahananda upto 18:00hrs of 12.05.19. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 13/05/2019 00:30 | 13/05/2019 00:30 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  | Presently 220KV Siliguri-Dalkhola-II ,A/R sucessfull at both end .R/I at Siliguri end: B-N Fault,F/D- 42.95 KM,F/C-3.63KA. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 26:39 |  |  |  |  | ERPC | 100
44 | ER2L46 | Dalkhola-Kishengunj-I | 30.9 | ER-II | ----- | 2019-05-11 09:25 | 2019-05-12 11:13 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 25:48 | ----- | ----- | ----- | S/D taken for Erection & stringing of new Anchor- 2 and Loc-35 which needs to be shifted due to change in course of river Mahananda upto 18:00hrs of 12.05.19. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 25:48 |  |  |  |  | ERPC | 100
45 | ER2L47 | Dalkhola-Kishengunj-II | 30.9 | ER-II | ----- | 2019-05-11 09:26 | 2019-05-12 11:59 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 26:33 | ----- | ----- | ----- | S/D taken for Erection & stringing of new Anchor- 2 and Loc-35 which needs to be shifted due to change in course of river Mahananda upto 18:00hrs of 12.05.19. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 13/05/2019 00:30 | 13/05/2019 00:30 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  | Presently 220KV Siliguri-Dalkhola-II ,A/R sucessfull at both end .R/I at Dalkhola end: B-N Fault,F/D- 83.772 KM,F/C-1.718KA. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 26:33 |  |  |  |  | ERPC | 100
46 | ER2L48 | Dalkhola-Malda-I | 116 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
47 | ER2L49 | Dalkhola-Malda-II | 116 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
48 | ER2L50 | Binaguri-Siliguri-I | 9 | ER-II | ----- | 2019-05-02 00:25 | 2019-05-02 00:25 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | A/R operated successfully at both end. R/I at Binaguri:R-N fault, Z-1, F/C: 2.637KA, F/D:2.181kms; R/I at Siliguri:R-N fault, Z-1, F/C: 5.9617KA, F/D:2.875kms | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
49 | ER2L51 | Binaguri-Siliguri-II | 9 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
50 | ER2L52 | Rangpo-New Melli-I | 26.1 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
51 | ER2L53 | Rangpo-Tashiding | 26.1 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
52 | ER2L55 | Siliguri-Kurseong-I (up to LILO) | 31.3 | ER-II | ----- | 2019-05-13 10:12 | 2019-05-13 12:52 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 2:40 |  |  | ----- | S/D taken by WBSETCL for installation of Apex 100 type meters at WBSETCL Kurseong end. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-22 17:28 | 2019-05-22 17:49 | ----- | ----- | ----- | 0:00 | 0:21 | 0:00 | 0:00 |  |  |  | Tripped on R-Y-N fault. R/I at Siliguri end: F/D: 34.7KM, F/C : Ir: 3.58KA, Iy: 3.51kA. Fault is under Kurseong(WBSETCL) jurisdiction | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:21 | 0:00 | 2:40 |  |  |  |  | ERPC | 100
53 | ER2L56 | Kurseong-Rangit-I (up to LILO) | 61.2 | ER-II | ----- | 2019-05-13 12:58 | 2019-05-13 14:14 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 1:16 | ----- | ----- | ----- | S/D taken by WBSETCL for installation of Apex 100 type meters at WBSETCL Kurseong end. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 1:16 |  |  |  |  | ERPC | 100
54 | ER2L57 | RANGIT-Rangpo | 54.17 | ER-II | ----- | 2019-05-26 22:03 | 2019-05-26 22:35 | ----- | ----- | ----- | 0:00 | 0:32 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped due to problem at Rangit end.R/I at Gangtok end: Zone-2, B-N fault, FC: 0.677 KA, FD: 80.5 KM. For Erection of GIS bays at Rangpo 400/220/132KV GIS pertaining to Chuzachen Ckts. present reconfiguration, 132KV Gangtok Rangpo line and 132 KV Rangpo Rangit line became 132 KV Gangtok Rangit line. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-25 08:35 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 159:25 |  |  |  | S/D taken by Sikkim for Erection of GIS bays at Rangpo 400/220/132KV GIS pertaining to Chuzachen Ckts.As per present reconfiguration, 132KV Gangtok Rangpo line and 132 KV Rangpo Rangit line became 132 KV Gangtok Rangit line and same has been taken into service at 14:51 Hrs. on 25.05.19. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:32 | 0:00 | 159:25 |  |  |  |  | ERPC | 100
55 | ER2L58 | Rangpo-GANGTOK-II | 26.36 | ER-II | ----- | 2019-05-26 22:03 | 2019-05-26 22:35 | ----- | ----- | ----- | 0:00 | 0:32 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped due to problem at Rangit end.R/I at Gangtok end: Zone-2, B-N fault, FC: 0.677 KA, FD: 80.5 KM. For Erection of GIS bays at Rangpo 400/220/132KV GIS pertaining to Chuzachen Ckts. present reconfiguration, 132KV Gangtok Rangpo line and 132 KV Rangpo Rangit line became 132 KV Gangtok Rangit line. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-25 08:33 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 159:27 |  |  |  | S/D taken by Sikkim for Erection of GIS bays at Rangpo 400/220/132KV GIS pertaining to Chuzachen Ckts. As per present reconfiguration, 132KV Gangtok Rangpo line and 132 KV Rangpo Rangit line became 132 KV Gangtok Rangit line and same has been taken into service at 14:51 Hrs. on 25.05.19. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:32 | 0:00 | 159:27 |  |  |  |  | ERPC | 100
56 | ER2L59 | Chujacheng-Rangpo (LILO) | 1 | ER-II | ----- | 2019-05-19 13:27 | 2019-05-19 15:42 | ----- | ----- | ----- | 0:00 | 2:15 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped on B-N fault. R/I at Rangpo: B-N fault,FD: 3.6KM , FC: 5.3KA fault is under Chuzachen jurisdiction. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-26 09:22 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 134:38 |  |  |  | S/D taken by Sikkim for Erection of GIS bays at Rangpo 400/220/132KV GIS pertaining to Chuzachen Ckts. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 2:15 | 0:00 | 134:38 |  |  |  |  | ERPC | 100
57 | ER2L60 | 132KV-GANGTOK -CHUZACHEN-1 | 28.06 | ER-II | ----- | 2019-05-17 21:05 | 2019-05-17 21:58 | ----- | ----- | ----- | 0:00 | 0:53 | 0:00 | 0:00 | ----- | ----- | ----- | TRIPPED on Y-B-N fault during heavy rain & thunderstorm at or near the affected area.R/I at Gangtok: F/C: Iy:1.33KA,Ib:1.13KA; F/D: 38.34kms. FAULT IS UNDER CHUZACHEN JURISDICTION. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-27 18:23 | 2019-05-27 18:44 | ----- | ----- | ----- | 0:00 | 0:21 | 0:00 | 0:00 |  |  |  | Tripped on Y-N fault. R/I at Gangtok: Y-N,FD: 36.63KM,FC: 1.109KA. Fault is under Chuzachen jurisdiction. | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 1:14 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
58 | ER2L61 | MELLI-SILIGURI | 92.45 | ER-II | --- | 2019-05-22 17:32 | 2019-05-22 18:01 | ----- | ----- | ----- | 0:29 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped on Y-N fault during heavy rain & thunderstorm. R/I at Siliguri end: F/D: 24.7KM, F/C : Iy: 2.78kA. | ERPC | 99.94 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:29 | 0:00 | 0:00 | 0:00
59 | ER2L62 | RANGPO-MELLI | 16.61 | ER-II | ---- | 2019-05-25 08:58 | 2019-06-01 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 159:02 | ----- | ----- | ----- | S/D taken by Sikkim for Erection of GIS bays at Rangpo 400/220/132KV GIS pertaining to Chuzachen Ckts. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 159:02 |  |  |  |  | ERPC | 100
60 | ER2L63 | Rangit-Rammam | 27.15 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
61 | ER2L64 | Rangit-Rabangla(up to LILO) | 1 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
62 | ER2L65 | Rabangla - Melli(up to LILO) | 36 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
63 | ER2L66 | Binaguri-Bongaigaon-I | 217.275 | ER-II | ----- | 2019-05-20 22:49 | 2019-05-20 22:49 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | A/R successful at both end. R/I at Binaguri:B-N fault,FD: 153.3KM,FC: 2.6KA. R/I at Bongaigaon::B-N,FD: 64KM, FC: 3.3KA. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
64 | ER2L67 | Binaguri-Bongaigaon-II | 217.275 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
65 | ER2L70 | Baharampore - Bheramara - I(Indian portion) | 71.51 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
66 | ER2L71 | Baharampore - Bheramara - II(Indian Portion) | 71.51 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
67 | ER2L74 | Rangpo-Teesta-III(LILO) | 10.78 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
68 | ER2L75 | Rangpo_Kishengunj(LILO) | 10.78 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
69 | ER2L72 | Farakka-Gokarna-I | 120 | ER-II | ----- | 2019-05-28 17:02 | 2019-05-28 17:24 | ----- | ----- | ----- | 0:22 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped due to DT received at Farakka/NTPC end from remote end. | ERPC | 99.95 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-30 21:08 | 2019-05-30 21:59 | ----- | ----- | ----- | 0:00 | 0:00 | 0:51 | 0:00 |  |  |  | During rain and thunder storm the line tripped. R/I at Gokarna(WBSETCL) end:- Z1, B-N fault, F/D-39.5KM, F/C:-5.7KA
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:22 | 0:00 | 0:51 | 0:00
70 | ER2L73 | Farakka-Gokarna-II | 120 | ER-II | --- | 2019-05-28 17:02 | 2019-05-28 17:28 | ----- | ----- | ----- | 0:26 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped due to DT received at Farakka/NTPC end from remote end. | ERPC | 99.94 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:26 | 0:00 | 0:00 | 0:00
71 | ER2L74 | BINAGURI-KISUNGANJ-1-LILO | 5 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
72 | ER2L75 | BINAGURI-KISUNGANJ-2-LILO | 5 | ER-II | ----- | 2019-05-15 19:20 | 2019-05-15 19:20 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | A/R operated successfully both end. R/I at Binaguri end: B-N fault, F/C:4.89KA, F/D: 153.5KM; R/I at Kishanganj end: B-N fault, F/C: 15.64KA, F/D: 1.5KM | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
73 | ER2L76 | 400KV-KISHANGANJ-PURNEA-1 LILO | 5 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
74 | ER2L77 | 400KV-KISHANGANJ-PURNEA-2 LILO | 5 | ER-II | ----- | 2019-05-15 19:14 | 2019-05-15 19:14 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | A/R operated successfully both end . R/I at Kishanganj: Y-N fault, F/C: 16.66KA, F/D: 1.0KM; R/I at New Purnea end: Y-N fault, F/C: 5.339KA, F/D: 80.89KM | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
75 | ER2L78 | 400KV FARAKKA-SAGARDIGHI-II | 76 | ER-II | ----- | 2019-05-27 07:29 | 2019-05-27 15:48 | ----- | ----- | ----- | 8:19 | 0:00 | 0:00 | 0:00 | ----- | ----- | ----- | S/D taken for rectification work of damage earth peak at Tower Loc no 15 and 10 | ERPC | 97.68 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-28 07:03 | 2019-05-28 15:58 | ----- | ----- | ----- | 8:55 | 0:00 | 0:00 | 0:00 |  |  |  | S/D taken for rectification work of damage earth peak at Tower Loc no 15 and 10
[6 empty] | 2019-05-30 20:34 | 2019-05-30 22:26 | ----- | ----- | ----- | 0:00 | 1:52 | 0:00 | 0:00 |  |  |  | Tripped on B-N fault, F/D- 12.2KM( Lilo portion of WBPDCL portion), F/C:- Not shown.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 17:14 | 1:52 | 0:00 | 0:00
76 | ER2L79 | 400 KV SAGARDIGHI-JEERAT | 199.5 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
77 | ER2L80 | LILO OF BINAGURI-BONGAIGAION-III AT ALIPURDUAR | 12.89 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
78 | ER2L81 | LILO OF BINAGURI-BONGAIGAION-IV AT ALIPURDUAR | 12.89 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
79 | ER2L82 | 400KV FARAKKA-BAHARAMPORE-I | 83 | ER-II | ----- | 2019-05-09 09:44 | 2019-05-09 18:57 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 9:13 | ----- | ----- | ----- | H/T to facilitate shutdown of 400KV Bus-1 at Farakka/NTPC end for Isolator jumper disconnection work. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 9:13 |  |  |  |  | ERPC | 100
80 | ER2L83 | 400KV FARAKKA-BAHARAMPORE-II | 83 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
81 | ER2L84 | 400 KV ALIPURDUAR-PUNATSANGHCUN -I | 64.152 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
82 | ER2L85 | 400 KV ALIPURDUAR-PUNATSANGHCUN -II | 64.152 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
83 | ER2L86 | 400 KV RAJARHAT-JEERAT | 41 | ER-II |  |  |  | ----- | ----- | ----- | [8 empty] | ERPC | 100
84 | ER2L87 | 400 KV RAJARHAT-SUBHASGRAM | 33.6 | ER-II |  | 2019-05-25 03:03 | 2019-05-25 03:03 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 0:00 |  |  |  | A/R successful at both end. R/I at Subhasgram: B-N fault, F/C: 8.038KA, F/D:7.628kms R/I at Rajarhat: B-N fault, F/C: 6.11KA, F/D:22.874kms | ERPC | 100
[6 empty] | 2019-05-26 07:01 | 2019-05-26 09:54 | ----- | ----- | ----- | 0:00 | 2:53 | 0:00 | 0:00 |  |  |  | S/D taken for insulator replacement at Tower no 139 with CLR for system improvement | ERPC | 100
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 2:53 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
85 | ER2T1 | ICT-I,DGP | 315 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
86 | ER2T2 | ICT-II,DGP | 315 | ER-II | --- | 2019-05-22 10:08 | 2019-05-22 15:51 | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 5:43 | ----- | ----- | ----- | S/D taken to construction work of new bay with existing 220KV Main Bus-II at Durgapur under ERSS-XVII | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 0:00 | 0:00 | 5:43 |  |  |  |  | ERPC | 100
87 | ER2T3 | ICT-I,MTN | 500 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
88 | ER2T4 | ICT-II,MTN | 500 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
89 | ER2T5 | ICT-I,FKK | 315 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
90 | ER2T6 | ICT-III,MLD | 315 | ER-II | --- | 2019-05-17 14:34 | 2019-05-17 15:44 | ----- | ----- | ----- | 0:00 | 1:10 | 0:00 | 0:00 | ----- | ----- | ----- | ICT tripped on HV side Over current during tripping of Malda-Purnea-I line. Fault current was very high(13.03 kA)in the line and due to that ICT tripped on O/C as being a part of Chukha Transmission system Malda SS has no directional feature. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  | ----- | ----- | ----- | 0:00 | 1:10 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
91 | ER2T7 | ICT-V,MLD | 315 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
92 | ER2T8 | ICT-I, NSLG | 315 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
93 | ER2T9 | ICT-II, NSLG | 315 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
94 | ER2T10 | ICT-I, SGM | 315 | ER-II | --- | 2019-05-20 14:42 | 2019-05-20 17:32 | ----- | ----- | ----- | 0:00 | 2:50 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped due to low IR value of one cable which is replaced with spare one. | ERPC | 99.51 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-25 06:01 | 2019-05-25 09:37 | ----- | ----- | ----- | 3:36 | 0:00 | 0:00 | 0:00 |  |  |  | S/D taken for replacement of Buchholz relay.
[6 empty] | TOTAL |  | ----- | ----- | ----- | 3:36 | 2:50 | 0:00 | 0:00
95 | ER2T11 | ICT-II, SGM | 315 | ER-II | ---- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
96 | ER2T12 | ICT-V, SGM | 500 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
97 | ER2T13 | ICT-V RANGPO | 315 | ER-II | ----- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
98 | ER2T14 | ICT-IV RANGPO | 315 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
99 | ER2T15 | ICT-III RANGPO | 315 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
100 | ER2T16 | ICT-II RANGPO | 315 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
101 | ER2T17 | ICT-I RANGPO | 315 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
102 | ER2T18 | ICT-I,SLG | 160 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
103 | ER2T19 | ICT-II,SLG | 160 | ER-II | --- |  |  | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
104 | ER2T20 | ICT-I,BRP | 160 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
105 | ER2T21 | ICT-II,BRP | 160 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
106 | ER2T22 | ICT-II, Malda | 160 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
107 | ER2T23 | ICT-I, Malda | 160 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
108 | ER2T24 | ICT-IV, MLD | 50 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
109 | ER2T25 | ICT-I, RANGPO | 100 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
110 | ER2T26 | ICT-II, RANGPO | 100 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
111 | ER2T27 | ICT-III, RANGPO | 100 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
112 | ER2T28 | ICT-I, GTK | 50 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
113 | ER2T29 | ICT-II,GTK | 50 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
114 | ER2T30 | ALIPURDUAR-ICT-I | 315 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
115 | ER2T31 | ALIPURDUAR-ICT-II | 315 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
116 | ER2T32 | RAJARHAT-ICT-I | 500 | ER-II | --- | [13 empty] | ERPC | 100
117 | ER2R1 | 125 3ph B/R- II NSLG | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
118 | ER2R2 | 125 3ph B/R- I NSLG | 125 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
119 | ER2R3 | 80 BONGG-III L/R at Binaguri | 80 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
120 | ER2R4 | 80 BONGG-IV L/R at Binaguri | 80 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
121 | ER2R5 | 50 Gaya-I L/R at Maithon | 50 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
122 | ER2R6 | 50 Gaya-II L/R at Maithon | 50 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
123 | ER2R7 | 80 MVAR B/R at Berhampore | 80 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
124 | ER2R8 | 80 MVAR B/R -I at Rangpo | 80 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
125 | ER2R9 | 80 MVAR B/R -II at Rangpo | 80 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
126 | ER2R10 | 50 MVAR B/R-I ,DGP | 50 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
127 | ER2R11 | 125 MVAR B/R-II ,DGP | 51 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
128 | ER2R11 | MAITHAN-MEJIA-I LR | 50 | ER-II | --- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
129 | ER2R12 | 2*50 1ph B/R ,JRT | 100 | ER-II | ----- | 2019-04-23 14:56 | 2019-05-03 06:50 |  |  |  | 0:00 | 0:00 | 0:00 | 231:54 | ----- | ----- | ----- | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 06/05/19 15:18 | 2019-05-13 21:52 |  |  |  | 0:00 | 0:00 | 0:00 | 174:34 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-14 11:48 | 2019-05-15 02:30 |  |  |  | 0:00 | 0:00 | 0:00 | 14:42 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-15 11:28 | 2019-05-25 18:15 |  |  |  | 0:00 | 0:00 | 0:00 | 246:47 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 667:57 |  |  |  |  | ERPC | 100
130 | ER2R13 | 31.5MVAR B/R-I at New Melli | 31.5 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
131 | ER2R14 | 31.5MVAR B/R-II at New Melli | 31.5 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
132 | ER2R15 | 125MVAR B/R-I at Maithan | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
133 | ER2R16 | 125MVAR B/R-II at Maithan | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
134 | ER2R17 | 125MVAR B/R-III AT DURGAPUR | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
135 | ER2R18 | 80MVAR B/R AT GOKARNA | 80 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
136 | ER2R19 | ALIPURDUAR-125MVAR BUS REACTOR-I | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
137 | ER2R20 | ALIPURDUAR-125MVAR BUS REACTOR-II | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
138 | ER2R21 | FARAKKA -GOKARNA-I L/R | 80 | ER-II | ----- | 2019-05-30 20:34 | 2019-05-30 22:12 |  |  |  | 0:00 | 1:38 | 0:00 | 0:00 | ----- | ----- | ----- | Tripped during A/R of line as per prevelling scheme. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | TOTAL |  |  |  |  | 0:00 | 1:38 | 0:00 | 0:00 |  |  |  |  | ERPC | 100
139 | ER2R22 | 125MVAR BAHARAMPORE B/R | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
140 | ER2R23 | SUBHASGRAM SAGARDIGHI LR | 50 | ER-II | ----- | 2019-05-01 | 2019-05-03 11:37 |  |  |  | 0:00 | 0:00 | 0:00 | 59:37 | ----- | ----- | ----- | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[6 empty] | 2019-05-06 15:23 | 2019-05-13 22:06 |  |  |  | 0:00 | 0:00 | 0:00 | 174:43 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-14 10:49 | 2019-06-01 |  |  |  | 0:00 | 0:00 | 0:00 | 421:11 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 655:31 |  |  |  |  | ERPC | 100
141 | ER2R24 | 125MVAR B/R-IV AT DURGAPUR | 125 | ER-II | ----- | [9 empty] | ----- | ----- | ----- |  | ERPC | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
142 | ER2R25 | 125MVAR B/R-I AT RAJARHAT | 125 | ER-II | ----- | 2019-05-01 | 2019-05-03 20:45 |  |  |  | 0:00 | 0:00 | 0:00 | 68:45 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-04-22 15:30 | 2019-05-03 20:53 |  |  |  | 0:00 | 0:00 | 0:00 | 269:23 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-04 18:35 | 2019-05-13 22:08 |  |  |  | 0:00 | 0:00 | 0:00 | 219:33 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-14 11:04 | 2019-05-25 05:16 |  |  |  | 0:00 | 0:00 | 0:00 | 258:12 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-26 22:53 | 2019-06-01 |  |  |  | 0:00 | 0:00 | 0:00 | 121:07 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation | ERPC | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 937:00 |  |  |  |  | ERPC | 100
143 | ER2R26 | 125MVAR B/R-II AT RAJARHAT | 125 | ER-II | ----- | 2019-05-04 18:40 | 2019-05-15 06:11 |  |  |  | 0:00 | 0:00 | 0:00 | 251:31 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-15 11:19 | 2019-05-26 05:41 |  |  |  | 0:00 | 0:00 | 0:00 | 258:22 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation. | ERPC | 100
[6 empty] | 2019-05-26 07:33 | 2019-06-01 |  |  |  | 0:00 | 0:00 | 0:00 | 136:27 |  |  |  | H/T as per ERLDC instruction for Voltage Regulation | ERPC | 100
[6 empty] | TOTAL |  |  |  |  | 0:00 | 0:00 | 0:00 | 646:20 |  |  |  |  | ERPC
[8 empty] | ----- | ----- | -----
[8 empty] | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Note on C151: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C152: Author: LILO made by DOP, Govt os Sikkim, Declared w.e.f 01.03.2011
Note on C205: Author: DOCO 09.06.2014 3 X 105 MVA
Note on C216: Author: DOCO 24.04.14
Note on C217: Author: DOCO 30.06.2014
Note on C225: Author: DOCO wef 01.05.2013
Note on C226: Author: DOCO wef 01.06.2013
Note on C227: Author: D.O.C.O w.e.f 01.04.2012
Note on C228: Author: D.O.C.O w.e.f 01.04.2012