## PMJTL APRIL SOP
Standard Operational Performance data for the month of April 2021 | [28 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Name of Transmission Licensee : POWER GRID MEDINIPORE JEERAT TRANSMISSION LIMITED | [28 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | OUTAGE | RESTORATION | Outage Attributable to |  |  |  | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as proposed to certifying agency | Type of failure | No. of towers damaged | no. of insulator failed | Total outage in days (1) | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | Date Time | Date Time | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | [10 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
1 | PMJTLL1 | 765 KV New Ranchi-Medinipur-I | 269 | PMJTL | 2021-04-09 17:32 | 2021-04-09 18:38 | 0:00 | 0:00 | 1:06 | 0:00 | Tripped. 'R/I at MDN: R-N, Z2, F/C-2.68 kA, F/D-237 km; R/I at Ranchi: R-N, Z1, F/C-8.6kA, F/D-34.5 Km; |  |  |  | ERPC ERPC/MS/TAC/PMJTL/2021-22/352 dated: 23.06.21 | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-04-15 09:30 | 2021-04-15 11:21 | 0:00 | 0:00 | 1:51 | 0:00 | Tripped. R/I at Mednipur: O/V STAGE-2 TRIP.
[5 empty] | 2021-04-16 11:57 | 2021-04-16 14:09 | 0:00 | 0:00 | 2:12 | 0:00 | Tripped. R/I at Mednipur: O/V STAGE-1 TRIP.
[5 empty] | TOTAL |  | 0:00 | 0:00 | 5:09 | 0:00
2 | PMJTLL2 | 765 KV New Ranchi-Medinipur-II | 269 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
3 | PMJTLL3 | LILO of Kharagpur-Chandital line for Medinipur-Khargapur#1 | 36.96 |  | 2021-04-13 14:58 | 2021-04-13 17:10 | 0:00 | 2:12 | 0:00 | 0:00 | Line tripped. R/I at Medinipur: Y-ph A/R attempted, F/D:106.02kms. Carrier Received in Ch-1. R/I at Kharagpur(WBSETCL): Y-B-N fault, F/C:Iy:18.12KA, Ib:16.9KA, F/D:4.663kms. Fault is under WBSETCL jurisdiction(37kms from Medinipur i.e. LILO portion only under POWERGRID jurisdiction). Patrolling carried out by WBSETCL but no discrepancy found. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 0:00 | 2:12 | 0:00 | 0:00
4 | PMJTLL4 | LILO of Kharagpur-Chandital line for Medinipur-Khargapur#2 | 36.96 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
5 | PMJTLL5 | LILO of Kharagpur-Chandital line for Medinipur-Chanditala#1 | 36.79 | [12 empty] | 100
6 | PMJTLL6 | LILO of Kharagpur-Chandital line for Medinipur-Chanditala#2 | 36.79 | [12 empty] | 100
7 | PMJTLT1 | MEDINIPORE-ICT-I | 1500 |  | 2021-04-19 10:15 | 2021-04-19 16:31 | 6:16 | 0:00 | 0:00 | 0:00 | Emergency S/D for rectification of water leakage of detection line of hydrant system |  |  |  |  | 99.13 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 6:16 | 0:00 | 0:00 | 0:00
8 | PMJTLT2 | MEDINIPORE-ICT-II | 1500 |  | 2021-04-24 10:19 | 2021-04-24 17:18 | 0:00 | 6:59 | 0:00 | 0:00 | S/D taken by PMJTL for taking spare ICT into service. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 0:00 | 6:59 | 0:00 | 0:00
9 | PMJTLR1 | MEDINIPORE 330MVAR BUS REACTOR-I | 330 |  | 2021-04-28 12:17 | 2021-04-28 14:05 | 1:48 | 0:00 | 0:00 | 0:00 | S/D to replace defective VT selection relay |  |  |  |  | 99.75 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 1:48 | 0:00 | 0:00 | 0:00
10 | PMJTLR2 | MEDINIPORE 330MVAR BUS REACTOR-II | 330 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
11 | PMJTLR3 | 240 MVAR L/R OF 765 kV MEDINIPORE-RANCHI-I AT MEDINIPORE END | 240 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
12 | PMJTLR4 | 240 MVAR L/R OF 765 kV MEDINIPORE-RANCHI-II AT MEDINIPORE END | 240 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
13 | PMJTLR5 | MEDINIPORE 125MVAR BUS REACTOR-I | 125 | [12 empty] | 100
14 | PMJTLR6 | MEDINIPORE 125MVAR BUS REACTOR-II | 125 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- |  | ----- | ----- |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
-----
-----
-----
-----
-----