## PMJTL JUNE SOP
Standard Operational Performance data for the month of JUNE 2021 | [28 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Name of Transmission Licensee : POWER GRID MEDINIPORE JEERAT TRANSMISSION LIMITED | [28 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | OUTAGE | RESTORATION | Outage Attributable to |  |  |  | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as proposed to certifying agency | Type of failure | No. of towers damaged | no. of insulator failed | Total outage in days (1) | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | Date Time | Date Time | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | [10 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
1 | PMJTLL1 | 765 KV New Ranchi-Medinipur-I | 269 | PMJTL | 2021-06-02 10:18 | 2021-06-02 19:06 | 0:00 | 8:48 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  | ERPC ERPC/MS/ TAC/PMJTL/2021-22/625 dated: 26.08.21 | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-06-15 07:29 | 2021-06-15 23:20 | 0:00 | 15:51 | 0:00 | 0:00 | S/D for rectification of S/D nature of defects in extreme ROW area in between Sec 116/2-117/0 like removal of rollers from conductor, removal of pulleys from earthwire etc.
[5 empty] | TOTAL |  | 0:00 | 24:39 | 0:00 | 0:00
2 | PMJTLL2 | 765 KV New Ranchi-Medinipur-II | 269 |  | 2021-06-03 10:20 | 2021-06-03 20:49 | 0:00 | 10:29 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100
[5 empty] | 2021-06-12 07:21 | 2021-06-12 19:23 | 0:00 | 12:02 | 0:00 | 0:00 | S/D for rectification of S/D nature of defects in extreme ROW area in between Sec 116/2-117/0 like removal of rollers from conductor, removal of pulleys from earthwire etc.
[5 empty] | 2021-06-13 07:00 | 2021-06-13 16:37 | 0:00 | 9:37 | 0:00 | 0:00 | S/D for rectification of S/D nature of defects in extreme ROW area in between Sec 116/2-117/0 like removal of rollers from conductor, removal of pulleys from earthwire etc.
[5 empty] | 2021-06-16 10:16 | 2021-06-16 19:53 | 0:00 | 9:37 | 0:00 | 0:00 | S/D for rectification of S/D nature of defects in extreme ROW area in between Sec 116/2-117/0 like removal of rollers from conductor, removal of pulleys from earthwire etc.
[5 empty] | 30/06/2021 19:41:00 | 30/06/2021 19:41:00 | 0:00 | 0:00 | 0:00 | 0:00 | Auto-reclose successful. R/I at Medinipur: M1: Y-N, Z1, Iy - 5.976 kA, F/D - 2.6 km; M2: Y-N, Z1, Iy - 5.64 kA, F/D - 1.89 km.
[5 empty] | TOTAL |  | 0:00 | 41:45 | 0:00 | 0:00 | [6 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
3 | PMJTLL3 | LILO of Kharagpur-Chandital line for Medinipur-Khargapur#1 | 36.96 |  | 2021-06-07 16:25 | 2021-06-07 16:55 | 0:00 | 0:30 | 0:00 | 0:00 | Tripped. R/I at Mednipur end: R-N, F/D:12.5 km, F/C:3.612kA; R/I at Kharagpur end: R-N, F/D:30.83 km, F/C:7.427kA [fault under WBSETCL Jurisdiction] |  |  |  |  | 99.67
[5 empty] | 2021-06-12 13:37 | 2021-06-12 15:59 | 2:22 | 0:00 | 0:00 | 0:00 | S/D FOR MAINTENANCE OF ISOLATOR 405-89B AT MEDINIPUR END | [5 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-06-15 12:04 | 2021-06-15 14:22 | 0:00 | 0:00 | 0:00 | 2:18 | Emergency S/D taken by WBSETCL for rectification of fault of Main-II DC protection scheme at Kharagpur(WBSETCL) end.
[5 empty] | 2021-06-10 07:48 | 2021-06-10 18:15 | 0:00 | 10:27 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET.
[5 empty] | TOTAL |  | 2:22 | 10:57 | 0:00 | 2:18
4 | PMJTLL4 | LILO of Kharagpur-Chandital line for Medinipur-Khargapur#2 | 36.96 |  | 2021-06-09 07:58 | 2021-06-09 16:01 | 0:00 | 8:03 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 0:00 | 8:03 | 0:00 | 0:00
5 | PMJTLL5 | LILO of Kharagpur-Chandital line for Medinipur-Chanditala#1 | 36.79 |  | 2021-06-16 08:03 | 2021-06-16 14:35 | 0:00 | 6:32 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100
[5 empty] | 2021-06-02 12:31 | 2021-06-02 12:31 | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both ends . R/I at Mednipur end : B-N, F/D:58.80KM , F/C: 3.7KA Chanditala end : B-N, F/D: 4.31KM, F/C: 15.03KA
[5 empty] | TOTAL |  | 0:00 | 6:32 | 0:00 | 0:00
6 | PMJTLL6 | LILO of Kharagpur-Chandital line for Medinipur-Chanditala#2 | 36.79 |  | 2021-06-07 15:32 | 2021-06-07 15:32 | 0:00 | 0:00 | 0:00 | 0:00 | A/R successful at both ends R/I at Mednipur end: R-N fault, Z1, F/D: 31 KM, F/C: 6.213KA |  |  |  |  | 100
[5 empty] | 2021-06-07 15:57 | 2021-06-07 16:46 | 0:00 | 0:49 | 0:00 | 0:00 | Tripped. R/I at Mednipur end: R-N, Z2, F/D:113.7 km, F/C:2.71kA; R/I at Chanditala end: R-N, Z1, F/D:2.18 km, F/C:17.66kA [fault under WBSETCL Jurisdiction]
[5 empty] | 2021-06-12 07:37 | 2021-06-12 12:43 | 0:00 | 5:06 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET.
[5 empty] | TOTAL |  | 0:00 | 5:55 | 0:00 | 0:00
7 | PMJTLT1 | MEDINIPORE-ICT-I | 1500 |  | 2021-06-17 09:38 | 2021-06-17 17:55 | 0:00 | 8:17 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 99.13 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-06-04 10:12 | 2021-06-04 18:39 | 0:00 | 8:27 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET.
[5 empty] | TOTAL |  | 0:00 | 16:44 | 0:00 | 0:00
8 | PMJTLT2 | MEDINIPORE-ICT-II | 1500 |  | 2021-06-18 10:02 | 2021-06-18 19:15 | 0:00 | 9:13 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-06-05 10:57 | 2021-06-05 18:14 | 0:00 | 7:17 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET.
[5 empty] | TOTAL |  | 0:00 | 16:30 | 0:00 | 0:00
9 | PMJTLR1 | MEDINIPORE 330MVAR BUS REACTOR-I | 330 |  | 2021-06-01 10:51 | 2021-06-01 19:15 | 0:00 | 8:24 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 99.69 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-06-02 10:43 | 2021-06-08 02:59 | 0:00 | 0:00 | 0:00 | 136:16 | H/T as per ERLDC instruction for Voltage Regulation.
[5 empty] | 2021-06-29 07:24 | 2021-06-29 09:38 | 2:14 | 0:00 | 0:00 | 0:00 | Tripped due to Maloperation of CT B Phase SF6 gas density monitor
[5 empty] | TOTAL |  | 2:14 | 8:24 | 0:00 | 136:16
10 | PMJTLR2 | MEDINIPORE 330MVAR BUS REACTOR-II | 330 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
11 | PMJTLR3 | 240 MVAR L/R OF 765 kV MEDINIPORE-RANCHI-I AT MEDINIPORE END | 240 |  | 2021-06-02 10:32 | 2021-06-02 19:06 | 0:00 | 8:34 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 0:00 | 8:34 | 0:00 | 0:00
12 | PMJTLR4 | 240 MVAR L/R OF 765 kV MEDINIPORE-RANCHI-II AT MEDINIPORE END | 240 |  | 2021-06-03 10:20 | 2021-06-03 20:49 | 0:00 | 10:29 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 0:00 | 10:29 | 0:00 | 0:00
13 | PMJTLR5 | MEDINIPORE 125MVAR BUS REACTOR-I | 125 |  | 2021-06-08 10:06 | 08/06/21 15:19 | 0:00 | 5:13 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100
[5 empty] | TOTAL |  | 0:00 | 5:13 | 0:00 | 0:00
14 | PMJTLR6 | MEDINIPORE 125MVAR BUS REACTOR-II | 125 |  | 2021-06-07 10:23 | 2021-06-07 18:21 | 0:00 | 7:58 | 0:00 | 0:00 | S/D FOR DATA VALIDATION OF RTAMC SIGNAL FOR REMOTE MONITORING OF THE ASSET. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 0:00 | 7:58 | 0:00 | 0:00
----- | ----- | ----- | ----- | ----- |  | ----- | ----- |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
-----
-----
-----
-----
-----