## PMJTL JULY SOP
Standard Operational Performance data for the month of JULY 2021 | [28 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Name of Transmission Licensee : POWER GRID MEDINIPORE JEERAT TRANSMISSION LIMITED | [28 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | OUTAGE | RESTORATION | Outage Attributable to |  |  |  | Detailed Reason(s) for Outage | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Outage Certifying Agency and Reference Document | % Availability as proposed to certifying agency | Type of failure | No. of towers damaged | no. of insulator failed | Total outage in days (1) | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | Date Time | Date Time | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | [10 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
1 | PMJTLL1 | 765 KV New Ranchi-Medinipur-I | 269 | PMJTL | 2021-07-12 08:05 | 2021-07-12 17:56 | 0:00 | 9:51 | 0:00 | 0:00 | S/D FOR RECTIFICATION OF SHUT-DOWN NATURE OF DEFECTS IN EXTREME ROW AREA IN BETWEEN SECTION 116/2-117/0 LIKE REMOVAL OF ROLLERS FROM CONDUCTOR, REMOVAL OF PULLEYS FROM EARTH WIRE ETC. |  |  |  | ERPC ERPC/MS/ TAC/PMJTL/2021-22/918 dated: 07.10.21 | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-07-13 08:03 | 2021-07-13 18:38 | 0:00 | 10:35 | 0:00 | 0:00 | S/D FOR RECTIFICATION OF SHUT-DOWN NATURE OF DEFECTS IN EXTREME ROW AREA IN BETWEEN SECTION 116/2-117/0 LIKE REMOVAL OF ROLLERS FROM CONDUCTOR, REMOVAL OF PULLEYS FROM EARTH WIRE ETC.
[5 empty] | TOTAL |  | 0:00 | 20:26 | 0:00 | 0:00
2 | PMJTLL2 | 765 KV New Ranchi-Medinipur-II | 269 |  | 2021-07-11 13:07 | 2021-07-11 19:33 | 0:00 | 6:26 | 0:00 | 0:00 | S/D FOR RECTIFICATION OF SHUT-DOWN NATURE OF DEFECTS IN EXTREME ROW AREA IN BETWEEN SECTION 116/2-117/0 LIKE REMOVAL OF ROLLERS FROM CONDUCTOR, REMOVAL OF PULLEYS FROM EARTH WIRE ETC. |  |  |  |  | 100
[5 empty] | TOTAL |  | 0:00 | 6:26 | 0:00 | 0:00 | [6 empty] | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
3 | PMJTLL3 | LILO of Kharagpur-Chandital line for Medinipur-Khargapur#1 | 36.96 |  | 2021-07-03 18:10 | 2021-07-03 18:10 | 0:00 | 0:00 | 0:00 | 0:00 | Auto-reclose successfully at both ends, R/I at Medinipur: M1: Y-N, Z1, F/C- 6.3 kA, F/D- 33.70 km ; M2: Y-N, Z1, F/C- 6.6 kA, F/D- 34.21 km. Rainfall and thunderstorm has been reported in nearby locations. |  |  |  |  | 100
[5 empty] | TOTAL |  | 0:00 | 0:00 | 0:00 | 0:00
4 | PMJTLL4 | LILO of Kharagpur-Chandital line for Medinipur-Khargapur#2 | 36.96 | [12 empty] | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
5 | PMJTLL5 | LILO of Kharagpur-Chandital line for Medinipur-Chanditala#1 | 36.79 |  | 2021-07-05 15:06 | 2021-07-05 15:06 | 0:00 | 0:00 | 0:00 | 0:00 | A/R Successful at both ends. R/I at Medinipur: R-N, F/D-39.5 km, F/C-5.694 kA; R/I at Chanditala: R-N, F/D-54.15 km, F/C-4.618 kA |  |  |  |  | 100
[5 empty] | 2021-07-07 09:17 | 2021-07-07 16:59 | 0:00 | 0:00 | 0:00 | 7:42 | S/D AVAILED BY WBSETCL FOR ROW CLEARANCE BY TREE TRIMMING.
[5 empty] | 2021-07-08 09:17 | 2021-07-08 16:13 | 0:00 | 0:00 | 0:00 | 6:56 | S/D AVAILED BY WBSETCL FOR ROW CLEARANCE BY TREE TRIMMING.
[5 empty] | 2021-07-21 11:05 | 2021-07-21 11:05 | 0:00 | 0:00 | 0:00 | 0:00 | A/R Successful at both ends; [ FAULT UNDER WBSETCL JURISDICTION] R/I at Medinipur end: M1: Y-N, Z2, F/D-92.20 km, F/C- 3.15 kA; M2: Y-N, Z2, F/D-119.34 km, F/C- 2.35 kA R/I at Chanditala end: M1: Y-N, Z1, F/D-3.47 km, F/C- 16.36 kA; M2: Y-N, Z1, F/D-3.25 km, F/C- 16.36 kA;
[5 empty] | 2021-07-22 06:05 | 2021-07-22 15:17 | 0:00 | 9:12 | 0:00 | 0:00 | S/D taken by WBSETCL for checking rectification of hotspot near tension tower jumpers at Y-phase & B-phase at tower location no 350.
[5 empty] | TOTAL |  | 0:00 | 9:12 | 0:00 | 14:38
6 | PMJTLL6 | LILO of Kharagpur-Chandital line for Medinipur-Chanditala#2 | 36.79 |  | 2021-07-09 09:14 | 2021-07-09 14:58 | 0:00 | 0:00 | 0:00 | 5:44 | S/D AVAILED BY WBSETCL FOR ROW CLEARANCE BY TREE TRIMMING. |  |  |  |  | 100
[5 empty] | 2021-07-10 09:04 | 2021-07-10 15:56 | 0:00 | 0:00 | 0:00 | 6:52 | S/D AVAILED BY WBSETCL FOR ROW CLEARANCE AND TREE TRIMMING.
[5 empty] | 2021-07-18 22:30 | 2021-07-19 19:22 | 0:00 | 20:52 | 0:00 | 0:00 | TRIPPED due to R-B fault under WBSETCL JURISDICTION. R/I at Medinipur: M1: F/D:73.8kms, Ir:3.989KA, Ib:4.620KA; M2: F/D: 74.12kms, Ir:4.027KA, Ib:4.651KA R/I at Chanditala(WBSETCL): F/D: 17.24kms. Ir: 12.14KA, Ib:11.53KA. Charging attempt taken from Medinipur end at 23:08 hrs on 18.07.21 but TIPPED immediately on SOTF. R/I at Medinipur: M1: F/D:72.7kms, Ir:6.06KA, Ib:6.301KA; M2: F/D: 73.45kms, Ir:6.095KA, Ib:6.161KA Fault is UNDER WBSETCL JURISDICTION. As per information received from Chandita C/R B-ph conductor SNAPPED between Loc 347-348( WBSETCL JURISDICTION) and fallen over 11KV LT line of WBSEDCL. Both end earth switch closed at 02:07 hrs on 19.07.21 vide ERLDC code for breakdown maintenance by WBSETCL.
[5 empty] | TOTAL |  | 0:00 | 20:52 | 0:00 | 12:36
7 | PMJTLT1 | MEDINIPORE-ICT-I | 1500 |  | 2021-07-15 10:07 | 2021-07-15 18:15 | 0:00 | 8:08 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-07-16 09:43 | 2021-07-16 17:29 | 0:00 | 7:46 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD.
[5 empty] | TOTAL |  | 0:00 | 15:54 | 0:00 | 0:00
8 | PMJTLT2 | MEDINIPORE-ICT-II | 1500 |  | 2021-07-20 10:16 | 2021-07-20 14:36 | 0:00 | 4:20 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 23/07/21 10:05 | 23/07/21 17:42 | 0:00 | 7:37 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD
[5 empty] | TOTAL |  | 0:00 | 11:57 | 0:00 | 0:00
9 | PMJTLR1 | MEDINIPORE 330MVAR BUS REACTOR-I | 330 |  | 2021-07-16 00:42 | 2021-07-16 06:18 | 0:00 | 0:00 | 0:00 | 5:36 | H/T as per ERLDC/NLDC instruction for Voltage Regulation. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-07-17 09:44 | 2021-07-17 17:28 | 0:00 | 7:44 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD.
[5 empty] | TOTAL |  | 0:00 | 7:44 | 0:00 | 5:36
10 | PMJTLR2 | MEDINIPORE 330MVAR BUS REACTOR-II | 330 |  | 2021-07-16 21:10 | 2021-07-17 09:42 | 0:00 | 0:00 | 0:00 | 12:32 | H/T as per ERLDC instruction for Voltage Regulation. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-07-21 10:00 | 2021-07-21 18:23 | 0:00 | 8:23 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD.
[5 empty] | TOTAL |  | 0:00 | 8:23 | 0:00 | 12:32
11 | PMJTLR3 | 240 MVAR L/R OF 765 kV MEDINIPORE-RANCHI-I AT MEDINIPORE END | 240 |  | 2021-07-06 09:28 | 2021-07-06 13:00 | 0:00 | 0:00 | 3:32 | 0:00 | During heavy and incessant rain, water droplets entered into PRD contacts and cause tripping. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | TOTAL |  | 0:00 | 0:00 | 3:32 | 0:00
12 | PMJTLR4 | 240 MVAR L/R OF 765 kV MEDINIPORE-RANCHI-II AT MEDINIPORE END | 240 |  | 2021-07-30 02:32 | 2021-07-30 11:36 | 0:00 | 0:00 | 9:04 | 0:00 | Tripped due to heavy and incessant rain in the area causing waterlogging in cable trench |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-07-30 12:13 | 30/07/21 15:10 | 0:00 | 2:57 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD.
[5 empty] | TOTAL |  | 0:00 | 2:57 | 9:04 | 0:00
13 | PMJTLR5 | MEDINIPORE 125MVAR BUS REACTOR-I | 125 |  | 2021-07-25 22:17 | 2021-07-30 03:13 | 0:00 | 0:00 | 0:00 | 100:56 | H/T as per ERLDC instruction for Voltage Regulation. |  |  |  |  | 100
[5 empty] | 2021-07-17 23:26 | 2021-07-21 09:56 | 0:00 | 0:00 | 0:00 | 82:30 | H/T as per ERLDC instruction for Voltage Regulation.
[5 empty] | 2021-07-24 10:34 | 2021-07-24 15:22 | 0:00 | 4:48 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD
[5 empty] | TOTAL |  | 0:00 | 4:48 | 0:00 | 183:26
14 | PMJTLR6 | MEDINIPORE 125MVAR BUS REACTOR-II | 125 |  | 2021-07-25 22:18 | 2021-07-30 03:14 | 0:00 | 0:00 | 0:00 | 100:56 | H/T as per ERLDC instruction for Voltage Regulation. |  |  |  |  | 100 | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
[5 empty] | 2021-07-17 23:28 | 2021-07-21 10:33 | 0:00 | 0:00 | 0:00 | 83:05 | H/T as per ERLDC instruction for Voltage Regulation.
[5 empty] | 2021-07-22 10:00 | 2021-07-22 15:46 | 0:00 | 5:46 | 0:00 | 0:00 | S/D FOR FINAL TUNING OF CSD
[5 empty] | TOTAL |  | 0:00 | 5:46 | 0:00 | 184:01
----- | ----- | ----- | ----- | ----- |  | ----- | ----- |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | ----- |  |  |  |  | ----- | ----- | ----- | ----- | ----- | ----- | ----- | -----
-----
-----
-----
-----
-----