## Cal-internal
AVAILABILITY CALCULATION AS PER CERC GUIDE LINES
For The Month :- January-'2011
A. Transmission Lines : - | [14 empty] | Annexure-II
Sl.No. | Transmission Lines | Line Length (KMs) | NSC | Cktkm* NSC | (Date of Commer-cial Operation) D.O.C.O | Total Hours of line during the period under consi-deration in mns.( a) | Non-avail. of line due to Force Majeure events. (b) Hrs. min |  | (Ti) (a-b) | Non -Avail. of line in Hrs. (Tnal) Attri. to Powergrid Hrs. min |  | OH x Cktkm x NSC | Line wise NAFM | Line wise TAFM | W (Ti-Tnal)/Ti | Element wise % availibility | Others | System | Total
1 | 132KV D/C RC Nagar-Agartala-I | 8.384 | 1 | 8.384 | 01.04.98 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 8.384 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
2 | 132KV D/C RC Nagar-Agartala-II | 8.384 | 1 | 8.384 | 01.04.98 | 40320 | 720 | 10 | -2890 |  |  | 0 | 0 | 100 | 8.384 | 100 | 0:10 | 0:00 | 0:10 | 30 | 0 | 720 | 10
3 | 132KV S/C Badarpur-Kolasib | 107.226 | 1 | 107.226 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 107.226 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
4 | 132KV S/C Kolasib-Aizwal | 66.098 | 1 | 66.098 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 66.098 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
5 | 132 KV S/C Aizwal-Kumarghat | 131 | 1 | 131 | 01.02.89 | 40320 | 727 | 44 | -3344 |  |  | 0 | 0 | 100 | 131 | 100 | 0:00 | 7:44 | 7:44 | 30 | 7 | 727 | 44
6 | 132 KV S/C Aizwal - Zemabawk | 6.719 | 1 | 6.719 | 01.09.88 | 40320 | 720 | 21 | -2901 |  |  | 0 | 0 | 100 | 6.719 | 100 | 0:21 | 0:00 | 0:21 | 30 | 0 | 720 | 21
7 | 132KV S/C Badarpur - Badarpur | 1.023 | 1 | 1.023 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 1.023 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
8 | 132KV S/C Badarpur - Jiribam | 67.21 | 1 | 67.21 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 67.21 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
9 | 132 KV S/C Badarpur - Khliehriat | 76.646 | 1 | 76.646 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 76.646 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
10 | 132kV S/C Badarpur-Kumarghat | 118.513 | 1 | 118.513 | 01.04.00 | 40320 | 721 | 55 | -2995 |  |  | 0 | 0 | 100 | 118.513 | 100 | 0:00 | 1:55 | 1:55 | 30 | 1 | 721 | 55
11 | 132 KV S/C Dimapur - Imphal | 168.865 | 1 | 168.865 | 01.04.97 | 40320 | 722 | 55 | -3055 | 1 | 33 | 15704.445 | -0.030442 | 103.0442 | 174.0056 | 103.0442 | 0:00 | 2:55 | 2:55 | 30 | 2 | 722 | 55
12 | 132KV D/C Doyang - Dimapur-I | 92.526 | 1 | 92.526 | 01.04.97 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 92.526 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
13 | 132KV D/C Doyang - Dimapur-II | 92.526 | 1 | 92.526 | 01.04.97 | 40320 | 720 | 12 | -2892 |  |  | 0 | 0 | 100 | 92.526 | 100 | 0:00 | 0:12 | 0:12 | 30 | 0 | 720 | 12
14 | 132KV S/C Gohpur - Nirjuli | 42.5 | 1 | 42.5 | 01.07.91 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 42.5 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
15 | 132 KV S/C Imphal - Imphal-I | 1.5 | 1 | 1.5 | 01.04.97 | 40320 | 721 | 27 | -2967 |  |  | 0 | 0 | 100 | 1.5 | 100 | 1:27 | 0:00 | 1:27 | 30 | 1 | 721 | 27
16 | 132KV S/C Imphal-Ningthoukong(State) | 0.442 | 1 | 0.442 | 01.04.13 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 0.442 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
17 | 132 KV S/C Imphal - Imphal-II | 0.339 | 1 | 0.339 | 01.09.13 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 0.339 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
18 | 132 KV S/C Jiribam - Aizwal | 172.315 | 1 | 172.315 | 01.09.88 | 40320 | 720 | 8 | -2888 |  |  | 0 | 0 | 100 | 172.315 | 100 | 0:00 | 0:08 | 0:08 | 30 | 0 | 720 | 8
19 | 132 KV S/C Jiribam-Haflong | 100.63 | 1 | 100.63 | 01.08.87 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 100.63 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
20 | 132KV S/C Jiribam - Loktak-II | 82.4 | 1 | 82.4 | 01.07.89 | 40320 | 720 | 38 | -2918 |  |  | 0 | 0 | 100 | 82.4 | 100 | 0:38 | 0:00 | 0:38 | 30 | 0 | 720 | 38
21 | 132KV S/C Khandong - Haflong | 63.166 | 1 | 63.166 | 01.10.87 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 63.166 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
22 | 132 KV S/C Khandong - Khliehriat-I | 42.48 | 1 | 42.48 | 01.03.84 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 42.48 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
23 | 132 KV S/C Khandong - Khliehriat-II | 40.933 | 1 | 40.933 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 40.933 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
24 | 132 KV S/C Khandong - Kopili -I | 10.914 | 1 | 10.914 | 01.03.84 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 10.914 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
25 | 132 KV S/C Khandong - Kopili - II | 11.56 | 1 | 11.56 | 01.11.10 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 11.56 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
26 | 132 KV S/C Khliehriat-Khliehriat | 7.801 | 1 | 7.801 | 01.02.00 | 40320 | 720 | 54 | -2934 |  |  | 0 | 0 | 100 | 7.801 | 100 | 0:54 | 0:00 | 0:54 | 30 | 0 | 720 | 54
27 | 132kV S/C Kumarghat-R.C.Nagar | 104.02 | 1 | 104.02 | 01.01.01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 104.02 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
28 | 132 KV S/C Loktak - Imphal-II | 35.04 | 1 | 35.04 | 01.07.83 | 40320 | 725 | 55 | -3235 |  |  | 0 | 0 | 100 | 35.04 | 100 | 5:55 | 0:00 | 5:55 | 30 | 5 | 725 | 55
29 | 132KV S/C Nirjuli-Ranganadi | 22.29 | 1 | 22.29 | 2001-10-01 | 40320 | 464 | 14 | 12466 |  |  | 0 | 0 | 100 | 22.29 | 100 | 488:14 | 0:00 | 488:14 | 19 | 8 | 464 | 14
30 | 132KV S/C Ranganadi-Ziro | 44.523 | 1 | 44.523 | 2004-04-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 44.523 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
31 | 132 KV Dimapur(PG)-Kohima(LILO portion) | 0.347 | 1 | 0.347 | 2011-04-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 0.347 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
32 | 132KV Dimapur(PG)-Dimapur(LILO portion) | 0.347 | 1 | 0.347 | 2011-04-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 0.347 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
33 | 132KV Silchar-Srikona-I | 1.199 | 1 | 1.199 | 2012-04-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 1.199 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
34 | 132KV Silchar-Srikona-II | 1.199 | 1 | 1.199 | 2012-04-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 1.199 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
35 | 132KV Silchar-Badarpur-I | 19.195 | 1 | 19.195 | 2012-05-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 19.195 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
36 | 132KV Silchar-Badarpur-II | 19.195 | 1 | 19.195 | 2012-05-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 19.195 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
37 | 132KV Silchar-Hailkandi-I | 17.3 | 1 | 17.3 | 2012-07-01 | 40320 | 731 | 21 | -3561 |  |  | 0 | 0 | 100 | 17.3 | 100 | 11:21 | 0:00 | 11:21 | 30 | 11 | 731 | 21
38 | 132KV Silchar-Hailkandi-II | 17.3 | 1 | 17.3 | 2012-07-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 17.3 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
39 | 220 KV S/C Balipara-Tezpur | 8.623 | 1 | 8.623 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 8.623 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
40 | 220 KV D/C Misa-Dimapur-I | 123.52 | 1 | 123.52 | 01.04.96 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 123.52 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
41 | 220 KV D/C Misa-Dimapur-II | 123.52 | 1 | 123.52 | 01.04.96 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 123.52 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
42 | 220 KV D/C Misa-Kopili - I | 72.791 | 1 | 72.791 | 01.03.84 | 40320 | 721 | 30 | -2970 |  |  | 0 | 0 | 100 | 72.791 | 100 | 0:00 | 1:30 | 1:30 | 30 | 1 | 721 | 30
43 | 220 KV D/C Misa-Kopili - II | 72.791 | 1 | 72.791 | 01.02.88 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 72.791 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
44 | 220 KV Misa-Kopili-III. | 75.788 | 1 | 75.788 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 75.788 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
45 | 220 KV D/C Misa-Samaguri-I | 34.439 | 1 | 34.439 | 01.03.84 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 34.439 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
46 | 220 KV D/C Misa-Samaguri-II | 34.439 | 1 | 34.439 | 01.02.88 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 34.439 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
47 | 400 KV D/C Misa- Mariani | 220 | 2 | 440 | 01.04.98 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 440 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
48 | 400 KV D/C Kathalguri-Mariani | 162.864 | 2 | 325.728 | 01.08.95 | 40320 | 720 | 0 | -2880 |  | 18 | 5863.104 | -0.00625 | 100.625 | 327.7638 | 100.625 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
49 | 400 KV D/C Misa- Mariani(new) | 222.682 | 2 | 445.364 | 01.04.98 | 40320 | 200 | 55 | 28265 |  |  | 0 | 0 | 100 | 445.364 | 100 | 0:00 | 224:55 | 224:55 | 8 | 8 | 200 | 55
50 | 400 KV D/C Kathalguri-Mariani(new) | 160.536 | 2 | 321.072 | 01.04.98 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 321.072 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
51 | 400 KV D/C Balipara-Bongaigaon-I | 289.721 | 2 | 579.442 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 579.442 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
52 | 400 KV D/C Balipara-Bongaigaon-II | 289.721 | 2 | 579.442 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 579.442 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
53 | 400 KV D/C Misa-Balipara-I | 95.407 | 2 | 190.814 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 190.814 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
54 | 400 KV D/C Misa-Balipara-II | 95.407 | 2 | 190.814 | 01.02.00 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 190.814 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
55 | 400KV D/C Balipara-Ranganadi-I | 166.335 | 2 | 332.67 | 2003-01-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 332.67 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
56 | 400KV D/C Balipara-Ranganadi-II | 166.335 | 2 | 332.67 | 2003-01-01 | 40320 | 724 | 20 | -3140 |  |  | 0 | 0 | 100 | 332.67 | 100 | 0:00 | 4:20 | 4:20 | 30 | 4 | 724 | 20
57 | 400KV D/C Pallatana-SurjamaniNagar-I | 37.2 | 2 | 74.4 | 2012-07-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 74.4 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
58 | 400KV D/C Pallatana-SurjamaniNagar-II | 37.2 | 2 | 74.4 | 2012-07-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 74.4 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
59 | 400 KV D/C BTPS-Bongaigaon-I | 3.119 | 2 | 6.238 | 2013-01-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 6.238 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
60 | 400 KV D/C BTPS-Bongaigaon-II | 3.119 | 2 | 6.238 | 2013-01-01 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 6.238 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
|  | 4299.612 |  | 6249.258 |  | 2419200 | 42464 | 39 | -128679 | 1 | 51 | 21567.549 | -0.036692 | 103.6692 |  |  | 509:00 | 243:39 | 752:39 |  |  | 39584 | 39
B. ICTs : -
61 | ICT at Bongaigaon | 315 | 2.5 | 787.5 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 787.5 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
62 | ICT at Balipara | 315 | 2.5 | 787.5 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 787.5 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
63 | ICT-I at Misa | 315 | 2.5 | 787.5 | 01.02.2000 | 40320 | 720 | 0 | -2880 | 1 | 3 | 49612.5 | -0.021875 | 102.1875 | 804.7266 | 102.1875 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
64 | ICT-II at Misa | 315 | 2.5 | 787.5 | 01.07.2012 | 40320 | 0 | 0 | 40320 | 8 | 44 | 412650 | 0.012996 | 98.7004 | 777.2656 | 98.7004 | 0:00 | 0:00 | 0:00
65 | ICT at Salakati | 50 | 2.5 | 125 | 14.08.1992 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 125 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
66 | ICT-I at Dimapur | 100 | 2.5 | 250 | 01.04.1994 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 250 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
67 | ICT-II at Dimapur | 100 | 2.5 | 250 | 2011-01-01 | 40320 | 0 | 0 | 40320 |  |  | 0 | 0 | 100 | 250 | 100 | 0:00 | 0:00 | 0:00
68 | ICT at Ziro | 15 | 2.5 | 37.5 | 01.04.2004 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 37.5 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
69 | ICT at Kumarghat | 5 | 2.5 | 12.5 | 05.05.1987 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 12.5 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
70 | ICT-I at Nirjuli | 10 | 2.5 | 25 | 09.01.2009 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 25 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
71 | ICT-II at Nirjuli | 10 | 2.5 | 25 | 20.10.1991 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 25 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
72 | ICT-I at Imphal | 50 | 2.5 | 125 | 01.04.2013 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 125 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
73 | ICT-II at Imphal | 50 | 2.5 | 125 | 01.05.2013 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 125 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
74 | ICT at Kopili | 160 | 2.5 | 400 | 01.02.2010 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 400 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
75 | ICT-I at Silchar | 200 | 2.5 | 500 | 01.07.2012 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 500 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
76 | ICT-II at Silchar | 200 | 2.5 | 500 | 01.07.2012 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 500 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
|  |  |  | 5525 |  | 645120 | 10080 | 0 | 40320 | 9 | 47 | 462262.5 | -0.008879 | 100.8879 |  |  | 0:00 | 0:00 | 0:00 |  |  | 8640 | 0
C. BRs : -
77 | Reactor-I at Bongaigaon SS | 50 | 4 | 200 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 200 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
78 | Reactor-II at Bongaigaon SS | 50 | 4 | 200 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 200 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
79 | Reactor-III at Bongaigaon SS | 80 | 4 | 320 | 01.11.2012 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 320 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
80 | Reactor-IV at Bongaigaon SS | 80 | 4 | 320 | 01.02.2013 | 40320 | 720 | 0 | -2880 |  |  | 0 |  |  | 320 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
81 | Reactor-I at Silchar S/s | 63 | 4 | 252 | 01.07.2012 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 252 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
82 | Reactor-II at Silchar S/s | 63 | 4 | 252 | 01.07.2012 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 252 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
83 | Reactor-I at Balipara SS | 50 | 4 | 200 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 200 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
84 | Reactor-II at Balipara SS | 80 | 4 | 320 | 01.10.2012 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 320 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
85 | Misa SS | 50 | 4 | 200 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 200 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
86 | Mariani Ss | 20 | 4 | 80 | 01.04.2013 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 80 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
87 | Kumarghat SS | 20 | 4 | 80 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 80 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
88 | Aizwal SS | 20 | 4 | 80 | 01.02.2000 | 40320 | 720 | 0 | -2880 |  |  | 0 | 0 | 100 | 80 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
89 | Ziro SS | 20 | 4 | 80 | 01.02.2013 | 40320 | 720 | 0 | -2880 |  |  | 0 |  |  | 80 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
90 | Imphal SS | 20 | 4 | 80 | 01.03.2013 | 40320 | 720 | 0 | -2880 |  |  | 1 |  |  | 80 | 100 | 0:00 | 0:00 | 0:00 | 30 | 0 | 720 | 0
|  |  |  | 2664 |  | 564480 | 10080 | 0 | -40320 | 0 | 0 | 1101 | 0 | 100 | 2664 |  | 0:00 | 0:00 | 0:00 | 10080:00 | 0:00 | 10080 | 0:00
| No of days in month | 28
| Total elements | 90
| THM | -1429.7667
NAFM =
Sum (Outage hours attributable to PG x Ckm x NSC) + Sum (Outage hours x MVA x 2.5 ) + Sum (Outage hours x MVAR x 4 )
THM x [Sum (Ckm x NSC) + Sum (MVA x 2.5) + Sum (MVAR x 4)]
|  | = | -0.023491
| TAFM | = | [ 100 - (100 x NAFM)]
|  | = | 102.3491
| Availability for the month of Feb-14 |  | = | 102.3491 | %
Comments
The formula for calculation of overall availaiblity is
| NAFM | = | Sum (Outage hours attributable to PG x Ckm x NSC) + Sum (Outage hours x MVA x 2.5 ) + Sum (Outage hours x MVAR x 4 )
THM x Sum of all weightage
Kind Attn : Sh. Pulakesh Roy
The calculation forwarded by you is generally OK
However for clarity while submitting to RPC, first you can do separate sum for all lines, all ICTs and all Bus reactors etc. then do
overall sum for all elements for calculation of overall availability.
THM - by definition it is the total hours in a month. In your calculation, you have deducted the outages under clause 6(i) & (ii)
practically this is the procedure. But the formula says total hours in a month, there is no mention about net overall hours in a month.
It is not clear. Other regions considering the way you have considered.
Column 'N' & 'O' not required. If you keep it there is no harm.
Heading of 'M' to be changed
Consideration of elements
For RPC purpose - Salakati - BTPC both ckts and Salakati - Geylegphug lines not to be considered as was done earlier
For internal purpose these elements are to be considered.