## Table-II
II. Elements where restoration time has exceeded the standards specified in Regulation 5 (b).
MONTH | S.No | Element Name | Restoration time as specified in Regulation 5 (b) (in days) | Actual restoration time (in days)
2018-04-01 |  | NOT APPLICABLE
2018-05-01 |  | NOT APPLICABLE
2018-06-01 |  | NOT APPLICABLE
2018-07-01 |  | NOT APPLICABLE
2018-08-01 |  | NOT APPLICABLE
2018-09-01 |  | NOT APPLICABLE

## Table-III
III. Details of compensation paid by the inter-State transmission licensee
MONTH | Element Name | Violation of Regulation 5 (a) |  | Violation of Regulation 5 (b) |  | Compensation paid (in `)
2018-04-01 |  | % Availability prescribed | Actual % Availability | Restoration time prescribed (in days) | Actual restoration time (in days)
2018-05-01 | NOT APPLICABLE
2018-06-01 | NOT APPLICABLE
2018-07-01 | NOT APPLICABLE
2018-08-01 | NOT APPLICABLE
2018-09-01 | NOT APPLICABLE

## APRIL 2018 - TABLE I
Unique ID of transmission Element | Element Name |  | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee Hr min |  | OTHERS Hr min |  | System Constraints/ Natural calamity / Militancy Hr min |  | Deemed Available Hr min
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-04-03 09:27 | 43193.3938 | 2018-04-03 15:52 | 43193.6611 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 25 | N/A | N/A | N/A | EMERGENCY S/D TAKEN FOR OP[GW WORK | NERPC/OP/TAC/2018-19/2130 dtd 23.07.2018 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 25
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region |  | 2018-04-03 09:33 | 43193.3979 | 2018-04-03 16:22 | 43193.6819 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 49 | N/A | N/A | N/A | E/S/D TAKEN FOR OPGW STRINGING WORKS |  | 99.55
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region |  | 2018-04-24 11:40 | 43214.4861 | 2018-04-24 14:56 | 43214.6222 | -- | -- | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN GOR HOTSPOT RECTIFICATION AT RCNAGAR BAY B-PH BUS ISOLATOR AT AGARTALA.
[6 empty] | Sub Total --> | [6 empty] | 3 | 16 | 0 | 0 | 0 | 0 | 6 | 49
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-04-08 15:18 | 43198.6375 | 2018-04-08 15:47 | 43198.6576 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AND THUNDERSTORM AS SUPPORTED BY BADARPUR END DR |  | 98.72
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-04-09 08:56 | 43199.3722 | 2018-04-09 18:10 | 43199.7569 | -- | -- | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN FOR C & TAN DELTA TESTING OF CT & REPLACMENT OF CT MARSHALLING BOX
[6 empty] | Sub Total --> | [6 empty] | 9 | 14 | 0 | 0 | 0 | 29 | 0 | 0
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-04-04 08:09 | 43194.3396 | 2018-04-04 17:56 | 43194.7472 | -- | -- | 0 | 9 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | INFRINGEMENT CLEARANCE BETWEEN LOC 72-73,76-79,83-91 & 110-115 |  | 98.52
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-04-19 10:15 | 43209.4271 | 2018-04-19 14:53 | 43209.6201 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 38 | N/A | N/A | N/A | S/D TAKEN FOR TESTING PURPOSE OF NTAMC ADAPTION WORKS.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region | Conductor grounded | 2018-04-23 10:18 | 43213.4292 | 2018-04-25 11:58 | 43215.4986 | -- | -- | 2 | 0 | 0 | 0 | 0 | 49 | 40 | 0 | 0 | 3 | N | -1 | Y-PH CONDUCTOR GROUNDED DUE TO FALLING OF TREE FROM UPHILL, CUT BY UNKNOWN MISCREANTS B/W LOC 34-35.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-04-26 10:03 | 43216.4187 | 2018-04-26 16:08 | 43216.6722 | -- | -- | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR PERMANENT RECTIFICATION OF OPGW B/W LOC. NO. 34-35, TREE CUT BY MISCREANTS.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region | Conductor snapped | 2018-04-29 07:54 | 43219.3292 | 2018-04-29 11:50 | 43219.4931 | -- | -- | 0 | 0 | 0 | 0 | 0 | 3 | 56 | 0 | 0 | 3 | N | -3 | TREE FROM OUTSIDE LINE CORRIDOR FELL ON R & B-PH CONDUCTOR AT LOC 7-8 DUE TO THUNDERSTORM.
[6 empty] | Sub Total --> | [6 empty] | 9 | 47 | 0 | 0 | 59 | 42 | 4 | 38
NER L105 | AIZWAL_ZEMEBAK | # 2 | 6.719 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-04-13 08:34 | 43203.3569 | 2018-04-13 18:58 | 43203.7903 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | N/A | N/A | N/A | BAY UPGRADATION WORK-CT MB REPLACEMENT |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24
NER L107 | BADARPUR_JIRIBAM |  | 67.21 | North Eastern Region |  | 2018-04-01 | 43191 | 2018-04-01 16:17 | 43191.6785 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | N/A | N/A | N/A | SHUTDOWN TAKEN FOR STRINGING OF 400KV SILCHAR-MELRIAT LINE |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region |  | 2018-04-17 11:35 | 43207.4826 | 2018-04-17 11:48 | 43207.4917 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 3 | N | -3 | BAMBOO FROM OUTSIDE LINE CORRIDOR CAME IN PROXIMITY TO R-PH CONDUCTOR DUE TO STORM AT LOC 41-50 |  | 99.13
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region |  | 2018-04-21 10:22 | 43211.4319 | 2018-04-21 16:26 | 43211.6847 | -- | -- | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP ACTIVITIES.
[6 empty] | Sub Total --> | [6 empty] | 6 | 4 | 0 | 0 | 0 | 13 | 0 | 0
NER L109 | BADARPUR_KUMARGHAT |  | 118.513 | North Eastern Region |  | 2018-04-10 08:49 | 43200.3674 | 2018-04-10 19:51 | 43200.8271 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2 | N/A | N/A | N/A | SD TAKEN FOR RETROFITTING OF OLD DISTANCE PROTECTION RELAY WITH NEW ONE |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-04-05 11:05 | 43195.4618 | 2018-04-05 11:14 | 43195.4681 | -- | -- | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRANSIENT E/F |  | 98.86
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-04-09 09:46 | 43199.4069 | 2018-04-09 15:49 | 43199.659 | -- | -- | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO JHOOM FIRE AT LOC 365-366
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-04-11 07:56 | 43201.3306 | 2018-04-11 15:38 | 43201.6514 | -- | -- | 0 | 0 | 0 | 7 | 42 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FLASHOVER WITH UNDER CROSSING 33KV STATE LINE B/W LOC 327-373
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region | Line isolator sparking | 2018-04-12 10:52 | 43202.4528 | 2018-04-12 18:44 | 43202.7806 | -- | -- | 0 | 7 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ATTENDING HEAVY SPARKING IN LINE ISOLATOR OF IMPHAL BAY AT DIMAPUR
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-04-14 12:45 | 43204.5312 | 2018-04-14 13:05 | 43204.5451 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | N/A | N/A | N/A | TRIPPING DUE TO TREE FELLING BY MISCREANTS AT LOC 171-172
[6 empty] | Sub Total --> | [6 empty] | 8 | 1 | 7 | 42 | 6 | 23 | 0 | 0
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region | Insulator punctured | 2018-04-11 15:06 | 43201.6292 | 2018-04-11 15:43 | 43201.6549 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 2 | N | -2 | TRIPPED DUE TO LIGHTNING AS FLASHOVER MARKS ARE OBSERED AT LOC 84 ON R-PH INSULATOR STRINGS |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-04-09 15:11 | 43199.6326 | 2018-04-09 15:55 | 43199.6632 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO JHUM FIER AT LOC 134-135 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-16 09:10 | 43206.3819 | 2018-04-16 17:51 | 43206.7438 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 41 | N/A | N/A | N/A | SD FOR RECONDUCTORING OF EXISTING PANTHER CONDUCTOR BY HTLS CONDUCTOR |  | 100
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-17 08:49 | 43207.3674 | 2018-04-17 17:34 | 43207.7319 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 45 | N/A | N/A | N/A | S/D FOR RECONDUCTORING OF EXISITNG PANTHER CONDUCTOR BY HTLS CONDUCTOR
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-18 08:46 | 43208.3653 | 2018-04-18 16:18 | 43208.6792 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 32 | N/A | N/A | N/A | SD FOR RECONDUCTORING OF EXISTING PANTHER CONDUCTOR BY HTLS CONDUCTOR
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-19 08:37 | 43209.359 | 2018-04-19 15:44 | 43209.6556 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | N/A | N/A | N/A | S/D FOR RECONDUCTORING OF EXISITNG PANTHER CONDUCTOR BY HTLS CONDUCTOR.
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-20 08:43 | 43210.3632 | 2018-04-20 17:36 | 43210.7333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 53 | N/A | N/A | N/A | S/D FOR RE-CONDUCTORING OF EXISTING PANTHER CONDUCTOR BY HTLS CONDUCTOR.
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-21 10:14 | 43211.4264 | 2018-04-21 16:11 | 43211.6743 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57 | N/A | N/A | N/A | S/D FOR RE-CONDUCTORING OF EXISTING PANTHER CONDUCTOR BY HTLS CONDUCTOR.
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-22 08:28 | 43212.3528 | 2018-04-22 16:49 | 43212.7007 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | N/A | N/A | N/A | S/D FOR RE-CONDUCTORING OF EXISTING PANTHER CONDUCTOR BY HTLS CONDUCTOR.
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-04-23 08:38 | 43213.3597 | 2018-04-23 17:42 | 43213.7375 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | N/A | N/A | N/A | S/D FOR RE-CONDUCTORING OF EXISTING PANTHER CONDUCTOR BY HTLS CONDUCTOR.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 20
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-04-01 | 43191 | 2018-04-02 23:14 | 43192.9681 | -- | -- | 2 | 0 | 0 | 0 | 0 | 47 | 14 | 0 | 0 | 3 | N | -1 | TREE FELLED BETWEEN LOC 211-212 |  | 97.78
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-04-03 05:00 | 43193.2083 | 2018-04-03 19:36 | 43193.8167 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 14 | 36 | 0 | 0 | N/A | N/A | N/A | S/D FOR INFRINGEMENT CLEARANCE BETWEEN LOC 234-260
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-04-05 15:05 | 43195.6285 | 2018-04-05 15:14 | 43195.6347 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO THUNDESTORMA AND LIGHTNING AS SUPPORTED BY DR
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-04-06 08:59 | 43196.3743 | 2018-04-06 15:12 | 43196.6333 | -- | -- | 0 | 0 | 0 | 0 | 0 | 6 | 13 | 0 | 0 | N/A | N/A | N/A | ESD AVAILED FOR CLEARING OF BAMBOO WHICH SLIPPED INTO LINE PROXIMITY DUE TO LANDSLIDE B/W LOC189-190
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-04-14 07:25 | 43204.309 | 2018-04-14 07:45 | 43204.3229 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 3 | N | -3 | A TWIG WAS FOUND HANGING FROM R-PH CONDUCTOR BETWEEN LOC 29-30
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-04-14 08:02 | 43204.3347 | 2018-04-14 17:22 | 43204.7236 | -- | -- | 0 | 0 | 0 | 9 | 20 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY STATE FOR TESTING OF TIPAIMUKH
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 9 | 20 | 68 | 32 | 0 | 0
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region |  | 2018-04-02 13:44 | 43192.5722 | 2018-04-02 17:52 | 43192.7444 | -- | -- | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN TO ATTEND SPARKING AT R-PH CT TERMINAL CONNECTOR OF 132KV JIRIBAM BAY AT HAFLONG SS |  | 99.43
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region |  | 2018-04-03 15:59 | 43193.666 | 2018-04-03 16:15 | 43193.6771 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | N/A | N/A | N/A | FOREST FIRE OBSERVED BETWEEN LOC 281-282
[6 empty] | Sub Total --> | [6 empty] | 4 | 8 | 0 | 0 | 0 | 16 | 0 | 0
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-04-04 09:16 | 43194.3861 | 2018-04-04 14:12 | 43194.5917 | -- | -- | 0 | 0 | 0 | 4 | 56 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY LOKTAK END |  | 99.94
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-04-11 15:53 | 43201.6618 | 2018-04-11 16:19 | 43201.6799 | -- | -- | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRANSIENT FAULT
[6 empty] | Sub Total --> | [6 empty] | 0 | 26 | 4 | 56 | 0 | 0 | 0 | 0
NER L118 | KHANDONG-HAFLONG |  | 63.166 | North Eastern Region |  | 2018-04-07 07:30 | 43197.3125 | 2018-04-07 17:50 | 43197.7431 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | N/A | N/A | N/A | SD AVAILED FOR REPLACEMENT OF INSULATORS |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-04-14 04:17 | 43204.1785 | 2018-04-14 04:55 | 43204.2049 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | N/A | N/A | N/A | TRIPPING DUE TO LIGHTNING AND HEAVY THUNDERSTORM AS CONCLUDED FROM DR & WEATHER REPORT |  | 100
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-04-16 13:16 | 43206.5528 | 2018-04-16 13:31 | 43206.5632 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AND THUNDERSHOWERS AS SUPPORTED BY DR AND WEATHER REPORT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-04-14 04:35 | 43204.191 | 2018-04-14 04:56 | 43204.2056 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AND HEAVY THUNDERSTORM AS CONCLUDED FROM WEATHER REPORT |  | 99.95
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-04-16 13:14 | 43206.5514 | 2018-04-16 13:34 | 43206.5653 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AND THUNDERSHOWER AS SUPPORTED BY DR AND WEATHER REPORT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0
NER L121 | KHANDONG_KOPILI | # 1 | 10.914 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region |  | 2018-04-29 02:13 | 43219.0924 | 2018-04-29 02:36 | 43219.1083 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO THEN PREVAILING INCLEMENT WEATHER NEAR KHLIEHRIAT END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region |  | 2018-04-05 12:21 | 43195.5146 | 2018-04-05 12:38 | 43195.5264 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO INCLEMENT WEATHER ACCOMPANIED BY INTENSE LIGHTNING. DR INDICATES LIGNTNING FAULT |  | 100
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region | Insulator punctured | 2018-04-12 03:07 | 43202.1299 | 2018-04-12 03:32 | 43202.1472 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | N | -2 | TRIPPED DUE TO LIGHTNING AS CONFIRMED BY FLASH OVER MARKS AT LOC 181 R-PH INSULATORS
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region |  | 2018-04-27 03:11 | 43217.1326 | 2018-04-27 03:40 | 43217.1528 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | N/A | N/A | N/A | K'GHT: RY-PH, Z-2, 87.41KM; RCN: O/C. TRIPPED DUE TO INCLEMENT WEATHER OVER THE REGION.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 11 | 0 | 0
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L125 | SALAKATI-GELEPHUG |  | 49.217 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L126 | LEKHI - RANGANADI |  | 12.59 | North Eastern Region |  | 2018-04-25 13:08 | 43215.5472 | 2018-04-25 13:55 | 43215.5799 | -- | -- | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY NEEPCO ( PARE). |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-04-20 10:05 | 43210.4201 | 2018-04-20 16:10 | 43210.6736 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | N/A | N/A | N/A | S/D TAKEN FOR TESTING PURPOSE OF NTAMC ADAPTATION WORKS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-04-26 21:31 | 43216.8965 | 2018-04-26 22:25 | 43216.934 | -- | -- | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LINE H/T UPON 33KV KIMING FEEDER CATCHING FIRE IN THE PANELS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0
NER L130 | KHANDONG_KOPILI | # 2 | 11.56 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region |  | 2018-04-05 07:58 | 43195.3319 | 2018-04-05 18:05 | 43195.7535 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | N/A | N/A | N/A | LINE H/T FOR FACILATING 132KV BUS-I & HUS-II SD AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 100
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region |  | 2018-04-28 09:05 | 43218.3785 | 2018-04-28 17:06 | 43218.7125 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region |  | 2018-04-29 08:44 | 43219.3639 | 2018-04-29 16:43 | 43219.6965 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 59 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 7
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region |  | 2018-04-05 07:58 | 43195.3319 | 2018-04-05 16:41 | 43195.6951 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-IU & II SD AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 100
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region |  | 2018-04-28 09:05 | 43218.3785 | 2018-04-28 17:06 | 43218.7125 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region |  | 2018-04-29 08:44 | 43219.3639 | 2018-04-29 16:43 | 43219.6965 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 59 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 43
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region |  | 2018-04-05 07:15 | 43195.3021 | 2018-04-05 16:52 | 43195.7028 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 37 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I & II S/D AT SILCHR UNDER NERSS CONSTRUCTION PROJECT |  | 100
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region |  | 2018-04-28 08:53 | 43218.3701 | 2018-04-28 17:02 | 43218.7097 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region |  | 2018-04-29 08:43 | 43219.3632 | 2018-04-29 16:45 | 43219.6979 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region |  | 2018-04-05 07:16 | 43195.3028 | 2018-04-05 16:52 | 43195.7028 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 36 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I & II S/D AT SILCHAR UNDER NERSS PROJECT |  | 100
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region |  | 2018-04-28 08:54 | 43218.3708 | 2018-04-28 17:02 | 43218.7097 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region |  | 2018-04-29 08:43 | 43219.3632 | 2018-04-29 16:45 | 43219.6979 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 46
NER L137 | IMPHAL-IMPHAL | # 2 | 0.442 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L138 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-04-05 07:12 | 43195.3 | 2018-04-05 16:56 | 43195.7056 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 44 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 99.54
NER L138 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-04-08 08:41 | 43198.3618 | 2018-04-08 15:25 | 43198.6424 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 44 | N/A | N/A | N/A | HT FOR POWER REGULATION TO FACILITIATE ICT-2 SD AT SILCHAR UNDER NERSS ACTIVITY
NER L138 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-04-17 11:19 | 43207.4715 | 2018-04-17 14:36 | 43207.6083 | -- | -- | 0 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ATTENDING HOTSPOT NEARLOC NO 54/0 AND 53B/0
NER L138 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-04-28 08:39 | 43218.3604 | 2018-04-28 17:22 | 43218.7236 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L138 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-04-29 08:24 | 43219.35 | 2018-04-29 16:47 | 43219.6993 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 3 | 17 | 0 | 0 | 0 | 0 | 17 | 6
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-04-05 07:13 | 43195.3007 | 2018-04-05 16:56 | 43195.7056 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 43 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I & II AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 100
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-04-08 08:41 | 43198.3618 | 2018-04-08 15:19 | 43198.6382 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 38 | N/A | N/A | N/A | HT FOR POWER REGULATION TO FACILITATE ICT 2 SD AT SILCHAR UNDER NERSS CONSTRUCTION ACTIVITY
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-04-28 08:40 | 43218.3611 | 2018-04-28 17:23 | 43218.7243 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-04-29 08:24 | 43219.35 | 2018-04-29 16:47 | 43219.6993 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L142 | B.CHARAILI_PAVOI | #1 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L143 | B.CHARAILI_PAVOI | #2 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L144 | ROING_PASIGHAT |  |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L146 | AIZAWL MELRIAT |  |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NERL147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-08 07:10 | 43198.2986 | 2018-04-08 18:26 | 43198.7681 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16 | N/A | N/A | N/A | SD AVAILED FOR MASS REPLACMENT OF POLYMER INSULATOR |  | 100
NERL147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-09 07:05 | 43199.2951 | 2018-04-09 18:05 | 43199.7535 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | N/A | N/A | N/A | SD AVAILED FOR MASS EEPLACEMNT OF EXISTING INSULATORS WITH POLYMER INSULATORS |  | 100
NERL147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-10 09:20 | 43200.3889 | 2018-04-10 18:11 | 43200.7576 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 51 | N/A | N/A | N/A | SD AVAILED FOR MASS REPLACMENT OF POLYMER INSULATOR |  | 100
NERL147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-11 07:03 | 43201.2937 | 2018-04-11 18:27 | 43201.7688 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 24 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF POLYMER INSULATOR |  | 100
NERL147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-12 07:03 | 43202.2937 | 2018-04-12 17:54 | 43202.7458 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51 | N/A | N/A | N/A | SD AVAILED FOR MASS REPLACMENT OF POLYMER INSULATORS |  | 100
NERL147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-13 07:12 | 43203.3 | 2018-04-13 19:06 | 43203.7958 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 54 | N/A | N/A | N/A | S/D TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16
NERL149 | KHANGDONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-15 07:07 | 43205.2965 | 2018-04-15 18:37 | 43205.7757 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | N/A | N/A | N/A | S/D TAKEN FOR REPALCMENT OF DISC INSULATOR WITH POLYMER INSULATOR |  | 100
NERL149 | KHANGDONG-UMRANGSO |  |  | North Eastern Region |  | 2018-04-16 07:40 | 43206.3194 | 2018-04-16 16:40 | 43206.6944 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | N/A | N/A | N/A | SD TAKEN FOR REPLACMENT OF DSC INSULATOR WITH POLYMER INSULATOR |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L202 | KATHALGURI_MARIANI(OLD) |  | 162.864 | North Eastern Region |  | 2018-04-10 06:03 | 43200.2521 | 2018-04-10 14:15 | 43200.5938 | -- | -- | 0 | 0 | 0 | 8 | 12 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY OLD MARIANI-STATE END |  | 100
NER L202 | KATHALGURI_MARIANI(OLD) |  | 162.864 | North Eastern Region |  | 2018-04-11 08:48 | 43201.3667 | 2018-04-11 09:33 | 43201.3979 | -- | -- | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | FAULT IN 132KV NAMRUP-MARIANI STATE LINE
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 8 | 57 | 0 | 0 | 0 | 0
NER L203 | MISA_DIMAPUR | # 1 | 123.52 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L204 | MISA_DIMAPUR | # 2 | 123.52 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L205 | MISA_KATHALGURI |  | 382.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L206 | MISA-KOPILI | # 1 | 72.791 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L207 | MISA_KOPILI | # 2 | 72.791 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L208 | MISA_KOPILI | # 3 | 75.788 | North Eastern Region |  | 2018-04-06 14:22 | 43196.5986 | 2018-04-06 14:49 | 43196.6174 | -- | -- | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY NEEPCO |  | 100
NER L208 | MISA_KOPILI | # 3 | 75.788 | North Eastern Region |  | 2018-04-10 11:33 | 43200.4812 | 2018-04-10 13:16 | 43200.5528 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 43 | 0 | 0 | N/A | N/A | N/A | ESD TAKEN FOR REMOVAL OF KITE THREADS AT LOC 188-189
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27 | 1 | 43 | 0 | 0
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region |  | 2018-04-10 06:41 | 43200.2785 | 2018-04-10 11:09 | 43200.4646 | -- | -- | 0 | 0 | 0 | 4 | 28 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY OLD MARIANI STATE END |  | 98.93
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region |  | 2018-04-11 08:48 | 43201.3667 | 2018-04-11 09:18 | 43201.3875 | -- | -- | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | FAULT IN 132KV NAMRUP-MARIANI STATE LINE
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region |  | 2018-04-26 09:15 | 43216.3854 | 2018-04-26 16:53 | 43216.7035 | -- | -- | 0 | 7 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF DAMAGED BUS ISOLATOR ARM AT MISA.
[6 empty] | Sub Total --> | [6 empty] | 7 | 38 | 4 | 58 | 0 | 0 | 0 | 0
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L212 | SALAKATI_BTPS | # 2 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L213 | SALAKATI-BTPS | # 1 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region | [21 empty] | 100
|  |  |  | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region |  | 2018-04-03 12:55 | 43193.5382 | 2018-04-03 13:14 | 43193.5514 | -- | -- | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS SD TAKEN BY KATHALGURI |  | 100
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region |  | 2018-04-06 10:18 | 43196.4292 | 2018-04-06 16:02 | 43196.6681 | -- | -- | 0 | 0 | 0 | 5 | 44 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ESD TAKEN Y NEEPCO
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region |  | 2018-04-08 08:15 | 43198.3438 | 2018-04-08 17:13 | 43198.7174 | -- | -- | 0 | 0 | 0 | 8 | 58 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ESD TAKEN BY KATHALGURI END
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-04-03 01:18 | 43193.0542 | 2018-04-03 06:16 | 43193.2611 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 58 | N/A | N/A | N/A | LINE H/T VIDE CODE 0027 |  | 100
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-04-06 02:07 | 43196.0882 | 2018-04-06 09:27 | 43196.3938 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 20 | N/A | N/A | N/A | LINE H/T VIDE CODE 112
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-04-07 02:20 | 43197.0972 | 2018-04-07 08:34 | 43197.3569 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 14 | N/A | N/A | N/A | LINE H/.T VIDE CODE 144
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-04-08 02:25 | 43198.1007 | 2018-04-08 07:00 | 43198.2917 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | N/A | N/A | N/A | LINE H/T VIDE CODE 0176
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-04-26 02:15 | 43216.0938 | 2018-04-26 09:14 | 43216.3847 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 59 | N/A | N/A | N/A | LINE H/T VIDE CODE 0637.
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-04-29 05:03 | 43219.2104 | 2018-04-29 09:19 | 43219.3882 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | N/A | N/A | N/A | LINE H/T VIDE CODE 0725.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 22
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L401 | BALIPARA_BONGAIGAON | # 1 | 289.721 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-04-05 15:39 | 43195.6521 | 2018-04-05 15:50 | 43195.6597 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | N/A | N/A | N/A | LONG BAMBOO FROM OUTSIDE LINE CORRIDOR TOUCHED B-PH BETN LOC 426-427 DUEING THUNDERSTORM |  | 98.69
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-04-09 09:17 | 43199.3868 | 2018-04-09 17:43 | 43199.7382 | -- | -- | 0 | 8 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN FOR LA REPLACMENT AT BALIPARA
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-04-12 04:32 | 43202.1889 | 2018-04-12 06:13 | 43202.259 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 41 | N/A | N/A | N/A | LINE H/T VIDE CODE 0342
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-04-18 07:50 | 43208.3264 | 2018-04-18 08:50 | 43208.3681 | -- | -- | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MALOPERATION
[6 empty] | Sub Total --> | [6 empty] | 9 | 26 | 0 | 0 | 0 | 11 | 1 | 41
NER L403 | MISA_BALIPARA | # 1 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L404 | MISA-BALIPARA | #2 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L405 | BONGAIGAON-MALDA | # 1 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L406 | BONGAIGAON-MALDA | # 2 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L407 | BALIPARA-RANGANADI | # 1 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L408 | BALIPARA-RANGANADI | # 2 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L409 | PALLATANA-SURAJMANINAGAR | # 1 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L411 | BTPS-BONGAIGAON | #1 | 3.119 | North Eastern Region |  | 2018-04-10 09:08 | 43200.3806 | 2018-04-10 17:19 | 43200.7215 | -- | -- | -- | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY NTPC |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0
NER L412 | BTPS-BONGAIGAON | #2 | 3.119 | North Eastern Region |  | 2018-04-11 09:44 | 43201.4056 | 2018-04-11 10:53 | 43201.4535 | -- | -- | -- | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY NTPC |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-03 22:30 | 43193.9375 | 2018-04-04 17:05 | 43194.7118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 35 | N/A | N/A | N/A | LINE H/T VIDE CODE 0054 |  | 100
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-07 22:01 | 43197.9174 | 2018-04-08 09:28 | 43198.3944 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 27 | N/A | N/A | N/A | LINE H/T VIDE CODE 0173
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-08 22:31 | 43198.9382 | 2018-04-09 09:32 | 43199.3972 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | N/A | N/A | N/A | LINE H/T VIDE CODE 0209
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-10 23:26 | 43200.9764 | 2018-04-11 18:42 | 43201.7792 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | N/A | N/A | N/A | LINE H/T VIDE CODE 311
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-12 21:59 | 43202.916 | 2018-04-13 18:17 | 43203.7618 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 0359
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-14 22:48 | 43204.95 | 2018-04-15 19:29 | 43205.8118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | N/A | N/A | N/A | LINE H/T VIDE CODE 0399
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-17 23:17 | 43207.9701 | 2018-04-18 08:03 | 43208.3354 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 46 | N/A | N/A | N/A | LINE H/T VIDE CODE 453
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-19 23:55 | 43209.9965 | 2018-04-20 17:36 | 43210.7333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 41 | N/A | N/A | N/A | LINE H/T VIDE CODE 0498.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-22 23:06 | 43212.9625 | 2018-04-23 19:09 | 43213.7979 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | N/A | N/A | N/A | LINE H/T VIDE CODE 0552.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-23 21:37 | 43213.9007 | 2018-04-24 14:33 | 43214.6062 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 56 | N/A | N/A | N/A | LINE H/T VIDE CODE 0575.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-04-26 22:44 | 43216.9472 | 2018-04-27 18:37 | 43217.7757 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 53 | N/A | N/A | N/A | LINE H/T VIDE CODE 0677.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 37
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-01 | 43191 | 2018-04-01 06:57 | 43191.2896 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 57 | N/A | N/A | N/A | LINE H/T VIDE CODE 7563 |  | 100
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-01 14:14 | 43191.5931 | 2018-04-02 17:08 | 43192.7139 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 54 | N/A | N/A | N/A | LINE H/T VIDE CODE 0001
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-02 22:15 | 43192.9271 | 2018-04-03 16:51 | 43193.7021 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | N/A | N/A | N/A | LINE H/T VIDE CODE 0022
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-04 22:04 | 43194.9194 | 2018-04-05 09:40 | 43195.4028 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 36 | N/A | N/A | N/A | LINE H/T VIDE CODE 0072
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-05 12:13 | 43195.509 | 2018-04-05 16:04 | 43195.6694 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 51 | N/A | N/A | N/A | LINE H/T VIDE CODE 0090
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-05 21:13 | 43195.884 | 2018-04-07 18:16 | 43197.7611 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 3 | N/A | N/A | N/A | LINE H/T VIDE CODE 108
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-09 22:38 | 43199.9431 | 2018-04-10 10:48 | 43200.45 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | N/A | N/A | N/A | LINE H/T VIDE CODE 0240
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-11 22:00 | 43201.9167 | 2018-04-12 18:02 | 43202.7514 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | N/A | N/A | N/A | LINE H/T VIDE CODE 336
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-13 23:31 | 43203.9799 | 2018-04-14 18:17 | 43204.7618 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | N/A | N/A | N/A | LINE H/T VIDE CODE 0379
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-15 23:15 | 43205.9688 | 2018-04-16 12:51 | 43206.5354 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 36 | N/A | N/A | N/A | LINE H/T VIDE CODE 413
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-16 23:22 | 43206.9736 | 2018-04-17 18:20 | 43207.7639 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | N/A | N/A | N/A | LINE H/T VIDE CODE 435
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-18 09:32 | 43208.3972 | 2018-04-18 16:53 | 43208.7035 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 21 | N/A | N/A | N/A | LINE H/T VIDE CODE 4612
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-18 23:06 | 43208.9625 | 2018-04-19 17:51 | 43209.7438 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 45 | N/A | N/A | N/A | LINE H/T VIDE CODE 0475
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-20 22:37 | 43210.9424 | 2018-04-22 19:33 | 43212.8146 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 56 | N/A | N/A | N/A | LINE H/T VIDE CODE 0518.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-24 22:28 | 43214.9361 | 2018-04-26 15:31 | 43216.6465 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 3 | N/A | N/A | N/A | LINE H/T VIDE CODE 0601.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-04-26 15:35 | 43216.6493 | 2018-04-26 18:45 | 43216.7812 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | N/A | N/A | N/A | LINE H/T VIDE CODE 0667.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 46
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-04-05 07:27 | 43195.3104 | 2018-04-05 16:47 | 43195.6993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 100
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-04-06 10:55 | 43196.4549 | 2018-04-06 16:13 | 43196.6757 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-04-07 07:10 | 43197.2986 | 2018-04-07 18:57 | 43197.7896 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 47 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I SD AT SILCHAR UNDER NERSS CONSTRUCTIIN PROJECT
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-04-08 08:28 | 43198.3528 | 2018-04-08 15:14 | 43198.6347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 46 | N/A | N/A | N/A | SD TAKEN FOR ERECTION OF 1 NO BEAM UNDER NERSS CONSTRUCTION PROJECT
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-04-19 07:58 | 43209.3319 | 2018-04-19 17:22 | 43209.7236 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 24 | N/A | N/A | N/A | S/D TAKEN FOR SHIFTING OF LA & CVT FOR CONSTRUCTION OF 400KV BAYS AT IMPHAL.
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-04-28 08:46 | 43218.3653 | 2018-04-28 17:13 | 43218.7174 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 27 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-04-29 08:39 | 43219.3604 | 2018-04-29 16:34 | 43219.6903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 55 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 57
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-04-05 07:29 | 43195.3118 | 2018-04-05 16:48 | 43195.7 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 19 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I & II SD AT SILCHAR UNDER NERSS PROJECT |  | 100
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-04-18 09:03 | 43208.3771 | 2018-04-18 17:53 | 43208.7451 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | N/A | N/A | N/A | SD TAKEN FOR SHIFTING OF LA & CVT FOR CONSTRUCTION OF 400KV BAYS AT IMPHAL
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-04-18 12:10 | 43208.5069 | 2018-04-18 12:17 | 43208.5118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY THUNDERSTORM AND LIGHTNING AS SUPPPORTED BY DR
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-04-28 08:47 | 43218.366 | 2018-04-28 16:58 | 43218.7069 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-04-29 08:39 | 43219.3604 | 2018-04-29 16:34 | 43219.6903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 55 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-01 02:04 | 43191.0861 | 2018-04-01 18:28 | 43191.7694 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 24 | N/A | N/A | N/A | LINE H/T VIDE CODE 7564 |  | 99.97
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-02 02:01 | 43192.084 | 2018-04-02 18:16 | 43192.7611 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 0012
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-05 22:03 | 43195.9187 | 2018-04-06 09:55 | 43196.4132 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 52 | N/A | N/A | N/A | LINE H/T VIDE CODE 109
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-06 09:55 | 43196.4132 | 2018-04-06 18:39 | 43196.7771 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 44 | N/A | N/A | N/A | SD AVAILED FOR CVT IR TESTS AND CHECKING OF STUB PROTECTION
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-08 01:46 | 43198.0736 | 2018-04-08 18:30 | 43198.7708 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | N/A | N/A | N/A | LINE H/T VIDE CODE 0175
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-12 03:37 | 43202.1507 | 2018-04-12 14:30 | 43202.6042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53 | N/A | N/A | N/A | LINE H/T VIDE CODE 341
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-25 15:49 | 43215.659 | 2018-04-26 15:17 | 43216.6368 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 0616.
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-04-27 19:05 | 43217.7951 | 2018-04-27 19:20 | 43217.8056 | -- | -- | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 104 | 20
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-06 22:54 | 43196.9542 | 2018-04-07 09:45 | 43197.4062 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51 | N/A | N/A | N/A | LINE H/T VIDE CODE 143 |  | 99.57
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-07 09:45 | 43197.4062 | 2018-04-07 18:49 | 43197.784 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | N/A | N/A | N/A | SD AVAILED FOR CVT IR TESTS AND CHECKING OF STUB PROTECTION
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-13 01:11 | 43203.0493 | 2018-04-15 18:22 | 43205.7653 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | N/A | N/A | N/A | LINE H/T VIDE CODE 363
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-16 12:52 | 43206.5361 | 2018-04-16 15:57 | 43206.6646 | -- | -- | 0 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ATTENDING HOTSPOTS IN JUMPERS AT LOC 138 & LOC 139
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-16 15:57 | 43206.6646 | 2018-04-16 18:33 | 43206.7729 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 36 | N/A | N/A | N/A | LINE KEPT OPEN AS PER NERLDC INSTRUCTION
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-18 07:50 | 43208.3264 | 2018-04-18 08:37 | 43208.359 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AND THUNDERSTORM AS SUPPORTED BY DR AND PATROL REPORT
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-18 08:37 | 43208.359 | 2018-04-18 10:25 | 43208.434 | -- | -- | -- | 0 | 0 | 0 | 0 | 1 | 48 | 0 | 0 | N/A | N/A | N/A | LINE KEPT OPEN DUE TO SYSTEM CONSTRAINTS AS PER INSTRUCTION OF NERLDC
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-04-29 04:02 | 43219.1681 | 2018-04-30 00:20 | 43220.0139 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 0724.
[6 empty] | Sub Total --> | [6 empty] | 3 | 5 | 0 | 0 | 2 | 35 | 108 | 0
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-01 08:00 | 43191.3333 | 2018-04-01 18:19 | 43191.7632 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19 | N/A | N/A | N/A | S/D TAKEN FOR ERECTION OF NEW TOWER ON PILE FOUNDATION |  | 100
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-01 23:04 | 43191.9611 | 2018-04-02 08:30 | 43192.3542 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 26 | N/A | N/A | N/A | LINE H/T VIDE CODE 0011
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-02 08:30 | 43192.3542 | 2018-04-04 18:45 | 43194.7812 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 15 | N/A | N/A | N/A | S/D TAKEN FOR ERECTION OF NEW TOWER ON PILE FOUNDATION
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-04 21:19 | 43194.8882 | 2018-04-05 07:54 | 43195.3292 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35 | N/A | N/A | N/A | LINE H/T VIDE CODE 0071
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-05 07:54 | 43195.3292 | 2018-04-05 18:02 | 43195.7514 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | N/A | N/A | N/A | SD TAKEN FOR ERECTION OF NEW TOWER ON PILE FOUNDATION
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-05 22:49 | 43195.9507 | 2018-04-06 08:00 | 43196.3333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 11 | N/A | N/A | N/A | LINE H/T VIDE CODE 111
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-06 08:00 | 43196.3333 | 2018-04-06 17:15 | 43196.7188 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | N/A | N/A | N/A | SD TAKEN FOR ERECTION OF NEW TOWER ON PILE FOUNDATION
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-06 22:51 | 43196.9521 | 2018-04-07 08:00 | 43197.3333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | N/A | N/A | N/A | LINE H/T VIDE CODE 142
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-07 08:00 | 43197.3333 | 2018-04-07 17:45 | 43197.7396 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | N/A | N/A | N/A | SD TAKEN FOR ERECTION OF NEW TOWER ON PILE FOUNDATION
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-07 22:58 | 43197.9569 | 2018-04-08 07:54 | 43198.3292 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | N/A | N/A | N/A | LINE H/T VIDE CODE 0174
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-08 07:54 | 43198.3292 | 2018-04-08 18:05 | 43198.7535 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | N/A | N/A | N/A | SD TAKEN FOR ERECTION OF NEW TOWER ON PILE FOUNDATION
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-11 00:32 | 43201.0222 | 2018-04-11 17:47 | 43201.741 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 0312
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-12 00:06 | 43202.0042 | 2018-04-12 16:19 | 43202.6799 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 337
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-12 23:58 | 43202.9986 | 2018-04-13 09:01 | 43203.3757 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 3 | N/A | N/A | N/A | LINE H/Y VIDE CODE 361
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-14 22:38 | 43204.9431 | 2018-04-15 18:26 | 43205.7681 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 48 | N/A | N/A | N/A | LINE H/T VIDE CODE 398
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-17 23:18 | 43207.9708 | 2018-04-18 16:28 | 43208.6861 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | N/A | N/A | N/A | LINE H/T VIDE CODE 454
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-19 22:23 | 43209.9326 | 2018-04-20 18:26 | 43210.7681 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | N/A | N/A | N/A | LINE H/T VIDE CODE 0497.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-23 09:05 | 43213.3785 | 2018-04-23 17:20 | 43213.7222 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 0555.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-25 00:53 | 43215.0368 | 2018-04-25 06:40 | 43215.2778 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 0603.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-25 23:33 | 43215.9812 | 2018-04-26 16:48 | 43216.7 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 0629.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-27 23:04 | 43217.9611 | 2018-04-28 17:32 | 43218.7306 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 0704.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-04-28 22:48 | 43218.95 | 2018-04-29 18:26 | 43219.7681 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | N/A | N/A | N/A | LINE H/T VIDE CODE 0718.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 5
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-09 01:47 | 43199.0743 | 2018-04-09 08:02 | 43199.3347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 0210 |  | 100
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-09 08:02 | 43199.3347 | 2018-04-09 18:14 | 43199.7597 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | N/A | N/A | N/A | SD TAKEN FOR SHIFTING OF CONDUCTORS FROM ERS TO NEW TOWER
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-09 22:24 | 43199.9333 | 2018-04-10 09:15 | 43200.3854 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51 | N/A | N/A | N/A | LINE H/T VIDE CODE 0239
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-10 09:15 | 43200.3854 | 2018-04-10 17:50 | 43200.7431 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 35 | N/A | N/A | N/A | SD TAKEN FOR SHIFTING OF CONDUCTORS FROM ERS TO NEW TOWER
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-13 23:58 | 43203.9986 | 2018-04-14 18:10 | 43204.7569 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 0380
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-21 00:36 | 43211.025 | 2018-04-21 18:38 | 43211.7764 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | N/A | N/A | N/A | LINE H/T VIDE CODE 0519.
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-22 01:08 | 43212.0472 | 2018-04-22 16:21 | 43212.6813 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 0539.
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-24 08:52 | 43214.3694 | 2018-04-24 17:00 | 43214.7083 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | N/A | N/A | N/A | LINE H/T VIDE CODE 0580.
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-04-27 00:02 | 43217.0014 | 2018-04-27 14:40 | 43217.6111 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 38 | N/A | N/A | N/A | LINE H/T VIDE CODE 0678.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 55
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-04-05 09:34 | 43195.3986 | 2018-04-05 18:07 | 43195.7549 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 33 | N/A | N/A | N/A | SD AVAILED FOR CVT IR TESTS AND CHECKING OF STUB PROTECTION |  | 100
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-04-05 09:34 | 43195.3986 | 2018-04-05 18:07 | 43195.7549 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 33 | N/A | N/A | N/A | SD AVAILED FOR CVT IR TESTS AND CHECKING OF STUB PROTECTION
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-04-05 18:07 | 43195.7549 | 2018-04-05 22:01 | 43195.9174 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | N/A | N/A | N/A | LINE KEPT OPEN AS PER NERLDC ISNTRUCTION
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 6
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region | [5 empty] | -- | -- | -- | [13 empty] | 100
Sub Total -->
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-04-01 | 43191 | 2018-04-15 16:11 | 43205.6743 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 11 | N/A | N/A | N/A | E/S/D TAKEN FOR RECTIFICATION OF ERS TOWER AT LOC 126-128 |  | 100
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-04-28 08:35 | 43218.3576 | 2018-04-28 17:18 | 43218.7208 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-04-29 00:30 | 43219.0208 | 2018-04-29 00:49 | 43219.034 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO PREVAILING INCLEMENT WEATHER IN THE REGION.
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-04-29 08:37 | 43219.359 | 2018-04-29 16:56 | 43219.7056 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 19 | 369 | 13
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-04-05 07:00 | 43195.2917 | 2018-04-05 17:17 | 43195.7201 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS-I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 100
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-04-13 10:15 | 43203.4271 | 2018-04-13 16:11 | 43203.6743 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56 | N/A | N/A | N/A | S/D TAKEN FOR RESTORATION OF SILCHAR-PKBARI I CKT
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-04-15 10:04 | 43205.4194 | 2018-04-15 15:55 | 43205.6632 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51 | N/A | N/A | N/A | S/D TAKEN FOR RESTORATION WORKS OF 132KV SILCHAR-PKBARI-I
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-04-28 08:36 | 43218.3583 | 2018-04-28 17:18 | 43218.7208 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 42 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-04-29 08:37 | 43219.359 | 2018-04-29 16:56 | 43219.7056 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 5
NER RBR1 | BR_BONGAIGAON (50MVAR) | # 1 | 50 | North Eastern Region | [21 empty] | 100
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR5 | BR_KUMARGHAT (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR6 | BR_AIZWAL (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | [22 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region | Tie bay CT failed | 2018-04-05 17:25 | 43195.7257 | 2018-04-05 19:08 | 43195.7972 | -- | -- | 0 | 1 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | N | -120 | REACTOR TRIPPED DURING FAILURE OF R-PH CT AT TIE BAY OF 400KV SILCHAR-PALATANA-I & BR-2 |  | 99.76
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-04-05 08:09 | 43195.3396 | 2018-04-05 11:59 | 43195.4993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | N/A | N/A | N/A | BUS REACTOR H/T VIDE CODE 083
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-04-16 09:25 | 43206.3924 | 2018-04-16 17:37 | 43206.734 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 12 | N/A | N/A | N/A | SD TAKEN FOR CASTING OF REMAINING TWO LIFTS OF FIREWALL OF ICT-3
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-04-17 09:48 | 43207.4083 | 2018-04-17 16:35 | 43207.691 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 47 | N/A | N/A | N/A | SD FOR CASTING OF REMAINING TWO LIFTS OF FIREWALL OF ICT-3
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-04-18 09:24 | 43208.3917 | 2018-04-18 16:53 | 43208.7035 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 29 | N/A | N/A | N/A | SD FOR CASTING OF REMAINING TWO LIFTS OF FIREWALL FOR ICT-3
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-04-23 10:10 | 43213.4236 | 2018-04-23 17:16 | 43213.7194 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | N/A | N/A | N/A | S/D TAKEN FOR CASTING OF REMAINING TWO LIFT OF FIREWALL FOR ICT-3 UNDER NERSS PROJECT.
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-04-25 10:13 | 43215.4257 | 2018-04-25 16:47 | 43215.6993 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | N/A | N/A | N/A | S/D TAKEN FOR CASTING OF REMAINING TWO LIFT OF FIREWALL FOR ICT-3 UNDER NERSS PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 1 | 43 | 0 | 0 | 0 | 0 | 39 | 58
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR13 | BR_B'CHARIALI(80MVAR) | #2 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR14 | BR_B'CHARIALI(63MVAR) | #3 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR15 | BR_B'CHARIALI(63MVAR) | #4 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR16 | BR_New_MARIANI(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR17 | BR_BALIPARA(125MVAR) | #3 | 125 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR19 | BR_ROING(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
| BR_ROING(20MVAR) | #1 |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT1 | ICT_BONGAIGAON(315MVA) |  | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT2 | ICT_BALIPARA (315MVA) | #1 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT3 | ICT_BALIPARA(315MVA) | #2 | 315 | North Eastern Region |  | 2018-04-05 11:19 | 43195.4715 | 2018-04-05 13:07 | 43195.5465 | -- | -- | -- | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD AVAILED FOR AMP |  | 98.87
NER TICT3 | ICT_BALIPARA(315MVA) | #2 | 315 | North Eastern Region |  | 2018-04-27 10:19 | 43217.4299 | 2018-04-27 16:41 | 43217.6951 | -- | -- | -- | 6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP.
[6 empty] | Sub Total --> | [6 empty] | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-04-12 12:12 | 43202.5083 | 2018-04-12 12:28 | 43202.5194 | -- | -- | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DURING CONSTRUCTION ACTIVITIES GOING ON AT SS FOR COMMISSIONING OF NEW ICT |  | 99.96
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-04-20 10:33 | 43210.4396 | 2018-04-20 18:07 | 43210.7549 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 34 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF ICT-I UNDER NERSS-IV PROJECT WITH NEW 500 MVA ICT.
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-04-21 08:23 | 43211.3493 | 2018-04-21 17:44 | 43211.7389 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 21 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF ICT-I UNDER NERSS-IV PROJECT WITH NEW 500 MVA ICT.
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-04-22 09:24 | 43212.3917 | 2018-04-22 14:49 | 43212.6174 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF ICT-I UNDER NERSS-IV PROJECT WITH NEW 500 MVA ICT.
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-04-23 09:15 | 43213.3854 | 2018-04-23 17:26 | 43213.7264 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF ICT-I UNDER NERSS-IV PROJECT WITH NEW 500 MVA ICT.
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-04-24 09:55 | 43214.4132 | 2018-04-25 16:26 | 43215.6847 | -- | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 31 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF ICT-I UNDER NERSS-IV PROJECT WITH NEW 500 MVA ICT.
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-04-26 10:00 | 43216.4167 | 2018-04-26 16:30 | 43216.6875 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF ICT-I UNDER NERSS-IV PROJECT WITH NEW 500 MVA ICT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 12 | 0 | 0 | 0 | 0 | 67 | 32
NER TICT5 | ICT_MISA | #2 | 315 | North Eastern Region | [21 empty] | 100
Sub Total -->
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region |  | 2018-04-05 08:05 | 43195.3368 | 2018-04-05 16:23 | 43195.6826 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | N/A | N/A | N/A | ICT H/T FOR FACILITATING 132JV BUS I & II SD AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 100
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region |  | 2018-04-28 09:02 | 43218.3764 | 2018-04-28 16:51 | 43218.7021 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 49 | N/A | N/A | N/A | H/T FOR FACILITATING 132 KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region |  | 2018-04-29 08:49 | 43219.3674 | 2018-04-29 16:31 | 43219.6882 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 42 | N/A | N/A | N/A | H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 49
NER TICT7 | ICT_B'CHARIALI (200MVA) | #1 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT8 | ICT_B'CHARIALI (200MVA) | #2 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT9 | ICT_IMPHAL(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT10 | ICT_IMPHAL(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT12 | ICT_DIMAPUR (100 MVA) | # 1 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT13 | ICT_DIMAPUR (100 MVA) | #2 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-04-05 08:06 | 43195.3375 | 2018-04-05 16:23 | 43195.6826 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | N/A | N/A | N/A | ICT H/T FOR FACILITATING 132KV BUS I & II SD AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT |  | 100
| ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-04-06 10:54 | 43196.4542 | 2018-04-06 16:02 | 43196.6681 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | N/A | N/A | N/A | ICT H/T FOR FACILITATING 132KV BUS-I SD AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT
| ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-04-07 08:43 | 43197.3632 | 2018-04-07 17:42 | 43197.7375 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 59 | N/A | N/A | N/A | ICT H/T FOR FACILITATING 132KV BUS-I SD AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT
| ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-04-08 08:45 | 43198.3646 | 2018-04-08 15:07 | 43198.6299 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 22 | N/A | N/A | N/A | SD TAKEN FOR ERECTION OF 1 NO BEAM UNDER NERSS CONSTRUCTION PROJECT
| ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-04-28 09:03 | 43218.3771 | 2018-04-28 16:53 | 43218.7035 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | N/A | N/A | N/A | H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-04-29 08:49 | 43219.3674 | 2018-04-29 16:32 | 43219.6889 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 43 | N/A | N/A | N/A | H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 19
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region |  | 2018-04-26 09:17 | 43216.3868 | 2018-04-26 17:44 | 43216.7389 | -- | -- | -- | 8 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP. |  | 98.83
[6 empty] | Sub Total --> | [6 empty] | 8 | 27 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT16 | ICT_MOKOKCHUNG(30MVA) | #2 | 30 | North Eastern Region |  | 2018-04-27 09:05 | 43217.3785 | 2018-04-27 16:43 | 43217.6965 | -- | -- | -- | 7 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP. |  | 98.94
[6 empty] | Sub Total --> | [6 empty] | 7 | 38 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT17 | ICT_NIRJULI(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT18 | ICT_NIRJULI(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT19 | ICT_ZIRO (15MVA) |  | 15 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT20 | ICT_KOPILI (160 MVA) | # 2 | 160 | North Eastern Region |  | 2018-04-30 10:16 | 43220.4278 | 2018-04-30 13:15 | 43220.5521 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 59 | N/A | N/A | N/A | S/D TAKEN FOR TIGHTENING WORKS FOR ARRESTING OIL LEAKAGE |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 59
NER TICT21 | ICT_KUMARGHAT(5MVA) |  | 5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT22 | ICT_SILCHAR(315MVA) | #3 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## MAY 2018 - TABLE I
Unique ID of transmission Element | Element Name |  | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee Hr min |  | OTHERS Hr min |  | System Constraints/ Natural calamity / Militancy Hr min |  | Deemed Available Hr min
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region | [20 empty] | NERPC/OP/TAC/2018-19/2130 dtd 23.07.2018 | 100 | 100
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-05-18 09:46 | 43238.4069 | 2018-05-18 17:04 | 43238.7111 | -- | -- | -- | 0 | 0 | 0 | 0 | 7 | 18 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR CLEARING OF INFRINGEMENT AT 292,297,300&305. |  | 99.02
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 7 | 18 | 0 | 0
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-08 14:35 | 43228.6076 | 2018-05-08 14:44 | 43228.6139 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AND PASSING THUNDERSTORM CONCLUDED FROM DR AND WEATHER REPORT |  | 97.8
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-10 13:58 | 43230.5819 | 2018-05-10 16:00 | 43230.6667 | -- | -- | -- | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FAILURE OF B-PH TLA DISCONNECTOR at loc 41
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-10 16:01 | 43230.6674 | 2018-05-11 08:00 | 43231.3333 | -- | -- | -- | 0 | 0 | 0 | 0 | 15 | 59 | 0 | 0 | N/A | N/A | N/A | LINE KEPT UNDER S/D AS S/D WORKS FOR TLA REPLACEMENT CEASED DUE TO INCLEMENT WEATHER AT SITE
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-11 08:01 | 43231.334 | 2018-05-11 10:58 | 43231.4569 | -- | -- | -- | 2 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF TLA AT LOC 41
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-12 11:01 | 43232.459 | 2018-05-12 15:11 | 43232.6326 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | N/A | N/A | N/A | E/S/D IS TAKEN TO GIVE BACKSTAY AT LOC. NO. 22, LOC VULNERABLE DUE TO LANDSLIDE.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-13 15:13 | 43233.634 | 2018-05-13 16:05 | 43233.6701 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTENING STRIKES, FLASHOVER MARKS SEEN AT LOC 24.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region | Jumper opened | 2018-05-16 11:45 | 43236.4896 | 2018-05-16 16:00 | 43236.6667 | -- | -- | 0 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -3 | B-PH JUMPER OPENED AT LOC 188
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-16 16:01 | 43236.6674 | 2018-05-17 08:00 | 43237.3333 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 15 | 59 | 0 | 0 | N/A | N/A | N/A | LINE KEPT UNDER S/D AS S/D WORKS FOR B-PH REJUMPERING AT LOC 188 CEASED ON A/C of INCLEMENT WEATHE
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-17 08:01 | 43237.334 | 2018-05-17 14:26 | 43237.6014 | -- | -- | -- | 6 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR B-PH REJUMPERING WORKS AT LOC 188
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-21 09:02 | 43241.3764 | 2018-05-21 18:56 | 43241.7889 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 54 | N/A | N/A | N/A | INFRINGEMENT CLEARING BETWEEN LOC 81-82, CHANGING OF TOP & BOTTOM CONDUCTOR OF LOC 109-110
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-05-22 09:14 | 43242.3847 | 2018-05-22 16:01 | 43242.6674 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 47 | N/A | N/A | N/A | INFRINGEMENT CLEARING BEWEEN LOC 81-82 & CHANGING OF TOP & BOTTOM CONDUCTOR OF LOC 109-110
[6 empty] | Sub Total --> | [6 empty] | 15 | 39 | 0 | 0 | 32 | 59 | 20 | 51
NER L105 | AIZWAL_ZEMEBAK | # 2 | 6.719 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-05-15 03:22 | 43235.1403 | 2018-05-15 04:05 | 43235.1701 | -- | -- | -- | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT |  | 100
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-05-15 04:09 | 43235.1729 | 2018-05-15 04:21 | 43235.1813 | -- | -- | -- | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-05-18 06:11 | 43238.2576 | 2018-05-18 06:47 | 43238.2826 | -- | -- | -- | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | (TRIPPED DUE TO DOWNSTREAM FAULT)
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-05-19 08:37 | 43239.359 | 2018-05-19 19:18 | 43239.8042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41 | N/A | N/A | N/A | S/D OF REPLACEMENT OF CVT MB BOX & ARRESTING OIL LEAKAGE IN CT AT ASEB PANCHGRAM.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 31 | 0 | 0 | 10 | 41
NER L107 | BADARPUR_JIRIBAM |  | 67.21 | North Eastern Region | Insulator Flashover | 2018-05-05 21:45 | 43225.9062 | 2018-05-05 21:56 | 43225.9139 | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 2 | N | -2 | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY FLASHMARK FINDING AT Y-PH INSULATOR AT LOC 97 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region |  | 2018-05-09 12:53 | 43229.5368 | 2018-05-09 13:05 | 43229.5451 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0
NER L109 | BADARPUR_KUMARGHAT |  | 118.513 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-05-05 14:18 | 43225.5958 | 2018-05-05 14:25 | 43225.6007 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR AND WEATHER REPORT |  | 99.96
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-05-07 04:07 | 43227.1715 | 2018-05-07 04:25 | 43227.184 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AND THUNDERSTORM.
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-05-09 12:30 | 43229.5208 | 2018-05-09 12:39 | 43229.5271 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-05-10 14:23 | 43230.5993 | 2018-05-10 14:40 | 43230.6111 | -- | -- | -- | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DURING TRANSIENT FAULT.
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region |  | 2018-05-31 10:54 | 43251.4542 | 2018-05-31 23:59 | 43251.9993 | -- | -- | -- | 0 | 0 | 0 | 0 | 13 | 5 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY MSPDCL FOR LILO WORKS IN TIPAIMUKH SS (MANIPUR STATE)
[6 empty] | Sub Total --> | [6 empty] | 0 | 17 | 0 | 0 | 13 | 39 | 0 | 0
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-05-04 13:13 | 43224.5507 | 2018-05-04 13:20 | 43224.5556 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR ,PATROLLING AND WEATHER REPORT |  | 100
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-05-24 09:32 | 43244.3972 | 2018-05-24 17:00 | 43244.7083 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 28 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-05-25 08:44 | 43245.3639 | 2018-05-25 17:07 | 43245.7132 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-05-26 08:00 | 43246.3333 | 2018-05-26 18:08 | 43246.7556 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTINF PORCELAIN INSULATOR WITH POLYMER INSULATOR
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-05-28 08:14 | 43248.3431 | 2018-05-28 18:18 | 43248.7625 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | N/A | N/A | N/A | S/D AVAILEED FOR MASS REPLACMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-05-29 08:01 | 43249.334 | 2018-05-29 17:47 | 43249.741 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 46 | N/A | N/A | N/A | SD AVAIELD FOR AMSS REPLACMENT OF EXISTING PORCELAIN INSULATORS WITH POLYMER INSULATORS
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-05-30 08:00 | 43250.3333 | 2018-05-30 17:35 | 43250.7326 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 35 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 7 | 55 | 24
NER L118 | KHANDONG-HAFLONG |  | 63.166 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-05-09 09:32 | 43229.3972 | 2018-05-09 09:47 | 43229.4076 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | N/A | N/A | N/A | INCLEMENT WEATHER PREVAILING OVER ENTIRE NORTH-EASTERN INDIA. |  | 100
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-05-09 11:58 | 43229.4986 | 2018-05-09 12:07 | 43229.5049 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR AND PATROLLING REPORT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-05-15 18:00 | 43235.75 | 2018-05-15 18:11 | 43235.7576 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR ,PATROLLING AND WEATHER REPORT |  | 100
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-05-25 22:26 | 43245.9347 | 2018-05-25 22:43 | 43245.9465 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0
NER L121 | KHANDONG_KOPILI | # 1 | 10.914 | North Eastern Region |  | 2018-05-04 09:28 | 43224.3944 | 2018-05-04 12:33 | 43224.5229 | -- | -- | -- | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP OF BAY EQUIPMENTS. |  | 99.57
NER L121 | KHANDONG_KOPILI | # 1 | 10.914 | North Eastern Region |  | 2018-05-14 13:59 | 43234.5826 | 2018-05-14 14:07 | 43234.5882 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FELLING OF TREES B/W LOC 22-23.
[6 empty] | Sub Total --> | [6 empty] | 3 | 5 | 0 | 0 | 0 | 8 | 0 | 0
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region |  | 2018-05-09 08:48 | 43229.3667 | 2018-05-09 09:18 | 43229.3875 | -- | -- | -- | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 100
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region |  | 2018-05-14 08:28 | 43234.3528 | 2018-05-14 17:23 | 43234.7243 | -- | -- | -- | 0 | 0 | 8 | 55 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY STATE END.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 9 | 25 | 0 | 0 | 0 | 0
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region | Conductor Snapped | 2018-05-07 03:05 | 43227.1285 | 2018-05-07 17:27 | 43227.7271 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 3 | N | -2.5 | R-PH CONDUCTOR SNAPPED AT LOC 86-87 DUE TO FALLING OF TREE FROM OUTSIDE CORRIDOR ON A/C OF T-STORM |  | 100
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region |  | 2018-05-10 12:31 | 43230.5215 | 2018-05-10 12:42 | 43230.5292 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 3 | N | -3 | CGI SHEET FLEW FROM OUTSIDE CORRIDOR AND TOUCHED B-PH CONDUCTOR BETWEEN LOC 130-131.
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region |  | 2018-05-10 13:03 | 43230.5437 | 2018-05-10 13:12 | 43230.55 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR ,PATROLLING AND WEATHER REPORT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 14 | 42 | 0 | 0
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region | [21 empty] | 100
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L125 | SALAKATI-GELEPHUG |  | 49.217 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L126 | LEKHI - RANGANADI |  | 12.59 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-05-10 13:53 | 43230.5785 | 2018-05-10 14:43 | 43230.6132 | -- | -- | -- | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT. |  | 99.89
[6 empty] | Sub Total --> | [6 empty] | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-05-13 10:05 | 43233.4201 | 2018-05-13 11:05 | 43233.4618 | -- | -- | -- | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY RANGANADI. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
NER L130 | KHANDONG_KOPILI | # 2 | 11.56 | North Eastern Region |  | 2018-05-02 10:05 | 43222.4201 | 2018-05-02 19:28 | 43222.8111 | -- | -- | -- | 9 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP OF BAY EQUIPMENTS. |  | 98.74
[6 empty] | Sub Total --> | [6 empty] | 9 | 23 | 0 | 0 | 0 | 0 | 0 | 0
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L132 | DIMAPUR(PG)-DIMAPUR(LILO PORTION) |  |  | North Eastern Region |  | 2018-05-05 09:00 | 43225.375 | 2018-05-05 15:49 | 43225.659 |  |  |  | 6 | 49 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S/D TAKEN FOR AMP. |  | 99.08
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region |  | 2018-05-18 06:33 | 43238.2729 | 2018-05-18 06:41 | 43238.2785 | -- | -- | -- | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | (TRIPPED DUE TO DOWNSTREAM FAULT). |  | 100
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region |  | 2018-05-27 09:01 | 43247.3757 | 2018-05-27 16:29 | 43247.6868 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 28 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8 | 0 | 0 | 7 | 28
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region |  | 2018-05-18 06:33 | 43238.2729 | 2018-05-18 06:41 | 43238.2785 | -- | -- | -- | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | (TRIPPED DUE TO DOWNSTREAM FAULT) |  | 100
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region |  | 2018-05-27 09:01 | 43247.3757 | 2018-05-27 16:30 | 43247.6875 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 29 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8 | 0 | 0 | 7 | 29
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region |  | 2018-05-11 08:50 | 43231.3681 | 2018-05-11 09:07 | 43231.3799 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | N/A | N/A | N/A | SPS-1 & 2 OPERATED AT SILCHAR. |  | 100
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region |  | 2018-05-27 08:52 | 43247.3694 | 2018-05-27 16:35 | 43247.691 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 43 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 43
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region |  | 2018-05-11 08:50 | 43231.3681 | 2018-05-11 09:22 | 43231.3903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | N/A | N/A | N/A | SPS-1 & 2 OPERATED AT SILCHAR |  | 100
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region |  | 2018-05-27 08:52 | 43247.3694 | 2018-05-27 16:34 | 43247.6903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 42 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 32 | 7 | 42
NER L137 | IMPHAL-IMPHAL | # 2 | 0.442 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-05-11 08:50 | 43231.3681 | 2018-05-11 09:08 | 43231.3806 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | N/A | N/A | N/A | SPS-1 & 2 OPERATED AT SILCHAR. |  | 100
NER L139 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-05-27 08:43 | 43247.3632 | 2018-05-27 16:23 | 43247.6826 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 40 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 40
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-05-26 17:23 | 43246.7243 | 2018-05-26 17:35 | 43246.7326 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR AND WEATHER REPORT |  | 100
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-05-27 08:43 | 43247.3632 | 2018-05-27 16:23 | 43247.6826 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 40 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-05-29 11:41 | 43249.4868 | 2018-05-29 13:44 | 43249.5722 | -- | -- | -- | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR INFRINGEMENT CLEARING B/W LOC 5-7 WHICH CAME INTO ROW DUE TO RECENT LOCALIZED STORMS
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 2 | 15 | 7 | 40
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 |  |  | 2018-05-02 13:41 | 43222.5701 | 2018-05-02 13:54 | 43222.5792 | -- | -- | -- | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 100
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 |  |  | 2018-05-06 10:07 | 43226.4215 | 2018-05-06 10:43 | 43226.4465 | -- | -- | -- | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 |  |  | 2018-05-06 12:13 | 43226.509 | 2018-05-06 12:30 | 43226.5208 | -- | -- | -- | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 | North Eastern Region |  | 2018-05-09 13:17 | 43229.5535 | 2018-05-09 13:26 | 43229.5597 | -- | -- | -- | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region |  | 2018-05-02 13:41 | 43222.5701 | 2018-05-02 13:57 | 43222.5813 | -- | -- | -- | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 100
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region |  | 2018-05-06 10:07 | 43226.4215 | 2018-05-06 10:44 | 43226.4472 | -- | -- | -- | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region |  | 2018-05-06 12:13 | 43226.509 | 2018-05-06 12:31 | 43226.5215 | -- | -- | -- | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region |  | 2018-05-09 13:17 | 43229.5535 | 2018-05-09 13:28 | 43229.5611 | -- | -- | -- | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 22 | 0 | 0 | 0 | 0
NER L142 | B.CHARAILI_PAVOI | #1 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L143 | B.CHARAILI_PAVOI | #2 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L144 | ROING_PASIGHAT |  |  | North Eastern Region |  | 2018-05-29 11:20 | 43249.4722 | 2018-05-29 11:55 | 43249.4965 | -- | -- | -- | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT EARTH FAULT |  | 99.92
[6 empty] | Sub Total --> | [6 empty] | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L146 | AIZAWL MELRIAT |  |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L153 | MELRIAT - ZEMABAWK |  |  | North Eastern Region |  | 2018-05-13 15:37 | 43233.6507 | 2018-05-13 16:09 | 43233.6729 | -- | -- | -- | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWN STREAM FAULT. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L202 | KATHALGURI_MARIANI(OLD) |  | 162.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L203 | MISA_DIMAPUR | # 1 | 123.52 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 18:51 | 43241.7854 | -- | -- | -- | 3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS B Y-PH PT EXPLODED AT MISA |  | 99.55
NER L203 | MISA_DIMAPUR | # 1 | 123.52 |  |  | 2018-05-29 13:06 | 43249.5458 | 2018-05-29 16:59 | 43249.7076 | -- | -- | -- | 0 | 0 | 0 | 0 | 3 | 53 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING CGI SHEET HANGING FROM BOTTOM CONDUCTOR AT LOC 82 CAUSED BY RECENT T-STORMS
[6 empty] | Sub Total --> | [6 empty] | 3 | 21 | 0 | 0 | 3 | 53 | 0 | 0
NER L204 | MISA_DIMAPUR | # 2 | 123.52 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 18:52 | 43241.7861 | -- | -- | -- | 3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS B Y-PH PT EXPLODED AT MISA |  | 99.55
NER L204 | MISA_DIMAPUR | # 2 | 123.52 | North Eastern Region |  | 2018-05-23 09:48 | 43243.4083 | 2018-05-23 17:12 | 43243.7167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 24 | N/A | N/A | N/A | RESTRINGING OF BOTTOM CONDUCTOR BETWEEN LOC 288 & 289 FOR PROPER PHASE TO PHASE CLEARANCE
[6 empty] | Sub Total --> | [6 empty] | 3 | 22 | 0 | 0 | 0 | 0 | 7 | 24
NER L205 | MISA_KATHALGURI |  | 382.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L206 | MISA-KOPILI | # 1 | 72.791 | North Eastern Region |  | 2018-05-20 11:30 | 43240.4792 | 2018-05-20 12:07 | 43240.5049 | -- | -- | -- | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY KOPILI (NEEPCO) |  | 9953
NER L206 | MISA-KOPILI | # 1 | 72.791 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 19:00 | 43241.7917 | -- | -- | -- | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS-B Y-PH PT EXPLODED AT MISA.
[6 empty] | Sub Total --> | [6 empty] | 3 | 30 | 0 | 37 | 0 | 0 | 0 | 0
NER L207 | MISA_KOPILI | # 2 | 72.791 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 18:48 | 43241.7833 | -- | -- | -- | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS B Y-PH PT EXPLODED AT MISA |  | 99.53
[6 empty] | Sub Total --> | [6 empty] | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0
NER L208 | MISA_KOPILI | # 3 | 75.788 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 17:32 | 43241.7306 | -- | -- | -- | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS-B Y-PH PT EXPLODED AT MISA |  | 99.73
[6 empty] | Sub Total --> | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region |  | 2018-05-21 10:10 | 43241.4236 | 2018-05-21 20:00 | 43241.8333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | N/A | N/A | N/A | 220KV BPI & PIPE BUS ERECTION UNDER NERSS IV CONSTRUCTION PROJECT |  | 100
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region |  | 2018-05-22 10:10 | 43242.4236 | 2018-05-22 18:30 | 43242.7708 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | N/A | N/A | N/A | 220KV BPI & PIPE BUS ERECTION UNDER NERSS IV CONSTRUCTION PROJECT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region |  | 2018-05-09 10:11 | 43229.4243 | 2018-05-09 12:37 | 43229.5257 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | N/A | N/A | N/A | S/D AVAILED FOR ISOLATOR REPLACEMENT WORK , DISCONNECTING AND RECONNECTING OF JUMPERS. |  | 99.66
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 18:01 | 43241.7507 | -- | -- | -- | 2 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS-B Y-PH PT EXPLODED AT MISA
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region | Insulator Flashover | 2018-05-24 11:33 | 43244.4812 | 2018-05-24 12:00 | 43244.5 | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 2 | N | -2 | TRIPPED DURING LIGHTENING STIKE; FLASHOVER MARK FOUND ON R-PH INSULATORS AT LOC 94.
[6 empty] | Sub Total --> | [6 empty] | 2 | 31 | 0 | 0 | 0 | 27 | 2 | 26
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region |  | 2018-05-11 10:05 | 43231.4201 | 2018-05-11 11:11 | 43231.466 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | N/A | N/A | N/A | S/D AVAILED FOR ISOLATOR REPLACEMENT WORK , DISCONNECTING AND RECONNECTING OF JUMPERS. |  | 99.53
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 18:58 | 43241.7903 | -- | -- | -- | 3 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS-B Y-PH PT EXPLODED AT MISA
[6 empty] | Sub Total --> | [6 empty] | 3 | 28 | 0 | 0 | 0 | 0 | 1 | 6
NER L212 | SALAKATI_BTPS | # 2 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L213 | SALAKATI-BTPS | # 1 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region |  | 2018-05-16 09:14 | 43236.3847 | 2018-05-16 15:50 | 43236.6597 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 36 | N/A | N/A | N/A | S/D TAKEN FOR ERECTION OF 220 KV EQUIPMENT UNDER NERSS IV CONSTRUCTION PROJECT. |  | 99.58
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region |  | 2018-05-21 15:30 | 43241.6458 | 2018-05-21 18:37 | 43241.7757 | -- | -- | -- | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS-B Y-PH PT EXPLODED AT MISA
|  |  |  | North Eastern Region |  | Sub Total --> | [6 empty] | 3 | 7 | 0 | 0 | 0 | 0 | 6 | 36
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L401 | BALIPARA_BONGAIGAON | # 1 | 289.721 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L403 | MISA_BALIPARA | # 1 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L404 | MISA-BALIPARA | #2 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L405 | BONGAIGAON-MALDA | # 1 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L406 | BONGAIGAON-MALDA | # 2 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L407 | BALIPARA-RANGANADI | # 1 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L408 | BALIPARA-RANGANADI | # 2 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L409 | PALLATANA-SURAJMANINAGAR | # 1 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L411 | BTPS-BONGAIGAON | #1 | 3.119 | North Eastern Region |  | 2018-05-08 17:39 | 43228.7354 | 2018-05-08 18:02 | 43228.7514 | -- | -- | -- | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RALAY MAL-OPERATION. |  | 99.95
[6 empty] | Sub Total --> | [6 empty] | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0
NER L412 | BTPS-BONGAIGAON | #2 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-01 00:01 | 43221.0007 | 2018-05-03 18:29 | 43223.7701 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 0764. |  | 100
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-04 23:12 | 43224.9667 | 2018-05-05 13:40 | 43225.5694 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 0834.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-05 23:23 | 43225.9743 | 2018-05-08 19:56 | 43228.8306 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 33 | N/A | N/A | N/A | LINE H/T VIDE CODE 0851.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-08 23:30 | 43228.9792 | 2018-05-09 20:01 | 43229.834 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 31 | N/A | N/A | N/A | LINE H/T VIDE CODE 0896.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-11 00:03 | 43231.0021 | 2018-05-11 19:55 | 43231.8299 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 52 | N/A | N/A | N/A | LINE H/T VIDE CODE 0952.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-15 00:14 | 43235.0097 | 2018-05-15 13:07 | 43235.5465 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 53 | N/A | N/A | N/A | LINE H/T VIDE CODE 1012.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-15 16:46 | 43235.6986 | 2018-05-17 18:13 | 43237.759 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 27 | N/A | N/A | N/A | LINE H/T VIDE CODE 1032.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-17 23:14 | 43237.9681 | 2018-05-18 08:32 | 43238.3556 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 1061.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-18 23:53 | 43238.9951 | 2018-05-19 08:16 | 43239.3444 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | N/A | N/A | N/A | LINE H/T VIDE CODE 1086.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-20 23:32 | 43240.9806 | 2018-05-21 12:37 | 43241.5257 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | N/A | N/A | N/A | LINE H/T VIDE CODE 1112
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-22 22:20 | 43242.9306 | 2018-05-23 10:15 | 43243.4271 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 55 | N/A | N/A | N/A | LINE H/T VIDE CODE 1150
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-23 10:15 | 43243.4271 | 2018-05-23 13:10 | 43243.5486 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 55 | N/A | N/A | N/A | COMMISSIONING OF NGR BY-PASS SCHEME & AMP OF LINE REACTOR
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-23 13:10 | 43243.5486 | 2018-05-25 16:19 | 43245.6799 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 9 | N/A | N/A | N/A | LINE KEPT OPEN AS PER NERLDC INSTRUCTION DUE TO SYSTEM CONSTRANTS
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-26 00:08 | 43246.0056 | 2018-05-26 18:59 | 43246.791 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 51 | N/A | N/A | N/A | LINE H/T VIDE CODE 1210
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-27 00:43 | 43247.0299 | 2018-05-27 18:49 | 43247.784 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | N/A | N/A | N/A | LINE H/T VIDE CODE 1225.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-28 22:14 | 43248.9264 | 2018-05-29 19:22 | 43249.8069 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | N/A | N/A | N/A | LINE H/T VIDE CODE 1269
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-05-29 23:22 | 43249.9736 | 2018-05-31 14:38 | 43251.6097 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 16 | N/A | N/A | N/A | LINE H/T VIDE CODE 1311
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 446 | 21
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-04 00:25 | 43224.0174 | 2018-05-04 17:58 | 43224.7486 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 33 | N/A | N/A | N/A | LINE H/T VIDE CODE 0815. |  | 100
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-09 03:21 | 43229.1396 | 2018-05-09 03:51 | 43229.1604 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR ,PATROLLING AND WEATHER REPORT
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-10 00:42 | 43230.0292 | 2018-05-10 19:29 | 43230.8118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 0937.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-11 23:53 | 43231.9951 | 2018-05-14 16:36 | 43234.6917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 43 | N/A | N/A | N/A | LINE H/T VIDE CODE 0981.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-19 14:16 | 43239.5944 | 2018-05-19 19:10 | 43239.7986 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 54 | N/A | N/A | N/A | LINE H/T VIDE CODE 1092.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-19 23:38 | 43239.9847 | 2018-05-20 19:04 | 43240.7944 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 26 | N/A | N/A | N/A | LINE H/T VIDE CODE 1099
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-22 00:08 | 43242.0056 | 2018-05-22 19:17 | 43242.8035 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | N/A | N/A | N/A | LINE H/T VIDE CODE 1130
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-27 22:52 | 43247.9528 | 2018-05-28 19:03 | 43248.7937 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | N/A | N/A | N/A | LINE H/T VIDE CODE 1242
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-27 22:52 | 43247.9528 | 2018-05-28 19:03 | 43248.7937 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | N/A | N/A | N/A | LINE H/T VIDE CODE 1242
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-29 22:30 | 43249.9375 | 2018-05-30 19:21 | 43250.8063 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 51 | N/A | N/A | N/A | LINE H/T VIDE CODE 1289
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-29 22:30 | 43249.9375 | 2018-05-30 19:21 | 43250.8063 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 51 | N/A | N/A | N/A | LINE H/T VIDE CODE 1289
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-05-31 21:33 | 43251.8979 | 2018-05-31 23:59 | 43251.9993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | N/A | N/A | N/A | LINE H/T VIDE CODE 1327
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 30 | 229 | 2
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-05-27 09:03 | 43247.3771 | 2018-05-27 16:47 | 43247.6993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 44 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 44
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-05-02 13:56 | 43222.5806 | 2018-05-02 14:15 | 43222.5938 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR ,PATROLLING AND WEATHER REPORT |  | 100
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-05-10 16:04 | 43230.6694 | 2018-05-10 16:15 | 43230.6771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS CONCLUDED BY DR AND WEATHER REPORT
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-05-27 09:03 | 43247.3771 | 2018-05-27 16:26 | 43247.6847 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 23 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-05-27 09:03 | 43247.3771 | 2018-05-27 16:26 | 43247.6847 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 23 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 30 | 14 | 46
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-05-18 08:07 | 43238.3382 | 2018-05-18 17:34 | 43238.7319 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 27 | N/A | N/A | N/A | MASS JUMPER TIGHTENING AT ALL TENSION TOWERS. |  | 100
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-05-19 07:44 | 43239.3222 | 2018-05-19 16:15 | 43239.6771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 31 | N/A | N/A | N/A | MASS JUMPER TIGHTENING AT ALL TENSION TOWERS.
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-05-24 00:38 | 43244.0264 | 2018-05-30 18:21 | 43250.7646 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 43 | N/A | N/A | N/A | LINE H/T VIDE CODE 1173
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 41
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-05-01 00:01 | 43221.0007 | 2018-05-02 16:31 | 43222.6882 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | N/A | N/A | N/A | LINE H/T VIDE CODE 0748. |  | 100
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-05-16 00:48 | 43236.0333 | 2018-05-16 09:22 | 43236.3903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 34 | N/A | N/A | N/A | LINE H/T VIDE CODE 1038.
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-05-17 01:00 | 43237.0417 | 2018-05-17 16:47 | 43237.6993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 1051.
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-05-20 09:37 | 43240.4007 | 2018-05-21 08:12 | 43241.3417 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | N/A | N/A | N/A | LINE H.T VIDE CODE 1103
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-05-21 08:12 | 43241.3417 | 2018-05-21 20:23 | 43241.8493 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 11 | N/A | N/A | N/A | MASS JUMPER TIGHTENING AT ALL TENSION TOWER LOCATION
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-05-21 23:23 | 43241.9743 | 2018-05-22 08:15 | 43242.3438 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | N/A | N/A | N/A | LINE H/T VIDE CODE 1129
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-05-22 08:15 | 43242.3438 | 2018-05-22 19:00 | 43242.7917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46 | N/A | N/A | N/A | MASS JUMPER TIGHTENING AT ALL TENSION TOWER LOCTIONS
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 15
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-02 13:38 | 43222.5681 | 2018-05-02 17:12 | 43222.7167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 34 | N/A | N/A | N/A | LINE H/T VIDE CODE 0788. |  | 100
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-05 02:13 | 43225.0924 | 2018-05-05 13:15 | 43225.5521 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2 | N/A | N/A | N/A | LINE H/T VIDE CODE 0836.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-07 01:05 | 43227.0451 | 2018-05-07 12:20 | 43227.5139 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 0866.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-14 05:05 | 43234.2118 | 2018-05-14 16:10 | 43234.6736 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | N/A | N/A | N/A | LINE H/T VIDE CODE 0955.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-14 22:54 | 43234.9542 | 2018-05-15 18:01 | 43235.7507 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | N/A | N/A | N/A | LINE H/T VIDE CODE 1011.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-18 03:23 | 43238.141 | 2018-05-18 08:38 | 43238.3597 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 1064.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-20 00:41 | 43240.0285 | 2018-05-20 14:53 | 43240.6201 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 1102
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-05-23 12:47 | 43243.5326 | 2018-05-23 17:53 | 43243.7451 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | N/A | N/A | N/A | LINE H/T VIDE CODE 1163
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 36
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-05-01 00:15 | 43221.0104 | 2018-05-01 17:46 | 43221.7403 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 31 | N/A | N/A | N/A | LINE H/T VIDE CODE 0765. |  | 100
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-05-03 00:06 | 43223.0042 | 2018-05-03 07:43 | 43223.3215 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 37 | N/A | N/A | N/A | LINE H/T VIDE CODE 0804.
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-05-03 23:29 | 43223.9785 | 2018-05-04 15:14 | 43224.6347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 45 | N/A | N/A | N/A | LINE H/T VIDE CODE 0805.
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-05-18 23:08 | 43238.9639 | 2018-05-19 16:21 | 43239.6813 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 1085.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 6
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-05-04 23:01 | 43224.959 | 2018-05-04 23:26 | 43224.9764 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO OVERVOLTAGE AT BÇHARIALI END. |  | 100
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region | Insulator damaged | 2018-05-16 10:00 | 43236.4167 | 2018-05-16 17:20 | 43236.7222 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 7 | 20 | 0 | 0 | 2 | N | -2 | E/S/D TAKEN FOR INSULATOR REPLACEMENT AT LOC 356 DAMAGED DUE TO LIGHTENING.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 7 | 48 | 0 | 0
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region | Jumper snapped | 2018-05-08 04:30 | 43228.1875 | 2018-05-08 16:00 | 43228.6667 | -- | -- | 0.5 | 11 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -2.5 | B-PH JUMPER SNAPPED AT LOC 79 |  | 97
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-05-08 16:01 | 43228.6674 | 2018-05-09 08:00 | 43229.3333 | -- | -- | -- | 0 | 0 | 0 | 0 | 15 | 59 | 0 | 0 | N/A | N/A | N/A | LINE PUT UNDER S/D AS S/D WORKS FOR B-PH REJUMPERING AT LOC 79 CEASED DUE SUDDEN INCLEMENT WEATHER
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-05-09 08:01 | 43229.334 | 2018-05-09 18:10 | 43229.7569 | -- | -- | -- | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR B-PH REJUMPERING WORKS AT LOC 79
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-05-20 10:28 | 43240.4361 | 2018-05-20 16:06 | 43240.6708 | -- | -- | -- | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY PKBARI (STATE) END
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-05-27 08:39 | 43247.3604 | 2018-05-27 16:38 | 43247.6931 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 59 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
|  |  |  | North Eastern Region |  | Sub Total --> | [6 empty] | 21 | 39 | 5 | 38 | 15 | 59 | 7 | 59
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-05-20 10:28 | 43240.4361 | 2018-05-20 16:06 | 43240.6708 | -- | -- | -- | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY PKBARI END (STATE0 |  | 100
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-05-27 08:39 | 43247.3604 | 2018-05-27 18:39 | 43247.7771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 5 | 38 | 0 | 0 | 10 | 0
NER RBR1 | BR_BONGAIGAON (50MVAR) | # 1 | 50 | North Eastern Region |  | 2018-05-22 11:06 | 43242.4625 | 2018-05-22 13:24 | 43242.5583 | -- | -- | -- | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP |  | 99.69
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | Sub Total --> | [6 empty] | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region |  | 2018-05-23 09:58 | 43243.4153 | 2018-05-23 16:21 | 43243.6813 | -- | -- | -- | 6 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ARRESTING OIL LEAKAGE OF B-PH BUSHING TOP |  | 99.14
[6 empty] | Sub Total --> | [6 empty] | 6 | 23 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR5 | BR_KUMARGHAT (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR6 | BR_AIZWAL (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-05-02 10:15 | 43222.4271 | 2018-05-02 16:28 | 43222.6861 | -- | -- | -- | 6 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP WORKS. |  | 99.16
[6 empty] | Sub Total --> | [6 empty] | 6 | 13 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-05-30 10:18 | 43250.4292 | 2018-05-30 16:59 | 43250.7076 | -- | -- | -- | 6 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D AVAIELD FOR CHARNGING FAULTY DIFFERENTIAL RELAY |  | 99.1
[6 empty] | Sub Total --> | [6 empty] | 6 | 41 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR13 | BR_B'CHARIALI(80MVAR) | #2 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR14 | BR_B'CHARIALI(63MVAR) | #3 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR15 | BR_B'CHARIALI(63MVAR) | #4 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR16 | BR_New_MARIANI(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR17 | BR_BALIPARA(125MVAR) | #3 | 125 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR19 | BR_ROING(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
| BR_ROING(20MVAR) | #1 |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT1 | ICT_BONGAIGAON(315MVA) |  | 315 | North Eastern Region |  | 2018-05-09 08:56 | 43229.3722 | 2018-05-09 09:33 | 43229.3979 | -- | -- | -- | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FAULT IN 132KV BTPS-DHALIGAON STATE LINE. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0
NER TICT2 | ICT_BALIPARA (315MVA) | #1 | 315 | North Eastern Region |  | 2018-05-28 10:59 | 43248.4576 | 2018-05-28 13:34 | 43248.5653 | -- | -- | -- | 2 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ES/D TAKEN FOR ATTENDING HOT SPOT IN 33KV SIDE R-PH |  | 99.65
[6 empty] | Sub Total --> | [6 empty] | 2 | 35 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT3 | ICT_BALIPARA (315MVA) | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-05-07 09:44 | 43227.4056 | 2018-05-07 17:21 | 43227.7229 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 37 | N/A | N/A | N/A | REPLACEMENT OF EXISTING ICT-1 UNDER NERSS-IV PROJECT WITH NEW 500MVA ICT. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 37
NER TICT5 | ICT_MISA | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region |  | 2018-05-27 09:11 | 43247.3826 | 2018-05-27 16:06 | 43247.6708 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 55 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 55
NER TICT7 | ICT_B'CHARIALI (200MVA) | #1 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT8 | ICT_B'CHARIALI (200MVA) | #2 | 200 | North Eastern Region |  | 2018-05-04 10:37 | 43224.4424 | 2018-05-04 17:25 | 43224.7257 | -- | -- | -- | 6 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR B-PH CT REPLACEMENT. |  | 99.09
[6 empty] | Sub Total --> | [6 empty] | 6 | 48 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT9 | ICT_IMPHAL(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT10 | ICT_IMPHAL(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT12 | ICT_DIMAPUR (100 MVA) | # 1 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT13 | ICT_DIMAPUR (100 MVA) | #2 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-05-10 17:05 | 43230.7118 | 2018-05-10 19:37 | 43230.8174 | -- | -- | -- | 2 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MALOPERATION. |  | 97.24
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-05-11 01:18 | 43231.0542 | 2018-05-11 18:11 | 43231.7576 | -- | -- | -- | 16 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MAL-OPERATION.
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-05-25 16:32 | 43245.6889 | 2018-05-25 17:40 | 43245.7361 | -- | -- | -- | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MALOPERATION
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-05-27 09:12 | 43247.3833 | 2018-05-27 16:07 | 43247.6715 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 55 | N/A | N/A | N/A | LINE H/T FOR FACILITATING 132KV BUS - I & II S/D AT SILCHAR UNDER NERSS CONSTRUCTION PROJECT.
[6 empty] | Sub Total --> | [6 empty] | 20 | 33 | 0 | 0 | 0 | 0 | 6 | 55
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT16 | ICT_MOKOKCHUNG(30MVA) | #2 | 30 | North Eastern Region |  | 2018-05-15 15:56 | 43235.6639 | 2018-05-15 16:38 | 43235.6931 | -- | -- | -- | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT. |  | 99.91
[6 empty] | Sub Total --> | [6 empty] | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT17 | ICT_NIRJULI(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT18 | ICT_NIRJULI(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT19 | ICT_ZIRO (15MVA) |  | 15 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT20 | ICT_KOPILI (160 MVA) | # 2 | 160 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT21 | ICT_KUMARGHAT(5MVA) |  | 5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT22 | ICT_SILCHAR(315MVA) | #3 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## JUNE 2018 - TABLE I
Unique ID of transmission Element | Element Name |  | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee Hr min |  | OTHERS Hr min |  | System Constraints/ Natural calamity / Militancy Hr min |  | Deemed Available Hr min
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region | [20 empty] | NERPC/OP/TAC/2018-19/3423 Dtd 26.09.2018 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-06-09 02:00 | 43260.0833 | 2018-06-09 02:31 | 43260.1049 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO THUNDERSTORM |  | 99.94
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-06-11 15:35 | 43262.6493 | 2018-06-11 15:47 | 43262.6576 | -- | -- | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT PHASE TO PHASE FAULT
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-06-14 11:40 | 43265.4861 | 2018-06-14 11:55 | 43265.4965 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO CONTACT WITH BAMBOO FROM OUTSIDE LINE CORRIDOR BETWEEN LOC 138-139 ON ACCOUNT OF LANDSLIDE DUE TO HEAVY RAINFALL
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-06-25 13:32 | 43276.5639 | 2018-06-25 13:47 | 43276.5743 | -- | -- | -- | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRANSIENT PHASE TO PHASE FAULT
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-06-28 08:00 | 43279.3333 | 2018-06-28 17:50 | 43279.7431 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | N/A | N/A | N/A | PROVIDEINF ADDITIONAL JUMPE AT LOC 188
[6 empty] | Sub Total --> | [6 empty] | 0 | 27 | 0 | 0 | 0 | 46 | 9 | 50
NER L105 | AIZWAL_ZEMEBAK | # 2 | 6.719 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-06-22 11:38 | 43273.4847 | 2018-06-22 13:57 | 43273.5813 | -- | -- | -- | 2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | EMERGENCY S/D TAKEN FOR REPLACEMENT OF B-PH LINE ISOLATOR FINGER CONTACT AT BDP (STATE) END. |  | 99.68
[6 empty] | Sub Total --> | [6 empty] | 2 | 19 | 0 | 0 | 0 | 0 | 0 | 0
NER L107 | BADARPUR_JIRIBAM |  | 67.21 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region |  | 2018-06-07 10:24 | 43258.4333 | 2018-06-07 13:42 | 43258.5708 | -- | -- | -- | 0 | 0 | 0 | 0 | 3 | 18 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING TREE BETWEEN LOC. 148-149; INFRINGEMENT FUR TO RECENT STORMS. |  | 100
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region |  | 2018-06-18 01:44 | 43269.0722 | 2018-06-18 02:20 | 43269.0972 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO GRID DISTURBANCE.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 3 | 54 | 0 | 0
NER L109 | BADARPUR_KUMARGHAT |  | 118.513 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-06-06 11:06 | 43257.4625 | 2018-06-06 17:11 | 43257.716 | -- | -- | 0 | 0 | 0 | 6 | 5 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO INSUFFICIENT CLEARANCE WITH NEW 33kV STATE LINE FEEDER B/W LOC. NO. 372-373. |  | 100
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-06-07 17:40 | 43258.7361 | 2018-06-07 18:42 | 43258.7792 | -- | -- | -- | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ESD TAKEN FOR DISMANTLING OF NEWLY ERRECTED 33 KV STATE LINE B/W LOC 372-373.
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-06-18 01:39 | 43269.0687 | 2018-06-18 02:44 | 43269.1139 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO GRID DISTURBANCE.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 7 | 7 | 1 | 6 | 0 | 0
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region | Insulator broken | 2018-06-04 01:25 | 43255.059 | 2018-06-04 01:59 | 43255.0826 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 2 | N | -2 | ONE NO INSULATOR OF R-PH FOUND BROKEN AT LOC 24 DUE TO LIGHTNING STRIKE. |  | 100
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region |  | 2018-06-18 01:39 | 43269.0687 | 2018-06-18 02:47 | 43269.116 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO GRID DISTURBANCE
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 42 | 0 | 0
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-06-18 01:39 | 43269.0687 | 2018-06-18 02:52 | 43269.1194 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 13 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO GRID DISTURBANCES. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 13 | 0 | 0
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region |  | 2018-06-14 11:00 | 43265.4583 | 2018-06-14 12:22 | 43265.5153 | -- | -- | -- | 0 | 0 | 0 | 0 | 1 | 22 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING OF TREES AT LOC 23-24; INFRINGEMENT DUE TO INCESSANT RAIN. |  | 98.54
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region |  | 2018-06-26 08:04 | 43277.3361 | 2018-06-26 17:10 | 43277.7153 | -- | -- | -- | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP WORK
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region |  | 2018-06-26 19:07 | 43277.7965 | 2018-06-27 10:48 | 43278.45 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 41 | N/A | N/A | N/A | H/T FOR POWER REGULATION ON RLDC INSTRUCTION
[6 empty] | Sub Total --> | [6 empty] | 9 | 6 | 0 | 0 | 1 | 22 | 15 | 41
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-06-06 10:55 | 43257.4549 | 2018-06-06 11:10 | 43257.4653 | -- | -- | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ( TRIPPED DUE TO DOWN STREAM FAULT OF MANIPUR STATE END) |  | 100
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-06-18 10:29 | 43269.4368 | 2018-06-18 10:54 | 43269.4542 | -- | -- | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-06-23 10:08 | 43274.4222 | 2018-06-23 10:14 | 43274.4264 | -- | -- | -- | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | FAULT WAS IN 132V IMPHAL(STATE)-KARONG (STATE FEEDER)
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region |  | 2018-06-06 01:42 | 43257.0708 | 2018-06-06 02:10 | 43257.0903 | -- | -- | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 99.97
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region |  | 2018-06-30 14:59 | 43281.6243 | 2018-06-30 15:10 | 43281.6319 | -- | -- | -- | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRANSIENT PHASE TO PHASE FAULT
[6 empty] | Sub Total --> | [6 empty] | 0 | 11 | 0 | 28 | 0 | 0 | 0 | 0
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-01 08:03 | 43252.3354 | 2018-06-01 20:49 | 43252.8674 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 46 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR. |  | 100
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-02 07:03 | 43253.2937 | 2018-06-02 19:12 | 43253.8 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 9 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-03 07:24 | 43254.3083 | 2018-06-03 19:25 | 43254.809 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-04 07:23 | 43255.3076 | 2018-06-04 19:00 | 43255.7917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 37 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-05 07:23 | 43256.3076 | 2018-06-05 19:19 | 43256.8049 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 56 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-06 01:42 | 43257.0708 | 2018-06-06 02:10 | 43257.0903 | -- | -- | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-06 08:03 | 43257.3354 | 2018-06-06 17:11 | 43257.716 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-07 08:02 | 43258.3347 | 2018-06-07 17:29 | 43258.7285 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 27 | N/A | N/A | N/A | S/D AVAILED FOR MASS REPLACEMENT OF EXISTING PORCELAIN INSULATOR WITH POLYMER INSULATOR.
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-06-21 20:50 | 43272.8681 | 2018-06-21 21:02 | 43272.8764 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO THUNDERSTORM.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 28 | 0 | 12 | 79 | 4
NER L118 | KHANDONG-HAFLONG |  | 63.166 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-06-06 06:52 | 43257.2861 | 2018-06-06 07:18 | 43257.3042 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | N/A | N/A | N/A | (TRIPPED DUE TO HEAVY LIGHTENING). |  | 100
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-06-07 14:27 | 43258.6021 | 2018-06-07 14:36 | 43258.6083 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY THUNDER STORM.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-06-08 14:36 | 43259.6083 | 2018-06-08 14:46 | 43259.6153 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO THUNDERSTORM. |  | 100
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-06-14 02:00 | 43265.0833 | 2018-06-14 02:12 | 43265.0917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N/A | N/A | N/A | INTENSE THUNDERSTORM PREVAILING OVER KHLIEHRIAT REGION.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0
NER L121 | KHANDONG_KOPILI | # 1 | 10.914 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region |  | 2018-06-07 14:23 | 43258.5993 | 2018-06-07 14:37 | 43258.609 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY THUNDER STORM. |  | 100
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region |  | 2018-06-30 14:20 | 43281.5972 | 2018-06-30 15:55 | 43281.6632 | -- | -- | -- | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY STATE TO FACILITATE BUS S/D AT KHLIEHRIAT END
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 35 | 0 | 14 | 0 | 0
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L125 | SALAKATI-GELEPHUG |  | 49.217 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L126 | LEKHI - RANGANADI |  | 12.59 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region |  | 2018-06-27 10:40 | 43278.4444 | 2018-06-27 15:40 | 43278.6528 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | N/A | N/A | N/A | NTAMC ADAPTATION WORKS |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-06-09 02:33 | 43260.1062 | 2018-06-09 03:21 | 43260.1396 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO THUNDERSTORM. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-06-09 11:00 | 43260.4583 | 2018-06-09 13:05 | 43260.5451 | -- | -- | -- | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ATTENDING HOT SPOT IN B-PH. BUS ISOLATOR AT ZIRO. |  | 99.71
[6 empty] | Sub Total --> | [6 empty] | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0
NER L130 | KHANDONG_KOPILI | # 2 | 11.56 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L137 | IMPHAL-IMPHAL | # 2 | 0.442 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-06-06 02:20 | 43257.0972 | 2018-06-06 02:36 | 43257.1083 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING FAULT AS SUPPORTED BY DR AND WEATHER REPORT |  | 100
NER L139 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-06-21 04:37 | 43272.1924 | 2018-06-21 05:11 | 43272.216 | -- | -- | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 34 | 0 | 16 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-06-06 02:20 | 43257.0972 | 2018-06-06 02:35 | 43257.1076 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING FAULT AS SUPPORTED BY DR AND WEATHER REPORT |  | 100
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-06-21 04:37 | 43272.1924 | 2018-06-21 04:57 | 43272.2063 | -- | -- | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 20 | 0 | 15 | 0 | 0
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L142 | B.CHARAILI_PAVOI | #1 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L143 | B.CHARAILI_PAVOI | #2 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L144 | ROING_PASIGHAT |  |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L146 | AIZAWL MELRIAT |  |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L153 | MELRIAT - ZEMABAWK |  |  | North Eastern Region |  | 2018-06-02 10:12 | 43253.425 | 2018-06-02 16:49 | 43253.7007 | -- | -- | -- | 0 | 0 | 6 | 37 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY STATE. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 6 | 37 | 0 | 0 | 0 | 0
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-06-06 01:42 | 43257.0708 | 2018-06-06 01:55 | 43257.0799 | -- | -- | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 100
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-06-16 04:46 | 43267.1986 | 2018-06-16 05:06 | 43267.2125 | -- | -- | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | (TRIPPED DUE TO DOWN STREAM FAULT )
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region |  | 2018-06-24 01:21 | 43275.0563 | 2018-06-24 07:59 | 43275.3326 | -- | -- | -- | 0 | 0 | 0 | 0 | 6 | 38 | 0 | 0 | N/A | N/A | N/A | LINE KEPT OPEN AS RESTORATION WORK COULDN’T BE COMMENCED DUE TO INCLEMENT WEATHER DURING NIGHT HRS. |  | 97.96
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region | Conductor snapped | 2018-06-24 08:00 | 43275.3333 | 2018-06-24 16:00 | 43275.6667 | -- | -- | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -3 | CONDUCTOR AT LOC 25 SNAPPED DUE TO HARDWARE FAILURE
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region |  | 2018-06-24 16:01 | 43275.6674 | 2018-06-25 07:59 | 43276.3326 | -- | -- | -- | 0 | 0 | 0 | 0 | 15 | 58 | 0 | 0 | N/A | N/A | N/A | LINE KEPT UNDER S/D SINCE RESTORATION WORK HALTED ON A/C OF HEAVY RAINFALL AND INCLEMENT WEATHER
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region | Conductor snapped | 2018-06-25 08:00 | 43276.3333 | 2018-06-25 14:14 | 43276.5931 | -- |  | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -3 | CONDUCTOR AT LOC 25 SNAPPED DUE TO FAILURE OF HARDWARE
[6 empty] | Sub Total --> | [6 empty] | 14 | 14 | 0 | 0 | 22 | 36 | 0 | 0
NER L202 | KATHALGURI_MARIANI(OLD) |  | 162.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L203 | MISA_DIMAPUR | # 1 | 123.52 |  |  | 2018-06-26 10:39 | 43277.4437 | 2018-06-26 22:03 | 43277.9187 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 24 | 3 | N | -2.5 | RE STRINING OF CONDUCTOR BETWEEN LOC 202-203 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 24
NER L204 | MISA_DIMAPUR | # 2 | 123.52 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L205 | MISA_KATHALGURI |  | 382.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L206 | MISA-KOPILI | # 1 | 72.791 | North Eastern Region |  | 2018-06-17 17:15 | 43268.7188 | 2018-06-17 18:28 | 43268.7694 | -- | -- | -- | 0 | 0 | 0 | 0 | 1 | 13 | 0 | 0 | N/A | N/A | N/A | ESD TAKEN FOR CLEARING BAMBOO BETWEEN LOC 137-138; INFRINGEMENT DUE TO FLOOD & EROSION. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 13 | 0 | 0
NER L207 | MISA_KOPILI | # 2 | 72.791 | North Eastern Region |  | 2018-06-02 14:02 | 43253.5847 | 2018-06-02 14:22 | 43253.5986 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING STROKE AT LOC 281 RESULTING IN MELTING OF COPPER BOND |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0
NER L208 | MISA_KOPILI | # 3 | 75.788 | North Eastern Region |  | 2018-06-14 12:02 | 43265.5014 | 2018-06-14 13:05 | 43265.5451 | -- | -- | -- | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY NEEPCO FOR ATTENDING SF₆ GAS LEAKAGE AT KOPILI END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region | Copper Bond melt | 2018-06-21 12:16 | 43272.5111 | 2018-06-21 12:27 | 43272.5188 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 3 | N | -3 | TRIPPED DUE TO LIGHTNING STROKE AT LOC 18 TOWER RESULTING IN MELTGING OF COPPER BOND |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0
NER L212 | SALAKATI_BTPS | # 2 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L213 | SALAKATI-BTPS | # 1 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region | [21 empty] | 100
|  |  |  | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region | [5 empty] | -- | -- | -- | [13 empty] | 100
Sub Total -->
NER L401 | BALIPARA_BONGAIGAON | # 1 | 289.721 | North Eastern Region | [5 empty] | -- | -- | -- | [13 empty] | 100
Sub Total -->
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-06-21 11:40 | 43272.4861 | 2018-06-21 12:47 | 43272.5326 | -- | -- | -- | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CUTTING BAMBOO TREE WHICH CAME NEAR THE LINE DUE TO RECENT STORM. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 0
NER L403 | MISA_BALIPARA | # 1 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L404 | MISA-BALIPARA | #2 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L405 | BONGAIGAON-MALDA | # 1 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L406 | BONGAIGAON-MALDA | # 2 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L407 | BALIPARA-RANGANADI | # 1 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L408 | BALIPARA-RANGANADI | # 2 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L409 | PALLATANA-SURAJMANINAGAR | # 1 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L411 | BTPS-BONGAIGAON | #1 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L412 | BTPS-BONGAIGAON | #2 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-06-01 23:34 | 43252.9819 | 2018-06-02 12:46 | 43253.5319 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 1346. |  | 100
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-06-14 02:16 | 43265.0944 | 2018-06-14 18:01 | 43265.7507 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 45 | N/A | N/A | N/A | LINE H/T VIDE CODE 1550.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-06-18 03:21 | 43269.1396 | 2018-06-18 19:04 | 43269.7944 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 43 | N/A | N/A | N/A | LINE H/T VIDE CODE 1608.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-06-20 01:50 | 43271.0764 | 2018-06-20 11:27 | 43271.4771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 37 | N/A | N/A | N/A | LINE H/T VIDE CODE 1627.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-06-27 01:35 | 43278.066 | 2018-06-27 19:01 | 43278.7924 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 26 | N/A | N/A | N/A | H/T VIDE CODE 1746
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-06-29 05:11 | 43280.216 | 2018-06-29 18:41 | 43280.7785 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 30 | N/A | N/A | N/A | LINE H/T VIDE CODE 1785
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-06-30 22:36 | 43281.9417 | 2018-06-30 23:59 | 43281.9993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 23 | N/A | N/A | N/A | LINR H/T VIDE CODE 1818
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 36
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-01 00:01 | 43252.0007 | 2018-06-01 18:58 | 43252.7903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 57 | N/A | N/A | N/A | LINE H/T VIDE CODE 1327. |  | 100
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-05 13:38 | 43256.5681 | 2018-06-05 16:23 | 43256.6826 | -- | -- | -- | 0 | 0 | 0 | 0 | 2 | 45 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR SAFETY PURPOSE FOR CLEARING TREE BETWEEN LOC 464-465.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-05 16:23 | 43256.6826 | 2018-06-05 18:32 | 43256.7722 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 9 | N/A | N/A | N/A | LINE KEPT OPEN AS PER NERLDC INSTRUCTION DUE TO SYSTEM CONSTRAINTS.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-09 17:34 | 43260.7319 | 2018-06-09 18:47 | 43260.7826 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 1491.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-10 06:55 | 43261.2882 | 2018-06-11 19:04 | 43262.7944 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 9 | N/A | N/A | N/A | LINE H/T VIDE CODE 1499.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-12 08:02 | 43263.3347 | 2018-06-13 19:18 | 43264.8042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | N/A | N/A | N/A | LINE H/T VIDE CODE 1522.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-15 06:23 | 43266.266 | 2018-06-15 18:37 | 43266.7757 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | N/A | N/A | N/A | LINE H/T VIDE CODE 1575.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-19 01:57 | 43270.0813 | 2018-06-19 14:33 | 43270.6062 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 36 | N/A | N/A | N/A | LINE H/T VIDE CODE 1619.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-25 01:06 | 43276.0458 | 2018-06-25 12:20 | 43276.5139 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | N/A | N/A | N/A | H/T VIDE CODE 1702
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-26 00:31 | 43277.0215 | 2018-06-26 19:24 | 43277.8083 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 53 | N/A | N/A | N/A | LINE H/T VIDE CODE 1722
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-28 01:12 | 43279.05 | 2018-06-28 18:39 | 43279.7771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 27 | N/A | N/A | N/A | H/T VIDE CODE 1765
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-06-30 03:35 | 43281.1493 | 2018-06-30 18:19 | 43281.7632 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 44 | N/A | N/A | N/A | LINE H/T VIDE CODE 1798
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 2 | 45 | 180 | 52
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-06-21 20:50 | 43272.8681 | 2018-06-21 21:06 | 43272.8792 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO THUNDERSTORM. |  | 100
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-06-29 08:18 | 43280.3458 | 2018-06-29 19:07 | 43280.7965 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49 | N/A | N/A | N/A | S/D TAKEN FOR REPLACMENT OF EXISTING EQUIPMENT BY HIGHER RATING EQUIPMENT UNDER NERSS PROJECT
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-06-30 08:13 | 43281.3424 | 2018-06-30 17:23 | 43281.7243 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | N/A | N/A | N/A | S/D TAKEN FOR REPLACMENT OF EXISTING EQUIPMENT BY HIGHER RATING EQUIPMENT UNDER THE PROJECT OF NERSS
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 59
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-06-16 23:58 | 43267.9986 | 2018-06-18 19:10 | 43269.7986 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 1598. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 12
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-03 05:20 | 43254.2222 | 2018-06-03 14:48 | 43254.6167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 1372. |  | 100
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-04 04:44 | 43255.1972 | 2018-06-04 16:15 | 43255.6771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | N/A | N/A | N/A | LINE H/T VIDE CODE 1391.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-05 00:02 | 43256.0014 | 2018-06-05 14:59 | 43256.6243 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 57 | N/A | N/A | N/A | LINE H/T VIDE CODE 1409.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-05 23:24 | 43256.975 | 2018-06-06 15:52 | 43257.6611 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 1423.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-07 00:33 | 43258.0229 | 2018-06-07 14:58 | 43258.6236 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 25 | N/A | N/A | N/A | LINE H/T VIDE CODE 1450.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-08 00:30 | 43259.0208 | 2018-06-08 16:53 | 43259.7035 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 23 | N/A | N/A | N/A | LINE H/T VIDE CODE 1466.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-09 00:26 | 43260.0181 | 2018-06-09 17:37 | 43260.734 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | N/A | N/A | N/A | LINE H/T VIDE CODE 1478.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-09 17:58 | 43260.7486 | 2018-06-09 20:30 | 43260.8542 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 32 | N/A | N/A | N/A | LINE H/T VIDE CODE 1492 AS PER NERLDC INSTRUCTION DUE TO CB PROBLEM AT RANGANADI END.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-10 04:59 | 43261.2076 | 2018-06-10 17:51 | 43261.7438 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 52 | N/A | N/A | N/A | LINE H/T VIDE CODE 1498.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-12 00:07 | 43263.0049 | 2018-06-12 14:13 | 43263.5924 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 6 | N/A | N/A | N/A | LINE H/T VIDE CODE 1519.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-06-25 01:49 | 43276.0757 | 2018-06-25 17:03 | 43276.7104 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | N/A | N/A | N/A | LINE H/T VIDE CODE 1704
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 7
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region |  | 2018-06-22 11:38 | 43273.4847 | 2018-06-22 14:46 | 43273.6153 | -- | -- | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 3 | N | -3 | TREE CAME IN CONTACT WITH CONDUCTOR AT LOC 09-10 WHICH FALLS UNDER AREA OF SEVERE ROW ISSUES. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-06-09 10:22 | 43260.4319 | 2018-06-09 17:56 | 43260.7472 | -- | -- | -- | 0 | 0 | 0 | 0 | 7 | 34 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR CLEARING INFRIGEMENT AT 163,164,153,154. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 7 | 34 | 0 | 0
NER RBR1 | BR_BONGAIGAON (50MVAR) | # 1 | 50 | North Eastern Region |  | 2018-06-02 18:51 | 43253.7854 | 2018-06-02 20:05 | 43253.8368 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | N/A | N/A | N/A | B/R H/T VIDE CODE 1365. |  | 100
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 14
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-06-02 19:02 | 43253.7931 | 2018-06-02 22:15 | 43253.9271 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 13 | N/A | N/A | N/A | B/R H/T VIDE CODE 1366 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 13
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR5 | BR_KUMARGHAT (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR6 | BR_AIZWAL (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-06-23 21:25 | 43274.8924 | 2018-06-24 00:21 | 43275.0146 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 56 | N/A | N/A | N/A | BR H/T VIDE CODE 1689 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 56
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | [22 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-06-18 19:06 | 43269.7958 | 2018-06-18 23:39 | 43269.9854 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33 | N/A | N/A | N/A | BUS REACTOR H/T VIDE CODE 1615. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-06-25 11:09 | 43276.4646 | 2018-06-25 17:12 | 43276.7167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | N/A | N/A | N/A | ICT-III CONDTRUCTION WORK |  | 100
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-06-26 11:01 | 43277.459 | 2018-06-26 17:25 | 43277.7257 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 24 | N/A | N/A | N/A | ICT-III CONSTRUCTION WORK
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-06-27 11:05 | 43278.4618 | 2018-06-27 17:21 | 43278.7229 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 16 | N/A | N/A | N/A | ICT-III CONSTRUCTION WORK
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 43
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-02 19:59 | 43253.8326 | 2018-06-02 23:21 | 43253.9729 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 22 | N/A | N/A | N/A | B/R H/T VIDE CODE 1367 |  | 100
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-03 18:59 | 43254.791 | 2018-06-03 21:54 | 43254.9125 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 55 | N/A | N/A | N/A | B/R H/T VIDE CODE 1386.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-06 20:22 | 43257.8486 | 2018-06-07 00:09 | 43258.0062 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 47 | N/A | N/A | N/A | BUS REACTOR H/T VIDE CODE 1446 FOR VOLTAGE REGULATION.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-07 21:12 | 43258.8833 | 2018-06-08 06:53 | 43259.2868 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 41 | N/A | N/A | N/A | BUS REACTOR H/T VIDE CODE 1465 FOR VOLTAGE REGULATION.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-08 19:24 | 43259.8083 | 2018-06-09 17:56 | 43260.7472 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 32 | N/A | N/A | N/A | BUS REACTOR H/T VIDE CODE 1476 FOR VOLTAGE REGULATION.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-11 20:20 | 43262.8472 | 2018-06-12 00:21 | 43263.0146 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | N/A | N/A | N/A | BUS REACTOR H/T VIDE CODE 1518 FOR VOLTAGE REGULATION.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-14 18:53 | 43265.7868 | 2018-06-15 00:26 | 43266.0181 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33 | N/A | N/A | N/A | BUS REACTOR H/T VIDE CODE 1572 FOR VOLTAGE REGULATION.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-15 19:18 | 43266.8042 | 2018-06-15 22:53 | 43266.9535 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 35 | N/A | N/A | N/A | B/R H/T VIDE CODE 1584.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-18 19:19 | 43269.8049 | 2018-06-18 22:37 | 43269.9424 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | N/A | N/A | N/A | B/R H/T VIDE CODE 1616
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-19 19:41 | 43270.8201 | 2018-06-19 22:27 | 43270.9354 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | N/A | N/A | N/A | B/R H/T VIDE CODE 1624.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-06-23 19:39 | 43274.8187 | 2018-06-24 01:29 | 43275.0618 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | N/A | N/A | N/A | BR H/T VIDE CODE 1686
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR13 | BR_B'CHARIALI(80MVAR) | #2 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR14 | BR_B'CHARIALI(63MVAR) | #3 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR15 | BR_B'CHARIALI(63MVAR) | #4 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR16 | BR_New_MARIANI(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR17 | BR_BALIPARA(125MVAR) | #3 | 125 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR19 | BR_ROING(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
| BR_ROING(20MVAR) | #1 |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT1 | ICT_BONGAIGAON(315MVA) |  | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT2 | ICT_BALIPARA (315MVA) | #1 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT3 | ICT_BALIPARA (315MVA) | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT5 | ICT_MISA | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region |  | 2018-06-25 14:58 | 43276.6236 | 2018-06-25 15:15 | 15:15 | -- | -- | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO MALOPERATION OF WTI |  | 99.15
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region |  | 2018-06-25 18:09 | 43276.7562 | 2018-06-25 18:58 | 18:58 | -- | -- | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO MAL-OPERATION OF OTI
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region |  | 2018-06-26 10:58 | 43277.4569 | 2018-06-26 16:00 | 16:00 | -- | -- | -- | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN TO ATTEND OSR PROBLEM
[6 empty] | Sub Total --> | [6 empty] | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT7 | ICT_B'CHARIALI (200MVA) | #1 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT8 | ICT_B'CHARIALI (200MVA) | #2 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT9 | ICT_IMPHAL(50MVA) | #1 | 50 | North Eastern Region |  | 2018-06-27 09:57 | 43278.4146 | 2018-06-27 17:51 | 17:51:00 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 54 | N/A | N/A | N/A | NEW CONSTRUCTION RELATED SHUTDOWN |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 54
NER TICT10 | ICT_IMPHAL(50MVA) | #2 | 50 | North Eastern Region |  | 2018-06-28 09:19 | 43279.3882 | 2018-06-28 15:42 | 15:42:00 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 23 | N/A | N/A | N/A | NEW CONSTRUCTION RELATED SHUTDOWN |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 23
NER TICT11 | ICT_SALAKATI (50 MVA) | # 1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT12 | ICT_DIMAPUR (100 MVA) | # 1 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT13 | ICT_DIMAPUR (100 MVA) | #2 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region |  | 2018-06-16 06:08 | 43267.2556 | 2018-06-16 08:00 | 8:00 | -- | -- | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON PRD ( MALOPERATION OF PRD ). |  | 99.74
[6 empty] | Sub Total --> | [6 empty] | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT16 | ICT_MOKOKCHUNG(30MVA) | #2 | 30 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT17 | ICT_NIRJULI(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT18 | ICT_NIRJULI(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT19 | ICT_ZIRO (15MVA) |  | 15 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT20 | ICT_KOPILI (160 MVA) | # 2 | 160 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT21 | ICT_KUMARGHAT(5MVA) |  | 5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT22 | ICT_SILCHAR(315MVA) | #3 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## JULY 2018 - TABLE I
Unique ID of transmission Element | Element Name |  | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee Hr min |  | OTHERS Hr min |  | System Constraints/ Natural calamity / Militancy Hr min |  | Deemed Available Hr min
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-07-31 04:03 | 43312.1687 | 2018-07-31 07:30 | 43312.3125 | -- | -- | -- | 0 | 0 | 3 | 27 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ATTENDING HOTSPOTS AT BUS SECTION 1 & 2 AT AGARTALA S/S (STATE). | Awaited | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3 | 27 | 0 | 0 | 0 | 0
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-07-12 16:15 | 43293.6771 | 2018-07-12 19:02 | 43293.7931 | -- | -- | -- | 0 | 0 | 2 | 47 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | 66KV CT BELONGING TO STATE BLASTED AT KOLASIB STATE END. |  | 100
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-07-13 16:53 | 43294.7035 | 2018-07-13 17:32 | 43294.7306 | -- | -- | -- | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY KOLASIB (MIZORAM P&E DEPT.) FOR CT REPLACEMENT AT KOLASIB S/S.
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-07-20 18:07 | 43301.7549 | 2018-07-20 18:18 | 43301.7625 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | N/A | N/A | N/A | INCLEMENT WEATHER AT KOLASIB END
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region | Flashover mark insulator | 2018-07-26 10:00 | 43307.4167 | 2018-07-26 10:18 | 43307.4292 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 2 | N | -2 | TRIPPED DUE TO LIGHTNING AS FLASHOVER MARK OBSERVED ON Y-PH INSULATOR AT LOC 283 .
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3 | 26 | 0 | 29 | 0 | 0
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-07-06 12:41 | 43287.5285 | 2018-07-06 12:49 | 43287.534 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | N/A | N/A | N/A | BANANA TREE FROM OUTSIDE LINE CORRIDOR FELLED BY MISCREANTS OVER R-PH BETWEEN LOC 136-137
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-07-12 16:17 | 43293.6785 | 2018-07-12 16:48 | 43293.7 | -- | -- | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MAL OPERATION.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-07-14 09:26 | 43295.3931 | 2018-07-14 09:46 | 43295.4069 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TOUCHING OF BAMBOOS ON A/C OF LANDSLIDE BETWEEN LOC 93-94
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-07-15 12:43 | 43296.5299 | 2018-07-15 12:49 | 43296.534 | -- | -- | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT E/F
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-07-15 16:00 | 43296.6667 | 2018-07-15 16:21 | 43296.6813 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS SUPPORTED BY DR AND 3-PH NATURE OF FAULT
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-07-19 12:06 | 43300.5042 | 2018-07-19 16:11 | 43300.6743 | -- | -- | -- | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR REMOVAL OF TREE BRANCHES BETWN LOC 93-94 LEANING TOWARDS CONDUCTORS
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-07-20 11:52 | 43301.4944 | 2018-07-20 12:00 | 43301.5 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FELLING OF BANANA TREE FROM OUTSIDE LINE CORRIDOR B/W LOC 126-127 BY MISCREANTS
[6 empty] | Sub Total --> | [6 empty] | 0 | 37 | 0 | 0 | 5 | 2 | 0 | 0
NER L105 | AIZWAL_ZEMEBAK | # 2 | 6.719 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-07-20 13:44 | 43301.5722 | 2018-07-20 13:56 | 43301.5806 | -- | -- | -- | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | FAULT BEYOND LINE LENGTH
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-07-29 09:22 | 43310.3903 | 2018-07-29 15:29 | 43310.6451 | -- | -- | -- | 6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | REPLACEMENT OF MALE & FEMALE ISOLATOR ARM OF BUS ISOLATOR IN PG BAY AT ASEB (P.GRAM) SS.
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-07-30 13:54 | 43311.5792 | 2018-07-30 18:33 | 43311.7729 | -- | -- | -- | 4 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR B-PH CT REPLACEMENT IN BADARPUR BAY AT PANCHGRAM(STATE) S/S.
[6 empty] | Sub Total --> | [6 empty] | 10 | 46 | 0 | 12 | 0 | 0 | 0 | 0
NER L107 | BADARPUR_JIRIBAM |  | 67.21 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L109 | BADARPUR_KUMARGHAT |  | 118.513 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region |  | 2018-07-16 12:30 | 43297.5208 | 2018-07-16 14:11 | 43297.591 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 41 | 0 | 0 | N/A | N/A | N/A | TEMPORARY ARRANGEMENT FOR GUYING OF TOWER AT VULNERABLE LOC. NO. 390 CAUSED BY LANDSLIDE. |  | 100
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region | partial damage tower | 2018-07-25 18:22 | 43306.7653 | 2018-07-31 23:59 | 43312.9993 | 1 | -- | 7 | 0 | 0 | 0 | 0 | 149 | 37 | 0 | 0 | 50 | N | -43 | E/S/D DUE TO PARTIAL DAMAGE OF TOWER AT LOC 390 ON ACCOUNT OF LANDSLIDE; RESTORATION GOING ON.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 151 | 18 | 0 | 0
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region |  | 2018-07-14 23:26 | 43295.9764 | 2018-07-15 00:01 | 43296.0007 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | N/A | N/A | N/A |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-07-22 03:27 | 43303.1438 | 2018-07-22 03:56 | 43303.1639 | -- | -- | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPED DUE TO TRANSIENT FAULT
[6 empty] | Sub Total --> | [6 empty] | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0
NER L118 | KHANDONG-HAFLONG |  | 63.166 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-07-20 14:48 | 43301.6167 | 2018-07-20 14:55 | 43301.6215 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | N/A | N/A | N/A | HRAVY LIHHTNING PREVAILED DURING THE TIMEOF TRIPPING AROUND KHLIEHRIAT REGION |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-07-17 08:30 | 43298.3542 | 2018-07-17 18:19 | 43298.7632 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 49 | N/A | N/A | N/A | S/D TAKEN FOR INSTALLATION OF TLA AT ALL LOCATIONS IN LINE. |  | 100
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-07-18 08:18 | 43299.3458 | 2018-07-18 18:18 | 43299.7625 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | N/A | N/A | N/A | S/D TAKEN FOR INSTALLATION OF TLA AT ALL LOCATIONS IN LINE.
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-07-19 08:33 | 43300.3562 | 2018-07-19 18:17 | 43300.7618 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 44 | N/A | N/A | N/A | S/D TAKEN FOR INSTALLATION OF TLA AT ALL LOCATIONS IN LINE.
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-07-20 09:41 | 43301.4035 | 2018-07-20 15:21 | 43301.6396 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | N/A | N/A | N/A | S/D TAKEN FOR INSTALLATION OF TLA AT ALL LOCATIONS IN LINE
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-07-21 08:03 | 43302.3354 | 2018-07-21 16:28 | 43302.6861 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 25 | N/A | N/A | N/A | S/D TAKEN FOR ISNTALLATION OF TLA AT ALL LOCATIONS IN LINE
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-07-22 08:42 | 43303.3625 | 2018-07-22 16:57 | 43303.7063 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | N/A | N/A | N/A | S/D TAKEN FOR INSTALLATION OF TLA AT ALL LOCATIONS IN LINE
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 53
NER L121 | KHANDONG_KOPILI | # 1 | 10.914 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region | punctured insulator | 2018-07-25 09:09 | 43306.3812 | 2018-07-25 13:07 | 43306.5465 | -- | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 58 | 0 | 0 | 2 | N | -2 | S/D TAKEN FOR REPLACMENT OF INSULATOR AT LOC 9 & LOC 13. INSULATORS DAAMGED DUE TO LIGHTNING STRIKE |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 3 | 58 | 0 | 0
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region |  | 2018-07-21 10:25 | 43302.434 | 2018-07-21 17:19 | 43302.7215 | -- | -- | 0 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR GIVING STAY WIRE TO TOWER AT LOC 237 FOR SAFEGUARD OF TOWER |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L125 | SALAKATI-GELEPHUG |  | 49.217 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L126 | LEKHI - RANGANADI |  | 12.59 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region |  | 2018-07-21 00:47 | 43302.0326 | 2018-07-21 02:30 | 43302.1042 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 43 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LOSS OF VOLTAGE. PROBLEM IN GENERATING END AT PARE END |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 43 | 0 | 0
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-07-12 16:15 | 43293.6771 | 2018-07-12 19:27 | 43293.8104 | -- | -- | -- | 0 | 0 | 3 | 12 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | 66KV CT BELONGING TO STATE BLASTED AT KOLASIB (MIZORAM) SS. |  | 100
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-07-20 18:07 | 43301.7549 | 2018-07-20 18:18 | 43301.7625 | -- | -- | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO NON CLEARANCE OF FAULT IN 132KV BADARPUR-KOLASIB AT KOLASIB STATE SS
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3 | 23 | 0 | 0 | 0 | 0
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L130 | KHANDONG_KOPILI | # 2 | 11.56 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L137 | IMPHAL-IMPHAL | # 2 | 0.442 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L138 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-07-07 05:38 | 43288.2347 | 2018-07-07 06:26 | 43288.2681 | -- | -- | -- | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | N/A | N/A | N/A
NER L139 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region |  | 2018-07-09 08:56 | 43290.3722 | 2018-07-09 17:11 | 43290.716 | -- | -- | -- | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | JUMPER TIGHTENING IN PG JURISDICTION & INFRINGEMENT CLEARANCEAT LOC 23-24, 58-59
[6 empty] | Sub Total --> | [6 empty] | 8 | 15 | 0 | 48 | 0 | 0 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region |  | 2018-07-09 08:58 | 43290.3736 | 2018-07-09 17:12 | 43290.7167 | -- | -- | -- | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | JUMPER TIGHTENING IN PG JURISDICTION & INFRINGEMENT CLEARANCEAT LOC 23-24, 58-59
[6 empty] | Sub Total --> | [6 empty] | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L142 | B.CHARAILI_PAVOI | #1 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L143 | B.CHARAILI_PAVOI | #2 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L144 | ROING_PASIGHAT |  |  | North Eastern Region |  | 2018-07-06 12:55 | 43287.5382 | 2018-07-06 13:40 | 43287.5694 | -- | -- | -- | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRANSIENT EARTH FAULT
[6 empty] | Sub Total --> | [6 empty] | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-07-12 16:17 | 43293.6785 | 2018-07-12 16:48 | 43293.7 | -- | -- | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MAL OPERATION.
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-07-14 17:34 | 43295.7319 | 2018-07-14 17:50 | 43295.7431 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | N/A | N/A | N/A | TRIP ON TOUCHING OF BAMBOO FROM OUTSIDE LINE CORRIDOR BETWN LOC 277-278 ON A/C OF TURBULENT WEATHER
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-07-16 13:45 | 43297.5729 | 2018-07-16 14:22 | 43297.5986 | -- | -- | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-07-17 11:20 | 43298.4722 | 2018-07-17 12:42 | 43298.5292 | -- | -- | -- | 0 | 0 | 0 | 0 | 1 | 22 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING INFRINGMENT CAME NEAR LINE FROM OUT SIDE CORIDOR BETWEEN LOC. 277-278.
[6 empty] | Sub Total --> | [6 empty] | 1 | 8 |  |  | 1 | 38
NER L146 | AIZAWL MELRIAT |  |  | North Eastern Region |  | 2018-07-12 13:53 | 43293.5785 | 2018-07-12 14:17 | 43293.5951 | -- | -- | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED FOR DOWNSTREAM FAULT. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-07-25 22:05 | 43306.9201 | 2018-07-25 22:34 | 43306.9403 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | N/A | N/A | N/A | FLASHOVER MARK OVER INSULATION OF R-PH CT IN TIPAIMUKH BAY AT JRIRIBAM SS DUE TO LIGHTNING |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region |  | 2018-07-01 12:59 | 43282.541 | 2018-07-01 13:21 | 43282.5563 | -- | -- | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON DOWNSTREAM FAULT & FAULT BEYOND POWERGRID JURISDICTION |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0
NER L202 | KATHALGURI_MARIANI(OLD) |  | 162.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L203 | MISA_DIMAPUR | # 1 | 123.52 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L204 | MISA_DIMAPUR | # 2 | 123.52 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L205 | MISA_KATHALGURI |  | 382.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L206 | MISA-KOPILI | # 1 | 72.791 | North Eastern Region |  | 2018-07-24 09:17 | 43305.3868 | 2018-07-24 15:50 | 43305.6597 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 33 | N/A | N/A | N/A | BUS PIPE CONSTRUCTION WORKS AS PER NER CONSTRUCTION RELATED SHUTDOWN. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 33
NER L207 | MISA_KOPILI | # 2 | 72.791 | North Eastern Region | [5 empty] | X | [15 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L208 | MISA_KOPILI | # 3 | 75.788 | North Eastern Region |  | 2018-07-31 12:13 | 43312.509 | 2018-07-31 12:30 | 43312.5208 | -- | -- | -- | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY KOPILI P/S. (NEEPCO). |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region | [5 empty] | X | [15 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region |  | 2018-07-26 05:16 | 43307.2194 | 2018-07-26 09:20 | 43307.3889 | -- | -- | -- | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY SAMAGURI (STATE0 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region |  | 2018-07-02 09:55 | 43283.4132 | 2018-07-02 14:22 | 43283.5986 | -- | -- | 0 | 0 | 0 | 4 | 27 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LOSS OF SECONFARY VOLTAGES TO THE DISTANCE PROTECTION RELYA DURING S/D OF BUS-B |  | 100
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region |  | 2018-07-26 05:16 | 43307.2194 | 2018-07-26 09:20 | 43307.3889 | -- | -- | -- | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY STATE
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0
NER L212 | SALAKATI_BTPS | # 2 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L213 | SALAKATI-BTPS | # 1 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-07-13 11:30 | 43294.4792 | 2018-07-13 14:21 | 43294.5979 | -- | -- | -- | 0 | 0 | 0 | 0 | 2 | 51 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING BAMBOOS B/W LOC. NO. 108-109 CAME FROM OUTSIDE CORIDOR. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 2 | 51 | 0 | 0
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region | jumper opened | 2018-07-11 22:32 | 43292.9389 | 2018-07-12 13:14 | 43293.5514 | -- | -- | 0.5 | 14 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -2.5 | R-PH JUMPER N.MARIANI SIDE AT LOC 99 SNAPPED. |  | 100
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region |  | 2018-07-19 10:47 | 43300.4493 | 2018-07-19 11:05 | 43300.4618 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FELLING OF BAMBOOS FROM OUTSIDE LINE CORRIDOR BY MISCREANT BETWEEN LOC 61-62
[6 empty] | Sub Total --> | [5 empty] | 0.5 | 14 | 42 | 0 | 0 | 0 | 18 | 0 | 0
NER L401 | BALIPARA_BONGAIGAON | # 1 | 289.721 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L403 | MISA_BALIPARA | # 1 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L404 | MISA-BALIPARA | #2 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L405 | BONGAIGAON-MALDA | # 1 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L406 | BONGAIGAON-MALDA | # 2 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L407 | BALIPARA-RANGANADI | # 1 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L408 | BALIPARA-RANGANADI | # 2 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L409 | PALLATANA-SURAJMANINAGAR | # 1 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region | Conductor snapped | 2018-07-07 19:17 | 43288.8035 | 2018-07-07 19:30 | 43288.8125 | -- | -- | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -3 | TRIPPED DUE TO SNAPPING OF R-PH CT CONNECTOR TO WAVETRAP AT COMILLA-II BAY OF SURAJMANINAGAR SS
[6 empty] | Sub Total --> | [6 empty] | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0
NER L411 | BTPS-BONGAIGAON | #1 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L412 | BTPS-BONGAIGAON | #2 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-01 00:01 | 43282.0007 | 2018-07-01 18:51 | 43282.7854 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | N/A | N/A | N/A | LINE H/T VIDE CODE 1818
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-03 23:40 | 43284.9861 | 2018-07-04 19:17 | 43285.8035 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | N/A | N/A | N/A | H/T VIDE CODE 1862
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-07 08:38 | 43288.3597 | 2018-07-07 17:46 | 43288.7403 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | N/A | N/A | N/A | H/T VIDE CODE 1908
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-09 00:45 | 43290.0312 | 2018-07-09 18:58 | 43290.7903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 1944
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-11 03:03 | 43292.1271 | 2018-07-11 09:54 | 43292.4125 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 51 | N/A | N/A | N/A | LINE H/T VIDE CODE 1959.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-11 13:58 | 43292.5819 | 2018-07-11 14:12 | 43292.5917 | -- | -- | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-11 17:39 | 43292.7354 | 2018-07-11 17:55 | 43292.7465 | -- | -- | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MAL OPERATION.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-11 18:03 | 43292.7521 | 2018-07-11 19:02 | 43292.7931 | -- | -- | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MAL OPERATION.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-12 00:05 | 43293.0035 | 2018-07-14 17:32 | 43295.7306 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | N/A | N/A | N/A | LINE H/T VIDE CODE 1995.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-17 09:51 | 43298.4104 | 2018-07-17 11:50 | 43298.4931 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 59 | N/A | N/A | N/A | LINE H/T VIDE CODE 2084.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-17 11:50 | 43298.4931 | 2018-07-17 16:50 | 43298.7014 | -- | -- | -- | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING BAMBOO BUSH BETWEEN LOC.235-236 IN PRESENCE OF SECURITY.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-19 23:15 | 43300.9688 | 2018-07-20 10:22 | 43301.4319 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 7 | N/A | N/A | N/A | LINE H/T VIDE CODE 2127
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-21 00:50 | 43302.0347 | 2018-07-21 15:37 | 43302.6507 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 2160
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-22 01:52 | 43303.0778 | 2018-07-22 19:00 | 43303.7917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | N/A | N/A | N/A | LINE H/T VIDE CODE 2183
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-23 08:21 | 43304.3479 | 2018-07-23 18:54 | 43304.7875 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33 | N/A | N/A | N/A | LINE H/T VIDE CODE 2195
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-24 23:03 | 43305.9604 | 2018-07-25 17:23 | 43306.7243 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | N/A | N/A | N/A | LINE H/T VIDE CODE 2228
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-26 08:23 | 43307.3493 | 2018-07-26 08:31 | 43307.3549 | -- | -- | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MALOPERATION
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-30 00:05 | 43311.0035 | 2018-07-30 19:02 | 43311.7931 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 57 | N/A | N/A | N/A | LINE H/T VIDE CODE 2537.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-07-31 22:31 | 43312.9382 | 2018-07-31 23:59 | 43312.9993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 2567.
[6 empty] | Sub Total --> | [6 empty] | 1 | 37 | 0 | 0 | 5 | 0 | 232 | 42
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-02 00:15 | 43283.0104 | 2018-07-03 19:33 | 43284.8146 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 1828 |  | 100
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-05 03:35 | 43286.1493 | 2018-07-05 19:27 | 43286.8104 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 52 | N/A | N/A | N/A | H/T VIDE CODE 1873
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-08 03:56 | 43289.1639 | 2018-07-08 18:50 | 43289.7847 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 54 | N/A | N/A | N/A | LINR H/T VIDE CODE 1932
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-15 04:50 | 43296.2014 | 2018-07-16 19:31 | 43297.8132 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 41 | N/A | N/A | N/A | LINE H/T VIDE CODE 2049.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-17 23:26 | 43298.9764 | 2018-07-18 12:20 | 43299.5139 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 54 | N/A | N/A | N/A | LINE H/T VIDE CODE 2095.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-19 00:31 | 43300.0215 | 2018-07-19 19:00 | 43300.7917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 29 | N/A | N/A | N/A | LINE H/T VIDE CODE 2107.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-20 10:23 | 43301.4326 | 2018-07-20 21:45 | 43301.9062 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | N/A | N/A | N/A | LINE H/T VIDE CODE 2137
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-24 03:56 | 43305.1639 | 2018-07-24 18:44 | 43305.7806 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 48 | N/A | N/A | N/A | LINE H/T VIDE CODE 2204
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-26 00:08 | 43307.0056 | 2018-07-26 19:14 | 43307.8014 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | N/A | N/A | N/A | LINE H/T VIDE CODE 2260
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-26 23:42 | 43307.9875 | 2018-07-28 18:53 | 43309.7868 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 11 | N/A | N/A | N/A | LINE H/T VIDE CODE 2320.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-29 00:11 | 43310.0076 | 2018-07-29 18:22 | 43310.7653 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | N/A | N/A | N/A | LINE H/T VIDE CODE 2320.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-07-30 22:40 | 43311.9444 | 2018-07-31 19:19 | 43312.8049 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | N/A | N/A | N/A | LINE H/T VIDE CODE 2549.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 42
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-07-03 07:52 | 43284.3278 | 2018-07-03 18:04 | 43284.7528 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF EXISTING BY HIGHER RATING EQUIPMENT UNDER PROJECT NERSS IV_& VII |  | 100
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-07-04 08:05 | 43285.3368 | 2018-07-04 17:33 | 43285.7312 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 28 | N/A | N/A | N/A | S/D TAKEN FOR REPLACMENT OF EXISTING EQUIPMENT BY HIGHER RAING EQUIPMENT UNDER THE PROJECTS NERSS IV
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-07-05 08:19 | 43286.3465 | 2018-07-05 17:58 | 43286.7486 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 39 | N/A | N/A | N/A | S/D TAKEN FOR REPLACEMENT OF EXISTING EQUIIPEMENT BY HIGHER RATING EQUIPMENT UNDER NERSS PROJECTS IV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 16
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-07-01 08:48 | 43282.3667 | 2018-07-01 16:31 | 43282.6882 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMNT OF EXISTING EQUIPMENT BY HIGHER RATING EQUIPMENT UNDER THE PROJECTS NERSS IV |  | 100
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-07-02 08:07 | 43283.3382 | 2018-07-02 17:03 | 43283.7104 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | N/A | N/A | N/A | S/D TAKEN FOR REPLACMENT OF EXISTING EQUIPMENT BY HIGHER RATING EQUIPMENT UNDER THE PREOJECTS NERSS
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-07-15 05:06 | 43296.2125 | 2018-07-15 18:20 | 43296.7639 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 14 | N/A | N/A | N/A | LINE H/T VIDE CODE 2050. |  | 100
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-07-25 06:43 | 43306.2799 | 2018-07-25 15:22 | 43306.6403 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | N/A | N/A | N/A | LINE H/T VIDE CODE 2231
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-07-28 03:45 | 43309.1562 | 2018-07-28 19:00 | 43309.7917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 2305.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 8
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-07-01 06:36 | 43282.275 | 2018-07-01 18:28 | 43282.7694 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 52 | N/A | N/A | N/A | H/T VIDE CODE 1821 |  | 100
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-07-03 08:14 | 43284.3431 | 2018-07-03 18:53 | 43284.7868 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39 | N/A | N/A | N/A | H/T VIDE CODE 1852
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-07-06 07:22 | 43287.3069 | 2018-07-06 18:31 | 43287.7715 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 9 | N/A | N/A | N/A | LINE H/T VIDE CODE 1886
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-07-12 07:58 | 43293.3319 | 2018-07-14 14:56 | 43295.6222 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 58 | N/A | N/A | N/A | LINE H/T VIDE CODE 1996.
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-07-20 23:51 | 43301.9938 | 2018-07-22 17:38 | 43303.7347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 2159
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-07-26 00:15 | 43307.0104 | 2018-07-27 12:31 | 43308.5215 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 16 | N/A | N/A | N/A | LINE H/T VIDE CODE 2261
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-07-29 05:42 | 43310.2375 | 2018-07-29 19:29 | 43310.8118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 2324.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 47
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-07-11 10:05 | 43292.4201 | 2018-07-11 15:11 | 43292.6326 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | N/A | N/A | N/A | LINE H/T VIDE CODE 1963. |  | 100
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-07-12 08:42 | 43293.3625 | 2018-07-12 14:31 | 43293.6049 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49 | N/A | N/A | N/A | LINE H/T VIDE CODE 1997.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-07-15 08:38 | 43296.3597 | 2018-07-15 16:35 | 43296.691 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 57 | N/A | N/A | N/A | LINE H/T VIDE CODE 2055.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-07-16 08:58 | 43297.3736 | 2018-07-16 17:37 | 43297.734 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | N/A | N/A | N/A | LINE H/T VIDE CODE 2069.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-07-22 09:08 | 43303.3806 | 2018-07-22 14:21 | 43303.5979 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 2188
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-07-28 13:12 | 43309.55 | 2018-07-28 16:16 | 43309.6778 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | N/A | N/A | N/A | LINE H/T VIDE CODE 2311.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-07-29 08:57 | 43310.3729 | 2018-07-29 14:46 | 43310.6153 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49 | N/A | N/A | N/A | LINE H/T VIDE CODE 2526.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 62
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-07-19 12:35 | 43300.5243 | 2018-07-19 15:57 | 43300.6646 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 22 | N/A | N/A | N/A | E/S/D TAKEN FOR ARRESTING SUDDEN OIL LEAKAGE ON B-PH CT OF PKBARI-II BAY AT SILCHAR SS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 22
NER RBR1 | BR_BONGAIGAON (50MVAR) | # 1 | 50 | North Eastern Region | [21 empty] | 100
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR5 | BR_KUMARGHAT (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR6 | BR_AIZWAL (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-07-13 19:21 | 43294.8063 | 2018-07-13 22:00 | 43294.9167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 39 | N/A | N/A | N/A | H/T VIDE CODE 2033. |  | 100
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-07-19 18:57 | 43300.7896 | 2018-07-20 23:10 | 43301.9653 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 13 | N/A | N/A | N/A | B/R H/T VIDE CODE 2125
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 52
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-07-05 10:36 | 43286.4417 | 2018-07-05 19:03 | 43286.7937 | -- | -- | -- | 8 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ARRESTING OIL LEAKAGE FROM R-PH BUSHING
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-07-05 19:03 | 43286.7937 | 2018-07-05 23:27 | 43286.9771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 24 | N/A | N/A | N/A | REACTOR KEPT OPEN AS PER NERLDC INSTRUCTION
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-07-29 19:32 | 43310.8139 | 2018-07-29 22:33 | 43310.9396 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | N/A | N/A | N/A | B/R H/T VIDE CODE 2533.
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-07-27 19:02 | 43308.7931 | 2018-07-28 23:06 | 43309.9625 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 4 | N/A | N/A | N/A | B/R H/T VIDE CODE 2318.
[6 empty] | Sub Total --> | [6 empty] | 8 | 27 | 0 | 0 | 0 | 0 | 35 | 29
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-07-25 19:02 | 43306.7931 | 2018-07-26 00:06 | 43307.0042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | N/A | N/A | N/A | B/R H/T VIDE CODE 2255 |  | 100
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-07-27 19:11 | 43308.7993 | 2018-07-29 00:08 | 43310.0056 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 57 | N/A | N/A | N/A | B/R H/T VIDE CODE 2302.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-07-29 19:41 | 43310.8201 | 2018-07-29 22:14 | 43310.9264 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | N/A | N/A | N/A | B/R H/T VIDE CODE 2534.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 34
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-07-26 10:06 | 43307.4208 | 2018-07-26 12:23 | 43307.516 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17 | N/A | N/A | N/A | S/D TKAEN FOR CHECKING OF CANOPY OF PRV AND BUCCHOLZ RELAY |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17
NER RBR13 | BR_B'CHARIALI(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-07-27 10:12 | 43308.425 | 2018-07-27 12:58 | 43308.5403 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | N/A | N/A | N/A | S/D TAKEN TO CHECK & EMASURE FOR CANOPY OF PRV & BUCCHOLZ RELAY |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46
NER RBR14 | BR_B'CHARIALI(63MVAR) | #3 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR15 | BR_B'CHARIALI(63MVAR) | #4 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR16 | BR_New_MARIANI(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT1 | ICT_BONGAIGAON(315MVA) |  | 315 | North Eastern Region |  | 2018-07-23 09:37 | 43304.4007 | 2018-07-23 15:12 | 43304.6333 | -- | -- | -- | 5 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN TO ATTEND JUMPER HOTSPOT
[6 empty] | Sub Total --> | [6 empty] | 5 | 35 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT2 | ICT_BALIPARA (315MVA) | #1 | 315 | North Eastern Region |  | 2018-07-04 14:24 | 43285.6 | 2018-07-04 15:22 | 43285.6403 |  |  | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | R-PH WTI & OTI MAL-TRIPPED DUE TO COMAND ON A/C TO BURNING OF CONTROL WIRES IN MARSHALLING BOX
[6 empty] | Sub Total --> | [6 empty] | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT3 | ICT_BALIPARA (315MVA) | #2 | 315 | North Eastern Region |  | 2018-07-24 09:41 | 43305.4035 | 2018-07-24 19:05 | 43305.7951 |  |  |  | 9 | 24 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S/D TAKEN FOR HOTPOST RECTIFICATION IN LV SIDE LINE ISOLATOR
[6 empty] | Sub Total --> | [6 empty] | 9 | 24 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-07-30 09:51 | 43311.4104 | 2018-07-30 17:55 | 43311.7465 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 4 |  |  |  | BEAM ERECTION AND HIGH LEVEL ISOLATOR ERECTION WORK UNDER NERSS - IV CONSTRUCTION PROJECT.
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-07-31 09:55 | 43312.4132 | 2018-07-31 16:08 | 43312.6722 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 13 |  |  |  | S/D TAKEN FOR CONSTRUCTION ACTIVITY UNDER NERSS IV.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 17
NER TICT5 | ICT_MISA | #2 | 315 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT7 | ICT_B'CHARIALI (200MVA) | #1 | 200 | North Eastern Region |  | 2018-07-30 11:45 | 43311.4896 | 2018-07-30 12:42 | 43311.5292 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 |  |  |  | TO CHECK & MEASURE FOR CANOPY OF PRV AND BUCCHOLZ RELAY.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57
NER TICT8 | ICT_B'CHARIALI (200MVA) | #2 | 200 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT9 | ICT_IMPHAL(50MVA) | #1 | 50 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT10 | ICT_IMPHAL(50MVA) | #2 | 50 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 1 | 50 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 2 | 50 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT12 | ICT_DIMAPUR (100 MVA) | # 1 | 100 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT13 | ICT_DIMAPUR (100 MVA) | #2 | 100 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region |  | 2018-07-03 10:28 | 43284.4361 | 2018-07-03 14:53 | 43284.6201 |  |  |  | 4 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | SD TAKEN FOR RELAY TESTING (REF STABILITY)
[6 empty] | Sub Total --> | [6 empty] | 4 | 25 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT16 | ICT_MOKOKCHUNG(30MVA) | #2 | 30 | North Eastern Region |  | 2018-07-02 10:27 | 43283.4354 | 2018-07-02 20:16 | 43283.8444 |  |  |  | 9 | 49 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | SD TAKEN FOR RELAY TESTING
[6 empty] | Sub Total --> | [6 empty] | 9 | 49 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT17 | ICT_NIRJULI(50MVA) | #1 | 50 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT18 | ICT_NIRJULI(50MVA) | #2 | 50 | North Eastern Region |  | 2018-07-15 14:41 | 43296.6118 | 2018-07-15 16:59 | 43296.7076 |  |  |  | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | E/S/D TAKEN FOR REPLACEMENT OF BUS SIDE ISOLATOR AT LV SIDE
[6 empty] | Sub Total --> | [6 empty] | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT19 | ICT_ZIRO (15MVA) |  | 15 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT20 | ICT_KOPILI (160 MVA) | # 2 | 160 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT21 | ICT_KUMARGHAT(5MVA) |  | 5 | North Eastern Region
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## august 2018 - TABLE I
Unique ID of transmission Element | Element Name |  | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee Hr min |  | OTHERS Hr min |  | System Constraints/ Natural calamity / Militancy Hr min |  | Deemed Available Hr min
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-08-04 04:00 | 43316.1667 | 2018-08-04 07:28 | 43316.3111 | -- | -- | -- | 0 | 0 | 3 | 28 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY TSeCL (TRIPURA) | Awaited | 100
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-08-22 03:09 | 43334.1312 | 2018-08-22 05:37 | 43334.234 | -- | -- | -- | 0 | 0 | 2 | 28 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D OF 132KV BUS AVAILED BY AGARTALA END.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 5 | 56 | 0 | 0 | 0 | 0
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region |  | 2018-08-22 06:44 | 43334.2806 | 2018-08-22 08:35 | 43334.3576 | -- | -- | -- | 0 | 0 | 1 | 51 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D OF 132KV BUS AVAILED BY AGARTALA END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 51 | 0 | 0 | 0 | 0
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-08-15 13:11 | 43327.5493 | 2018-08-15 13:29 | 43327.5618 | -- | -- | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT EARTH FAULT.
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region | insulator flash over mark | 2018-08-13 13:56 | 43325.5806 | 2018-08-13 14:06 | 43325.5875 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | N | -2 | TRIPPED DUE TO LIGHTNING AS CONFIMRED BY FLASHOVER MARK IN Y-PH INSULATOR STRING AT LOC 273
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-08-12 16:15 | 43324.6771 | 2018-08-12 17:04 | 43324.7111 | -- | -- | -- | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | UNWANTED OVERLOAD PROTECTION AT KOLASIB END (MIZORAM STAE0
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-08-10 12:06 | 43322.5042 | 2018-08-10 13:15 | 43322.5521 | -- | -- | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | UNWANTED TRIPPING AT KOLASIB END DUE TO RELAY MALOPERATION SIMULTAENOUSLY WITH 132KV AZL-KGT TRIPPIN
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-08-17 10:50 | 43329.4514 | 2018-08-18 18:23 | 43330.766 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 33 | N/A | N/A | N/A | C/S/D TAKEN FOR CB OVERHAULING WORKS.
[6 empty] | Sub Total --> | [6 empty] | 0 | 18 | 1 | 58 | 0 | 10 | 31 | 33
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-04 14:32 | 43316.6056 | 2018-08-04 15:02 | 43316.6264 | -- | -- | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT EARTH FAULT
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-12 16:15 | 43324.6771 | 2018-08-12 16:37 | 43324.6924 | -- | -- | -- | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRANSIENT E/F
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-10 12:06 | 43322.5042 | 2018-08-10 12:38 | 43322.5264 | -- | -- | -- | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRANSIENT E/F
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-03 11:34 | 43315.4819 | 2018-08-03 16:56 | 43315.7056 | -- | -- | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING OF TREE BETWEEN LOC 166-167 WHICH LEANT TOWARDS CONDUCTORS ON A/C OF STOR,M
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-14 15:17 | 43326.6368 | 2018-08-14 15:36 | 43326.65 | -- | -- | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-06 12:38 | 43318.5264 | 2018-08-06 17:08 | 43318.7139 | -- | -- | -- | 4 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | EMERGENCY S.D TAKEN BY AIZAWL FOR DISTANCE PROTECTION RELAY TESTING
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-29 12:54 | 43341.5375 | 2018-08-29 13:06 | 43341.5458 | -- | -- | -- | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LA OF TRANSFORMER BLASTED AT P.K. BARI (STATE) S/S.
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-08-15 14:54 | 43327.6208 | 2018-08-15 15:13 | 43327.634 | -- | -- | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
[6 empty] | Sub Total --> | [6 empty] | 6 | 32 | 0 | 12 | 5 | 22 | 0 | 0
NER L105 | AIZWAL_ZEMEBAK | # 2 | 6.719 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-08-25 09:51 | 43337.4104 | 2018-08-25 10:07 | 43337.4215 | -- | -- | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT..
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0
NER L107 | BADARPUR_JIRIBAM |  | 67.21 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region | OPGW damaged | 2018-08-09 06:26 | 43321.2681 | 2018-08-09 12:05 | 43321.5035 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39 | N/A | N/A | N/A | E/S/D TAKEN FOR RECTIFICATION OF DAMAGED OPGW BETWEEN LOC 61-64
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region |  | 2018-08-28 11:25 | 43340.4757 | 2018-08-28 11:30 | 43340.4792 | -- | -- | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region |  | 2018-08-01 09:15 | 43313.3854 | 2018-08-01 15:42 | 43313.6542 | -- | -- | -- | 6 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP OF BAY EQUIPMENTS
[6 empty] | Sub Total --> | [6 empty] | 6 | 32 | 0 | 0 | 0 | 0 | 5 | 39
NER L109 | BADARPUR_KUMARGHAT |  | 118.513 | North Eastern Region | Conductor snapped | 2018-08-25 07:33 | 43337.3146 | 2018-08-25 18:33 | 43337.7729 | -- | -- | 0.5 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 3 | N | -2.5 | TREE FELL FROM UPHILL SIDE,OUT SIDE CORRIDOR, B/W LOC 239-240, SNAPPING CONDUCTOR.
NER L109 | BADARPUR_KUMARGHAT |  | 118.513 | North Eastern Region |  | 2018-08-08 08:31 | 43320.3549 | 2018-08-08 17:06 | 43320.7125 | -- | -- | -- | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR CLEARING INFRINGEMENT BETN LOC 254/255/264/265 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 8 | 35 | 0 | 0 | 11 | 0 | 0 | 0
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region | PARTIAL DAMAGE OF TOWER | 2018-08-01 | 43313 | 2018-08-31 23:59 | 43343.9993 | 1 | -- | 31 | 0 | 0 | 0 | 0 | 743 | 59 | 0 | 0 | 50 | N | -19 | LINE H/T UNDER E/S/D TO PARTIAL DAMAGE OF TOWER AT LOC 390 ON A/C OF LANDSLIDE FOR RESTORATION WORK
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 743 | 59 | 0 | 0
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region |  | 2018-08-25 10:07 | 43337.4215 | 2018-08-25 10:37 | 43337.4424 | -- | -- | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT. |  | 100
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region |  | 2018-08-16 04:50 | 43328.2014 | 2018-08-16 05:03 | 43328.2104 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING FAULT. |  | 100
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region |  | 2018-08-01 03:48 | 43313.1583 | 2018-08-01 04:03 | 43313.1687 | -- | -- | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TWO NO BAMBOO TOUCHED Y & B PH CONDUCTORS FROM OUTSIDE LINE CORRIDOE DUE TO CYCLONIC STORM |  | 100
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region |  | 2018-08-19 14:36 | 43331.6083 | 2018-08-19 14:47 | 43331.616 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | N/A | N/A | N/A | HEAVY LIGHTNING PREVAILED AT DIMAPUR REGION DURING THE TIME OF TRIPPING. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-08-16 04:50 | 43328.2014 | 2018-08-16 05:19 | 43328.2215 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING FAULT.
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-08-19 14:36 | 43331.6083 | 2018-08-19 14:48 | 43331.6167 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N/A | N/A | N/A | HEAVY LIGHTNING PREVAILED AT DIMAPUR REGION DURING THE TIME OF TRIPPING.
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-08-31 14:13 | 43343.5924 | 2018-08-31 14:37 | 43343.609 | -- | -- | -- | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Phase to Phase fault
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-08-18 09:52 | 43330.4111 | 2018-08-18 13:29 | 43330.5618 | -- | -- | -- | 3 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR RECTIFICATION OF HOTSPOT, OBSERVED IN WAVE TRAP AND CT TERMINAL OF R & B-PH.
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-08-18 04:07 | 43330.1715 | 2018-08-18 04:24 | 43330.1833 | -- | -- | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MAL-OPERATION. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 4 | 18 | 0 | 0 | 0 | 41 | 0 | 0
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region |  | 2018-08-08 08:36 | 43320.3583 | 2018-08-08 14:17 | 43320.5951 | -- | -- | -- | 5 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR AMP AT GOHPUR |  | 100
[6 empty] | Sub Total --> | [6 empty] | 5 | 41 | 0 | 0 | 0 | 0 | 0 | 0
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-08-09 11:00 | 43321.4583 | 2018-08-09 11:20 | 43321.4722 | -- | -- | -- | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-08-20 09:11 | 43332.3826 | 2018-08-20 09:21 | 43332.3896 | -- | -- | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTEAM FAULT. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region |  | 2018-08-25 08:07 | 43337.3382 | 2018-08-25 16:02 | 43337.6681 | -- | -- | -- | 7 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR T/L MAINTENANCE WORK. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 7 | 55 | 0 | 0 | 0 | 0 | 0 | 0
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-08-07 12:08 | 43319.5056 | 2018-08-07 15:09 | 43319.6312 | -- | -- | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING TREE BETWN LOC 95-97 WHICH CAME NEAR TO CONDUCTOR DUR TO STORM
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-08-15 12:41 | 43327.5285 | 2018-08-15 12:56 | 43327.5389 | -- | -- | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 15 | 0 | 0 | 3 | 1 | 0 | 0
NER L118 | KHANDONG-HAFLONG |  | 63.166 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-08-17 01:28 | 43329.0611 | 2018-08-17 01:31 | 43329.0632 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AT KHLIEHRIAT REGION. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region |  | 2018-08-23 12:55 | 43335.5382 | 2018-08-24 17:37 | 43336.734 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | N/A | N/A | N/A | C/S/D TAKEN FOR CB OVERHAULING WORKS AT KHANDONG.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42
NER L121 | KHANDONG_KOPILI | # 1 | 10.914 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region |  | 2018-08-01 12:34 | 43313.5236 | 2018-08-01 15:13 | 43313.634 | -- | -- | 0 | 0 | 0 | 0 | 0 | 2 | 39 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING OF BAMBOOS IN PROXIMITY TO CONDUCTORS BETN LOC 166-167 DUE TO STORM |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 2 | 39 | 0 | 0
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L125 | SALAKATI-GELEPHUG |  | 49.217 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L126 | LEKHI - RANGANADI |  | 12.59 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region |  | 2018-08-24 09:07 | 43336.3799 | 2018-08-24 09:23 | 43336.391 | -- | -- | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 100
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region |  | 2018-08-05 08:12 | 43317.3417 | 2018-08-05 17:05 | 43317.7118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 53 | N/A | N/A | N/A | BUS S/D TAKEN FOR ISOLATOR RETROFITTING WORKSIN RESPECT WITH 132/33 KV ICT-II |  | 100
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region |  | 2018-08-17 06:26 | 43329.2681 | 2018-08-17 17:05 | 43329.7118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39 | N/A | N/A | N/A | REPLACEMENT OF OLD/OBSOLETE BUS ISOLATORS WITH NEW BUS ISOLATORS. |  | 100
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region |  | 2018-08-16 06:00 | 43328.25 | 2018-08-16 17:06 | 43328.7125 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | N/A | N/A | N/A | EPLACEMENT OF OLD/OBSOLETE BUS ISOLATORS WITH NEW BUS ISOLATORS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 16 | 0 | 0 | 30 | 38
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-08-26 19:33 | 43338.8146 | 2018-08-26 19:52 | 43338.8278 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | N/A | N/A | N/A | INTENSE LIGHTENING PREVAILING OVER AIZAWL |  | 100
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-08-15 14:54 | 43327.6208 | 2018-08-15 15:23 | 43327.641 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING FAULT.
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-08-04 14:32 | 43316.6056 | 2018-08-04 15:57 | 43316.6646 | -- | -- | 0 | 1 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO NON CLEARING OF FAULT IN 132KV AIZAWL-KUMARGHAT AT AIZAWL END |  | 100
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-08-14 15:17 | 43326.6368 | 2018-08-14 18:09 | 43326.7562 | -- | -- | 0 | 2 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-08-16 08:56 | 43328.3722 | 2018-08-16 16:35 | 43328.691 | -- | -- | -- | 7 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR TLA INSTALLATION & RELAY TESTING. |  | 100
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-08-25 10:04 | 43337.4194 | 2018-08-25 16:58 | 43337.7069 | -- | -- | -- | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR INFRINGEMENT CLEARANCE LOC. NO. 127,123, 131,147, 92, 99-102.
[6 empty] | Sub Total --> | [6 empty] | 18 | 50 | 0 | 0 | 0 | 48 | 0 | 0
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-08-29 03:24 | 43341.1417 | 2018-08-29 03:43 | 43341.1549 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LOCAL GRID DISTURBANCE.
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-08-07 08:22 | 43319.3486 | 2018-08-07 18:26 | 43319.7681 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | N/A | N/A | N/A | FOR FACILITATING OF SHIFTING WORK OF EXISITNG VULNERABLE TOWER AT LOC 12
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-08-05 08:35 | 43317.3576 | 2018-08-05 16:20 | 43317.6806 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 45 | N/A | N/A | N/A | S/D FOR FACILITATING OF SHIFTING WORK OF THE EXSITING VULNERABLE AT TOWER LOC 12
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-08-08 13:40 | 43320.5694 | 2018-08-08 16:54 | 43320.7042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | N/A | N/A | N/A | S/D TAKEN FOR FACILITATING TOWER SHIFITNG WORK AT VULNERABLE LOC 12
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-08-06 08:14 | 43318.3431 | 2018-08-06 18:36 | 43318.775 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22 | N/A | N/A | N/A | SD TAKEN FOR FACILITATING OF SHIFTING WORK OF THE EXISTING VULNERABLE TOWER AT LCO 12
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region |  | 2018-08-25 00:59 | 43337.041 | 2018-08-25 01:14 | 43337.0514 | -- | -- | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT FAULT.
[6 empty] | Sub Total --> | [6 empty] | 0 | 15 | 0 | 0 | 0 | 19 | 31 | 25
NER L130 | KHANDONG_KOPILI | # 2 | 11.56 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region |  | 2018-08-10 11:28 | 43322.4778 | 2018-08-10 12:10 | 43322.5069 | -- | -- | -- | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ARRESTING OIL LEAKAGE FROM Y-PH CT |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0
100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L137 | IMPHAL-IMPHAL | # 2 | 0.442 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L142 | B.CHARAILI_PAVOI | #1 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L143 | B.CHARAILI_PAVOI | #2 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L144 | ROING_PASIGHAT |  |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-15 14:54 | 43327.6208 | 2018-08-15 15:25 | 43327.6424 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DISTURBANCE IN GRID.
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-04 14:32 | 43316.6056 | 2018-08-04 16:01 | 43316.6674 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 29 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO UNWANTED O/C PROTECTION OPERATION AT TIPAIMUKH SS
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-13 22:10 | 43325.9236 | 2018-08-13 22:52 | 43325.9528 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-12 16:15 | 43324.6771 | 2018-08-12 16:42 | 43324.6958 | -- | -- | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO UNWANTED OVERLOAD PROTECTION TRIPPING AT TIPAIMUKH SS (MANIPUR)
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-27 09:06 | 43339.3792 | 2018-08-27 12:55 | 43339.5382 | -- | -- | -- | 0 | 0 | 3 | 49 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D AVAILED BY STATE END.
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-10 12:06 | 43322.5042 | 2018-08-10 12:34 | 43322.5236 | -- | -- | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPED DUE TO RELAY MALOPERATION
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-20 05:15 | 43332.2188 | 2018-08-20 06:37 | 43332.2757 | -- | -- | -- | 0 | 0 | 1 | 22 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | FAULT OF JIRIBAM-TIPAIMUKH SECTION WAS NOT CLEARED BY TIPAIMUKH END; COMMUNICATIION ISSUE AT TIPAIMK
[6 empty] | Sub Total --> | [6 empty] | 0 | 28 | 5 | 38 | 2 | 42 | 0 | 0
NER L146 | AIZAWL MELRIAT |  |  | North Eastern Region |  | 2018-08-13 22:10 | 43325.9236 | 2018-08-13 23:01 | 43325.959 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | N/A | N/A | N/A |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0
147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-08-16 22:50 | 43328.9514 | 2018-08-16 23:11 | 43328.966 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AT HAFLONG REGION. |  | 100
147 | HAFLONG-UMRANGSO |  |  | North Eastern Region |  | 2018-08-10 15:09 | 43322.6312 | 2018-08-10 17:46 | 43322.7403 | -- | -- | 0 | 0 | 0 | 0 | 0 | 2 | 37 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS SUGGESTED BY DR.DELAY IN RESTORATION DUE TO CB ISSUE AT UMRANGSO END |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 2 | 58 | 0 | 0
NER L153 | MELRIAT - ZEMABAWK |  |  | North Eastern Region |  | 2018-08-28 10:13 | 43340.4257 | 2018-08-28 11:13 | 43340.4674 | -- | -- | -- | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CLEARING FOREIGN OBJECT WHICH INFRINGED INTO LINE FROM OUTSIDE CORRIDOR, AT LOC 01. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-20 05:05 | 43332.2118 | 2018-08-20 06:35 | 43332.2743 | -- | -- | -- | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | CHARGING DELAYED DUE TO COMMUNICATION PROBLEM WITH TIPAIMUKH.. |  | 100
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-27 08:19 | 43339.3465 | 2018-08-27 17:33 | 43339.7312 | -- | -- | -- | 0 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | N/A | N/A | N/A | E/S/D AVAILED FOR INFRINGEMENT CLEARING AT LOC. 235-240. TREES SLID TOWARDS LINE DUE TO LANDSLIDE. |  | 100
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-21 09:34 | 43333.3986 | 2018-08-21 10:39 | 43333.4437 | -- | -- | -- | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY MANIPUR STATE UTILITY. |  | 100
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-08-14 08:23 | 43326.3493 | 2018-08-14 16:39 | 43326.6937 | -- | -- | -- | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR INFRINGEMENT CLEARANCE. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 9 | 46 | 1 | 5 | 9 | 14 | 0 | 0
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region |  | 2018-08-30 09:58 | 43342.4153 | 2018-08-30 17:21 | 43342.7229 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 23 | N/A | N/A | N/A | S/D TAKEN FOR JUMPER TIGHTENING WORKS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 23
NER L202 | KATHALGURI_MARIANI(OLD) |  | 162.864 | North Eastern Region |  | 2018-08-28 08:17 | 43340.3451 | 2018-08-28 12:53 | 43340.5368 | -- | -- | -- | 0 | 0 | 4 | 36 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D AVAILED BY STATE END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 4 | 36 | 0 | 0 | 0 | 0
NER L203 | MISA_DIMAPUR | # 1 | 123.52 | North Eastern Region |  | 2018-08-28 13:22 | 43340.5569 | 2018-08-28 17:40 | 43340.7361 | -- | -- | -- | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR ATTENDING HEAVY SPARKING IN R-PH ISOLATOR AT MISA S/S.
NER L203 | MISA_DIMAPUR | # 1 | 123.52 | North Eastern Region |  | 2018-08-27 09:51 | 43339.4104 | 2018-08-28 02:35 | 43340.1076 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | N/A | N/A | N/A | S/D AVAILED FOR REPLACEMENT FOR EXISTING CB WITH NEW CB; EXISTING CB OVER 25 YEARS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 4 | 18 | 0 | 0 | 0 | 0 | 16 | 44
NER L204 | MISA_DIMAPUR | # 2 | 123.52 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L205 | MISA_KATHALGURI |  | 382.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L206 | MISA-KOPILI | # 1 | 72.791 | North Eastern Region |  | 2018-08-27 19:30 | 43339.8125 | 2018-08-27 23:26 | 43339.9764 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 56 | N/A | N/A | N/A | E/S/D AVAILED FOR FACILITATING CHARGING OF 220KV MISA-DIMAPUR-I THROUGH TRANSFER BUS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 56
NER L207 | MISA_KOPILI | # 2 | 72.791 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L208 | MISA_KOPILI | # 3 | 75.788 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region |  | 2018-08-28 08:26 | 43340.3514 | 2018-08-28 12:53 | 43340.5368 | -- | -- | -- | 0 | 0 | 4 | 27 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D AVAILED BY STATE END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 4 | 27 | 0 | 0 | 0 | 0
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region |  | 2018-08-15 12:03 | 43327.5021 | 2018-08-15 14:09 | 43327.5896 | -- | -- | -- | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR RECTIFICATION OF Y-PH WAVE-TRAP CLAMP AT SAMAGURI END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region |  | 2018-08-22 12:55 | 43334.5382 | 2018-08-22 21:00 | 43334.875 | -- | -- | -- | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | PROLONG DELAY DUE TO NO TRANSFER FACILITIES AT SAMAGURI (AEGCL) S/S.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 0
NER L212 | SALAKATI_BTPS | # 2 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L213 | SALAKATI-BTPS | # 1 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region |  | 2018-08-17 04:47 | 43329.1993 | 2018-08-17 05:44 | 43329.2389 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AT NEW MARIANI END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-08-08 02:05 | 43320.0868 | 2018-08-08 02:34 | 43320.1069 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO OVERVOLTAGE |  | 100
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-08-26 05:58 | 43338.2486 | 2018-08-26 06:33 | 43338.2729 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO OVERVOLTAGE PROTECTION. |  | 100
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-08-25 04:53 | 43337.2035 | 2018-08-25 05:22 | 43337.2236 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO OVERVOLTAGE PROTECTION. |  | 100
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-08-25 00:59 | 43337.041 | 2018-08-25 01:21 | 43337.0563 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO OVERVOLTAGE PROTECTION. |  | 100
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-08-17 04:47 | 43329.1993 | 2018-08-17 05:59 | 43329.2493 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AT NEW MARIANI END. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region |  | 2018-08-17 04:47 | 43329.1993 | 2018-08-17 06:01 | 43329.2507 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 14 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO HEAVY LIGHTNING AT NEW MARIANI END.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 1 | 14 | 0 | 0
NER L401 | BALIPARA_BONGAIGAON | # 1 | 289.721 | North Eastern Region |  | 2018-08-07 09:07 | 43319.3799 | 2018-08-07 09:27 | 43319.3938 | -- | -- | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MALOPERATION |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-08-30 08:37 | 43342.359 | 2018-08-30 09:00 | 43342.375 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | N/A | N/A | N/A | BALUKA BAMBOO TOUCHED LINE, B/W LOC 468-469, FROM OUSTIDE CORRIDOR DURING LOCALISED STORM. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0
NER L403 | MISA_BALIPARA | # 1 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L404 | MISA-BALIPARA | #2 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L405 | BONGAIGAON-MALDA | # 1 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L406 | BONGAIGAON-MALDA | # 2 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L407 | BALIPARA-RANGANADI | # 1 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L408 | BALIPARA-RANGANADI | # 2 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L409 | PALLATANA-SURAJMANINAGAR | # 1 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L411 | BTPS-BONGAIGAON | #1 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L412 | BTPS-BONGAIGAON | #2 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-03 00:44 | 43315.0306 | 2018-08-03 19:04 | 43315.7944 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | N/A | N/A | N/A | LINE H/T VIDE CODE 2595
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-15 03:58 | 43327.1653 | 2018-08-15 18:40 | 43327.7778 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 42 | N/A | N/A | N/A | LINE H/T VIDE CODE 2791.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-12 15:11 | 43324.6326 | 2018-08-12 17:45 | 43324.7396 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 34 | N/A | N/A | N/A | LINE H/T VIDE CODE 2740
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-31 00:16 | 43343.0111 | 2018-08-31 11:22 | 43343.4736 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | N/A | N/A | N/A | LIEN H/T VIDE CODE 3150
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-18 06:04 | 43330.2528 | 2018-08-18 10:24 | 43330.4333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 20 | N/A | N/A | N/A | LINE H/T VIDE CODE 2848.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-30 00:58 | 43342.0403 | 2018-08-30 18:02 | 43342.7514 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | N/A | N/A | N/A | LINE H/T VIDE CODE 3132.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-26 04:49 | 43338.2007 | 2018-08-26 18:05 | 43338.7535 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 16 | N/A | N/A | N/A | H/T VIDE CODE 2980.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-08-01 | 43313 | 2018-08-01 18:52 | 43313.7861 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | N/A | N/A | N/A | LINE H/T VIDE CODE 2567
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 14
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-29 11:05 | 43341.4618 | 2018-08-29 19:01 | 43341.7924 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 56 | N/A | N/A | N/A | H/T VIDE CODE 3111. |  | 100
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-20 05:01 | 43332.209 | 2018-08-20 10:31 | 43332.4382 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | N/A | N/A | N/A | LINE H/T VIDE CODE 2876.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-16 03:07 | 43328.1299 | 2018-08-16 09:05 | 43328.3785 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58 | N/A | N/A | N/A | LINE H/T VIDE CODE 2806.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-08 02:26 | 43320.1014 | 2018-08-08 12:47 | 43320.5326 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21 | N/A | N/A | N/A | LINE H.T VIDE CODE 2671
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-25 05:16 | 43337.2194 | 2018-08-25 14:52 | 43337.6194 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 36 | N/A | N/A | N/A | H/T VIDE CODE 2959.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-13 02:48 | 43325.1167 | 2018-08-13 12:06 | 43325.5042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2755
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-06 10:20 | 43318.4306 | 2018-08-06 10:57 | 43318.4563 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | N/A | N/A | N/A | LINE H/T VIDE CODE 2636 TO FACILITATE L/R S/D
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-27 00:41 | 43339.0285 | 2018-08-27 18:29 | 43339.7701 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 48 | N/A | N/A | N/A | H/T VIDE CODE 2990.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-12 05:41 | 43324.2368 | 2018-08-12 12:13 | 43324.509 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 32 | N/A | N/A | N/A | LINE H/T VIDE CODE 2735
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-08-02 00:46 | 43314.0319 | 2018-08-02 18:49 | 43314.784 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | N/A | N/A | N/A | LINE H/T VIDE CODE 2587
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 39
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-08-29 09:22 | 43341.3903 | 2018-08-29 09:34 | 43341.3986 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO 800KV BNC-AGRA POLE-1 TRIPPING. |  | 100
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-08-09 09:53 | 43321.4118 | 2018-08-09 15:05 | 43321.6285 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 2692
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-08-23 06:08 | 43335.2556 | 2018-08-23 14:55 | 43335.6215 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 2923.
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-08-20 00:17 | 43332.0118 | 2018-08-20 10:02 | 43332.4181 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | N/A | N/A | N/A | LINE H/T VIDE CODE 2874.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12 | 23 | 44
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-08-29 09:22 | 43341.3903 | 2018-08-29 10:16 | 43341.4278 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO 800KV BNC-AGRA POLE-1 TRIPPING. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-08-29 09:22 | 43341.3903 | 2018-08-29 09:32 | 43341.3972 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO 800KV BNC-AGRA POLE-1 TRIPPING. LINE KEPT OPEN AS PER INSTRUCTIONS OF NERLDC.
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-08-29 09:32 | 43341.3972 | 2018-08-29 18:23 | 43341.766 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 51 | N/A | N/A | N/A | LINE KEPT OPEN AS PER INSTRUCTIONS OF NERLDC. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 51
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-08-12 05:32 | 43324.2306 | 2018-08-12 08:34 | 43324.3569 | -- | -- | -- | 0 | 0 | 3 | 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY PKBARI END
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-08-29 12:54 | 43341.5375 | 2018-08-29 13:35 | 43341.566 | -- | -- | -- | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LA OF TRANSFORMER BLASTED AT P.K. BARI (STATE) S/S. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3 | 43 | 0 | 0 | 0 | 0
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-08-12 05:32 | 43324.2306 | 2018-08-12 08:35 | 43324.3576 | -- | -- | -- | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY PKBARI |  | 100
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-08-29 12:54 | 43341.5375 | 2018-08-29 13:35 | 43341.566 | -- | -- | -- | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LA OF TRANSFORMER BLASTED AT P.K. BARI (STATE) S/S. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3 | 44 | 0 | 0 | 0 | 0
NER RBR1 | BR_BONGAIGAON (50MVAR) | # 1 | 50 | North Eastern Region |  | 2018-08-12 20:46 | 43324.8653 | 2018-08-13 00:03 | 43325.0021 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | N/A | N/A | N/A | B/R H/T VIE CODE 2751 |  | 100
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-08-09 19:19 | 43321.8049 | 2018-08-09 23:03 | 43321.9604 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 44 | N/A | N/A | N/A | B/R H/T VIDE CODE 2699
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-08-10 20:44 | 43322.8639 | 2018-08-11 04:03 | 43323.1687 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 19 | N/A | N/A | N/A | B/R H/T VIDE CODE 2716
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-08-11 18:16 | 43323.7611 | 2018-08-12 15:01 | 43324.6257 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 45 | N/A | N/A | N/A | B/R H/T VIDE CODE 2727
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-08-16 18:45 | 43328.7812 | 2018-08-18 06:01 | 43330.2507 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2822. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 4
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region |  | 2018-08-27 22:40 | 43339.9444 | 2018-08-27 23:55 | 43339.9965 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 15 | N/A | N/A | N/A | B/R H/T VIDE CODE 3028.
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region |  | 2018-08-28 00:40 | 43340.0278 | 2018-08-28 20:44 | 43340.8639 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | N/A | N/A | N/A | B/R H/T VIDE CODE 3041.
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region |  | 2018-08-29 08:27 | 43341.3521 | 2018-08-29 09:02 | 43341.3764 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | N/A | N/A | N/A | B/R H/T VIDE CODE 3094. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 54
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR5 | BR_KUMARGHAT (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR6 | BR_AIZWAL (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-06 18:54 | 43318.7875 | 2018-08-06 23:08 | 43318.9639 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 14 | N/A | N/A | N/A | B/R H/T VIDE CODE 2650
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-07 19:54 | 43319.8292 | 2018-08-08 13:12 | 43320.55 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | N/A | N/A | N/A | B/R H/T VIDE CODE 2668
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-08 18:49 | 43320.784 | 2018-08-10 05:05 | 43322.2118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | N/A | N/A | N/A | B/R H/T VIDE CODE 2689
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-10 18:26 | 43322.7681 | 2018-08-11 05:04 | 43323.2111 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38 | N/A | N/A | N/A | B/R H/T VIDE CODE 2714
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-11 18:51 | 43323.7854 | 2018-08-12 01:23 | 43324.0576 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 32 | N/A | N/A | N/A | B/R H/T VIDE CODE 2729
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-12 19:08 | 43324.7972 | 2018-08-13 00:04 | 43325.0028 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 56 | N/A | N/A | N/A | B/R H/T VIDE CODE 2748
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-13 18:20 | 43325.7639 | 2018-08-14 01:34 | 43326.0653 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 14 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2764
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-14 18:40 | 43326.7778 | 2018-08-15 01:24 | 43327.0583 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 44 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2787.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-16 14:38 | 43328.6097 | 2018-08-17 07:05 | 43329.2951 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 27 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2818.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-17 18:39 | 43329.7771 | 2018-08-18 06:02 | 43330.2514 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 23 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2841.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-18 11:10 | 43330.4653 | 2018-08-19 05:07 | 43331.2132 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 57 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2853.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-21 19:09 | 43333.7979 | 2018-08-22 01:55 | 43334.0799 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 46 | N/A | N/A | N/A | B/R H/T VIDE CODE 2908.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-22 18:49 | 43334.784 | 2018-08-23 05:42 | 43335.2375 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53 | N/A | N/A | N/A | B/R H/T VIDE CODE 2919.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-28 20:26 | 43340.8514 | 2018-08-29 01:59 | 43341.0826 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33 | N/A | N/A | N/A | B/R H/T VIDE CODE 3079.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-08-29 18:19 | 43341.7632 | 2018-08-29 21:48 | 43341.9083 | -- | -- | -- | 0 | 0 | 3 | 29 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | B/R H/T VIDE CODE 3122. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3 | 29 | 0 | 0 | 160 | 51
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-08-27 22:36 | 43339.9417 | 2018-08-28 00:06 | 43340.0042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | N/A | N/A | N/A | B/R H/T VIDE CODE 3026.
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-08-28 10:08 | 43340.4222 | 2018-08-28 10:10 | 43340.4236 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N/A | N/A | N/A | B/R H/T VIDE CODE 3052(A).
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-08-28 20:28 | 43340.8528 | 2018-08-28 20:39 | 43340.8604 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | N/A | N/A | N/A | B/R H/T VIDE CODE 3078.
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-08-29 08:28 | 43341.3528 | 2018-08-29 10:49 | 43341.4507 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 21 | N/A | N/A | N/A | B/R H/T VIDE CODE 3095. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-08-04 19:04 | 43316.7944 | 2018-08-05 22:18 | 43317.9292 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 14 | N/A | N/A | N/A | B/R H/T VIDE CODE 2621 |  | 100
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-08-07 19:44 | 43319.8222 | 2018-08-09 22:09 | 43321.9229 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 25 | N/A | N/A | N/A | B/R H/T VIDE CODE 2667
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-08-11 18:22 | 43323.7653 | 2018-08-12 01:27 | 43324.0604 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | N/A | N/A | N/A | B/R H/T VIDE CODE 2728 |  | 100
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-08-25 18:37 | 43337.7757 | 2018-08-26 00:24 | 43338.0167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47 | N/A | N/A | N/A | REACTOR H.T. VIDE CODE 2977.
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-08-29 18:43 | 43341.7799 | 2018-08-30 00:06 | 43342.0042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23 | N/A | N/A | N/A | REACTOR H.T. VIDE CODE 3125. |  | 100
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-08-30 14:55 | 43342.6215 | 2018-08-31 00:11 | 43343.0076 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | N/A | N/A | N/A | REACTOR H.T. VIDE CODE 3142.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 10
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-08-06 19:10 | 43318.7986 | 2018-08-06 22:40 | 43318.9444 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | N/A | N/A | N/A | B/R H/T VIDE CODE 2651
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-08-13 19:29 | 43325.8118 | 2018-08-13 23:32 | 43325.9806 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | N/A | N/A | N/A | B/R H/T VIDE CODE 2766
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-08-29 18:45 | 43341.7812 | 2018-08-30 00:08 | 43342.0056 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23 | N/A | N/A | N/A | REACTOR H.T. VIDE CODE 3126.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 56
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-05 19:13 | 43317.8007 | 2018-08-06 01:10 | 43318.0486 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57 | N/A | N/A | N/A | B/R H/T VIDE CODE 2629 |  | 100
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-06 18:29 | 43318.7701 | 2018-08-06 23:51 | 43318.9938 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | N/A | N/A | N/A | B/R H/T VIDE CODE 2648
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-07 19:22 | 43319.8069 | 2018-08-12 01:25 | 43324.059 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 3 | N/A | N/A | N/A | B/R H/T VIDE CODE 2666
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-12 19:08 | 43324.7972 | 2018-08-13 00:04 | 43325.0028 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 56 | N/A | N/A | N/A | B/R H/T VIDE CODE 2749 |  | 100
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-13 17:08 | 43325.7139 | 2018-08-14 07:30 | 43326.3125 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2762.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-14 18:26 | 43326.7681 | 2018-08-15 07:12 | 43327.3 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 46 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2786.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-15 22:57 | 43327.9563 | 2018-08-19 05:07 | 43331.2132 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 10 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2805. |  | 100
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-19 20:00 | 43331.8333 | 2018-08-20 00:13 | 43332.009 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 13 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2870.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-20 18:44 | 43332.7806 | 2018-08-21 04:01 | 43333.1674 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 17 | N/A | N/A | N/A | B/R H/T VIDE CODE 2892.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-21 18:56 | 43333.7889 | 2018-08-22 06:46 | 43334.2819 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | N/A | N/A | N/A | B/R H/T VIDE CODE 2907. |  | 100
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-22 18:38 | 43334.7764 | 2018-08-23 05:47 | 43335.241 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 9 | N/A | N/A | N/A | B/R H/T VIDE CODE 2918.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-23 10:10 | 43335.4236 | 2018-08-25 01:26 | 43337.0597 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 16 | N/A | N/A | N/A | B/R H/T VIDE CODE 2927.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-25 18:26 | 43337.7681 | 2018-08-26 03:50 | 43338.1597 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 24 | N/A | N/A | N/A | B/R H/T VIDE CODE 2976.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-27 22:37 | 43339.9424 | 2018-08-27 23:46 | 43339.9903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | N/A | N/A | N/A | B/R H/T VIDE CODE 3027.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-28 18:59 | 43340.791 | 2018-08-29 05:34 | 43341.2319 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35 | N/A | N/A | N/A | B/R H/T VIDE CODE 3075. |  | 100
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-08-29 18:09 | 43341.7562 | 2018-08-29 22:59 | 43341.9576 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | N/A | N/A | N/A | B/R H/T VIDE CODE 3121.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 19
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-08-27 22:46 | 43339.9486 | 2018-08-28 08:03 | 43340.3354 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 17 | N/A | N/A | N/A | B/R H/T VIDE CODE 3029. |  | 100
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-08-28 09:17 | 43340.3868 | 2018-08-28 10:38 | 43340.4431 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | B/R H/T VIDE CODE 3050. |  | 100
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-08-28 11:42 | 43340.4875 | 2018-08-28 16:39 | 43340.6937 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 57 | N/A | N/A | N/A | B/R H/T VIDE CODE 3060. |  | 100
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-08-28 20:20 | 43340.8472 | 2018-08-28 20:47 | 43340.866 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | N/A | N/A | N/A | B/R H/T VIDE CODE 3076. |  | 100
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-08-29 08:47 | 43341.366 | 2018-08-29 09:24 | 43341.3917 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | N/A | N/A | N/A | B/R H/T VIDE CODE 3097. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18
NER RBR13 | BR_B'CHARIALI(80MVAR) | #2 | 80 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR14 | BR_B'CHARIALI(63MVAR) | #3 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR15 | BR_B'CHARIALI(63MVAR) | #4 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR16 | BR_New_MARIANI(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR17 | BR_BALIPARA(125MVAR) | #3 |  | North Eastern Region |  | 2018-08-27 22:09 | 43339.9229 | 2018-08-29 19:48 | 43341.825 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 39 | N/A | N/A | N/A | REACTOR H.T. VIDE CODE 3023. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 39
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 |  | North Eastern Region |  | 2018-08-13 18:20 | 43325.7639 | 2018-08-17 13:57 | 43329.5813 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 37 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2765.
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 |  | North Eastern Region |  | 2018-08-17 18:23 | 43329.766 | 2018-08-21 04:10 | 43333.1736 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 47 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 2840.
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 |  | North Eastern Region |  | 2018-08-24 19:15 | 43336.8021 | 2018-08-25 01:19 | 43337.0549 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | N/A | N/A | N/A | B/R H/T VIDE CODE 2952.
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 |  | North Eastern Region |  | 2018-08-27 18:39 | 43339.7771 | 2018-08-27 20:45 | 43339.8646 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | N/A | N/A | N/A | B/R H/T VIDE CODE 3016.
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 |  | North Eastern Region |  | 2018-08-27 22:00 | 43339.9167 | 2018-08-27 23:56 | 43339.9972 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 56 | N/A | N/A | N/A | B/R H/T VIDE CODE 3022.
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 |  | North Eastern Region |  | 2018-08-28 18:51 | 43340.7854 | 2018-08-29 13:14 | 43341.5514 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 23 | N/A | N/A | N/A | B/R H/T VIDE CODE 3074. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 53
NER RBR19 | BR_ROING(20MVAR) | #1 | 20 | North Eastern Region |  | 2018-08-16 08:01 | 43328.334 | 2018-08-31 23:59 | 43343.9993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 58 | N/A | N/A | N/A | SD TAKEN FOR OFFLINE DRYING OUT |  | 100
| BR_ROING(20MVAR) | #1 |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 58
NER TICT1 | ICT_BONGAIGAON(315MVA) |  | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT2 | ICT_BALIPARA (315MVA) | #1 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT3 | ICT_BALIPARA (315MVA) | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region |  | 2018-08-01 09:52 | 43313.4111 | 2018-08-01 17:14 | 43313.7181 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 22 | N/A | N/A | N/A | S/D TKAEN FOR BEAM ERECTION & HIGH LEVEL ISOLATOR ERECTION WORKS UNDER NERSS IV PROJECT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 22
NER TICT5 | ICT_MISA | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT7 | ICT_B'CHARIALI (200MVA) | #1 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT8 | ICT_B'CHARIALI (200MVA) | #2 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT9 | ICT_IMPHAL(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT10 | ICT_IMPHAL(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT12 | ICT_DIMAPUR (100 MVA) | # 1 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT13 | ICT_DIMAPUR (100 MVA) | #2 | 100 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT16 | ICT_MOKOKCHUNG(30MVA) | #2 | 30 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT17 | ICT_NIRJULI(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT18 | ICT_NIRJULI(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT19 | ICT_ZIRO (15MVA) |  | 15 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT20 | ICT_KOPILI (160 MVA) | # 2 | 160 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT21 | ICT_KUMARGHAT(5MVA) |  | 5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SEP 2018 - TABLE I
Unique ID of transmission Element | Element Name |  | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee Hr min |  | OTHERS Hr min |  | System Constraints/ Natural calamity / Militancy Hr min |  | Deemed Available Hr min
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-09-20 01:37 | 43363.0674 | 2018-09-20 01:53 | 43363.0785 | -- | -- | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | FAULT BEYOND LINE LENGTH & PROBLEM AT TRIPURA STATE SYSTEM | Awaited | 100
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-09-20 13:57 | 43363.5813 | 2018-09-20 14:23 | 43363.5993 | -- | -- | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO DOWNSTREAM FAULT OF TRIPURA
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-09-22 09:47 | 43365.4076 | 2018-09-22 16:52 | 43365.7028 | -- | -- | -- | 0 | 0 | 7 | 5 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY STATE
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-09-27 14:15 | 43370.5938 | 2018-09-27 14:30 | 43370.6042 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AROUND AGARTALA REGION.
NER L101 | RCN_AGARTALA | # 1 | 8.384 | North Eastern Region |  | 2018-09-30 04:12 | 43373.175 | 2018-09-30 07:08 | 43373.2972 | -- | -- | -- | 0 | 0 | 2 | 56 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN BY STATE.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 10 | 43 | 0 | 15 | 0 | 0
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region |  | 2018-09-20 01:37 | 43363.0674 | 2018-09-20 01:59 | 43363.0826 | -- | -- | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | FAULT BEYOND LINE LENGTH AND PROBLEM AT TRIPURA STATE SYSTEM
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region |  | 2018-09-20 10:22 | 43363.4319 | 2018-09-20 17:03 | 43363.7104 | -- | -- | -- | 0 | 0 | 6 | 41 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LINE H/T TO FACILITATE BUS S/D AT AGARTALA SS
NER L102 | RCN_AGARTALA | # 2 | 8.384 | North Eastern Region |  | 2018-09-27 14:15 | 43370.5938 | 2018-09-27 14:41 | 43370.6118 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AROUND AGARTALA REGION
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 7 | 3 | 0 | 26 | 0 | 0
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-09-03 13:05 | 43346.5451 | 2018-09-03 14:45 | 43346.6146 | -- | -- | -- | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 0 | N/A | N/A | N/A | S/D TAKEN FOR TREE REMOVAL WHICH LEANED TOWARDS LINE FROM OUTSIDE CORRIDOR DUE TO WIND PRESSURE
NER L103 | BADARPUR_KOLASIB |  | 107.226 | North Eastern Region |  | 2018-09-08 11:02 | 43351.4597 | 2018-09-08 13:25 | 43351.559 | -- | -- | -- | 0 | 0 | 0 | 0 | 2 | 23 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR TREE CLEARING INCLINED TOWARDS TOWER DUE TO WIND PRESSURE FROM OUTSIDE CORRIDOR
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0
NER L104 | AIZWAL_KUMARGHAT |  | 131 | North Eastern Region |  | 2018-09-23 08:07 | 43366.3382 | 2018-09-30 23:59 | 43373.9993 | -- | -- | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 52 | N/A | N/A | N/A | C/S/D TAKEN FOR SHIFTING OF EXISTING VULNERABLE TOWER AT LOC 70; RAILWAY WORK, LANDSLIDE.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 52
NER L105 | AIZWAL_ZEMEBAK | # 2 | 6.719 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L106 | BADARPUR-BADARPUR |  | 1.023 | North Eastern Region |  | 2018-09-01 22:27 | 43344.9354 | 2018-09-01 22:48 | 43344.95 | -- | -- | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FAULT IN DOWNSTREAM 132KV PANCHGRAM-LUMSHNONG STATE FEEDER
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0
NER L107 | BADARPUR_JIRIBAM |  | 67.21 | North Eastern Region |  | 2018-09-18 08:06 | 43361.3375 | 2018-09-21 17:13 | 43364.7174 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 7 | N/A | N/A | N/A | CONTINUOUS SD TAKEN FOR STRINGING OF 400KV SILCHAR-MELRIAT TL
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 7
NER L108 | BADARPUR_KHLIERIAT |  | 76.646 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L109 | BADARPUR_KUMARGHAT |  | 118.513 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L110 | DIMAPUR_IMPHAL |  | 168.865 | North Eastern Region | PARTIAL DAMAGED OF TOWER | 2018-09-01 00:01 | 43344.0007 | 2018-09-30 23:59 | 43373.9993 | 1 | -- | 30 | 0 | 0 | 0 | 0 | 719 | 58 | 0 | 0 | 50 | N | -20 | LINE PUT UNDER E/S/D DUE TO PARTIAL DAMAGE OF TOWER AT LOC 39; LANDSLIDE.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 719 | 58 | 0 | 0
NER L111 | DOYANG_DIMAPUR | # 1 | 92.526 | North Eastern Region |  | 2018-09-19 12:54 | 43362.5375 | 2018-09-19 13:19 | 43362.5549 | -- | -- | -- | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LBB OPERATED IN 132KV SIDE AT DIMAPUR SS
[6 empty] | Sub Total --> | [6 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-09-19 12:54 | 43362.5375 | 2018-09-19 13:20 | 43362.5556 | -- | -- | -- | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LBB OPERATED IN 132KV SIDE AT DIMAPUR
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-09-19 15:59 | 43362.666 | 2018-09-19 16:54 | 43362.7042 | -- | -- | -- | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ESD TAKEN FOR RECTIFICATION OF POLE DISCREPANCY AT DIMAPUR
NER L112 | DOYANG_DIMAPUR | # 2 | 92.526 | North Eastern Region |  | 2018-09-30 09:51 | 43373.4104 | 2018-09-30 12:13 | 43373.509 | -- | -- | -- | 2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY DIMAPUR TO ATTEND HOTSPOT IN B-PH CT CLAMP LINE SIDE IN DOYANG-II BAY.
[6 empty] | Sub Total --> | [6 empty] | 3 | 43 | 0 | 0 | 0 | 0 | 0 | 0
NER L113 | GOHPUR_NIRJULI |  | 42.5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-09-08 08:01 | 43351.334 | 2018-09-08 11:34 | 43351.4819 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 33 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONUCTOR UNDER PROJECT NERSSIV
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-09-10 08:12 | 43353.3417 | 2018-09-10 17:13 | 43353.7174 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER NERSS IV
NER L114 | IMPHAL_IMPHAL | #1 | 1.5 | North Eastern Region |  | 2018-09-11 08:03 | 43354.3354 | 2018-09-11 16:51 | 43354.7021 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 48 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER NERSS IV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22
NER L115 | JIRIBAM_AIZWAL |  | 172.315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L116 | JIRIBAM_HAFLONG |  | 100.63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L117 | JIRIBAM_LOKTAK | # 2 | 82.4 | North Eastern Region |  | 2018-09-02 08:39 | 43345.3604 | 2018-09-07 17:11 | 43350.716 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 32 | N/A | N/A | N/A | SD TAKEN FOR SHIFTING OF EXISTING TOWER AT LOC 241 & REPAIRING OF TOWER AT LOC 82 DUE TO LANDSLIDE
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 32
NER L118 | KHANDONG-HAFLONG |  | 63.166 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L119 | KHANDONG_KHLIERIAT | # 1 | 42.48 | North Eastern Region |  | 2018-09-19 05:57 | 43362.2479 | 2018-09-19 06:06 | 43362.2542 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS SUPPORTED BY DR FILE AND PATROL REPORT
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0
NER L120 | KHANDONG_KHLIERIAT | # 2 | 40.933 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L121 | KHANDONG_KOPILI | # 1 | 10.914 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L122 | KHLIERIAT_KHLIERIAT |  | 7.801 | North Eastern Region |  | 2018-09-27 07:59 | 43370.3326 | 2018-09-27 15:25 | 43370.6424 | -- | -- | -- | 0 | 0 | 7 | 26 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY STATE END.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 7 | 26 | 0 | 0 | 0 | 0
NER L123 | KUMARGHAT_R C NAGAR |  | 104.02 | North Eastern Region |  | 2018-09-16 09:33 | 43359.3979 | 2018-09-16 17:07 | 43359.7132 | -- | -- | -- | 7 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN FOR INFRINGEMENT CLEARING
[6 empty] | Sub Total --> | [6 empty] | 7 | 34 | 0 | 0 | 0 | 0 | 0 | 0
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region |  | 2018-09-04 14:28 | 43347.6028 | 2018-09-04 15:13 | 43347.634 | -- | -- | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | AT SAME TIME, DOWNSTREAM STATE FEEDER 132KV LOKTAK-NINGTHOUKONG LINE TRIPPED
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region |  | 2018-09-08 08:03 | 43351.3354 | 2018-09-08 09:23 | 43351.391 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER PROJECT NERSSI
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region |  | 2018-09-10 08:30 | 43353.3542 | 2018-09-10 17:13 | 43353.7174 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | N/A | N/A | N/A | SD TAKEN FOR REPLACMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER PROJECT NERSSIV
NER L124 | LOKTAK_IMPHAL | # 2 | 35.04 | North Eastern Region |  | 2018-09-11 08:05 | 43354.3368 | 2018-09-11 17:08 | 43354.7139 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 3 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER NERSS IV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 45 | 0 | 0 | 19 | 6
NER L125 | SALAKATI-GELEPHUG |  | 49.217 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L126 | LEKHI - RANGANADI |  | 12.59 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region |  | 2018-09-11 05:03 | 43354.2104 | 2018-09-11 05:21 | 43354.2229 | -- | -- | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FAULT IN 33KV AP-I STATE FEEDER
NER L127 | NIRJULI-LEKHI |  | 9.7 | North Eastern Region | ISOLATOR DROPPER OF 33KV AP-2 | 2018-09-19 18:25 | 43362.7674 | 2018-09-19 19:48 | 43362.825 | -- | -- | 0 | 1 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -3 | TRIPPED DUE TO SNAPPING OF 33V BUS SIDE R-PH ISOLATOR DROPPER OF 33KV AP-2 FEEDER
[6 empty] | Sub Total --> | [6 empty] | 1 | 23 | 0 | 18 | 0 | 0 | 0 | 0
NER L128 | KOLASIB-AIZAWL |  | 66.098 | North Eastern Region |  | 2018-09-21 17:50 | 43364.7431 | 2018-09-21 18:10 | 43364.7569 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0
NER L129 | RANGANADI-ZIRO |  | 44.523 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L130 | KHANDONG_KOPILI | # 2 | 11.56 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region |  | 2018-09-03 10:11 | 43346.4243 | 2018-09-03 13:21 | 43346.5563 | -- | -- | -- | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN TO ATTEND HOTSPOT IN ISOLATOR CONNECTOR BETWEEN AIS MAIN BUS & GIS MAIN BUS
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region |  | 2018-09-12 06:05 | 43355.2535 | 2018-09-18 18:15 | 43361.7604 | -- | -- | -- | 0 | 0 | 156 | 10 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY STATE END
NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) |  | 0.347 | North Eastern Region |  | 2018-09-21 06:35 | 43364.2743 | 2018-09-30 23:59 | 43373.9993 | -- | -- | -- | 0 | 0 | 233 | 24 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | CONTINUOUS S/D TAKEN BY STATE.
[6 empty] | Sub Total --> | [6 empty] | 3 | 10 | 389 | 34 | 0 | 0 | 0 | 0
NER L133 | SILCHAR-BADARPUR-I | #1 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L134 | SILCHAR-BADARPUR-II | #2 | 19.195 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L135 | SILCHAR-SRIKONA-I | #1 | 1.199 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region |  | 2018-09-14 08:47 | 43357.366 | 2018-09-14 23:34 | 43357.9819 | -- | -- | -- | 0 | 0 | 14 | 47 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN BY STATE
NER L136 | SILCHAR-SRIKONA-II | #2 | 1.199 | North Eastern Region |  | 2018-09-20 09:44 | 43363.4056 | 2018-09-20 17:36 | 43363.7333 | -- | -- | -- | 0 | 0 | 7 | 52 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY STATE
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 22 | 39 | 0 | 0 | 0 | 0
NER L137 | IMPHAL-IMPHAL | # 2 | 0.442 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #1 | 17.3 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L139 | SILCHAR-HAILAKANDI | #2 | 17.3 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L140 | MOKUKCHUNG_MOKUKCHUNG | #1 | 1.4 | North Eastern Region |  | 2018-09-24 20:29 | 43367.8535 | 2018-09-24 21:02 | 43367.8764 | -- | -- | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FAULT IN DOWNTREAM FAULT IN DOWNSTREAM 132KV DOYAND-MOKOKCHUNG STATE FEEDER
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0
NER L141 | MOKOCHUNG-MOKOKCHUNG | #2 | 1.4 | North Eastern Region |  | 2018-09-24 20:29 | 43367.8535 | 2018-09-24 21:02 | 43367.8764 | -- | -- | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FAULT IN DOWNSTREAM 132KV DOYANG-MOKOKCHUNG STATE FEEDER
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0
NER L142 | B.CHARAILI_PAVOI | #1 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L143 | B.CHARAILI_PAVOI | #2 | 12.93 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L144 | ROING_PASIGHAT |  |  | North Eastern Region | phase to phase fault | 2018-09-11 09:26 | 43354.3931 | 2018-09-11 09:50 | 43354.4097 | -- | -- | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TRANSIENT PHASE TO PHASE FAULT
[6 empty] | Sub Total --> | [6 empty] | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-09-13 11:10 | 43356.4653 | 2018-09-13 11:21 | 43356.4729 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | N/A | N/A | N/A | BAMBOO CUT BY UNKNOWN VILLAGERS BETWEEN LOC 394-395 FELL ON THE CONDUCTORS
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-09-19 12:04 | 43362.5028 | 2018-09-19 15:11 | 43362.6326 | -- | -- | -- | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | N/A | N/A | N/A | ESD TAKEN FOR CLEARING TREE CUT BY VILLAGERS WHICH WAS LEANING TOWARDS THE LINE FROM OTUSIDE LINE CORRIDOR BETWEEN LOC 394-395
NER L145 | AIZAWL - TIPAIMUKH | #1 |  | North Eastern Region | Jumper Opened | 2018-09-20 12:57 | 43363.5396 | 2018-09-20 14:10 | 43363.5903 | -- | -- | 0 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | N | -3 | ESD TAKEN FOR ATTENDING OPENED Y-PH JUMPER AT LOC 424
[6 empty] | Sub Total --> | [6 empty] | 1 | 13 | 0 | 0 | 3 | 18 | 0 | 0
NER L146 | AIZAWL MELRIAT |  |  | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L157 | JIRIBAM - TIPAIMUKH | #1 |  | North Eastern Region |  | 2018-09-14 08:15 | 43357.3438 | 2018-09-14 16:54 | 43357.7042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | N/A | N/A | N/A | SD TAKEN FOR TL INSTALLATION OF VARIOUS LOCATION
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39
NER L201 | BALIPARA_TEZPUR |  | 8.623 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L202 | KATHALGURI_MARIANI(OLD) |  | 162.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L203 | MISA_DIMAPUR | # 1 | 123.52 | North Eastern Region |  | 2018-09-07 11:44 | 43350.4889 | 2018-09-07 19:55 | 43350.8299 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | N/A | N/A | N/A | E/S/D TAKEN FOR JUMPERING WORKS & PROTECTION CLEARING OF NEW MAIN CB AT MISA
NER L203 | MISA_DIMAPUR | # 1 | 123.52 |  |  | 2018-09-11 15:06 | 43354.6292 | 2018-09-11 17:23 | 43354.7243 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17 | N/A | N/A | N/A | ESD TAKEN FOR JUMPERING WORKS AND CHARGING OF NEW MAIN CB AT MISA
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28
NER L204 | MISA_DIMAPUR | # 2 | 123.52 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L205 | MISA_KATHALGURI |  | 382.864 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L206 | MISA-KOPILI | # 1 | 72.791 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L207 | MISA_KOPILI | # 2 | 72.791 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L208 | MISA_KOPILI | # 3 | 75.788 | North Eastern Region | Burnt mark in E/W fitting | 2018-09-12 12:33 | 43355.5229 | 2018-09-12 12:38 | 43355.5264 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 3 | N | -3 | TRIPPED DUE TO LIGHTNING AS BURNING MARKS FOUND IN EARTHWIRE FITTINGS BETWEEN LOC 33-34
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0
NER L209 | MISA_MARIANI(OLD) |  | 220 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L210 | MISA_SAMAGURI | # 1 | 34.439 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L211 | MISA_SAMAGURI | # 2 | 34.439 | North Eastern Region |  | 2018-09-22 12:49 | 43365.534 | 2018-09-22 13:15 | 43365.5521 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO TEAK PLANTATIONS BETWEEN LOC 2 & 3 WHICH HAD BEEN LEFT UNATTENDED DUE TO SERVERE ROW
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0
NER L212 | SALAKATI_BTPS | # 2 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L213 | SALAKATI-BTPS | # 1 | 2.7 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region |  | 2018-09-19 00:43 | 43362.0299 | 2018-09-19 01:31 | 43362.0632 | -- | -- | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO RELAY MALOPERATION
NER L214 | MISA-MARIANI(NEW) |  | 222.682 | North Eastern Region |  | 2018-09-20 13:38 | 43363.5681 | 2018-09-20 17:33 | 43363.7312 | -- | -- | -- | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN TOA TTEND & CONFIGURE SIEMENS RELAY SETTINGS AT MISA
|  |  |  | North Eastern Region |  | Sub Total --> | [6 empty] | 4 | 43 | 0 | 0 | 0 | 0 | 0 | 0
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region | Damaged insulator | 2018-09-17 14:28 | 43360.6028 | 2018-09-17 15:10 | 43360.6319 | -- | 1 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -2 | TRIPPED DUE TO FAILURE OF ONE OF DOUBLE INSULATOR STRING IN R-PH AT LOC 15
NER L215 | KATHALGURI-MARIANI(NEW) |  | 160.536 | North Eastern Region |  | 2018-09-17 16:55 | 43360.7049 | 2018-09-19 17:59 | 43362.7493 | -- | -- | -- | 0 | 0 | 49 | 4 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LINE H/T VIDE DUE TO SAFETY ISUE AS REQUESTED BY KATHALGURI ON A/C INSULATOR STRING FAIL AT LOC 15
[6 empty] | Sub Total --> | [6 empty] | 0 | 42 | 49 | 4 | 0 | 0 | 0 | 0
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-09-02 04:06 | 43345.1708 | 2018-09-02 04:23 | 43345.1826 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON OVERVOLTAGE AT MOKOKCHUNG END
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-09-19 00:43 | 43362.0299 | 2018-09-19 01:34 | 43362.0653 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON OVERVOLTAGE PROTECTION AT MOKOKCHUNG END
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-09-26 02:30 | 43369.1042 | 2018-09-26 03:45 | 43369.1562 | -- | -- | 0 | 0 | 0 | 0 | 0 | 1 | 15 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON O/V PROTECTION AT MOKOKCHUNG END.
NER L216 | MARIANI_MOKUKCHUNG | #1 | 48.8 | North Eastern Region |  | 2018-09-27 19:30 | 43370.8125 | 2018-09-27 19:42 | 43370.8208 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON OVERVOLTAGE PROTECTION AT MOKOKCHUNG END.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 2 | 35 | 0 | 0
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region |  | 2018-09-11 11:30 | 43354.4792 | 2018-09-11 14:53 | 43354.6201 | -- | -- | -- | 3 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN FOR HOTSPOT RECTIFICATION AT VARIOUS LOCATION OF THE LINE
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region |  | 2018-09-19 00:43 | 43362.0299 | 2018-09-19 01:34 | 43362.0653 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS SUPPORTED BY PATROL REPORT AND DR FILE
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region |  | 2018-09-19 01:34 | 43362.0653 | 2018-09-19 08:50 | 43362.3681 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | N/A | N/A | N/A | LINE KEPT OPEN DUE TO SYSTEM CONSTRAINTS AS PER NERLDC INSTRUCTION
NER L217 | MARIANI_MOKUKCHUNG | #2 | 48.8 | North Eastern Region |  | 2018-09-19 22:26 | 43362.9347 | 2018-09-20 09:50 | 43363.4097 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 24 | N/A | N/A | N/A | LINE H/T VIDE CODE 3684
[6 empty] | Sub Total --> | [6 empty] | 3 | 23 | 0 | 0 | 0 | 51 | 18 | 34
NER L401 | BALIPARA_BONGAIGAON | # 1 | 289.721 | North Eastern Region |  | 2018-09-14 10:10 | 43357.4236 | 2018-09-14 19:04 | 43357.7944 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 54 | N/A | N/A | N/A | SD TAKEN FOR CSD COMISSIONING WORKS
NER L401 | BALIPARA_BONGAIGAON | # 1 | 289.721 | North Eastern Region |  | 2018-09-15 10:50 | 43358.4514 | 2018-09-16 00:39 | 43359.0271 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 49 | N/A | N/A | N/A | SD TAEKN FOR CSD COMISSIONING
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 43
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-09-11 09:26 | 43354.3931 | 2018-09-12 00:33 | 43355.0229 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | N/A | N/A | N/A | SD TAKEN FOR CSD COMMISSIONING & WORK RELATED TO LINE REACTOR
NER L402 | BALIPARA_BONGAIGAON | # 2 | 289.721 | North Eastern Region |  | 2018-09-18 11:17 | 43361.4701 | 2018-09-18 18:35 | 43361.7743 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 3626
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25
NER L403 | MISA_BALIPARA | # 1 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L404 | MISA-BALIPARA | #2 | 95.407 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L405 | BONGAIGAON-MALDA | # 1 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L406 | BONGAIGAON-MALDA | # 2 | 432 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L407 | BALIPARA-RANGANADI | # 1 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L408 | BALIPARA-RANGANADI | # 2 | 166.335 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L409 | PALLATANA-SURAJMANINAGAR | # 1 | 37.2 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region |  | 2018-09-02 09:23 | 43345.391 | 2018-09-02 16:45 | 43345.6979 | -- | -- | -- | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN FOR AMP OF BAY & JUMPER TIGTHENING WORKS
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region |  | 2018-09-08 08:30 | 43351.3542 | 2018-09-08 16:55 | 43351.7049 | -- | -- | -- | 0 | 0 | 8 | 25 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN BY OTPC
NER L410 | PALLATANA-SURAJMANINAGAR | # 2 | 37.2 | North Eastern Region |  | 2018-09-27 14:17 | 43370.5951 | 2018-09-27 14:34 | 43370.6069 | -- | -- | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO PROBLEM IN TRIPURA SYSTEM. .
[6 empty] | Sub Total --> | [6 empty] | 7 | 22 | 8 | 42 | 0 | 0 | 0 | 0
NER L411 | BTPS-BONGAIGAON | #1 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L412 | BTPS-BONGAIGAON | #2 | 3.119 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-04 06:09 | 43347.2562 | 2018-09-04 10:11 | 43347.4243 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 3336
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-08 11:20 | 43351.4722 | 2018-09-08 16:48 | 43351.7 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28 | N/A | N/A | N/A | LINE H/T VIDE CODE 3451
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-11 00:05 | 43354.0035 | 2018-09-11 09:22 | 43354.3903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 17 | N/A | N/A | N/A | LINE H/T VIDE CODE 3490
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-12 00:59 | 43355.041 | 2018-09-12 04:55 | 43355.2049 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 56 | N/A | N/A | N/A | LINE H/T VIDE CODE 3511
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-12 08:06 | 43355.3375 | 2018-09-12 11:51 | 43355.4938 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 45 | N/A | N/A | N/A | LINE H/T VIDE CODE 3523
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-13 22:50 | 43356.9514 | 2018-09-14 10:06 | 43357.4208 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16 | N/A | N/A | N/A | LINE H/T VIDE CODE 3551
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-14 23:35 | 43357.9826 | 2018-09-15 10:22 | 43358.4319 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47 | N/A | N/A | N/A | LINE H/T VIDE CODE 3569
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-16 23:09 | 43359.9646 | 2018-09-17 18:03 | 43360.7521 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | N/A | N/A | N/A | LINE H/T VIDE CODE 3604
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-19 00:16 | 43362.0111 | 2018-09-19 16:59 | 43362.7076 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 43 | N/A | N/A | N/A | LINE H/T VIDE CODE 3645
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-22 09:44 | 43365.4056 | 2018-09-22 14:00 | 43365.5833 | -- | -- | -- | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR SPARKING OBSERVED AT B-H WAVETRAP AT BALIPARA TO RECTIFY THE SAME
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-22 14:00 | 43365.5833 | 2018-09-22 17:36 | 43365.7333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 36 | N/A | N/A | N/A | LINE OPENED DUE TO SYSTEM CONSTRAINT
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-22 23:50 | 43365.9931 | 2018-09-23 17:50 | 43366.7431 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | N/A | N/A | N/A | LINE H/T VIDE CODE 3784
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-25 01:06 | 43368.0458 | 2018-09-25 17:24 | 43368.725 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 3820.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-27 01:06 | 43370.0458 | 2018-09-27 15:14 | 43370.6347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | N/A | N/A | N/A | LINE H/T VIDE CODE 3869.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-29 12:56 | 43372.5389 | 2018-09-29 18:02 | 43372.7514 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | N/A | N/A | N/A | LINE H/T VIDE CODE 3976.
NER L413 | BALIPARA-BONGAIGAON | #3 | 309 | North Eastern Region |  | 2018-09-29 22:52 | 43372.9528 | 2018-09-30 17:35 | 43373.7326 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 43 | N/A | N/A | N/A | LINE H/T VIDE CODE 3988.
[6 empty] | Sub Total --> | [6 empty] | 4 | 16 | 0 | 0 | 0 | 0 | 156 | 9
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-01 06:00 | 43344.25 | 2018-09-01 09:37 | 43344.4007 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 37 | N/A | N/A | N/A | LINE H/T VIDE CODE 3173
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-01 16:59 | 43344.7076 | 2018-09-01 18:17 | 43344.7618 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 3180
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-02 05:35 | 43345.2326 | 2018-09-02 18:04 | 43345.7528 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 29 | N/A | N/A | N/A | LINE H/T VIDE CODE 2391
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-03 05:22 | 43346.2236 | 2018-09-03 16:17 | 43346.6785 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55 | N/A | N/A | N/A | LINE H/T VIDE CODE 3311
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-06 05:13 | 43349.2174 | 2018-09-06 15:07 | 43349.6299 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 54 | N/A | N/A | N/A | LINE H/T VIDE CODE 3388
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region | jumper flash mark | 2018-09-12 04:44 | 43355.1972 | 2018-09-12 05:08 | 43355.2139 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 3 | N | -3 | TRIPPED DUE TO LIGHTNING AS FLASHOVER MARKS OBSERVED IN R-PH & B-PH JUMPER AT LOC 807
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-12 05:08 | 43355.2139 | 2018-09-12 07:59 | 43355.3326 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 51 | N/A | N/A | N/A | LINE KEPT OPEN POST TRIPPING ON 12.9.18 AT 0444HRS, AS DIRECTED BY NERLDC DUE TO SYSTEM CONSTRAINTS
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-13 00:38 | 43356.0264 | 2018-09-13 14:38 | 43356.6097 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | N/A | N/A | N/A | LINE H/T VIDE CODE 3535
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-13 21:04 | 43356.8778 | 2018-09-13 21:23 | 43356.891 | -- | -- | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LINE TRIPPED ONLY AT BALIPARA EN WHILE FSC AT BALIPARA
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-15 11:43 | 43358.4882 | 2018-09-15 18:37 | 43358.7757 | -- | -- | -- | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0 | N/A | N/A | N/A | TREES CAME IN PROXIMITY TO Y-PH AT LOC 431-432 FROM OUTSIDE CORRIDOR
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-15 19:05 | 43358.7951 | 2018-09-15 19:22 | 43358.8069 | -- | -- | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO FSC CAPACITOR CURRENT UNBALANCE AT BALIPARA
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-16 00:44 | 43359.0306 | 2018-09-16 18:08 | 43359.7556 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | N/A | N/A | N/A | LINE H/T VIDE CODE 3592
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-17 23:46 | 43360.9903 | 2018-09-18 10:08 | 43361.4222 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22 | N/A | N/A | N/A | LINE H/T VIDE CODE 3616
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-19 22:00 | 43362.9167 | 2018-09-20 17:45 | 43363.7396 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 45 | N/A | N/A | N/A | LINE H/T VIDE CODE 3682
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-20 23:56 | 43363.9972 | 2018-09-21 17:49 | 43364.7424 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 53 | N/A | N/A | N/A | LINE H/T VIDE CODE 3715
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-21 22:58 | 43364.9569 | 2018-09-22 09:18 | 43365.3875 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | N/A | N/A | N/A | LINE H/T VIDE CODE 3745
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-22 09:18 | 43365.3875 | 2018-09-22 10:01 | 43365.4174 | -- | -- | -- | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN FOR AMP OF REACTOR
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-24 01:26 | 43367.0597 | 2018-09-24 17:38 | 43367.7347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 3797
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region | Insulator flash over mark | 2018-09-25 03:30 | 43368.1458 | 2018-09-25 03:53 | 43368.1618 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 2 | N | -2 | FLASHOVER MARKS DUE TO LIGHTNING FOUND IN Y-PH INSULATORS AT LOC 763
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region | Insulator flash over mark | 2018-09-25 20:56 | 43368.8722 | 2018-09-25 21:02 | 43368.8764 | -- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 2 | N | -2 | .TRIPPED DUE TO LIGHTNING AROUND BONGAIGAON REGION. TRIPPED DUE TO LIGHTNING FOUND IN Y-PH INSULATOR AT LOC 665
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-26 02:36 | 43369.1083 | 2018-09-26 14:22 | 43369.5986 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 46 | N/A | N/A | N/A | LINE H/T VIDE CODE 3839.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-27 23:14 | 43370.9681 | 2018-09-28 10:58 | 43371.4569 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1144 | 0 | N/A | N/A | N/A | LINE H/T VIDE CODE 3908.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-28 22:01 | 43371.9174 | 2018-09-28 23:14 | 43371.9681 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 3937.
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region | Flash over mark in Arching horn | 2018-09-29 22:55 | 43372.9549 | 2018-09-29 23:16 | 43372.9694 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO LIGHTNING AS FLASHOVERMARKS OBSERVED IN LOC 562 B-PH ARCING HORN
NER L414 | BALIPARA-BONGAIGAON | #4 | 309 | North Eastern Region |  | 2018-09-30 23:22 | 43373.9736 | 2018-09-30 23:59 | 43373.9993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | N/A | N/A | N/A | LINE H/T VIDE CODE 4010.
[6 empty] | Sub Total --> | [6 empty] | 1 | 19 | 0 | 0 | 8 | 8 | 1304 | 36
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-09-08 08:06 | 43351.3375 | 2018-09-08 18:25 | 43351.7674 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19 | N/A | N/A | N/A | SD TAKEN FOR REPLACMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER PROJECT NERIV
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-09-09 08:29 | 43352.3535 | 2018-09-09 17:51 | 43352.7438 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 22 | N/A | N/A | N/A | SD TAKEN FOR REPLACMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER NERSS IV PROJEC
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-09-11 15:14 | 43354.6347 | 2018-09-11 16:39 | 43354.6937 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 25 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER NERSS IV
NER L415 | SILCHAR-IMPHAL | #1 | 167 | North Eastern Region |  | 2018-09-28 08:31 | 43371.3549 | 2018-09-28 15:50 | 43371.6597 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 19 | N/A | N/A | N/A | S/D TAKEN FOR CONSTRUCTION RELATED WORK AT IMPHAL SS.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 25
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-09-08 08:07 | 43351.3382 | 2018-09-08 18:21 | 43351.7646 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER PROJECT NERSIV
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-09-09 08:29 | 43352.3535 | 2018-09-09 17:57 | 43352.7479 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 28 | N/A | N/A | N/A | SD TAKEN FOR REPLACMENT OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER NERSSIV
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-09-11 15:14 | 43354.6347 | 2018-09-11 16:39 | 43354.6937 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 25 | N/A | N/A | N/A | SD TAKEN FOR REPLACEMNET OF EXISTING MAIN BUS CONDUCTOR BY TWIN ZEBRA CONDUCTOR UNDER NERSS IV
NER L416 | SILCHAR-IMPHAL | #2 | 167 | North Eastern Region |  | 2018-09-29 08:36 | 43372.3583 | 2018-09-29 15:37 | 43372.6507 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1 | N/A | N/A | N/A | S/D TAKEN FOR CONSTRUCTION RELATED WORK AT IMPHAL.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-09-02 06:10 | 43345.2569 | 2018-09-02 18:28 | 43345.7694 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | N/A | N/A | N/A | LINE H/T VIDE CODE 2392
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-09-21 05:54 | 43364.2458 | 2018-09-21 11:07 | 43364.4632 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13 | N/A | N/A | N/A | LINE H/T VIDE CODE 3718
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-09-22 05:05 | 43365.2118 | 2018-09-22 17:47 | 43365.741 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 42 | N/A | N/A | N/A | LINE H/T VIDE CODE 3747
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-09-23 05:34 | 43366.2319 | 2018-09-23 18:00 | 43366.75 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | N/A | N/A | N/A | LINE H/T VIDE CODE 3785
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-09-25 00:57 | 43368.0396 | 2018-09-26 15:36 | 43369.65 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 39 | N/A | N/A | N/A | LINE H/T VIDE CODE 3819.
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-09-27 04:59 | 43370.2076 | 2018-09-27 15:26 | 43370.6431 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27 | N/A | N/A | N/A | LINE H/T VIDE CODE 3870.
NER L417 | BALIPARA_B.CHAIRALI | #3 | 57.294 | North Eastern Region |  | 2018-09-30 02:21 | 43373.0979 | 2018-09-30 17:58 | 43373.7486 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | N/A | N/A | N/A | LINE H/T VIDE CODE 3991.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 2
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-09-17 08:31 | 43360.3549 | 2018-09-17 18:20 | 43360.7639 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 49 | N/A | N/A | N/A | LINE H/T VIDE CODE 3606
NER L418 | BALIPARA_B.CHAIRALI | #4 | 57.294 | North Eastern Region |  | 2018-09-19 05:21 | 43362.2229 | 2018-09-19 17:33 | 43362.7312 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | N/A | N/A | N/A | LINE H/T VIDE CODE 3649
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-09-04 23:23 | 43347.9743 | 2018-09-05 13:02 | 43348.5431 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 39 | N/A | N/A | N/A | LINE H/T VIE CODE 3360
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-09-05 23:18 | 43348.9708 | 2018-09-06 16:33 | 43349.6896 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | N/A | N/A | N/A | LINE H/T VIDE CODE 3382
NER L419 | B.CHAIRALI_RANGANADI | #1 | 129.335 | North Eastern Region |  | 2018-09-30 02:02 | 43373.0847 | 2018-09-30 15:02 | 43373.6264 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | N/A | N/A | N/A | LINE H/T VIDE CODE 3990.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 54
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-09-08 06:09 | 43351.2562 | 2018-09-08 07:33 | 43351.3146 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 24 | N/A | N/A | N/A | LINE H/T VIDE CODE 3443
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-09-09 00:35 | 43352.0243 | 2018-09-09 09:10 | 43352.3819 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 35 | N/A | N/A | N/A | LINE H/T VIDE CODE 3461
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-09-10 01:29 | 43353.0618 | 2018-09-10 06:52 | 43353.2861 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23 | N/A | N/A | N/A | LINE H/T VIDE CODE 3476
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-09-18 10:53 | 43361.4535 | 2018-09-18 16:13 | 43361.6757 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | N/A | N/A | N/A | LINE H.T VIDE CODE 3625
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-09-21 05:36 | 43364.2333 | 2018-09-21 09:31 | 43364.3965 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | N/A | N/A | N/A | LINE H/T VIDE CODE 3717
NER L420 | B.CHAIRALI_RANGANADI | #2 | 129.335 | North Eastern Region |  | 2018-09-22 03:44 | 43365.1556 | 2018-09-22 14:42 | 43365.6125 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58 | N/A | N/A | N/A | LINE H/T VIDE CODE 3746
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-09-13 00:28 | 43356.0194 | 2018-09-13 09:32 | 43356.3972 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | N/A | N/A | N/A | LINE H/T VIDE CODE 3534
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-09-13 09:32 | 43356.3972 | 2018-09-15 10:45 | 43358.4479 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 13 | N/A | N/A | N/A | CONTINUOUS SD AVAILED FOR REPLACEMENT OF OLD ISOLATOR WITH NEW ONES AT BALIPARA END
NER L421 | BALIPARA_B.CHAIRALI | #1 | 59.54 | North Eastern Region |  | 2018-09-16 10:13 | 43359.4257 | 2018-09-16 17:19 | 43359.7215 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | N/A | N/A | N/A | SD AVAILED FOR REPLACMENT OF OLD ISOLATOR WITH NEW ONE AT BALIPARA END
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region |  | 2018-09-07 08:29 | 43350.3535 | 2018-09-10 18:46 | 43353.7819 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 17 | N/A | N/A | N/A | C/S/D TAKEN FOR REPLACMENT OF OLD LINE ISOALTORS EITH NEW ISOLATORS
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region |  | 2018-09-11 06:02 | 43354.2514 | 2018-09-11 15:54 | 43354.6625 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 52 | N/A | N/A | N/A | lien h/t vide code 3491
NER L422 | BALIPARA_B.CHAIRALI | #2 | 59.54 | North Eastern Region |  | 2018-09-18 09:52 | 43361.4111 | 2018-09-18 17:24 | 43361.725 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 32 | N/A | N/A | N/A | SD AVAILED FOR REPALCEMENT OF OLD ISOLATOR WITH NEW ONES AT BALIPARA END
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 41
NER L423 | SILCHAR-PURBAKANCHANBARI | #1 | 127.2 | North Eastern Region |  | 2018-09-22 09:17 | 43365.3868 | 2018-09-22 18:10 | 43365.7569 | -- | -- | -- | 0 | 0 | 8 | 53 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY PKBARI
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 8 | 53 | 0 | 0 | 0 | 0
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-09-15 12:33 | 43358.5229 | 2018-09-15 15:37 | 43358.6507 | -- | -- | -- | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN TO RECTIFY DEFECT IN CC RING, JUMPER DUE TO SPARKING AT LOC 9 & LOC 164
NER L424 | SILCHAR-PURBAKANCHANBARI | #2 | 127.2 | North Eastern Region |  | 2018-09-22 09:17 | 43365.3868 | 2018-09-22 18:10 | 43365.7569 | -- | -- | -- | 0 | 0 | 8 | 53 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | BUS S/D TAKEN BY PKBARI
[6 empty] | Sub Total --> | [6 empty] | 3 | 4 | 8 | 53 | 0 | 0 | 0 | 0
NER RBR1 | BR_BONGAIGAON (50MVAR) | # 1 | 50 | North Eastern Region |  | 2018-09-12 10:20 | 43355.4306 | 2018-09-12 10:43 | 43355.4465 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON BUCCHOLZ RELAY OPERATION DUE TO EARTHQUAKE IN NER
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-09-05 18:14 | 43348.7597 | 2018-09-06 06:03 | 43349.2521 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 49 | N/A | N/A | N/A | REACTOR H/T VIE CODE 3380
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-09-12 11:06 | 43355.4625 | 2018-09-12 16:52 | 43355.7028 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46 | N/A | N/A | N/A | SD TAKEN FOR CSD COMMISIONING WORKS
NER RBR2 | BR_BONGAIGAON (50MVAR) | # 2 | 50 | North Eastern Region |  | 2018-09-15 18:03 | 43358.7521 | 2018-09-15 21:18 | 43358.8875 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 15 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3585
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 50
NER RBR3 | BR_BALIPARA (50MVAR) | #1 | 50 | North Eastern Region |  | 2018-09-28 23:41 | 43371.9868 | 2018-09-29 11:44 | 43372.4889 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3 | N/A | N/A | N/A | B/R H/T VIDE CODE 3942.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region |  | 2018-09-25 09:42 | 43368.4042 | 2018-09-25 17:45 | 43368.7396 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3 | N/A | N/A | N/A | S/D TAKEN FOR TESTING OF B/R AS PER GUIDELINES ON COMPLETION OF 25 YEARS OF SERVICE.
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region |  | 2018-09-26 09:58 | 43369.4153 | 2018-09-26 17:20 | 43369.7222 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 22 | N/A | N/A | N/A | S/D TAKEN FOR TESTING OF B/R AS PER GUIDELINES ON COMPLETION OF 25 YEARS OF SERVICE.
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region |  | 2018-09-29 01:06 | 43372.0458 | 2018-09-29 08:22 | 43372.3486 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | N/A | N/A | N/A | B/R H/T VIDE CODE 3949.
NER RBR4 | BR_MISA (50MVAR) |  | 50 | North Eastern Region |  | 2018-09-29 10:12 | 43372.425 | 2018-09-29 11:44 | 43372.4889 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 32 | N/A | N/A | N/A | B/R H/T VIDE CODE 3962.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 13
NER RBR5 | BR_KUMARGHAT (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR6 | BR_AIZWAL (20MVAR) |  | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-01 00:16 | 43344.0111 | 2018-09-01 03:59 | 43344.166 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 43 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3170.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-01 00:16 | 43344.0111 | 2018-09-01 03:59 | 43344.166 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 43 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3170
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-02 20:17 | 43345.8451 | 2018-09-03 03:36 | 43346.15 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 19 | N/A | N/A | N/A | B/R H/T VIDE CODE 3308
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-03 18:23 | 43346.766 | 2018-09-04 01:00 | 43347.0417 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 37 | N/A | N/A | N/A | REACTOR H.T VIDE CODE 3329
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-05 18:10 | 43348.7569 | 2018-09-05 23:30 | 43348.9792 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3378
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-07 18:31 | 43350.7715 | 2018-09-07 22:45 | 43350.9479 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 14 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3431
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-11 18:13 | 43354.759 | 2018-09-11 23:51 | 43354.9938 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3510
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-15 17:40 | 43358.7361 | 2018-09-15 21:23 | 43358.891 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 43 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3583
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-22 18:16 | 43365.7611 | 2018-09-22 22:05 | 43365.9201 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 49 | N/A | N/A | N/A | B/R H/T VIDE CODE 3778
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-26 18:19 | 43369.7632 | 2018-09-26 21:59 | 43369.916 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | N/A | N/A | N/A | B/R H/T VIDE CODE 3862.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-27 15:45 | 43370.6562 | 2018-09-27 16:34 | 43370.6903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | N/A | N/A | N/A | B/R H/T VIDE CODE 3895.
NER RBR7 | BR_BONGAIGAON(80MVAR) | #3 | 80 | North Eastern Region |  | 2018-09-28 23:41 | 43371.9868 | 2018-09-29 12:32 | 43372.5222 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 51 | N/A | N/A | N/A | B/R H/T VIDE CODE 3943.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 26
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-09-27 15:45 | 43370.6562 | 2018-09-27 16:20 | 43370.6806 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | N/A | N/A | N/A | B/R H/T VIDE CODE 3896.
NER RBR8 | BR_BALIPARA(80MVAR) | #2 | 80 |  |  | 2018-09-28 23:21 | 43371.9729 | 2018-09-29 08:08 | 43372.3389 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 47 | N/A | N/A | N/A | B/R H/T VIDE CODE 3940.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 22
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-01 | 43344 | 2018-09-02 04:11 | 43345.1743 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 11 | N/A | N/A | N/A | B/R H/T VIDE CODE 3165
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-03 18:13 | 43346.759 | 2018-09-03 23:51 | 43346.9938 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3328
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-04 17:55 | 43347.7465 | 2018-09-05 00:06 | 43348.0042 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 11 | N/A | N/A | N/A | REACTOR H/T VIE CODE 3353
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-05 18:05 | 43348.7535 | 2018-09-05 23:29 | 43348.9785 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3376
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-06 18:12 | 43349.7583 | 2018-09-06 22:23 | 43349.9326 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 11 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3409
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-07 18:28 | 43350.7694 | 2018-09-07 22:26 | 43350.9347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 58 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3432
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-09 18:24 | 43352.7667 | 2018-09-10 05:02 | 43353.2097 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3474
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-10 18:42 | 43353.7792 | 2018-09-10 22:37 | 43353.9424 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3487
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-11 18:16 | 43354.7611 | 2018-09-11 23:40 | 43354.9861 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3511
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-14 18:14 | 43357.7597 | 2018-09-14 22:38 | 43357.9431 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 24 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3563
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-18 18:22 | 43361.7653 | 2018-09-18 22:30 | 43361.9375 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | N/A | N/A | N/A | REACOT B/R H/T VIE CODE 3640
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-22 18:21 | 43365.7646 | 2018-09-22 22:35 | 43365.941 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 14 | N/A | N/A | N/A | B/R H/T VIDE CODE 3779
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-23 18:06 | 43366.7542 | 2018-09-23 22:00 | 43366.9167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 54 | N/A | N/A | N/A | B/R H/T VIDE CODE 3791
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-24 17:41 | 43367.7368 | 2018-09-26 23:27 | 43369.9771 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 46 | N/A | N/A | N/A | B/R H/T VIDE CODE 3813.
NER RBR9 | BR_SILCHAR(63MVAR) | #1 | 63 | North Eastern Region |  | 2018-09-29 10:22 | 43372.4319 | 2018-09-30 21:22 | 43373.8903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | N/A | N/A | N/A | B/R H/T VIDE CODE 3963.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 56
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-09-04 17:57 | 43347.7479 | 2018-09-05 00:08 | 43348.0056 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 11 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3354
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-09-06 18:12 | 43349.7583 | 2018-09-06 22:24 | 43349.9333 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 12 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3410
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-09-07 18:28 | 43350.7694 | 2018-09-07 22:26 | 43350.9347 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 58 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3433
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-09-23 18:24 | 43366.7667 | 2018-09-23 22:04 | 43366.9194 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | N/A | N/A | N/A | B/R H/T VIDE CODE 3792
NER RBR10 | BR_SILCHAR(63MVAR) | #2 | 63 | North Eastern Region |  | 2018-09-27 18:14 | 43370.7597 | 2018-09-27 23:10 | 43370.9653 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 56 | N/A | N/A | N/A | B/R H/T VIDE CODE 3904.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 57
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-01 00:07 | 43344.0049 | 2018-09-01 04:01 | 43344.1674 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 54 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3169
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-02 19:46 | 43345.8236 | 2018-09-03 04:31 | 43346.1882 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 45 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3307
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-03 15:01 | 43346.6257 | 2018-09-04 01:14 | 43347.0514 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13 | N/A | N/A | N/A | REACTOER H/T VIDE CODE 3322
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-04 12:48 | 43347.5333 | 2018-09-05 00:04 | 43348.0028 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3342
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-05 11:50 | 43348.4931 | 2018-09-06 05:07 | 43349.2132 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3370
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-06 14:16 | 43349.5944 | 2018-09-06 15:07 | 43349.6299 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | N/A | N/A | N/A | REACOT H/T VIDE CODE 3398
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-06 18:20 | 43349.7639 | 2018-09-07 00:01 | 43350.0007 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3411
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-07 14:42 | 43350.6125 | 2018-09-07 22:45 | 43350.9479 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3423
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-10 18:42 | 43353.7792 | 2018-09-10 22:34 | 43353.9403 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 52 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3486
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-11 17:52 | 43354.7444 | 2018-09-12 00:41 | 43355.0285 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 49 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3508
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-13 18:21 | 43356.7646 | 2018-09-13 22:27 | 43356.9354 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3546
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-14 18:25 | 43357.7674 | 2018-09-14 21:50 | 43357.9097 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 25 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3564
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-15 16:47 | 43358.6993 | 2018-09-15 22:00 | 43358.9167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3581
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-18 18:21 | 43361.7646 | 2018-09-18 22:29 | 43361.9368 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3641
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-20 17:46 | 43363.7403 | 2018-09-21 23:53 | 43364.9951 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7 | N/A | N/A | N/A | B/R H/T VIDE CODE 3712
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-22 18:16 | 43365.7611 | 2018-09-22 22:34 | 43365.9403 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 18 | N/A | N/A | N/A | B/R H/T VIDE CODE 3777
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-26 17:53 | 43369.7451 | 2018-09-26 23:16 | 43369.9694 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23 | N/A | N/A | N/A | B/R H/T VIDE CODE 3861.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-27 15:33 | 43370.6479 | 2018-09-27 16:34 | 43370.6903 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | N/A | N/A | N/A | B/R H/T VIDE CODE 3893.
NER RBR11 | BR_BONGAIGAON(80MVAR) | #4 | 80 | North Eastern Region |  | 2018-09-28 23:20 | 43371.9722 | 2018-09-29 12:32 | 43372.5222 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 12 | N/A | N/A | N/A | B/R H/T VIDE CODE 3941.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 34
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-09-28 16:38 | 43371.6931 | 2018-09-28 17:05 | 43371.7118 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | N/A | N/A | N/A | B/R H/T VIDE CODE 3928.
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-09-28 23:48 | 43371.9917 | 2018-09-29 01:30 | 43372.0625 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 42 | N/A | N/A | N/A | B/R H/T VIDE CODE 3944.
NER RBR12 | BR_B'CHARIALI(80MVAR) | #1 | 80 | North Eastern Region |  | 2018-09-29 09:47 | 43372.4076 | 2018-09-29 11:07 | 43372.4632 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | N/A | N/A | N/A | B/R H/T VIDE CODE 3960.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 29
NER RBR13 | BR_B'CHARIALI(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-09-28 23:48 | 43371.9917 | 2018-09-29 01:31 | 43372.0632 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 43 | N/A | N/A | N/A | B/R H/T VIDE CODE 3945.
NER RBR13 | BR_B'CHARIALI(80MVAR) | #2 | 80 | North Eastern Region |  | 2018-09-29 10:03 | 43372.4187 | 2018-09-29 11:44 | 43372.4889 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 41 | N/A | N/A | N/A | B/R H/T VIDE CODE 3961.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 24
NER RBR14 | BR_B'CHARIALI(63MVAR) | #3 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR15 | BR_B'CHARIALI(63MVAR) | #4 | 63 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR16 | BR_New_MARIANI(20MVAR) | #1 | 20 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER RBR17 | BR_BALIPARA(125MVAR) | #3 | 125 | North Eastern Region |  | 2018-09-29 00:11 | 43372.0076 | 2018-09-29 12:14 | 43372.5097 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3 | N/A | N/A | N/A | B/R H/T VIDE CODE 3946.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region |  | 2018-09-03 18:38 | 43346.7764 | 2018-09-04 00:46 | 43347.0319 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 8 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3330
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region |  | 2018-09-04 18:31 | 43347.7715 | 2018-09-06 17:12 | 43349.7167 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 41 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3355
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region |  | 2018-09-07 18:06 | 43350.7542 | 2018-09-07 23:28 | 43350.9778 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | N/A | N/A | N/A | REACTOR H/T VIDE CODE 3430
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region |  | 2018-09-09 19:11 | 43352.7993 | 2018-09-10 05:07 | 43353.2132 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 56 | N/A | N/A | N/A | REACTOR VIDE CODE 3475
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region |  | 2018-09-12 16:32 | 43355.6889 | 2018-09-12 21:47 | 43355.9076 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15 | N/A | N/A | N/A | SD TAKEN FOR CSD COMMISSIONING
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region |  | 2018-09-21 17:52 | 43364.7444 | 2018-09-22 12:45 | 43365.5312 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 53 | N/A | N/A | N/A | B/R H/T VIDE CODE 3738
NER RBR18 | BR_BONGAIGAON(125MVAR) | #5 | 125 | North Eastern Region |  | 2018-09-29 00:25 | 43372.0174 | 2018-09-29 12:30 | 43372.5208 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 5 | N/A | N/A | N/A | B/R H/T VIDE CODE 3948.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 20
NER RBR19 | BR_ROING(20MVAR) | #1 | 20 | North Eastern Region |  | 2018-09-01 00:01 | 43344.0007 | 2018-09-30 23:59 | 43373.9993 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 719 | 58 | N/A | N/A | N/A | S/D TAKEN FOR OFFLINE DRYING OUT. |  | 100
| BR_ROING(20MVAR) | #1 |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 719 | 58
NER TICT1 | ICT_BONGAIGAON(315MVA) |  | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT2 | ICT_BALIPARA (315MVA) | #1 | 315 | North Eastern Region |  | 2018-09-11 05:41 | 43354.2368 | 2018-09-11 07:57 | 43354.3313 | -- | -- | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | TRIPPED ON 3-PHASE DIFFERENTIAL FAULT. PROBABLE FAULT DUE TO MONKEY
NER TICT2 | ICT_BALIPARA (315MVA) | #1 | 315 | North Eastern Region |  | 2018-09-19 10:35 | 43362.441 | 2018-09-19 13:54 | 43362.5792 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 19 | N/A | N/A | N/A | SD TAKEN FOR CHANGE OVER OF ICT BANK UNIT & TESTING OF TURRENT CTs
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 2 | 16 | 0 | 0 | 3 | 19
NER TICT3 | ICT_BALIPARA (315MVA) | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT4 | ICT_MISA | #1 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT5 | ICT_MISA | #2 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT6 | ICT_SILCHAR (200MVA) | #1 | 315 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT7 | ICT_B'CHARIALI (200MVA) | #1 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT8 | ICT_B'CHARIALI (200MVA) | #2 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT9 | ICT_IMPHAL(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT10 | ICT_IMPHAL(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT11 | ICT_SALAKATI (50 MVA) | # 2 | 50 | North Eastern Region |  | 2018-09-12 10:22 | 43355.4319 | 2018-09-12 10:50 | 43355.4514 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | N/A | N/A | N/A | TRIPPED DUE TO BUCCHOLZ RELAY OEPRATION DUE TO EARTHQUAKE
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0
NER TICT12 | ICT_DIMAPUR (100 MVA) | # 1 | 100 | North Eastern Region
Sub Total -->
NER TICT13 | ICT_DIMAPUR (100 MVA) | #2 | 100 | North Eastern Region |  | 2018-09-10 08:50 | 43353.3681 | 2018-09-10 09:53 | 43353.4118 | -- | -- | -- | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | SD TAKEN FOR CT TAN DELTA TESTING, CB TIMING & DCRM, XR BUSHING TAN DELTA TESTING.
[6 empty] | Sub Total --> | [6 empty] | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT14 | ICT_SILCHAR(200MVA) | #2 | 200 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region |  | 2018-09-20 09:17 | 43363.3868 | 2018-09-20 16:13 | 43363.6757 | -- | -- | -- | 6 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR HEAVY SPARK IN ISOLATOR MARSHALLING BOX
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region |  | 2018-09-21 09:30 | 43364.3958 | 2018-09-21 16:27 | 43364.6854 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 57 | N/A | N/A | N/A | E/S/D TAKEN FOR EXTERNAL BUS DUCT ASSOCIATED WITH NERSS VII AT MOKOKCHUNG
NER TICT15 | ICT_MOKOKCHUNG(30MVA) | #1 | 30 | North Eastern Region |  | 2018-09-22 10:10 | 43365.4236 | 2018-09-22 17:44 | 43365.7389 | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 34 | N/A | N/A | N/A | ESD TAKEN SINCE SPARKING OBSERVED BETWN ICT-I CONDUCTOR & SCAFFOLDING/STAGING SET UP FOR ERECTION
[6 empty] | Sub Total --> | [6 empty] | 6 | 56 | 0 | 0 | 0 | 0 | 14 | 31
NER TICT16 | ICT_MOKOKCHUNG(30MVA) | #2 | 30 | North Eastern Region |  | 2018-09-28 09:15 | 43371.3854 | 2018-09-28 09:35 | 43371.3993 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | N/A | N/A | N/A | HAND TRIPPED ON EMERGENCY TO ALLOW CONSTRUCTION WORKS.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20
NER TICT17 | ICT_NIRJULI(50MVA) | #1 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT18 | ICT_NIRJULI(50MVA) | #2 | 50 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT19 | ICT_ZIRO (15MVA) |  | 15 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT20 | ICT_KOPILI (160 MVA) | # 2 | 160 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT21 | ICT_KUMARGHAT(5MVA) |  | 5 | North Eastern Region | [21 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NER TICT22 | ICT_SILCHAR(315MVA) | #3 | 315 | North Eastern Region |  | 2018-09-21 09:30 | 43364.3958 | 2018-09-21 14:20 | 43364.5972 | -- | -- | -- | 4 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | E/S/D TAKEN FOR CHECKING ABNORMAL SOUND
[6 empty] | Sub Total --> | [6 empty] | 4 | 50 | 0 | 0 | 0 | 0 | 0 | 0