## APRIL
PERIOD: April -16 to September - 16 | [21 empty] | ANNEXURE-A
S/No | Unique ID of Transmission Element | Element Name | Description (Length-km/Nos./MVA/ MVAr/MW/ etc. | Region | Type of failure | Outage Date & Time Hr Mn | Restoration Date & Time Hr Mn | Details of outage ( No. of Towers damaged, no. of insulators failed etc.) | Total Outage (in Days) (1) | Duration of Outage attribuatable to | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual & Norm (1 - 2) | Detailed Reason for Outage (3) | Outage certifying Agency & Reference Document | % Availability as certified by certifying agency
[10 empty] | ISTS Licensee Hr Min |  | Others Hr Min |  | System Constraint/ Natural calamity/ Milliitancy Hr Min |  | Deemed Available Hr Min
APRIL' 2016 | [21 empty] | NERPC
1 | NER L101 | RCN_AGARTALA 1 | 8.384 | North Eastern Region | --- | 2016-04-04 21:04 | 2016-04-04 21:55 | as given in (3) | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | NA | NA | NA | BEYOND JURISDICTION. TRIP DUE TO DOWNSTREAM FAULT |  | 100
[5 empty] | --- | 2016-04-29 10:30 | 2016-04-29 13:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 56 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARING TREE BRANCHES LEANING TOWARDS LINE AT LOC 29 DUE TO HEAVY THUNDERSTORM
2 | NER L102 | RCN_AGARTALA 2 | 8.384 | North Eastern Region | --- | 2016-04-04 21:04 | 2016-04-04 21:30 | as given in (3) | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | BEYOND JURISDICTION.TRIP DUE TO DOWNSTREAM FAULT |  | 100
3 | NER L103 | BADARPUR_KOLASIB | 107.226 | North Eastern Region | --- | 2016-04-21 16:30 | 2016-04-21 18:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 48 | 0 | 0 | NA | NA | NA | TREE BRANCHES CAME NEAR Y PH BETWEEN LOC 344-345 CAUSED BY WIND |  | 100
[5 empty] | --- | 2016-04-29 11:18 | 2016-04-29 12:09 | as given in (3) | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | NA | NA | NA | CURRENT INFEED FROM PANCHGRAM(BDP-PANCHGRAM LINE WAS UNDER S/D) BUSBAR PROTECTION OPTD AT BDP.
[5 empty] | --- | 2016-04-21 13:24 | 2016-04-21 13:41 | as given in (3) | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.SAME TIME KOLASIB-BHAIRABI TRIPPED
[5 empty] | --- | 2016-04-22 15:36 | 2016-04-22 16:03 | as given in (3) | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
[5 empty] | --- | 2016-04-16 00:42 | 2016-04-16 00:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
[5 empty] | --- | 2016-04-17 10:20 | 2016-04-17 11:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | NA | NA | NA | PATROL IN PROGRESS
[5 empty] | --- | 2016-04-17 23:28 | 2016-04-17 23:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | HEAVY LIGHTENING AND THUNDERSTORM PREVAILING IN AREA
[5 empty] | --- | 2016-04-20 15:02 | 2016-04-20 17:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 28 | 0 | 0 | NA | NA | NA
[5 empty] | --- | 2016-04-21 12:37 | 2016-04-21 13:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | NA | NA | NA | TREE BRANCHES COME NEAR Y PH BETWEEN LOC 344-345 CAUSED BY WIND
4 | NER L104 | AIZWAL_KUMARGHAT | 131 | North Eastern Region | --- | 2016-04-04 07:14 | 2016-04-04 07:46 | as given in (3) | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | NA | NA | NA | NON ISOLATION OF DOWNSTREAM FAULT IN AZL-ZEMBWK BY CB AT AZL(STATE OWNED) LED TO REFLECTION OF FAULT |  | 100
5 | NER L105 | AIZWAL_ZEMEBAK 2 | 6.719 | North Eastern Region | --- | 2016-04-04 09:10 | 2016-04-04 17:10 | as given in (3) | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE END |  | 100
[5 empty] | --- | 2016-04-05 09:23 | 2016-04-05 16:13 | as given in (3) | 0 | 0 | 0 | 6 | 50 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE END
[5 empty] | --- | 2016-04-05 20:27 | 2016-04-05 20:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM & LIGHTNING
[5 empty] | --- | 2016-04-05 21:24 | 2016-04-05 22:03 | as given in (3) | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | NA | NA | NA | REPORTED HEAVY THUNDERSTORM & LIGHTNING
[5 empty] | --- | 2016-04-05 22:26 | 2016-04-05 23:02 | as given in (3) | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM AND LIGHTNING (DO0WNSTREAM FAULT 33 kV cable FAULT AT STATE END)
[5 empty] | --- | 2016-04-12 21:54 | 2016-04-12 22:17 | as given in (3) | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault
[5 empty] | --- | 2016-04-16 05:28 | 2016-04-16 05:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
[5 empty] | --- | 2016-04-25 12:21 | 2016-04-25 12:32 | as given in (3) | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT
6 | NER L106 | BADARPUR-BADARPUR | 1.023 | North Eastern Region | --- | 2016-04-21 13:47 | 2016-04-21 18:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 45 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING AT BADARPUR |  | 100
[5 empty] | --- | 2016-04-13 23:35 | 2016-04-14 00:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | NA | NA | NA | HEAVY CYCLONE REPORTED AT BADARPUR
[5 empty] | --- | 2016-04-18 10:49 | 2016-04-18 15:19 | as given in (3) | 0 | 0 | 0 | 4 | 30 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS E/S/D TAKEN BY STATE
[5 empty] | --- | 2016-05-28 19:50 | 2016-05-29 01:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 0 | 0 | NA | NA | NA | Wave trap dropper at BDP(state) opened
[5 empty] | --- | 2016-04-29 00:39 | 2016-04-29 16:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 15 | 31 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO OPENING OF WAVE TRAP DROPPER AT BADARPUR STATE END. HEAVY THUNDERSTORM REPORTED
[5 empty] | --- | 2016-04-14 01:58 | 2016-04-14 13:51 | as given in (3) | 0 | 0 | 0 | 11 | 53 | 0 | 0 | 0 | 0 | NA | NA | NA | LINE OPENED DUE TO Y-PH CT JUMPER OPENED AT STATE END
7 | NER L107 | BADARPUR_JIRIBAM | 67.21 | North Eastern Region | --- | 2016-04-15 00:45 | 2016-04-15 01:12 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | HEAVY RAIN AND STORM |  | 100
[5 empty] | --- | 2016-04-29 11:18 | 2016-04-29 12:08 | as given in (3) | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | NA | NA | NA | CURRENT INFEED FROM PANCHGRAM STATE END.(BDP-PANCHGRAM WAS UNDER S/D) BUSBAR PROTECTION OPTD AT BDP
8 | NER L108 | BADARPUR_KHLIERIAT | 76.646 | North Eastern Region | --- | 2016-04-01 | 2016-04-01 16:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 0 | 0 | NA | NA | NA | Big tree fell from outside corridor on Y-B ph conductor at loc 155-156 |  | 100
[5 empty] | --- | 2016-04-13 23:35 | 2016-04-14 00:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | NA | NA | NA | HEAVY CYCLONE REPORTED AT BADARPUR
[5 empty] | --- | 2016-04-18 18:42 | 2016-04-18 18:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
[5 empty] | --- | 2016-04-19 02:12 | 2016-04-19 02:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | THUNDERSTORM PREVAILED IN THE AREA
[5 empty] | --- | 2016-04-23 17:48 | 2016-04-23 18:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | NA | NA | NA | Tripped due to Heavy thunderstorm.
[5 empty] | --- | 2016-04-27 11:02 | 2016-04-27 14:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 3 | 29 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR REPLACEMENT OF INSULATOR(DAMAGED DUE TO LIGHTNING) AT LOC 108 R-PH
9 | NER L109 | BADARPUR_KUMARGHAT | 118.513 | North Eastern Region | --- | 2016-04-19 19:37 | 2016-04-19 19:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | Tripped due to heavy lightening. |  | 98.41
[5 empty] | --- | 2016-04-29 11:18 | 2016-04-29 12:10 | as given in (3) | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | NA | NA | NA | CURRENT INFEED FROM PANCHGRAM END.(BDP-PANCHGRAM WAS UNDER S/D)BUSBAR PROTECTIOJNH OPTD AT BDP
[5 empty] | --- | 2016-04-07 04:19 | 2016-04-07 18:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 0 | 0 | NA | NA | NA | Tree fallen between loc 60-61 due to heavy storm
[5 empty] | conductor snapped | 2016-04-16 19:12 | 2016-04-17 17:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | NA | NA | NA | B-PH CONDUCTOR SNAP FOUND AT LOC 225-226 DUE TO FALLING OF TREE DURING THUNDERSTORM
[5 empty] | --- | 2016-04-13 07:19 | 2016-04-13 17:43 | as given in (3) | 0 | 10 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D FOR AMP WORKS
[5 empty] | --- | 2016-04-02 10:35 | 2016-04-02 11:36 | as given in (3) | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D FOR RECTIFICATION OF Y PH CVT AND ATTENDING HOTSPOTS
10 | NER L110 | DIMAPUR_IMPHAL | 168.865 | North Eastern Region | --- | 2016-04-02 08:43 | 2016-04-02 11:27 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 44 | NA | NA | NA | CONTINUOUS S/D FOR STRINGING OF OPGW AND CONDUCTORS.S/D RETURNED DUE TO INCLEMENT WEATHER |  | 100
[5 empty] | --- | 2016-04-03 08:06 | 2016-04-07 16:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 26 | NA | NA | NA | CONTINUOUS S/D FOR STRINGING OF OPGW & CONDUCTOR
[5 empty] | insulator damaged | 2016-04-19 06:16 | 2016-04-19 12:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 6 | 38 | 0 | 0 | NA | NA | NA | Insulator damaged due to lightening at Loc.No.112.
11 | NER L111 | DOYANG_DIMAPUR 1 | 92.526 | North Eastern Region | --- | 2016-04-18 19:36 | 2016-04-18 20:12 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | NA | NA | NA |  |  | 100
[5 empty] | --- | 2016-04-21 19:19 | 2016-04-21 19:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING PREVAILED IN THE AREA.DELAY DUE TO NON CLEARANCE FROM DOYANG
12 | NER L112 | DOYANG_DIMAPUR 2 | 92.526 | North Eastern Region | --- | 2016-04-18 19:36 | 2016-04-18 20:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | NA | NA | NA | THUNDERSTORM PREVAILED IN THE AREA |  | 100
[5 empty] | --- | 2016-04-18 22:47 | 2016-04-19 01:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 18 | 0 | 0 | NA | NA | NA | DELAY IN CHARGING AS LINE KEPT OPEN DUE TO INCLEMENT WEATHER
13 | NER L113 | GOHPUR_NIRJULI | 42.5 | North Eastern Region | --- | 2016-04-26 07:00 | 2016-04-26 18:41 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 41 | NA | NA | NA | S/D TAKEN FOR REPLACING EXISTING BUS CONDCTR WITH MOOSE CONDTR FOR ENHANCED LOADABILITY AT NRJ S/S |  | 100
14 | NER L114 | IMPHAL_IMPHAL 1 | 1.5 | North Eastern Region | --- | 2016-04-09 15:30 | 2016-04-09 16:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | NA | NA | NA | E/S/D taken for clearing tree between loc 4-5 (came near line due to storm) |  | 100
[5 empty] | --- | 2016-04-04 13:57 | 2016-04-04 14:06 | as given in (3) | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT(33 KV LAINAKHANG STATE FEEDER FAULTY)
[5 empty] | --- | 2016-04-08 02:43 | 2016-04-08 03:00 | as given in (3) | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE AIRPORT FEEDER
[5 empty] | --- | 2016-04-09 10:59 | 2016-04-09 11:28 | as given in (3) | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault.
[5 empty] | --- | 2016-04-10 11:30 | 2016-04-10 11:46 | as given in (3) | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault
[5 empty] | --- | 2016-04-10 12:04 | 2016-04-10 12:20 | as given in (3) | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault
[5 empty] | --- | 2016-04-10 12:31 | 2016-04-10 14:34 | as given in (3) | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault
[5 empty] | --- | 2016-04-23 11:05 | 2016-04-23 11:35 | as given in (3) | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault in 132KV Karong - Yankoypei state feeder.
[5 empty] | --- | 2016-04-09 09:37 | 2016-04-09 10:07 | as given in (3) | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault
15 | NER L115 | JIRIBAM_AIZWAL | 172.315 | North Eastern Region | --- | 2016-04-01 12:05 | 2016-04-01 13:52 | as given in (3) | 0 | 1 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TO ATTEND R PH ISOLATOR SPARKING AT JIRIBAM |  | 99.61
[5 empty] | --- | 2016-04-04 07:14 | 2016-04-04 07:55 | as given in (3) | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | NA | NA | NA | NON ISOLATION OF DOWNSTREAM FAULT IN AZL-ZMBWK BY CB AT AZL(STATE OWNED) LED TO REFLECTION OF FAULT
[5 empty] | --- | 2016-04-06 10:48 | 2016-04-06 12:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 0 | 0 | NA | NA | NA | E/S/D FOR CLEARING DEBRIS HANGING FROM CROSSARM OF Y PH AT LOC 7 DUE TO STORM
[5 empty] | --- | 2016-04-15 16:37 | 2016-04-15 17:38 | as given in (3) | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | PARTROLLING IN PROGRESS
[5 empty] | --- | 2016-04-19 11:42 | 2016-04-19 14:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 21 | 0 | 0 | NA | NA | NA | S/D taken for replacement of damaged insulator due to lightening at Loc.No.407.
[5 empty] | --- | 2016-04-22 02:33 | 2016-04-22 02:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM AND LIGHTNING
[5 empty] | --- | 2016-04-26 03:04 | 2016-04-26 03:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | NA | NA | NA
[5 empty] | insulator damaged | 2016-04-29 00:52 | 2016-04-29 15:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | NA | NA | NA | INSULATOR DAMAGED AT LOC 50 DUE TO HEAVY LIGHTNING
16 | NER L116 | JIRIBAM_HAFLONG | 100.63 | North Eastern Region | --- | X | X | as given in (3) | X | X | X | X | X | X | X | X | X | NA | NA | NA | X |  | 100
17 | NER L117 | JIRIBAM_LOKTAK 2 | 82.4 | North Eastern Region | --- | 2016-04-15 01:17 | 2016-04-15 01:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | HEAVY RAIN AND STORM |  | 99.97
[5 empty] | --- | 2016-04-06 19:05 | 2016-04-06 19:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM & LIGHTNING
[5 empty] | --- | 2016-04-15 21:37 | 2016-04-15 21:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
[5 empty] | --- | 2016-04-19 08:39 | 2016-04-19 16:38 | as given in (3) | 0 | 0 | 0 | 7 | 59 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by Loktak (NHPC).
[5 empty] | --- | 2016-04-23 21:12 | 2016-04-23 21:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-23 21:32 | 2016-04-23 21:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-23 21:59 | 2016-04-24 17:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 0 | 0 | NA | NA | NA | R-ph conductor snapped between loc 9-10 due to falling of a big tree during a cyclone.
[5 empty] | --- | 2016-04-25 15:36 | 2016-04-25 16:13 | as given in (3) | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT
[5 empty] | --- | 2016-04-26 14:33 | 2016-04-26 18:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 3 | 28 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REPAIRING OF OPGW CUT BY MISCREANTS AT LOC 201-202 AT CROSSING WITH 132 KV JBM-LKT
[5 empty] | --- | 2016-04-30 13:00 | 2016-04-30 13:11 | as given in (3) | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | PATROLLING IN PROGRESS
[5 empty] | --- | 2016-04-07 11:04 | 2016-04-07 14:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARING TREE AT LOC 104,105,106
18 | NER L118 | KHANDONG-HAFLONG | 63.166 | North Eastern Region | --- | 2015-04-05 13:10 | 2015-04-05 13:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | NA | NA | NA | CYCLONE & HEAVY STORM DURING TRIPPING |  | 100
19 | NER L119 | KHANDONG_KHLIERIAT 1 | 42.48 | North Eastern Region | --- | 2016-04-14 20:16 | 2016-04-14 20:52 | as given in (3) | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | NA | NA | NA | fault beyond line length |  | 100
[5 empty] | --- | 2016-04-18 19:51 | 2016-04-18 20:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTENING
20 | NER L120 | KHANDONG_KHLIERIAT 2 | 40.933 | North Eastern Region | --- | 2016-04-29 09:44 | 2016-04-29 16:23 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 6 | 39 | 0 | 0 | NA | NA | NA | FOR CLEARING OF TALL TREES ON UPHILL SIDE (LOC 6-8) |  | 100
21 | NER L121 | KHANDONG_KOPILI 1 | 10.914 | North Eastern Region | --- | 2016-04-25 22:30 | 2016-04-26 16:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 0 | 0 | NA | NA | NA | BIF TREE FALLEN ON B PH AT LOC 23-24 FOUND |  | 100
[5 empty] | --- | 2016-04-19 00:03 | 2016-04-19 00:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | THUNDERSTORM PREVAILED IN THE AREA
22 | NER L122 | KHLIERIAT_KHLIERIAT | 7.801 | North Eastern Region | --- | 2016-04-23 17:07 | 2016-04-23 18:21 | as given in (3) | 0 | 0 | 0 | 1 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length. |  | 100
[5 empty] | --- | 2016-04-23 19:05 | 2016-04-23 19:22 | as given in (3) | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-04-23 19:41 | 2016-04-23 20:59 | as given in (3) | 0 | 0 | 0 | 1 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-04-23 22:05 | 2016-04-23 23:06 | as given in (3) | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-04-24 00:07 | 2016-04-24 09:17 | as given in (3) | 0 | 0 | 0 | 9 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-04-24 13:26 | 2016-04-24 13:43 | as given in (3) | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-04-24 17:23 | 2016-04-24 17:32 | as given in (3) | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-25 02:31 | 2016-04-25 02:50 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-27 08:24 | 2016-04-27 08:59 | as given in (3) | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-27 21:06 | 2016-04-27 21:58 | as given in (3) | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-28 00:02 | 2016-04-28 00:27 | as given in (3) | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-23 10:07 | 2016-04-23 10:26 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-04-21 22:01 | 2016-04-21 22:48 | as given in (3) | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-29 08:48 | 2016-04-29 09:14 | as given in (3) | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-30 22:07 | 2016-04-30 23:13 | as given in (3) | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION
[5 empty] | --- | 2016-04-30 23:41 | 2016-05-01 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-23 15:03 | 2016-04-23 15:53 | as given in (3) | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-04-05 14:19 | 2016-04-05 14:53 | as given in (3) | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-04-06 02:25 | 2016-04-06 02:44 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-08 03:51 | 2016-04-08 05:23 | as given in (3) | 0 | 0 | 0 | 1 | 32 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT LOCATION BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-09 10:32 | 2016-04-09 13:19 | as given in (3) | 0 | 0 | 0 | 2 | 47 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D of Bus taken by state.
[5 empty] | --- | 2016-04-14 06:15 | 2016-04-14 06:32 | as given in (3) | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT LOCATION IS BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-16 07:47 | 2016-04-16 08:25 | as given in (3) | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-16 09:59 | 2016-04-16 10:17 | as given in (3) | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-17 20:55 | 2016-04-17 21:13 | as given in (3) | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-18 18:40 | 2016-04-18 19:09 | as given in (3) | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-04-19 03:41 | 2016-04-19 03:55 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-19 03:59 | 2016-04-19 04:35 | as given in (3) | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-19 08:45 | 2016-04-19 09:20 | as given in (3) | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-04-19 13:20 | 2016-04-20 10:07 | as given in (3) | 0 | 0 | 0 | 20 | 47 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.Line kept open as per NERLDC instruction.
23 | NER L123 | KUMARGHAT_R C NAGAR | 104.02 | North Eastern Region | --- | 2016-04-04 06:04 | 2016-04-04 08:00 | as given in (3) | 0 | 1 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | CB PROBLEM IN KUMARGHAT END |  | 99.73
[5 empty] | --- | 2016-04-15 04:04 | 2016-04-15 04:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | HEAVY RAIN & STORM
[5 empty] | --- | 2016-04-17 23:25 | 2016-04-17 23:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | HEAVY LIGHTENING AND THUNDERSTORM PREVAILING IN AREA
24 | NER L124 | LOKTAK_IMPHAL 2 | 35.04 | North Eastern Region | --- | 2016-04-15 08:36 | 2016-04-15 17:42 | as given in (3) | 0 | 0 | 0 | 9 | 6 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY LOKTAK END |  | 100
[5 empty] | --- | 2016-04-17 08:35 | 2016-04-18 13:20 | as given in (3) | 0 | 0 | 0 | 28 | 45 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY LOKTAK
[5 empty] | --- | 2016-04-25 15:37 | 2016-04-25 16:11 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault.
25 | NER L126 | NIRJULI-RANGANADI | 22.29 | North Eastern Region | --- | 2016-04-13 08:48 | 2016-04-13 11:53 | as given in (3) | 0 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE |  | 100
26 | NER L128 | KOLASIB-AIZAWL | 66.098 | North Eastern Region | --- | 2016-04-21 13:24 | 2016-04-21 13:45 | as given in (3) | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT |  | 100
[5 empty] | --- | 2016-04-04 07:06 | 2016-04-04 07:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | NA | NA | NA | THUNDERSTORM OBSERVED
[5 empty] | --- | 2016-04-07 02:00 | 2016-04-07 02:27 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM & LIGHTNING
[5 empty] | --- | 2016-04-16 19:54 | 2016-04-16 20:12 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | NA | NA | NA | heavy thunderstorm prevailing in the area
27 | NER L129 | RANGANADI-ZIRO | 44.523 | North Eastern Region | --- | X | X | as given in (3) | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
28 | NER L130 | KHANDONG_KOPILI 2 | 11.56 | North Eastern Region | --- | X | X | as given in (3) | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
29 | NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) | 0.347 | North Eastern Region | --- | X | X | as given in (3) | X | X | X | X | X | X | X | X | X | NA | NA | NA | X |  | 100
30 | NER L132 | DIMAPUR(PG)-DIMAPUR(LILO PORTION) | 0.347 | North Eastern Region | --- | X | X | as given in (3) | X | X | X | X | X | X | X | X | X | NA | NA | NA | X |  | 100
31 | NER L133 | SILCHAR-BADARPUR 1 | 19.195 | North Eastern Region | tower collapsed | 2016-04-29 00:21 | 2016-05-01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 47 | 39 | 0 | 0 | NA | NA | NA | TOWER COLLAPSED AT LOC 20 DUE TO HEAVY THUNDERSTORM |  | 98.25
[5 empty] | --- | 2016-04-06 09:46 | 2016-04-06 16:15 | as given in (3) | 0 | 6 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP WORKS AND ISOLATOR ADJUSTMENTS
[5 empty] | --- | 2016-04-13 23:35 | 2016-04-14 00:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | HEAVY CYCLONE REPORTED AT BADARPUR
[5 empty] | --- | 2016-04-05 09:05 | 2016-04-05 15:12 | as given in (3) | 0 | 6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP WORKS AND ISOLATOR ALIGNMENTS
32 | NER L134 | SILCHAR-BADARPUR 2 | 19.195 | North Eastern Region | --- | 2016-04-13 23:35 | 2016-04-14 00:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | NA | NA | NA | HEAVY CYCLONE REPORTED AT BADARPUR |  | 100
[5 empty] | tower collapsed | 2016-04-29 00:21 | 2016-05-01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 47 | 39 | 0 | 0 | NA | NA | NA | TOWER COLLAPSE AT LOC 20 DUE TO HEAVY THUNDERSTORM
[5 empty] | --- | 2016-04-20 21:54 | 2016-04-20 22:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-26 22:30 | 2016-04-26 22:38 | as given in (3) | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT
33 | NER L135 | SILCHAR-SRIKONA 1 | 1.199 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
34 | NER L136 | SILCHAR-SRIKONA 2 | 1.199 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
35 | NER L138 | SILCHAR-HAILAKANDI 1 | 17.3 | North Eastern Region | --- | 2016-04-09 09:34 | 2016-04-09 15:30 | as given in (3) | 0 | 5 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | AMP works and isolator sdjustments |  | 98.49
[5 empty] | --- | 2016-04-08 14:40 | 2016-04-08 15:55 | as given in (3) | 0 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D Availed by State
[5 empty] | --- | 2016-04-08 09:52 | 2016-04-08 14:40 | as given in (3) | 0 | 4 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Planned S/D for AMP and isolator alignments
[5 empty] | --- | 2016-04-08 06:01 | 2016-04-08 06:18 | as given in (3) | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT LOCATION BEYOND LINE LENGTH.
[5 empty] | --- | 2016-04-13 23:35 | 2016-04-14 00:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | NA | NA | NA | HEAVY CYCLONE REPORTED AT BADARPUR
[5 empty] | --- | 2016-04-25 00:17 | 2016-04-25 00:49 | as given in (3) | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION
[5 empty] | --- | 2016-04-29 13:40 | 2016-04-29 16:41 | as given in (3) | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE
[5 empty] | --- | 2016-05-29 00:23 | 2016-05-29 01:27 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | NA | NA | NA | Heavy thunderstorm reported during tripping
[5 empty] | --- | 2016-04-25 04:39 | 2016-04-25 05:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO THUNDERSTORM
[5 empty] | --- | 2016-04-04 19:09 | 2016-04-05 17:08 | as given in (3) | 0 | 0 | 0 | 21 | 59 | 0 | 0 | 0 | 0 | NA | NA | NA | GFAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-18 10:51 | 2016-04-18 15:29 | as given in (3) | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS E/S/D TAKEN BY STATE
[5 empty] | --- | 2016-04-20 21:59 | 2016-04-20 22:21 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line jurisdiction.
[5 empty] | --- | 2016-04-21 13:47 | 2016-04-21 14:09 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION
36 | NER L139 | SILCHAR-HAILAKANDI 2 | 17.3 | North Eastern Region | --- | 2016-04-15 02:32 | 2016-04-15 02:40 | as given in (3) | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION |  | 100
[5 empty] | --- | 2016-04-05 11:57 | 2016-04-08 17:38 | as given in (3) | 0 | 0 | 0 | 77 | 41 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped
[5 empty] | --- | 2016-04-04 02:40 | 2016-04-04 03:29 | as given in (3) | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | NA | NA | NA | Downstream fault beyond jurisdiction
[5 empty] | --- | 2016-04-04 19:57 | 2016-04-04 21:10 | as given in (3) | 0 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT LOCATION BEYOND LINE LENGTH
[5 empty] | --- | 2016-04-24 18:16 | 2016-04-25 16:06 | as given in (3) | 0 | 0 | 0 | 21 | 50 | 0 | 0 | 0 | 0 | NA | NA | NA | Faulr beyond jurisdiction.E/S/D taken by state.
[5 empty] | --- | 2016-04-22 14:43 | 2016-04-22 15:07 | as given in (3) | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | NA | NA | NA | THNDERSTORM PREVAILED IN THE AREA
[5 empty] | --- | 2016-04-16 19:38 | 2016-04-16 20:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | NA | NA | NA | FAULT DISTANCE BEYOND POWERGRID JURISDICTION
[5 empty] | --- | 2016-04-19 20:06 | 2016-04-19 20:27 | as given in (3) | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault location is beyond line length.
[5 empty] | --- | 2016-04-17 09:19 | 2016-04-17 09:33 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION
37 | NER L140 | MOKUKCHUNG_MOKUKCHUNG 1 | 1.4 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
38 | NER L141 | MOKOCHUNG-MOKOKCHUNG 2 | 1.4 | North Eastern Region | --- | 2016-04-16 12:03 | 2016-04-18 22:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 58 | 2 | 0 | 0 | NA | NA | NA | LINE KEPT OPEN |  | 100
[5 empty] | --- | 2016-04-21 12:59 | 2016-04-22 18:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 21 | NA | NA | NA | LINE KEPT OPEN AS PER NERLDC INSTRUCTION DUE TO SYSTEM CONSTRAINT
39 | NER L142 | B.CHARAILI_PAVOI 1 | 12.93 | North Eastern Region | --- | 2016-04-13 12:02 | 2016-04-13 14:11 | as given in (3) | 0 | 0 | 0 | 2 | 9 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE |  | 97.69
[5 empty] | Jumper damage | 2016-04-24 23:34 | 2016-04-25 16:10 | as given in (3) | 0.69167 | 16 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.3083 | R-ph jumper found opened at LOC 5 on patrolling
40 | NER L143 | B.CHARAILI_PAVOI 2 | 12.93 | North Eastern Region | --- | 2016-04-13 12:02 | 2016-04-13 13:02 | as given in (3) | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE |  | 100
41 | NER L144 | NIRJULI-LEKHI | 9.7 | North Eastern Region | --- | 2016-04-26 07:00 | 2016-04-26 18:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 38 | NA | NA | NA | S/D TAKEN FOR REPLACEMENT OF EXISTING BUS CONDUCTOR WITH MOOSE CONDUCTOR FOR ENHANCED LOAD AT NRJ SS |  | 100
|  |  | 9.7 | North Eastern Region | --- | 2016-04-13 08:48 | 2016-04-13 11:53 | as given in (3) | 0 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | 0 | NA | NA | NA | Shutdown taken by state
42 | NER L201 | BALIPARA_TEZPUR | 8.623 | North Eastern Region | --- | 2016-04-25 23:06 | 2016-04-25 23:57 | as given in (3) | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond POWERGRID's jurisdiction |  | 100
[5 empty] | --- | 2016-04-23 19:21 | 2016-04-23 19:49 | as given in (3) | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length. Tripped due to downstream fault.
[5 empty] | --- | 2016-04-21 11:43 | 2016-04-21 15:04 | as given in (3) | 0 | 0 | 0 | 3 | 21 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE
[5 empty] | --- | 2016-04-14 11:49 | 2016-04-14 12:28 | as given in (3) | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO STATE END
43 | NER L202 | KATHALGURI_MARIANI(OLD) | 162.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
44 | NER L203 | MISA_DIMAPUR 1 | 123.52 | North Eastern Region | --- | X | X | as given in (3) | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
45 | NER L204 | MISA_DIMAPUR 2 | 123.52 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
46 | NER L206 | MISA-KOPILI 1 | 72.791 | North Eastern Region | --- | 2016-04-24 04:57 | 2016-04-24 06:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 48 | NA | NA | NA | Line H/T vide code 573. |  | 100
[5 empty] | --- | 2016-04-24 04:57 | 2016-04-24 06:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 48 | NA | NA | NA | Line H/T vide code 573
47 | NER L207 | MISA_KOPILI 2 | 72.791 | North Eastern Region | --- | 2016-04-28 22:09 | 2016-04-29 16:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 18 | 1 | 0 | 0 | NA | NA | NA | INSULATOR DAMAGED AT LOC 288 DUE TO HEAVY LIGHTNING |  | 100
[5 empty] | --- | 2016-04-19 12:44 | 2016-04-21 15:59 | as given in (3) | 0 | 0 | 0 | 51 | 15 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN BY KOPILI STATE FOR ATTENDING Y-Ph LA problem
48 | NER L208 | MISA_KOPILI 3 | 75.788 | North Eastern Region | --- | 2016-04-01 09:34 | 2016-04-01 17:23 | as given in (3) | 0 | 7 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D OF AMP WORKS |  | 98.89
49 | NER L209 | MISA_MARIANI(OLD) | 220 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
50 | NER L210 | MISA_SAMAGURI 1 | 34.439 | North Eastern Region | --- | 2016-04-14 22:02 | 2016-04-14 23:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 0 | 0 | NA | NA | NA | HEAVY RAIN/STORM AT MISA) |  | 100
51 | NER L211 | MISA_SAMAGURI 2 | 34.439 | North Eastern Region | --- | 2016-04-14 21:45 | 2016-04-15 13:31 | as given in (3) | 0 | 0 | 0 | 15 | 46 | 0 | 0 | 0 | 0 | NA | NA | NA | JUMPER FROM WAVETRAP AT SAMAGURI( STATE) END SWITCHYARD BROKEN/GROUNDED |  | 100
52 | NER L214 | MISA-MARIANI(NEW) | 222.682 | North Eastern Region | --- | 2016-04-13 19:25 | 2016-04-13 20:11 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO HEAVY EARTHQUAKE IN NER. |  | 100
53 | NER L215 | KATHALGURI-MARIANI(NEW) | 160.536 | North Eastern Region | --- | 2016-04-13 19:25 | 2016-04-13 20:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | NA | NA | NA | TRIPPED ON OVER VOLTAGE |  | 100
54 | NER L216 | MARIANI_MOKUKCHUNG 1 | 48.8 | North Eastern Region | --- | 2016-04-01 22:52 | 2016-04-16 10:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 347 | 11 | 0 | 0 | NA | NA | NA | TRIPPED ON O/V |  | 100
[5 empty] | --- | 2016-04-16 11:59 | 2016-04-20 18:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 102 | 10 | 0 | 0 | NA | NA | NA | Tripped on over voltage.
[5 empty] | --- | 2016-04-20 22:03 | 2016-04-22 11:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 37 | 21 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
[5 empty] | --- | 2016-04-22 23:14 | 2016-05-01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 192 | 46 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
[5 empty] | --- | 2016-04-01 | 2016-04-01 18:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
55 | NER L217 | MARIANI_MOKUKCHUNG 2 | 48.8 | North Eastern Region | --- | 2016-04-01 | 2016-04-02 11:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 35 | 58 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE |  | 100
[5 empty] | --- | 2016-04-05 08:55 | 2016-04-05 10:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
[5 empty] | --- | 2016-04-05 22:44 | 2016-04-06 17:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 18 | 30 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
[5 empty] | --- | 2016-04-14 23:56 | 2016-04-16 19:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 43 | 46 | 0 | 0 | NA | NA | NA | TRIPPED ON O/V
[5 empty] | --- | 2016-04-20 17:33 | 2016-04-20 18:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-21 12:27 | 2016-04-21 12:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM REPORTED
[5 empty] | --- | 2016-04-22 11:25 | 2016-04-22 18:12 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 6 | 47 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CONDUCTOR REPAIRING DAMAGED DUE TO FELLING OF TREE LOC 24-25 DUE TO STORM
[5 empty] | --- | 2016-04-24 02:17 | 2016-04-24 17:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 0 | 0 | NA | NA | NA | Tripped on over-voltage
56 | NER L401 | BALIPARA_BONGAIGAON 1 | 289.721 | North Eastern Region | --- | 2016-04-01 | 2016-04-01 18:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 43 | NA | NA | NA | LINE H/T VIDE CODE 6301 |  | 100
[5 empty] | --- | 2016-04-08 13:49 | 2016-04-08 14:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | BAMBOO CAME IN PROXIMITY TO LINE CORRIDOR DUE TO WIND
[5 empty] | --- | 2016-04-29 11:40 | 2016-04-29 16:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 5 | 14 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO OVERVOLTAGE
[5 empty] | --- | 2016-04-29 09:23 | 2016-04-29 11:19 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 56 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO OVERVOLTAGE
[5 empty] | --- | 2016-04-29 11:40 | 2016-04-29 11:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | NA | NA | NA | LINE H/T VIDE CODE 725
57 | NER L402 | BALIPARA_BONGAIGAON 2 | 289.721 | North Eastern Region | --- | 2016-04-08 03:26 | 2016-04-08 13:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31 | NA | NA | NA | Line H/T vide code 0165 |  | 100
[5 empty] | --- | 2016-04-29 17:45 | 2016-04-30 00:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | NA | NA | NA | LINE KEPT OPEN AS PER NERLDC INSTRUCTYION
[5 empty] | --- | 2016-04-29 16:57 | 2016-04-29 17:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARING OF BAMBOOS WHICH CAME CLOSE TO LINE PROXIMITY FRO OUTSIDE LINE CORRIDOR
[5 empty] | --- | 2016-04-24 04:07 | 2016-04-24 17:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 37 | NA | NA | NA | Line H/T vide code 571
[5 empty] | --- | 2016-04-13 13:57 | 2016-04-15 04:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 34 | NA | NA | NA | LINE H/T VIDE CODE 281
[5 empty] | --- | 2016-04-07 14:36 | 2016-04-07 17:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | NA | NA | NA | LINE H/T VIDE CODE 141
[5 empty] | --- | 2016-04-07 09:38 | 2016-04-07 15:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52 | NA | NA | NA | LINE H/T VIDE CODE 0129
58 | NER L403 | MISA_BALIPARA 1 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
59 | NER L404 | MISA-BALIPARA 2 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
60 | NER L405 | BONGAIGAON-MALDA 1 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
61 | NER L406 | BONGAIGAON-MALDA 2 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
62 | NER L407 | BALIPARA-RANGANADI 1 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
63 | NER L408 | BALIPARA-RANGANADI 2 | 166.335 | North Eastern Region | --- | 2016-04-26 00:13 | 2016-04-26 07:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 41 | NA | NA | NA | Line H/T vide code 07:54 |  | 100
64 | NER L409 | PALLATANA-SURAJMANINAGAR 1 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
65 | NER L410 | PALLATANA-SURAJMANINAGAR 2 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
66 | NER L411 | BTPS-BONGAIGAON 1 | 3.119 | North Eastern Region | --- | 2016-04-19 11:39 | 2016-04-19 20:07 | as given in (3) | 0 | 0 | 0 | 8 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by NTPC. |  | 100
[5 empty] | --- | 2016-04-16 12:03 | 2016-04-16 15:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 58 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO HEAVY THUNDERSTORM
67 | NER L412 | BTPS-BONGAIGAON 2 | 3.119 | North Eastern Region | --- | 2016-04-16 12:03 | 2016-04-16 14:18 | as given in (3) | 0 | 0 | 0 | 2 | 15 | 0 | 0 | 0 | 0 | NA | NA | NA |  |  | 100
68 | NER L413 | BALIPARA-BONGAIGAON 3 | 309 | North Eastern Region | --- | 2016-04-02 22:03 | 2016-04-03 18:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 27 | NA | NA | NA | LINE H/T VIDE CODE 0036 |  | 100
[5 empty] | --- | 2016-04-04 23:18 | 2016-04-11 19:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 45 | NA | NA | NA | Line H/T vide code 0072
[5 empty] | --- | 2016-04-12 22:50 | 2016-04-13 17:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 34 | NA | NA | NA | LINE H/T VIDE CODE 0268
[5 empty] | --- | 2016-04-15 02:47 | 2016-04-27 19:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 31 | NA | NA | NA | LINE H/T VIDE CODE 323
[5 empty] | --- | 2016-05-28 19:56 | 2016-05-28 20:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm
[5 empty] | --- | 2016-04-28 20:15 | 2016-04-29 10:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 55 | NA | NA | NA | LINE KEPT OPEN AS PER NERLDC INSTRUCTION
[5 empty] | --- | 2016-04-30 00:20 | 2016-05-01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 40 | NA | NA | NA | LINE H/T VIDE CODE 751
69 | NER L414 | BALIPARA-BONGAIGAON 4 | 309 | North Eastern Region | --- | 2016-04-29 11:40 | 2016-04-29 12:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO OVERVOLTAGE |  | 100
[5 empty] | --- | 2016-04-01 | 2016-04-02 18:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 32 | NA | NA | NA | LINE H/T VIDE CODE 6254
[5 empty] | --- | 2016-04-03 22:54 | 2016-04-04 18:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 30 | NA | NA | NA | LINE H/T VIDE CODE 0047
[5 empty] | --- | 2016-04-11 21:27 | 2016-04-12 18:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 26 | NA | NA | NA | Line H/T vide code 0253
[5 empty] | --- | 2016-05-28 19:56 | 2016-05-28 20:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-29 09:41 | 2016-04-29 09:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
[5 empty] | --- | 2016-05-27 19:27 | 2016-05-28 19:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 42 | NA | NA | NA | Line H/T vide code 663
70 | NER L415 | SILCHAR-IMPHAL 1 | 167 | North Eastern Region | --- | 2016-04-21 19:07 | 2016-04-21 19:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING PREAVAILED IN THE AREA |  | 100
[5 empty] | --- | 2016-04-23 21:23 | 2016-04-23 21:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-24 10:19 | 2016-04-24 10:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-24 21:43 | 2016-04-24 21:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO HEAVY THUNDERSTORM
[5 empty] | --- | 2016-04-26 14:33 | 2016-04-26 18:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | NA | NA | NA | EPAIRING OF OPGW WIRE CUT BY MISCREANTS AT LOC 201-202 XING WITH 132 KV JBM-LKT
[5 empty] | --- | 2016-05-29 01:01 | 2016-05-29 01:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | NA | NA | NA | Heavy thunderstorm reported during tripping
[5 empty] | --- | 2016-04-30 23:15 | 2016-04-30 23:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM REPORTED
71 | NER L416 | SILCHAR-IMPHAL 2 | 167 | North Eastern Region | --- | 2016-05-28 08:20 | 2016-05-28 17:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 9 | 37 | 0 | 0 | NA | NA | NA | E/S/D taken for repairing of OPG wires cut by miscreants at loc 201-202 crossing 132KV Jbm-Loktak TL |  | 100
[5 empty] | --- | 2016-04-08 02:12 | 2016-04-08 02:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO HEAVY LIGHTNING WITH THUNDERSTORM
[5 empty] | --- | 2016-04-15 21:36 | 2016-04-15 22:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | NA | NA | NA | Tripped due to lightning
[5 empty] | --- | 2016-04-16 17:39 | 2016-04-16 17:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM PREVAILING IN THE AREA
[5 empty] | --- | 2016-04-23 21:30 | 2016-04-23 21:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-04-25 05:06 | 2016-04-25 05:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | tripped due to heavy thunderstorm
[5 empty] | --- | 2016-04-26 14:34 | 2016-04-26 18:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR OPGW CUT BY MISCREANTS AT LOC 201-202 XING WITH 132 KV JBM-LKT
72 | NER L417 | BALIPARA_B.CHAIRALI 3 | 57.294 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
73 | NER L418 | BALIPARA_B.CHAIRALI 4 | 57.294 | North Eastern Region | --- | 2016-04-13 13:55 | 2016-04-17 18:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 36 | NA | NA | NA | LINE H/T VIDE CODE 280 |  | 100
[5 empty] | --- | 2016-04-01 10:56 | 2016-04-01 12:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | NA | NA | NA | LINE H/T VIDE CODE 05
74 | NER L419 | B.CHAIRALI_RANGANADI 1 | 129.335 | North Eastern Region | --- | 2016-04-01 | 2016-04-01 18:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 43 | NA | NA | NA | LINE H/T VIDE CODE 6300 |  | 100
[5 empty] | --- | 2016-04-03 21:55 | 2016-04-04 17:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | NA | NA | NA | LINE H/T VIDE CODE 0045
[5 empty] | --- | 2016-04-05 22:21 | 2016-04-06 07:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | NA | NA | NA | LINE H/T VIDE CODE 0099
[5 empty] | --- | 2016-04-08 03:06 | 2016-04-08 17:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 25 | NA | NA | NA | Line H/T vide code 0163
[5 empty] | --- | 2016-04-12 00:09 | 2016-04-12 07:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 19 | NA | NA | NA | Line H/T vide code 0254
[5 empty] | --- | 2016-04-14 00:07 | 2016-04-14 16:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | NA | NA | NA | LINE H/T VIDE CODE 292
[5 empty] | --- | 2016-04-15 23:48 | 2016-04-16 18:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 45 | NA | NA | NA | LINE H/T VIDE CODE 337
[5 empty] | --- | 2016-04-18 23:15 | 2016-04-19 10:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | NA | NA | NA | Line H/T vide code 429.
[5 empty] | --- | 2016-04-24 22:41 | 2016-04-25 17:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | NA | NA | NA | Line H/T vide code 596
[5 empty] | --- | 2016-04-26 08:02 | 2016-04-26 17:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 36 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF VULNERABLE TOWER LOC 66 ON PILE FOUNDATION
[5 empty] | --- | 2016-05-28 00:16 | 2016-05-28 07:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 39 | NA | NA | NA | Line H/T vide code 667.
[5 empty] | --- | 2016-04-27 00:05 | 2016-04-27 08:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | NA | NA | NA | LINE H./T VIDE CODE 648
[5 empty] | --- | 2016-05-28 07:55 | 2016-05-28 17:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 29 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc.99 on pile foundation.
[5 empty] | --- | 2016-04-27 08:05 | 2016-04-27 16:36 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF VULNERABLE TOWER LOC 66 ON PILE FOUNDATION
75 | NER L420 | B.CHAIRALI_RANGANADI 2 | 129.335 | North Eastern Region | --- | 2016-04-28 22:57 | 2016-04-29 08:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | NA | NA | NA | LINE H/T VIDE CODE 702 |  | 100
[5 empty] | --- | 2016-04-01 22:28 | 2016-04-02 17:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | NA | NA | NA | LINE H/T VIDE CODE 0016
[5 empty] | --- | 2016-04-02 22:03 | 2016-04-03 17:23 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | NA | NA | NA | LINE H/T VIDE CODE 0037
[5 empty] | --- | 2016-04-04 22:01 | 2016-04-05 18:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 24 | NA | NA | NA | LINE H/T VIDE CODE 0071
[5 empty] | --- | 2016-04-06 23:02 | 2016-04-07 16:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | NA | NA | NA | LINE H/T VIDE CODE 0124
[5 empty] | --- | 2016-04-08 23:06 | 2016-04-09 17:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 28 | NA | NA | NA | Line H/T vide code 0197
[5 empty] | --- | 2016-04-09 23:06 | 2016-04-10 17:11 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | NA | NA | NA | Line H/T vide code 0223
[5 empty] | --- | 2016-04-11 01:05 | 2016-04-11 18:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | NA | NA | NA | Line H/T vide code 0241
[5 empty] | --- | 2016-04-13 13:05 | 2016-04-13 16:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | NA | NA | NA | LINE H/T VIDE CODE 277
[5 empty] | --- | 2016-04-14 21:44 | 2016-04-15 16:27 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 43 | NA | NA | NA | LINE H/T VIDE CODE 314
[5 empty] | --- | 2016-04-16 23:17 | 2016-04-17 17:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 51 | NA | NA | NA | LINE H/T VIDE CODE 375
[5 empty] | --- | 2016-04-20 01:51 | 2016-04-20 17:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 58 | NA | NA | NA | Line H/T vide code 671.
[5 empty] | --- | 2016-04-29 08:13 | 2016-04-29 19:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF VULNERABLE TOWER LOC 66 ON PILE FOUNDATION
[5 empty] | --- | 2016-04-29 23:40 | 2016-04-30 07:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | NA | NA | NA | LINE H/T VIDE CODE 749
[5 empty] | --- | 2016-04-30 07:49 | 2016-04-30 18:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF VULNERABLE TOWER LOC 66 ON PILE FOUNDATION
[5 empty] | --- | 2016-04-30 23:54 | 2016-05-01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | NA | NA | NA | LINE H/T VIDE CODE 773
[5 empty] | --- | 2016-04-18 00:07 | 2016-04-18 17:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | NA | NA | NA | LINE H/T VIDE CODE 407
76 | NER L421 | BALIPARA_B.CHAIRALI 1 | 59.54 | North Eastern Region | --- | 2016-04-16 12:03 | 2016-04-30 18:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 342 | 54 | 0 | 0 | NA | NA | NA | LINE KEPT OPEN AS PER NERLDC INSTRUCTION |  | 100
77 | NER L422 | BALIPARA_B.CHAIRALI 2 | 59.54 | North Eastern Region | --- | 2016-04-01 | 2016-04-14 10:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 59 | NA | NA | NA | LINE H/T VIDE CODE 6145 |  | 100
78 | NER L423 | SILCHAR-PURBAKANCHANBARI 1 | 127.2 | North Eastern Region | --- | 2016-04-16 00:30 | 2016-04-16 01:07 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING |  | 100
[5 empty] | --- | 2016-04-19 14:17 | 2016-04-19 17:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 3 | 23 | 0 | 0 | NA | NA | NA | Emergency S/D taken for clearing tree branches leaning towards the line due to heavy thunderstorm.
[5 empty] | --- | 2016-04-06 14:55 | 2016-04-06 16:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 55 | 0 | 0 | NA | NA | NA | EMERGENCY S/D TAKEN BY TREE CUTTING
[5 empty] | --- | 2016-04-05 16:35 | 2016-04-05 17:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM AND LIGHTNING
[5 empty] | --- | 2016-04-15 02:32 | 2016-04-15 02:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | NA | NA | NA | Heavy rain and storm in silchar
[5 empty] | --- | 2016-04-05 13:02 | 2016-04-05 14:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 18 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARING TREE BRANCHES CAME NEAR THE CONDUCTOR DUE TO HEAVY STORM BETWN LOC 326-327
[5 empty] | --- | 2016-04-05 08:08 | 2016-04-05 08:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | tree branches came near conductor at loc 326-327 due to heavy storm
79 | NER L424 | SILCHAR-PURBAKANCHANBARI 2 | 127.2 | North Eastern Region | --- | 2016-04-01 09:37 | 2016-04-01 16:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | NA | NA | NA | S/D TAKEN FOR EARTH WIRE WORKS |  | 100
[5 empty] | --- | 2016-04-09 00:36 | 2016-04-09 00:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | NA | NA | NA | Thunderstorm reported in the area
[5 empty] | --- | 2016-04-02 09:36 | 2016-04-02 17:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 53 | NA | NA | NA | S/D FOR EARTHWIRE WORKS
[5 empty] | --- | 2016-04-05 12:01 | 2016-04-05 12:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM AND LIGHTNING
[5 empty] | --- | 2016-04-05 16:11 | 2016-04-05 16:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM & LIGHTNING
[5 empty] | --- | 2016-04-07 12:58 | 2016-04-07 14:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 52 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR TREE CUTTING
[5 empty] | --- | 2016-04-09 00:45 | 2016-04-09 01:19 | as given in (3) | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | Charging was delayed due to non-receipt of clearance from P.K.Bari end.
[5 empty] | --- | 2016-04-14 16:36 | 2016-04-14 16:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | NA | NA | NA | FAULT DUE TO TREE IN PROXIMITY BELOW 190-191
[5 empty] | --- | 2016-04-19 19:16 | 2016-04-19 19:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | NA | NA | NA | Tripped due to heavy lightening.
[5 empty] | --- | 2016-04-19 20:49 | 2016-04-19 21:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | Tripped due to heavy lightening.
[5 empty] | --- | 2016-04-29 00:23 | 2016-04-29 16:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 16 | 23 | 0 | 0 | NA | NA | NA | EARTH WIRE SNAPPED AT LOC 5 & 6 DUE TO HEAVY CYCLOONE/THUNDERSTORM
[5 empty] | --- | 2016-04-20 13:13 | 2016-04-20 16:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | NA | NA | NA | E/S/D taken for clearing tree branches (Loc.No.170-171) leaning towards the line due to thunderstorm
80 | NER RBR1 | BR_BONGAIGAON (50MVAR) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
81 | NER RBR2 | BR_BONGAIGAON (50MVAR) 2 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
82 | NER RBR3 | BR_BALIPARA (50MVAR) 1 | 50 | North Eastern Region | --- | 2016-04-02 08:47 | 2016-04-02 17:05 | as given in (3) | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | AMP WORK AND NTAMC LOCAL TESTING |  | 98.85
83 | NER RBR4 | BR_MISA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
84 | NER RBR5 | BR_KUMARGHAT (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
85 | NER RBR6 | BR_AIZWAL (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
86 | NER RBR7 | BR_BONGAIGAON(80MVAR) 3 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
87 | NER RBR8 | BR_BALIPARA(80MVAR) 2 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
88 | NER RBR9 | BR_SILCHAR(63MVAR) 1 | 63 | North Eastern Region | --- | 2016-05-28 18:57 | 2016-05-28 21:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | NA | NA | NA | B/R H/T on NERLDC instruction. |  | 100
89 | NER RBR10 | BR_SILCHAR(63MVAR) 2 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
90 | NER RBR11 | BR_BONGAIGAON(80MVAR) 4 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
91 | NER TICT1 | ICT_DIMAPUR (100 MVA) 2 | 100 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
92 | NER TICT2 | ICT_BALIPARA (315MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
93 | NER TICT4 | ICT_SALAKATI (50 MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
94 | NER TICT5 | ICT_DIMAPUR (100 MVA) 1 | 100 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
95 | NER TICT6 | ICT_KUMARGHAT(5MVA) | 5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
96 | NER TICT7 | ICT_NIRJULI(16MVA) 1 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
97 | NER TICT8 | ICT_NIRJULI(10MVA) 2 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
98 | NER TICT10 | ICT_ZIRO (15MVA) | 15 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
99 | NER TICT11 | ICT_NIRJULI (16MVA) 2 | 16 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
100 | NER TICT12 | ICT_KOPILI (160 MVA) 2 | 160 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
101 | NER TICT15 | ICT_SILCHAR(200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
102 | NER TICT16 | ICT_SILCHAR(200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
103 | NER TICT18 | ICT_MISA 2 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
104 | NER TICT19 | ICT_MOKOKCHUNG(30MVA) 1 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
105 | NER TICT20 | ICT_MOKOKCHUNG(30MVA) 2 | 30 | North Eastern Region | --- | 2016-04-20 22:41 | 2016-04-22 17:54 | as given in (3) | X | 43 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | RESTRICTED E/F |  | 94
106 | NER TICT14 | ICT_MISA 1 | 315 | North Eastern Region | --- | 2016-04-26 08:31 | 2016-04-26 17:31 | as given in (3) | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D FOR AMP WORKS |  | 98.75
107 | NER ICT17 | ICT_BONGAIGAON(315MVA) | 315 | North Eastern Region | --- | 2016-04-16 12:03 | 2016-04-16 12:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO OVERLOAD |  | 100
108 | NER TICT21 | ICT_B'CHARIALI (200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
109 | NER TICT22 | ICT_B'CHARIALI (200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
110 | NER TICT23 | ICT_NIRJULI(50MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
52 | NER L123 | KUMARGHAT_R C NAGAR | 104.02 | North Eastern Region | Y ph -Conductortor snapped | 2015-10-09 07:05 | 2015-10-09 17:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 3 | N | -2 | Tripped coz Y-Ph conductor snapped between Loc No. 181-182 due to fallen of a tree cut by miscreant. | NERPC/SE(O)/TAC/2015/9463 DATED 27.01.2016
1541ou

## MAY
S/No | Unique ID of Transmission Element | Element Name | Description (Length-km/Nos./MVA/ MVAr/MW/ etc. | Region | Type of failure | Outage Date & Time Hr Mn | Restoration Date & Time Hr Mn | Details of outage ( No. of Towers damaged, no. of insulators failed etc.) | Total Outage (in Days) (1) | Duration of Outage attribuatable to | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual & Norm (1 - 2) | Detailed Reason for Outage (3) | Outage certifying Agency & Reference Document | % Availability as certified by certifying agency
[10 empty] | ISTS Licensee Hr Min |  | Others Hr Min |  | System Constraint/ Natural calamity/ Milliitancy Hr Min |  | Deemed Available Hr Min
MAY' 2016
1 | NER L101 | RCN_AGARTALA 1 | 8.384 | North Eastern Region | --- | 2016-05-02 15:43 | 2016-05-02 16:25 | as given in (3) | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault at R.C.Nagar end | NERPC | 99.25
[5 empty] | --- | 2016-05-28 09:23 | 2016-05-28 14:58 | as given in (3) | 0 | 5 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for isolator alignment.
2 | NER L102 | RCN_AGARTALA 2 | 8.384 | North Eastern Region | --- | [12 empty] | NA | NA | NA |  |  | 99.09
[5 empty] | --- | 2016-05-02 15:43 | 2016-05-02 19:55 | as given in (3) | 0 | 0 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | NA | NA | NA | CB problem at R.C.Nagar end.
3 | NER L103 | BADARPUR_KOLASIB | 107.226 | North Eastern Region | --- | 2016-05-03 01:45 | 2016-05-03 18:53 | as given in (3) | 0 | 0 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | NA | NA | NA | state problem |  | 98.96
[5 empty] | --- | 2016-05-04 05:44 | 2016-05-04 06:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | NA | NA | NA | lightening
[5 empty] | --- | 2016-05-24 08:36 | 2016-05-24 16:21 | as given in (3) | 0 | 7 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for Jumper tightening works.
[5 empty] | --- | 2016-05-04 07:06 | 2016-05-07 17:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 82 | 27 | 0 | 0 | NA | NA | NA | Fault due to lightening
[5 empty] | --- | 2016-05-09 13:13 | 2016-05-09 17:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 34 | 0 | 0 | NA | NA | NA | E/S/D taken for tree cutting between loc 352-353, fallen during a thunderstorm.
[5 empty] | --- | 2016-05-11 13:15 | 2016-05-11 16:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | NA | NA | NA | Emergency S/D taken for replacing damaged R-ph conductor at loc 352-353.
[5 empty] | --- | 2016-05-12 16:50 | 2016-05-12 16:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | NA | NA | NA | Heavy lightening was prevailing in the area at time of tripping
[5 empty] | --- | 2016-05-13 10:53 | 2016-05-13 11:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | NA | NA | NA | Heavy lightening was prevailing in the region at time of tripping
[5 empty] | --- | 2016-05-02 13:01 | 2016-05-02 18:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 5 | 39 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-03 00:58 | 2016-05-03 01:07 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | NA | NA | NA | lightening
[5 empty] | --- | 2016-05-02 21:05 | 2016-05-02 21:36 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | NA | NA | NA | lightening
[5 empty] | --- | 2016-05-01 03:59 | 2016-05-01 04:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | NA | NA | NA | Heavy thunderstorm reported
[5 empty] | --- | 2016-05-01 21:17 | 2016-05-01 23:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-01 23:28 | 2016-05-02 00:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-02 00:24 | 2016-05-02 00:36 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-02 12:02 | 2016-05-02 12:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | NA | NA | NA | Delay in charging due to bad weather at Kolasib end.
4 | NER L104 | AIZWAL_KUMARGHAT | 131 | North Eastern Region | --- | 2016-05-26 08:07 | 2016-05-26 18:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 10 | 9 | 0 | 0 | NA | NA | NA | S/D taken for clearing of infringemnets at loc 30,31,34,35,55,55A. |  | 100
[5 empty] | --- | 2016-05-12 18:14 | 2016-05-12 18:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | Heavy rainfall/lightening
[5 empty] | --- | 2016-05-01 21:08 | 2016-05-01 21:36 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
5 | NER L105 | AIZWAL_ZEMEBAK 2 | 6.719 | North Eastern Region | --- | 2016-05-14 09:20 | 2016-05-14 16:38 | as given in (3) | 0 | 7 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for AMP |  | 99.02
[5 empty] | --- | 2016-05-02 12:08 | 2016-05-02 14:04 | as given in (3) | 0 | 0 | 0 | 1 | 56 | 0 | 0 | 0 | 0 | NA | NA | NA | Conductor section between CB and transformer broken at state S/s.
[5 empty] | --- | 2016-05-25 19:46 | 2016-05-25 20:54 | as given in (3) | 0 | 0 | 0 | 1 | 8 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault.
[5 empty] | --- | 2016-05-10 08:40 | 2016-05-10 09:02 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault.
[5 empty] | --- | 2016-05-01 20:27 | 2016-05-02 00:14 | as given in (3) | 0 | 0 | 0 | 3 | 47 | 0 | 0 | 0 | 0 | NA | NA | NA | Wave trap sparking problem at Zemabawk end.
6 | NER L106 | BADARPUR-BADARPUR | 1.023 | North Eastern Region | --- | 2016-05-02 18:44 | 2016-05-02 19:07 | as given in (3) | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | Problem at State end. |  | 100
7 | NER L107 | BADARPUR_JIRIBAM | 67.21 | North Eastern Region | --- | 2016-05-20 16:15 | 2016-05-20 17:50 | as given in (3) | 0 | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken to attend sparking at Isolator at Jiribam S/s. |  | 99.79
[5 empty] | --- | 2016-05-27 12:05 | 2016-05-27 14:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 25 | 0 | 0 | NA | NA | NA | E/S/D taken for cutting of tree branches at loc 86 - 87.
8 | NER L108 | BADARPUR_KHLIERIAT | 76.646 | North Eastern Region | --- | 2016-05-01 21:40 | 2016-05-05 18:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 93 | 12 | 0 | 0 | NA | NA | NA | R-ph conductor snapped at loc 106-107 due to falling of large no.of big trees during a thunderstorm. |  | 99.95
[5 empty] | --- | 2016-05-14 10:39 | 2016-05-14 11:01 | as given in (3) | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Bus bar protection operrated at Khliehriat S/s while repairing of Bus Isolator
[5 empty] | --- | 2016-05-29 00:14 | 2016-05-29 00:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | NA | NA | NA | Heavy thunderstorm reported during tripping
9 | NER L109 | BADARPUR_KUMARGHAT | 118.513 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
10 | NER L110 | DIMAPUR_IMPHAL | 168.865 | North Eastern Region | --- | 2016-05-06 17:09 | 2016-05-06 17:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | NA | NA | NA | Tripped due to bamboo falling over B-ph conductor at loc 178-177 |  | 99.85
[5 empty] | --- | 2016-05-07 09:46 | 2016-05-07 12:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 51 | 0 | 0 | NA | NA | NA | E/S/D taken for clearing bamboo fallen on B-ph conductor at loc.178 due to storm.
[5 empty] | --- | 2016-05-16 16:13 | 2016-05-16 17:18 | as given in (3) | 0 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken for rectification of Y-ph CT connector at Dimpaur S/s which was sparking
11 | NER L111 | DOYANG_DIMAPUR 1 | 92.526 | North Eastern Region | --- | 2016-05-27 06:30 | 2016-05-27 12:40 | as given in (3) | 0 | 0 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken for checking of imbalance load wrt other circuit. |  | 100
[5 empty] | --- | 2016-05-28 17:27 | 2016-05-28 20:45 | as given in (3) | 0 | 0 | 0 | 3 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken by Doyang (NEEPCO).
[5 empty] | --- | 2016-05-17 12:07 | 2016-05-17 14:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 0 | NA | NA | NA | E/S/D taken for clearing bamboo leaning towards line at loc 285-286 due to a thunderstorm.
12 | NER L112 | DOYANG_DIMAPUR 2 | 92.526 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
13 | NER L113 | GOHPUR_NIRJULI | 42.5 | North Eastern Region | --- | 2016-05-14 09:20 | 2016-05-14 15:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 5 | 49 | 0 | 0 | NA | NA | NA | S/D taken for cutting of bamboo at loc 52-53, which came from uphill side due to a storm. |  | 99.16
[5 empty] | --- | 2016-05-16 10:24 | 2016-05-16 16:38 | as given in (3) | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Replacement of 145kV CB at Gohpur S/s.
[5 empty] | --- | 2016-05-18 09:10 | 2016-05-18 18:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | NA | NA | NA | Main and Transfer bus at Nirjuli S/s taken for replacement of transfer bus conductor
14 | NER L114 | IMPHAL_IMPHAL 1 | 1.5 | North Eastern Region | --- | 2016-05-15 21:28 | 2016-05-15 21:50 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to down stream fault. |  | 98.93
[5 empty] | --- | 2016-05-26 09:24 | 2016-05-26 17:22 | as given in (3) | 0 | 7 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for AMP.
15 | NER L115 | JIRIBAM_AIZWAL | 172.315 | North Eastern Region | --- | 2016-05-21 08:38 | 2016-05-21 08:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | Tripped due to lightening. |  | 100
[5 empty] | --- | 2016-05-01 22:03 | 2016-05-04 22:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 72 | 46 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-13 15:46 | 2016-05-13 15:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | Tubulent weather was prevailing in the region at time of tripping
[5 empty] | --- | 2016-05-13 16:02 | 2016-05-16 20:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 76 | 50 | 0 | 0 | NA | NA | NA | Tripped due to falling of big trees on the line at loc 146-147 from outside corridor.
16 | NER L116 | JIRIBAM_HAFLONG | 100.63 | North Eastern Region | --- | 2016-05-22 00:41 | 2016-05-22 16:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 15 | 51 | 0 | 0 | NA | NA | NA | Tripped due to fallen of a big tree on conductor at loc 14-15 caused by landslide. |  | 100
17 | NER L117 | JIRIBAM_LOKTAK 2 | 82.4 | North Eastern Region | --- | 2016-05-24 08:29 | 2016-05-24 11:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 51 | 0 | 0 | NA | NA | NA | Thunderstorm reported in the area. |  | 99.98
[5 empty] | --- | 2016-05-27 14:04 | 2016-05-27 14:14 | as given in (3) | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | transient fault
[5 empty] | --- | 2016-05-01 22:20 | 2016-05-01 22:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-12 17:39 | 2016-05-12 18:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | NA | NA | NA | Heavy lightening was prevailing in the area at time of tripping
[5 empty] | --- | 2016-05-26 10:52 | 2016-05-26 11:01 | as given in (3) | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | transient fault
[5 empty] | --- | 2016-05-25 20:23 | 2016-05-25 20:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | Thunderstorm reported in the area.
[5 empty] | --- | 2016-05-13 16:57 | 2016-05-13 17:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
18 | NER L118 | KHANDONG-HAFLONG | 63.166 | North Eastern Region | --- | 2016-05-11 11:48 | 2016-05-11 12:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | NA | NA | NA | Heavy lightening prevailing in the area at time of tripping. |  | 100
[5 empty] | --- | 2016-05-01 21:07 | 2016-05-01 21:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-29 00:18 | 2016-05-29 01:23 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | NA | NA | NA | Heavy thunderstorm reported during tripping
19 | NER L119 | KHANDONG_KHLIERIAT 1 | 42.48 | North Eastern Region | --- | 2016-05-14 10:39 | 2016-05-14 11:06 | as given in (3) | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Bus bar protection operrated at Khliehriat S/s while repairing of Bus Isolator |  | 99.94
[5 empty] | --- | 2016-05-12 11:41 | 2016-05-12 12:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | NA | NA | NA | Heavy lightening with thunderstorm was prevailing during tripping.
[5 empty] | --- | 2016-05-11 10:15 | 2016-05-11 10:34 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | Downstream fault
[5 empty] | --- | 2015-04-01 | 2015-04-06 20:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | NA | NA | NA | H/T for vol. regu. on RLDC instruction
20 | NER L120 | KHANDONG_KHLIERIAT 2 | 42.48 | North Eastern Region | --- | 2016-05-14 10:39 | 2016-05-14 11:08 | as given in (3) | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Bus bar protection operrated at Khliehriat S/s while repairing of Bus Isolator |  | 99.94
[5 empty] | --- | 2016-05-12 16:33 | 2016-05-12 16:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | Heavy lightening was prevailing in the area at time of tripping.
[5 empty] | --- | 2016-05-12 11:41 | 2016-05-12 12:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | NA | NA | NA | Heavy lightening was prevailing in the area at time of tripping
[5 empty] | --- | 2016-05-16 04:11 | 2016-05-16 04:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | NA | NA | NA | Tripped due to lightening
21 | NER L121 | KHANDONG_KOPILI 1 | 10.914 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
22 | NER L122 | KHLIERIAT_KHLIERIAT | 7.801 | North Eastern Region | --- | 2016-05-16 15:30 | 2016-05-16 16:18 | as given in (3) | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length |  | 99.93
[5 empty] | --- | 2016-05-17 11:16 | 2016-05-17 11:28 | as given in (3) | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-16 22:02 | 2016-05-16 22:30 | as given in (3) | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-16 17:38 | 2016-05-16 21:32 | as given in (3) | 0 | 0 | 0 | 3 | 54 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-11 09:53 | 2016-05-11 10:13 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-02 14:36 | 2016-05-02 14:55 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-04-30 23:41 | 2016-05-01 00:23 | as given in (3) | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-05-14 10:39 | 2016-05-14 11:10 | as given in (3) | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Bus bar protection operrated at Khliehriat S/s while repairing of Bus Isolator
[5 empty] | --- | 2016-05-01 21:42 | 2016-05-01 22:15 | as given in (3) | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-02 13:07 | 2016-05-02 13:19 | as given in (3) | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-10 18:20 | 2016-05-10 18:35 | as given in (3) | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-05-05 10:00 | 2016-05-05 10:11 | as given in (3) | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-01 22:48 | 2016-05-01 23:21 | as given in (3) | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-12 14:55 | 2016-05-12 17:48 | as given in (3) | 0 | 0 | 0 | 2 | 53 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-05-11 11:48 | 2016-05-11 12:06 | as given in (3) | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-05-11 10:39 | 2016-05-11 11:01 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-05-09 08:11 | 2016-05-09 18:45 | as given in (3) | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by state end.
[5 empty] | --- | 2016-05-16 03:50 | 2016-05-16 05:14 | as given in (3) | 0 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-05-06 09:42 | 2016-05-06 18:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | NA | NA | NA | Line H/T vide code 900. S/D taken by state.
[5 empty] | --- | 2016-05-07 09:10 | 2016-05-07 18:55 | as given in (3) | 0 | 0 | 0 | 9 | 45 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by state.
[5 empty] | --- | 2016-05-08 08:17 | 2016-05-08 18:19 | as given in (3) | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by state end.
[5 empty] | --- | 2016-05-15 20:38 | 2016-05-15 21:00 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
[5 empty] | --- | 2016-05-15 20:38 | 2016-05-15 21:00 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length
[5 empty] | --- | 2016-05-28 21:36 | 2016-05-28 22:09 | as given in (3) | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond POWERGRID's jurisdiction
[5 empty] | --- | 2016-05-28 17:53 | 2016-05-28 18:40 | as given in (3) | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond POWERGRID's jurisdiction
[5 empty] | --- | 2016-05-28 07:12 | 2016-05-28 07:53 | as given in (3) | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond POWERGRID's jurisdiction
23 | NER L123 | KUMARGHAT_R C NAGAR | 104.02 | North Eastern Region | --- | 2016-05-02 15:43 | 2016-05-02 15:50 | as given in (3) | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault at R.C.Nagar end. |  | 99.31
[5 empty] | --- | 2016-05-01 20:13 | 2016-05-01 20:47 | as given in (3) | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | Beyond line length
[5 empty] | --- |  |  |  |  | 5 | 9 | [6 empty] | NA | NA | NA
24 | NER L124 | LOKTAK_IMPHAL | 35.04 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
25 | NER L125 | SALAKATI-GELEPHUG | 49.217 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
26 | NER L126 | LEKHI-RANGANADI | 12.15 | North Eastern Region | --- | 2016-05-12 21:02 | 2016-05-12 21:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | NA | NA | NA | Turbulent weather was prevailing in the area at time of tripping. |  | 100
[5 empty] | --- | 2016-05-05 10:25 | 2016-05-05 10:35 | as given in (3) | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | D.C. problem at Ranganadi end.
[5 empty] | --- | 2016-05-23 14:00 | 2016-05-23 15:03 | as given in (3) | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken by Ranganadi(NEEPCO).
[5 empty] | --- | 2016-05-29 09:14 | 2016-05-29 15:48 | as given in (3) | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by Ranganadi (NEEPCO).
27 | NER L128 | KOLASIB-AIZAWL | 66.098 | North Eastern Region | --- | 2016-05-19 08:21 | 2016-05-19 18:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 10 | 28 | 0 | 0 | NA | NA | NA | S/D taken for clearing infringements leaning towards the line from outside. |  | 100
28 | NER L128 | KOLASIB-AIZAWL | 66.098 | North Eastern Region | --- | 2016-05-01 21:17 | 2016-05-01 22:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 27 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
29 | NER L129 | RANGANADI-ZIRO | 44.523 | North Eastern Region | --- | 2016-05-27 09:29 | 2016-05-27 16:24 | as given in (3) | 0 | 0 | 0 | 6 | 55 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by Ranganadi (NEEPCO). |  | 100
30 | NER L130 | KHANDONG_KOPILI | 11.56 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
31 | NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) | 0.347 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
32 | NER L132 | DIMAPUR(PG)-DIMAPUR(LILO PORTION) | 0.347 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
33 | NER L133 | SILCHAR-BADARPUR 1 | 19.195 | North Eastern Region | tower collapse | 2016-05-01 | 2016-06-01 | as given in (3) | 31 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 0 | NA | NA | NA
34 | NER L134 | SILCHAR-BADARPUR 2 | 19.195 | North Eastern Region | tower collapse | 2016-05-01 | 2016-05-05 17:33 | as given in (3) | 4.7313 | 0 | 0 | 0 | 0 | 113 | 33 | 0 | 0 | NA | NA | NA | Tower collapsed at loc 20 due to heavy thunderstorm |  | 100
35 | NER L135 | SILCHAR-SRIKONA 1 | 1.199 | North Eastern Region | --- | 2016-05-23 08:40 | 2016-05-23 16:00 | as given in (3) | 0 | 7 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Planned S/D taken for AMP works. |  | 99.01
[5 empty] | --- | 2016-05-12 17:11 | 2016-05-12 17:36 | as given in (3) | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | NA | NA | NA | Downstream Fault.
36 | NER L136 | SILCHAR-SRIKONA 2 | 1.199 | North Eastern Region | --- | 2016-05-25 08:58 | 2016-05-25 19:24 | as given in (3) | 0 | 10 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for CB testings and isolator alignments at Srikona end. |  | 98.6
[5 empty] | --- | 2016-05-12 17:11 | 2016-05-12 17:42 | as given in (3) | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | NA | NA | NA | Downstream Fault
37 | NER L137 | IMPHAL-IMPHAL 2 | 0.442 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
38 | NER L138 | SILCHAR-HAILAKANDI 1 | 17.3 | North Eastern Region | --- | 2016-05-02 23:15 | 2016-05-03 13:49 | as given in (3) | 0 | 0 | 0 | 14 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | Line H/T on NERLDC instructions due to unbalanced load current. |  | 100
39 | NER L139 | SILCHAR-HAILAKANDI 2 | 17.3 | North Eastern Region | --- | 2016-05-01 12:52 | 2016-05-01 15:20 | as given in (3) | 0 | 0 | 0 | 2 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D Availed by state end |  | 100
[5 empty] | --- | 2016-05-12 16:51 | 2016-05-12 18:17 | as given in (3) | 0 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line jurisdiction.
[5 empty] | --- | 2016-05-13 11:45 | 2016-05-13 11:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | Heavy rainfall/lightening
[5 empty] | --- | 2016-05-17 12:37 | 2016-05-17 12:53 | as given in (3) | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond POWERGRID's jurisdiction
40 | NER L140 | MOKOCHUNG-MOKOKCHUNG 1 | 1.4 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
41 | NER L142 | B.CHARAILI_PAVOI 1 | 12.93 | North Eastern Region | --- | 2016-05-12 20:01 | 2016-05-12 22:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 8 | 0 | 0 | NA | NA | NA | . Turbulent weather was prevailing in the area at time of tripping |  | 98.96
[5 empty] | jumper opened | 2016-05-20 11:54 | 2016-05-20 17:31 | as given in (3) | 0.23403 | 5 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.766 | E/S/D taken to attend hotspots at Y-ph Jumper at loc 52.
42 | NER L143 | B.CHARAILI_PAVOI 2 | 12.93 | North Eastern Region | --- | 2016-05-12 20:01 | 2016-05-13 16:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | NA | NA | NA | Turbulent weather was prevailing in the region at time of tripping |  | 99.18
[5 empty] | --- | 2016-05-20 11:54 | 2016-05-20 17:59 | as given in (3) | 0 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken to attend hotspots at Y-ph jumper at loc 52.
43 | NER L144 | NIRJULI-LEKHI | 9.7 | North Eastern Region | --- | 2016-05-25 09:22 | 2016-05-25 10:30 | as given in (3) | 0 | 0 | 0 | 1 | 8 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by State end. |  | 100
[5 empty] | --- | 2016-05-25 17:30 | 2016-05-25 17:46 | as given in (3) | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped at State end only
[5 empty] | --- | 2016-05-10 06:47 | 2016-05-11 11:50 | as given in (3) | 0 | 0 | 0 | 29 | 3 | 0 | 0 | 0 | 0 | NA | NA | NA | Emergency S/D taken for CT replacement by Ranganadi(NEEPCO)
[5 empty] | --- | 2016-05-18 09:12 | 2016-05-18 18:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | NA | NA | NA | Main and Transfer bus at Nirjuli S/s taken for replacement of Transfer Bus conductor
[5 empty] | --- | 2016-05-23 14:00 | 2016-05-23 15:13 | as given in (3) | 0 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken by Ranganadi (NEEPCO)
44 | NER L201 | BALIPARA_TEZPUR | 8.623 | North Eastern Region | --- | 2016-05-12 04:06 | 2016-05-12 04:29 | as given in (3) | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm and lightening |  | 100
[5 empty] | --- | 2016-05-07 09:28 | 2016-05-07 20:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47 | NA | NA | NA | 220kV Bus S/D taken for connecting ICT-II Bay (new installation).
[5 empty] | --- | 2016-05-26 04:06 | 2016-05-26 13:35 | as given in (3) | 0 | 0 | 0 | 9 | 29 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond jurisdiction.
45 | NER L202 | KATHALGURI_MARIANI(OLD) | 162.864 | North Eastern Region | --- | 2016-05-17 13:20 | 2016-05-17 16:30 | as given in (3) | 0 | 0 | 0 | 3 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken for repairing of CB at Mariani(ASEB) |  | 100
[5 empty] | --- | 2016-05-12 09:30 | 2016-05-12 16:21 | as given in (3) | 0 | 0 | 0 | 6 | 51 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by Kathalguri(NEEPCO) for commissiong
46 | NER L203 | MISA_DIMAPUR 1 | 123.52 | North Eastern Region | --- | 2016-05-10 08:15 | 2016-05-10 16:44 | as given in (3) | 0 | 8 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for conductor reparing and jumper tightening. |  | 97.57
[5 empty] | --- | 2015-04-18 16:49 | 2015-04-18 16:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | NA | NA | NA | STORM WITH LIGHTENING WAS PREVAILED DURING LIGHTENING
[5 empty] | jumper opened | 2016-05-04 02:06 | 2016-05-04 11:42 | as given in (3) | 0.4 | 9 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.6 | Jumper opened at Loc 353.
47 | NER L204 | MISA_DIMAPUR 2 | 123.52 | North Eastern Region | --- | 2016-05-11 08:19 | 2016-05-11 16:10 | as given in (3) | 0 | 7 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for jumper tightening works. |  | 98.94
48 | NER L205 | MISA_KATHALGURI | 382.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
49 | NER L206 | MISA-KOPILI 1 | 72.791 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
50 | NER L207 | MISA_KOPILI 2 | 72.791 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
51 | NER L208 | MISA_KOPILI 3 | 75.788 | North Eastern Region | --- | 2016-05-17 11:03 | 2016-05-17 11:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | Big tree cut by miscreants fell on the line |  | 100
52 | NER L209 | MISA_MARIANI(OLD) | 220 | North Eastern Region | --- | 2016-05-16 08:57 | 2016-05-16 14:53 | as given in (3) | 0 | 5 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for corona ring adjustments |  | 99.2
53 | NER L210 | MISA_SAMAGURI 1 | 34.439 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
54 | NER L211 | MISA_SAMAGURI 2 | 34.439 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
55 | NER L212 | SALAKATI_BTPS 2 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
56 | NER L213 | SALAKATI-BTPS 1 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
57 | NER L214 | MISA-MARIANI(NEW) | 222.682 | North Eastern Region | --- | 2016-05-01 19:31 | 2016-05-01 20:19 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | NA | NA | NA | Thunderstorm reported at N.Mariani end |  | 100
58 | NER L215 | KATHALGURI-MARIANI(NEW) | 160.536 | North Eastern Region | --- | 2016-05-11 09:37 | 2016-05-11 14:04 | as given in (3) | 0 | 0 | 0 | 4 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by Kathalguri(NEEPCO) for commissiong works. |  | 100
59 | NER L216 | MARIANI_MOKUKCHUNG 1 | 48.8 | North Eastern Region | --- | 2016-04-22 23:14 | 2016-05-20 18:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 42 | NA | NA | NA | Over Voltage |  | 100
60 | NER L217 | MARIANI_MOKUKCHUNG 2 | 48.8 | North Eastern Region | --- | 2016-05-20 19:43 | 2016-05-23 08:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 11 | NA | NA | NA | Line H/T vide code 1226 |  | 100
[5 empty] | --- | 2016-05-01 01:01 | 2016-05-03 19:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 66 | 13 | 0 | 0 | NA | NA | NA | Tripped due to over-voltage
61 | NER L401 | BALIPARA_BONGAIGAON 1 | 289.721 | North Eastern Region | --- | 2016-05-28 09:02 | 2016-05-28 09:08 | as given in (3) | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | mal operation |  | 99.71
[5 empty] | --- | 2016-05-18 15:25 | 2016-05-18 18:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 29 | NA | NA | NA | Line kept open as per NERLDC instruction
[5 empty] | --- | 2016-05-18 13:21 | 2016-05-18 15:25 | as given in (3) | 0 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken at Bongaigaon S/s to attend oil leakage in Y-ph CT
[5 empty] | --- | 2016-05-23 03:24 | 2016-05-23 08:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31 | NA | NA | NA | Line H/T vide code 1247
62 | NER L402 | BALIPARA_BONGAIGAON 2 | 289.721 | North Eastern Region | --- | 2016-05-28 09:02 | 2016-05-28 09:08 | as given in (3) | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | mal operation |  | 99.99
63 | NER L403 | MISA_BALIPARA 1 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
64 | NER L404 | MISA-BALIPARA 2 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
65 | NER L405 | BONGAIGAON-MALDA 1 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
66 | NER L406 | BONGAIGAON-MALDA 2 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
67 | NER L407 | BALIPARA-RANGANADI 1 | 166.335 | North Eastern Region | --- | 2015-04-27 22:58 | 2015-04-28 17:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | NA | NA | NA | H/T for vol. regu. on RLDC instruction |  | 100
68 | NER L408 | BALIPARA-RANGANADI 2 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
69 | NER L409 | PALLATANA-SURAJMANINAGAR 1 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
70 | NER L410 | PALLATANA-SURAJMANINAGAR 2 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
71 | NER L411 | BTPS-BONGAIGAON 1 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
72 | NER L412 | BTPS-BONGAIGAON 2 | 3.119 | North Eastern Region | --- | 2016-05-22 09:57 | 2016-05-22 12:32 | as given in (3) | 0 | 2 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for testing of DPR |  | 99.65
73 | NER L413 | BALIPARA-BONGAIGAON 3 | 309 | North Eastern Region | --- | 2016-05-14 21:22 | 2016-05-17 18:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 25 | NA | NA | NA | Line H/T vide code 1100 |  | 98.98
[5 empty] | --- | 2016-05-21 22:25 | 2016-05-22 18:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | NA | NA | NA | Line H/T vide code 1238
[5 empty] | --- | 2016-05-09 16:54 | 2016-05-10 15:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 36 | NA | NA | NA | Line kept open as per NERLDC instruction.
[5 empty] | --- | 2016-05-28 09:00 | 2016-05-28 22:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 59 | NA | NA | NA | Line H/T vide code 1363.
[5 empty] | --- | 2016-05-21 09:33 | 2016-05-21 19:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 30 | NA | NA | NA | Line H/T vide code 1232.
[5 empty] | --- | 2016-05-23 08:38 | 2016-05-23 21:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | NA | NA | NA | Line H/T vide code 1253
[5 empty] | --- | 2016-05-24 04:02 | 2016-05-24 19:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 54 | NA | NA | NA | Line H/T vide code 1272.
[5 empty] | --- | 2016-05-25 09:36 | 2016-05-26 18:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 56 | NA | NA | NA | Line H/T vide code 1339.
[5 empty] | --- | 2016-04-30 00:20 | 2016-05-05 19:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 41 | NA | NA | NA | Line H/T vide code 751
[5 empty] | --- | 2016-05-05 23:37 | 2016-05-06 11:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | NA | NA | NA | Line H/T vide code 899
[5 empty] | --- | 2016-05-06 11:55 | 2016-05-06 18:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 6 | 13 | 0 | 0 | NA | NA | NA | E/S/D taken to perform rectification works. Conductor theft by miscreants b/w loc 477-478.
[5 empty] | --- | 2016-05-29 06:29 | 2016-05-29 18:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 11 | NA | NA | NA | Line H/T vide code 1378.
[5 empty] | --- | 2016-05-07 22:42 | 2016-05-08 20:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | NA | NA | NA | Line H/T vide code 936
[5 empty] | --- | 2016-05-08 23:16 | 2016-05-09 09:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | NA | NA | NA | Line H/T vide code 948
[5 empty] | --- | 2016-05-09 09:20 | 2016-05-09 16:54 | as given in (3) | 0 | 7 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Planned S/D taken for collecting oil sample at Bongaigaon S/s
[5 empty] | --- | 2016-05-12 00:20 | 2016-05-14 19:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 4 | NA | NA | NA | Line H/T vide code 1017
[5 empty] | --- | 2016-05-17 20:04 | 2016-05-18 13:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | NA | NA | NA | Line H/T vide code 1177
[5 empty] | --- | 2016-05-18 23:10 | 2016-05-19 18:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | NA | NA | NA | Line H/T vide code 1198
[5 empty] | --- | 2016-05-19 23:30 | 2016-05-20 19:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | NA | NA | NA | Line H/T vide code 1211
[5 empty] | --- | 2016-05-06 22:15 | 2016-05-07 19:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | NA | NA | NA | Line H/T vide code 915
74 | NER L414 | BALIPARA-BONGAIGAON 4 | 309 | North Eastern Region | --- | 2016-05-28 09:02 | 2016-05-28 09:09 | as given in (3) | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | mal operation |  | 99.98
[5 empty] | --- | 2016-05-11 00:04 | 2016-05-11 18:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | NA | NA | NA | Line H/T vide code 992
75 | NER L415 | SILCHAR-IMPHAL 1 | 167 | North Eastern Region | --- | 2016-05-06 10:50 | 2016-05-06 16:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55 | NA | NA | NA | S/D taken for OPGW works |  | 100
[5 empty] | --- | 2016-05-04 09:28 | 2016-05-04 09:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | NA | NA | NA | Tripped due to heavy thunderstorm.
[5 empty] | --- | 2016-05-27 08:37 | 2016-05-27 17:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 58 | NA | NA | NA | S/D taken for OPGW works.
[5 empty] | --- | 2016-05-12 18:55 | 2016-05-12 19:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | NA | NA | NA | Heavy rainfall/Lightening
[5 empty] | --- | 2016-05-25 08:22 | 2016-05-25 18:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | NA | NA | NA | S/D taken for OPGW works.
[5 empty] | --- | 2016-05-26 08:22 | 2016-05-26 19:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2 | NA | NA | NA | S/D taken for OPGW works.
[5 empty] | --- | 2016-05-23 08:05 | 2016-05-23 18:11 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | NA | NA | NA | S/D taken for OPGW works.
76 | NER L416 | SILCHAR-IMPHAL 2 | 167 | North Eastern Region | --- | 2016-05-07 08:51 | 2016-05-07 17:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 47 | 0 | 0 | NA | NA | NA | S/D taken for clearing of line infringements caused by storm. |  | 100
77 | NER L417 | BALIPARA_B.CHAIRALI 3 | 57.294 | North Eastern Region | --- | 2016-05-09 18:17 | 2016-05-09 19:19 | as given in (3) | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | At same time HVDC pole 1 tripped due to filter differential protection operation at BNC. |  | 99.86
78 | NER L418 | BALIPARA_B.CHAIRALI 4 | 57.294 | North Eastern Region | --- | 2016-05-09 18:17 | 2016-05-09 18:36 | as given in (3) | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Due to filter differential protection operation at B'Chariali S/s. |  | 99.96
79 | NER L419 | B.CHAIRALI_RANGANADI 1 | 129.335 | North Eastern Region | --- | 2016-05-24 23:02 | 2016-05-25 18:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | NA | NA | NA | Line H/T vide code 1284. |  | 100
[5 empty] | --- | 2016-05-28 23:42 | 2016-05-29 18:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 24 | NA | NA | NA | Line H/T vide code 1377.
[5 empty] | --- | 2016-05-27 23:53 | 2016-05-28 18:44 | as given in (3) | 0 | 18 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Line H/T vide code 1361.
[5 empty] | --- | 2016-05-26 23:00 | 2016-05-27 18:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | NA | NA | NA | Line H/T vide code 1343.
[5 empty] | --- | 2016-05-21 08:05 | 2016-05-21 15:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 30 | NA | NA | NA | Line taken into S/D for shifting of vulnerable tower at loc 66 on pile foundation.
[5 empty] | --- | 2016-05-09 18:17 | 2016-05-09 19:44 | as given in (3) | 0 | 0 | 0 | 1 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | Generation failure at Ranganadi end.
[5 empty] | --- | 2016-05-23 15:18 | 2016-05-23 17:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 56 | NA | NA | NA | Line kept open on NERLDC instructions.
[5 empty] | --- | 2016-05-23 06:51 | 2016-05-23 15:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 27 | 0 | 0 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation
[5 empty] | --- | 2016-05-21 23:49 | 2016-05-22 19:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | NA | NA | NA | Line H/T vide code 1239
[5 empty] | --- | 2016-05-20 22:50 | 2016-05-21 08:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | NA | NA | NA | Line H/T vide code 1227
80 | NER L420 | B.CHAIRALI_RANGANADI 2 | 129.335 | North Eastern Region | --- | 2016-05-24 00:07 | 2016-05-24 18:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 54 | NA | NA | NA | Line H/T vide code 1269 |  | 100
[5 empty] | --- | 2016-05-02 16:56 | 2016-05-02 17:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | NA | NA | NA | Line kept open on NERLDC instructions
[5 empty] | --- | 2016-05-02 07:33 | 2016-05-02 16:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 23 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation
[5 empty] | --- | 2016-05-02 23:42 | 2016-05-03 18:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 53 | NA | NA | NA | Line H/T vide code 859
[5 empty] | --- | 2016-05-01 17:07 | 2016-05-01 18:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | NA | NA | NA | Line kept open as per NERLDC instructions
[5 empty] | --- | 2016-04-30 23:54 | 2016-05-01 08:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | NA | NA | NA | Line H/T vide code 773
[5 empty] | --- | 2016-05-01 08:03 | 2016-05-01 17:07 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation.
[5 empty] | --- | 2016-05-01 22:57 | 2016-05-02 07:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 36 | NA | NA | NA | Line H/T vide code 820
[5 empty] | --- | 2016-05-01 08:03 | 2016-05-01 17:07 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation
[5 empty] | --- | 2016-05-04 00:18 | 2016-05-04 08:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 46 | NA | NA | NA | Line H/T vide code 874
[5 empty] | --- | 2016-05-14 07:51 | 2016-05-14 17:27 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 36 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation
[5 empty] | --- | 2016-05-04 08:04 | 2016-05-04 17:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 24 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation
[5 empty] | --- | 2016-05-04 23:41 | 2016-05-05 07:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 56 | NA | NA | NA | Line H/T vide code 884
[5 empty] | --- | 2016-05-05 07:37 | 2016-05-05 18:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation
[5 empty] | --- | 2016-05-05 22:16 | 2016-05-06 17:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | NA | NA | NA | Line H/T vide 898
[5 empty] | --- | 2016-05-07 00:11 | 2016-05-07 17:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | NA | NA | NA | Line H/T vide code 916
[5 empty] | --- | 2016-05-08 00:01 | 2016-05-08 17:23 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | NA | NA | NA | Line H/T vide code 937.
[5 empty] | --- | 2016-05-08 22:52 | 2016-05-09 07:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 58 | NA | NA | NA | Line H/T vide code 947
[5 empty] | --- | 2016-05-09 07:50 | 2016-05-12 18:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation.
[5 empty] | --- | 2016-05-14 00:05 | 2016-05-14 07:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 46 | NA | NA | NA | Line H/T vide code 1068
[5 empty] | --- | 2016-05-14 21:34 | 2016-05-15 17:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 43 | NA | NA | NA | Line H/T vide code 1099
[5 empty] | --- | 2016-05-16 00:06 | 2016-05-16 18:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | NA | NA | NA | Line H/T vide code 1113
[5 empty] | --- | 2016-05-17 04:08 | 2016-05-17 07:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | NA | NA | NA | Line H/T vide code 1155
[5 empty] | --- | 2016-05-17 07:54 | 2016-05-17 16:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 57 | NA | NA | NA | S/D taken for shifting of vulnerable tower at loc 66 on pile foundation
[5 empty] | --- | 2016-05-17 23:17 | 2016-05-18 11:41 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | NA | NA | NA | Line H/T vide code 1178
[5 empty] | --- | 2016-05-19 09:42 | 2016-05-19 13:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | NA | NA | NA | E/S/D taken for dismantling of existing tower at loc 66.
[5 empty] | --- | 2016-05-13 00:07 | 2016-05-13 17:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | NA | NA | NA | Line H/T vide code 1052
81 | NER L421 | BALIPARA_B.CHAIRALI 1 | 59.54 | North Eastern Region | --- | 2016-05-02 01:52 | 2016-05-09 18:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 56 | NA | NA | NA | Line H/T vide code 828 |  | 100
[5 empty] | --- | 2016-05-12 09:23 | 2016-05-14 09:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 29 | NA | NA | NA | Line H/T vide code 1022
82 | NER L422 | BALIPARA_B.CHAIRALI 2 | 59.54 | North Eastern Region | --- | 2016-05-14 08:34 | 2016-05-19 19:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 55 | NA | NA | NA | Line H/T vide code 1074 |  | 100
83 | NER L423 | SILCHAR-PURBAKANCHANBARI 1 | 127.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
84 | NER L424 | SILCHAR-PURBAKANCHANBARI 2 | 127.2 | North Eastern Region | jumper opened | 2016-05-09 09:33 | 2016-05-09 18:21 | as given in (3) | 0.36667 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.6333 | Y-ph Jumper opened at Loc 166. |  | 98.82
[5 empty] | --- | 2016-05-09 18:21 | 2016-05-09 22:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 11 | NA | NA | NA | Line kept open under NERLDC instructions.
85 | NER RBR1 | BR_BONGAIGAON (50MVAR) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
86 | NER RBR2 | BR_BONGAIGAON (50MVAR) 2 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
87 | NER RBR3 | BR_BALIPARA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
88 | NER RBR4 | BR_MISA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
89 | NER RBR5 | BR_KUMARGHAT (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
90 | NER RBR6 | BR_AIZWAL (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
91 | NER RBR7 | BR_BONGAIGAON(80MVAR) 3 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
92 | NER RBR8 | BR_BALIPARA(80MVAR) 2 | 80 | North Eastern Region | --- | 2016-05-23 08:59 | 2016-05-23 16:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 57 | NA | NA | NA | S/D taken for statutory test as per approval of OCC |  | 100
93 | NER RBR9 | BR_SILCHAR(63MVAR) 1 | 63 | North Eastern Region | --- | 2016-05-12 08:18 | 2016-05-12 14:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | NA | NA | NA | S/D taken for statutory test as per approval of OCC |  | 100
94 | NER RBR10 | BR_SILCHAR(63MVAR) 2 | 63 | North Eastern Region | --- | 2016-05-20 10:30 | 2016-05-20 12:58 | as given in (3) | 0 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken to attend hotspots at jumper dropper. |  | 99.67
95 | NER RBR11 | BR_BONGAIGAON(80MVAR) 4 | 80 | North Eastern Region | --- | 2016-05-10 10:10 | 2016-05-10 13:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | NA | NA | NA | S/D taken for statutory test as per approval of OCC |  | 100
[5 empty] | --- | 2016-06-08 18:51 | 2016-06-30 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533 | 8 | NA | NA | NA | UPGRADATION OF BUSHING WITH RIP.
96 | NER TICT1 | ICT_SILCHAR (200MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
97 | NER ICT2 | ICT_BALIPARA (315MVA) 1 | 315 | North Eastern Region | --- | 2016-05-09 10:01 | 2016-05-09 12:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 44 | NA | NA | NA | To facilitate movement of trailer loaded with Bongaigaon -2 Reactor under ICT-1, for safety purposes |  | 100
98 | NER TICT4 | ICT_SALAKATI (50 MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
99 | NER TICT5 | ICT_DIMAPUR (100 MVA) 1 | 100 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
100 | NER TICT6 | ICT_KUMARGHAT(5MVA) | 5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
101 | NER TICT7 | ICT_NIRJULI(16MVA) 1 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
102 | NER TICT8 | ICT_NIRJULI(10MVA) 2 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
103 | NER TICT10 | ICT_ZIRO (15MVA) | 15 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
104 | NER TICT11 | ICT_NIRJULI (16MVA) 2 | 16 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
105 | NER TICT12 | ICT_KOPILI (160 MVA) 2 | 160 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
106 | NER TICT14 | ICT_MISA 1 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
107 | NER ICT15 | ICT_SILCHAR(200MVA) 1 | 200 | North Eastern Region | --- | 2016-05-16 08:25 | 2016-05-16 16:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 31 | NA | NA | NA | S/D taken for AMP works as approved in OCC for statutory test |  | 100
[5 empty] | --- | 2016-05-14 08:18 | 2016-05-14 15:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 32 | NA | NA | NA | S/D taken for AMP as per approval of OCC
108 | NER ICT16 | ICT_SILCHAR(200MVA) 2 | 200 | North Eastern Region | --- | 2016-05-18 10:38 | 2016-05-18 15:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18 | NA | NA | NA | S/D taken for AMP as per approval of OCC |  | 100
109 | NER ICT17 | ICT_BONGAIGAON(315MVA) | 315 | North Eastern Region | --- | 2016-05-26 11:50 | 2016-05-26 12:25 | as given in (3) | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for ICT Change over of units. |  | 99.92
110 | NER TICT18 | ICT_MISA 2 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
111 | NER TICT19 | ICT_MOKOKCHUNG(30MVA) 1 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
112 | NER TICT20 | ICT_MOKOKCHUNG(30MVA) 2 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
113 | NER ICT21 | ICT_B.CHAIRALI(200MVA) 1 | 200 | North Eastern Region | --- | 2016-05-09 14:40 | 2016-05-09 16:08 | as given in (3) | 0 | 1 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken for arresting oil leakage detected in the ICT |  | 99.8
114 | NER TICT22 | ICT_B'CHARIALI (200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
115 | NER TICT23 | ICT_NIRJULI(50MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
116 | NER ICT24 | ICT_MOKUKCHUNG(3*10MVA) 2 | 30 | North Eastern Region | --- | 2016-05-27 11:02 | 2016-05-27 12:40 | as given in (3) | 0 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 0 | NA | NA | NA | HV Side tripped on downstream fault |  | 100
|  |  |  | North Eastern Region |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | 100

## JUNE
S/No | Unique ID of Transmission Element | Element Name | Description (Length-km/Nos./MVA/ MVAr/MW/ etc. | Region | Type of failure | Outage Date & Time Hr Mn | Restoration Date & Time Hr Mn | Details of outage ( No. of Towers damaged, no. of insulators failed etc.) | Total Outage (in Days) (1) | Duration of Outage attribuatable to | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual & Norm (1 - 2) | Detailed Reason for Outage (3) | Outage certifying Agency & Reference Document | % Availability as certified by certifying agency
[10 empty] | ISTS Licensee Hr Min |  | Others Hr Min |  | System Constraint/ Natural calamity/ Milliitancy Hr Min |  | Deemed Available Hr Min
JUNE' 2016
1 | NER L101 | RCN_AGARTALA 1 | 8.384 | North Eastern Region | --- | 2016-06-27 13:16 | 2016-06-27 14:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | NA | NA | NA | KEPT OPEN DUE TO VOLTAGE CONSTRAINT. | NERPC | 99.66
[5 empty] | --- | 2016-06-27 10:48 | 2016-06-27 13:16 | as given in (3) | 0 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR RECTIFICATION OF R-PH ISOLATOR AT AGARTALA STATE S/S.
2 | NER L102 | RCN_AGARTALA 2 | 8.384 | North Eastern Region | --- | 2016-06-27 11:08 | 2016-06-27 17:22 | as given in (3) | 0 | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERLOAD AT RCNAGAR END (CHARGING DELAYED DUE TO CB PROBLEM AT RC NAGAR (NEEPCO )). |  | 100
3 | NER L103 | BADARPUR_KOLASIB | 107.226 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
3 | NER L104 | AIZWAL_KUMARGHAT | 131 | North Eastern Region | --- | 2016-06-27 15:36 | 2016-06-27 17:50 | as given in (3) | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS FAULT OCCURRED DUE TO FLASH OVER OF B-PH INSULATOR STRING OF MAIN BUS AT AIZWAL. |  | 99.69
4 | NER L105 | AIZWAL_ZEMEBAK 2 | 6.719 | North Eastern Region | --- | 2016-06-04 18:32 | 2016-06-04 18:55 | as given in (3) | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault. |  | 100
5 | NER L106 | BADARPUR-BADARPUR | 1.023 | North Eastern Region | --- | 2016-06-14 23:23 | 2016-06-14 23:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | NA | NA | NA | SPS I & II operated at Silchar due to Pallatana Generation tripped. |  | 100
|  |  | 1.023 | North Eastern Region | --- | 2016-06-15 00:46 | 2016-06-15 00:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | NA | NA | NA | H/T for load regulation on RLDC instruction.
6 | NER L109 | BADARPUR_KUMARGHAT | 118.513 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
7 | NER L110 | DIMAPUR_IMPHAL | 168.865 | North Eastern Region | --- | 2016-06-24 09:00 | 2016-06-24 16:41 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 7 | 41 | 0 | 0 | NA | NA | NA | S/D taken for replacement of insulators damaged due to lightening at loc 154, 157 and 195. |  | 100
8 | NER L111 | DOYANG_DIMAPUR 1 | 92.526 | North Eastern Region | --- | 2016-06-13 19:00 | 2016-06-13 19:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | NA | NA | NA | Bad weather reported. |  | 100
[5 empty] | --- | 2016-06-29 10:14 | 2016-06-29 10:33 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | Problem at Doyang end.
[5 empty] | --- | 2016-06-14 20:32 | 2016-06-16 15:00 | as given in (3) | 0 | 0 | 0 | 42 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | Emergency S/D taken by state end.
9 | NER L112 | DOYANG_DIMAPUR 2 | 92.526 | North Eastern Region | --- | 2016-06-13 19:00 | 2016-06-13 19:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | NA | NA | NA | Bad weather reported in the region. |  | 100
[5 empty] | --- | 2016-06-29 10:14 | 2016-06-29 10:52 | as given in (3) | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | NA | NA | NA | Problem at Doyang end.
10 | NER L113 | GOHPUR_NIRJULI | 42.5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
11 | NER L114 | IMPHAL_IMPHAL 1 | 1.5 | North Eastern Region | --- | 2016-06-30 04:11 | 2016-06-30 04:24 | as given in (3) | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault in 132kV Kareng Feeder. |  | 100
[5 empty] | --- | 2016-06-28 10:44 | 2016-06-28 11:15 | as given in (3) | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due downstream faultin 132kV Kareng feeder.
12 | NER L115 | JIRIBAM_AIZWAL | 172.315 | North Eastern Region | --- | 2016-06-27 15:36 | 2016-06-27 16:08 | as given in (3) | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS FAULT OCCURRED DUE TO FLASH OVER OF B-PH INSULATOR STRING OF MAIN BUS AT AIZWAL. |  | 99.93
[5 empty] | --- | 2016-06-12 08:03 | 2016-06-16 16:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 104 | 19 | 0 | 0 | NA | NA | NA | Rectification of tower loc. No. 80, damage caused due to slide.
13 | NER L116 | JIRIBAM_HAFLONG | 100.63 | North Eastern Region | --- | 2016-06-28 13:45 | 2016-06-28 14:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | NA | NA | NA | Thunderstorm was reported in the region. |  | 98.84
[5 empty] | --- | 2016-06-27 12:02 | 2016-06-27 20:21 | as given in (3) | 0 | 8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR Y-PH. JUMPER OPENED AT LOC. 121.
14 | NER L117 | JIRIBAM_LOKTAK 2 | 82.4 | North Eastern Region | --- | 2016-06-21 11:40 | 2016-06-21 11:59 | as given in (3) | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Transient fault |  | 99.89
[5 empty] | --- | 2016-06-26 01:14 | 2016-06-26 01:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | Thunderstorm reported at Jiribam.
[5 empty] | --- | 2016-06-26 01:35 | 2016-06-26 01:59 | as given in (3) | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | NA | NA | NA | Line Kept open due to problem at Loktak end.
15 | NER L118 | KHANDONG-HAFLONG | 63.166 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
16 | NER L119 | KHANDONG_KHLIERIAT 1 | 42.48 | North Eastern Region | --- | 2016-06-21 05:22 | 2016-06-21 07:34 | as given in (3) | 0 | 0 | 0 | 2 | 12 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped at Khangdong end only. No relay at Khangdong S/s |  | 100
17 | NER L120 | KHANDONG_KHLIERIAT 2 | 42.48 | North Eastern Region | --- | 2016-06-22 10:12 | 2016-06-22 18:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | NA | NA | NA | S/D taken for insulator replacement works at loc 31 & 52 which failed due to lightening. |  | 100
18 | NER L121 | KHANDONG_KOPILI 1 | 10.914 | North Eastern Region | --- | 2016-06-12 12:20 | 2016-06-12 12:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | NA | NA | NA | Inclement weather reported. |  | 100
19 | NER L122 | KHLIERIAT_KHLIERIAT | 7.801 | North Eastern Region | --- | 2016-06-06 11:36 | 2016-06-06 12:04 | as given in (3) | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | BEYOND LINE LENGTH |  | 100
[5 empty] | --- | 2016-06-09 00:45 | 2016-06-09 01:05 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | tripped at state end only.
[5 empty] | --- | 2016-06-26 16:52 | 2016-06-26 17:15 | as given in (3) | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length.
20 | NER L123 | KUMARGHAT_R C NAGAR | 104.02 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
21 | NER L124 | LOKTAK_IMPHAL 2 | 35.04 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
22 | NER L125 | SALAKATI-GELEPHUG | 49.217 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
23 | NER L126 | LEKHI-RANGANADI | 12.15 | North Eastern Region | --- | 2016-06-16 17:20 | 2016-06-16 17:40 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to overloading. |  | 100
24 | NER L127 | KOLASIB-AIZAWL | 66.098 | North Eastern Region | --- | 2016-06-27 15:36 | 2016-06-27 16:18 | as given in (3) | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS FAULT OCCURRED DUE TO FLASH OVER OF B-PH INSULATOR STRING OF MAIN BUS AT AIZWAL. |  | 99.9
25 | NER L129 | RANGANADI-ZIRO | 44.523 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
26 | NER L130 | KHANDONG_KOPILI 2 | 11.56 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
27 | NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) | 0.347 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
28 | NER L132 | DIMAPUR(PG)-DIMAPUR(LILO PORTION) | 0.347 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
29 | NER L133 | SILCHAR-BADARPUR 1 | 19.195 | North Eastern Region | tower collapsed | 2016-06-01 | 2016-06-06 20:03 | as given in (3) | 5.8354 | 0 | 0 | 0 | 0 | 140 | 3 | 0 | 0 | NA | NA | NA | TOWER COLLAPSED AT LOC 20. LINE IS PUT UNDER E/S/D |  | 100
[5 empty] | --- | 2016-06-07 12:45 | 2016-06-07 18:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF CKT II ON NEW TOWER AT LOC 20
[5 empty] | --- | 2016-06-08 08:38 | 2016-06-08 14:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF CKT II AT NEW TOWER AT LOC 20
30 | NER L134 | SILCHAR-BADARPUR 2 | 19.195 | North Eastern Region | --- | 2016-06-07 12:46 | 2016-06-07 18:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF CKTII ON NEW TOWER AT LOC 20 |  | 100
[5 empty] | --- | 2016-06-08 08:37 | 2016-06-08 14:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF CKT II ON NEW TOWER AT LOC 20
31 | NER L135 | SILCHAR-SRIKONA 1 | 1.199 | North Eastern Region | --- | 2016-06-14 23:23 | 2016-06-14 23:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | NA | NA | NA | SPS I & II operated at Silchar due to Pallatana Generation tripped. |  | 100
32 | NER L136 | SILCHAR-SRIKONA 2 | 1.199 | North Eastern Region | --- | 2016-06-14 23:23 | 2016-06-14 23:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | NA | NA | NA | SPS I & II operated at Silchar due to Pallatana Generation tripped. |  | 100
33 | NER L137 | IMPHAL-IMPHAL 2 | 0.442 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
34 | NER L138 | SILCHAR-HAILAKANDI 1 | 17.3 | North Eastern Region | --- | 2016-06-14 23:23 | 2016-06-14 23:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | NA | NA | NA | SPS I & II operated at Silchar due to Pallatana Generation tripped. |  | 99.31
[5 empty] | --- | 2016-06-13 11:17 | 2016-06-13 16:15 | as given in (3) | 0 | 4 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Planned S/D taken for AMP works.
35 | NER L139 | SILCHAR-HAILAKANDI 2 | 17.3 | North Eastern Region | --- | 2016-06-18 12:05 | 2016-06-18 16:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 43 | NA | NA | NA | Emergency S/D taken by State end. |  | 99.75
[5 empty] | --- | 2016-06-14 09:08 | 2016-06-14 17:51 | as given in (3) | 0 | 0 | 0 | 8 | 43 | 0 | 0 | 0 | 0 | NA | NA | NA | Planned S/D taken by state end.
[5 empty] | --- | 2016-06-10 16:02 | 2016-06-10 17:48 | as given in (3) | 0 | 1 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Emergency S/D taken for clearing of bamboos & tree branches.
36 | NER L140 | MOKOCHUNG-MOKOKCHUNG 1 | 1.4 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
37 | NER L142 | B.CHARAILI_PAVOI 1 | 12.93 | North Eastern Region | --- | 2016-06-17 08:09 | 2016-06-17 17:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 51 | 0 | 0 | NA | NA | NA | S/D taken for jumper tightening in lieu of increasing loadability of the line. |  | 100
[5 empty] | --- | 2016-06-16 08:08 | 2016-06-16 17:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 9 | 36 | 0 | 0 | NA | NA | NA | S/D taken for jumper tightening in lieu of increasing loadability of the line.
[5 empty] | --- | 2016-06-18 08:45 | 2016-06-18 16:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 12 | 0 | 0 | NA | NA | NA | S/D taken for jumper tightening in view of increasing loadability of the T/L.
38 | NER L143 | B.CHARAILI_PAVOI 2 | 12.93 | North Eastern Region | --- | 2016-06-20 07:09 | 2016-06-20 16:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 52 | 0 | 0 | NA | NA | NA | S/D taken for jumper tightening in view of inceasing loadability of the line. |  | 100
[5 empty] | --- | 2016-06-19 07:19 | 2016-06-19 16:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 9 | 39 | 0 | 0 | NA | NA | NA | S/D taken for jumper tighening in view of loadability of the T/L.
39 | NER L144 | NIRJULI-LEKHI | 9.7 | North Eastern Region | --- | 2016-06-14 14:45 | 2016-06-14 15:04 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | R-ph CB pole of 33kV AP-4 feeder blasted at Nirjuli S/s. |  | 100
[5 empty] | --- | 2016-06-05 02:14 | 2016-06-05 02:28 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped only at Lekhi end.
40 | NER L201 | BALIPARA_TEZPUR | 8.623 | North Eastern Region | --- | 2015-04-27 06:02 | 2015-04-27 07:14 | as given in (3) | 0 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND PGCIL JURISDICTION |  | 100
[5 empty] | --- | 2016-01-01 | 2016-01-05 12:51 | as given in (3) | 0 | 0 | 0 | 108 | 51 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D Availed by state (LILO portion at Sonabil taken in to service)
41 | NER L202 | KATHALGURI_MARIANI(OLD) | 162.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
42 | NER L203 | MISA_DIMAPUR 1 | 123.52 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
43 | NER L204 | MISA_DIMAPUR 2 | 123.52 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
44 | NER L205 | MISA_KATHALGURI | 382.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
45 | NER L206 | MISA-KOPILI 1 | 72.791 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
46 | NER L207 | MISA_KOPILI 2 | 72.791 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
47 | NER L208 | MISA_KOPILI 3 | 75.788 | North Eastern Region | --- | 2016-06-01 00:01 | 2016-06-30 23:59 | as given in (3) | 0 | 0 | 0 | 719 | 58 | 0 | 0 | 0 | 0 | NA | NA | NA | Emergency S/D taken by Kopili to attend CB Problem (NEEPCO). |  | 100
48 | NER L209 | MISA_MARIANI(OLD) | 220 | North Eastern Region | --- | 2016-06-27 11:15 | 2016-06-27 11:29 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED ON UNDER FREQUENCY DUE TO PROBLEM AT KATHALGURI GENERATION END(NEEPCO). |  | 100
49 | NER L210 | MISA_SAMAGURI 1 | 34.439 | North Eastern Region | --- | 2016-06-14 08:56 | 2016-06-14 15:44 | as given in (3) | 0 | 6 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Annual Maintainenance of bay of 220kV Misa#1 bay at Samaguri S/s. |  | 98.92
50 | NER L211 | MISA_SAMAGURI 2 | 34.439 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
51 | NER L212 | SALAKATI_BTPS 2 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
52 | NER L213 | SALAKATI-BTPS 1 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
53 | NER L214 | MISA-MARIANI(NEW) | 222.682 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
54 | NER L215 | KATHALGURI-MARIANI(NEW) | 160.536 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
55 | NER L216 | MARIANI_MOKUKCHUNG 1 | 48.8 | North Eastern Region | --- | 2016-06-13 05:40 | 2016-06-30 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426 | 19 | NA | NA | NA | LINE KEPT OPEN ON NERLDC INSTRUCTIONS. |  | 100
[5 empty] | --- | 2016-06-13 05:35 | 2016-06-13 05:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | NA | NA | NA | tripped on overvoltage
[5 empty] | --- | 2016-06-01 | 2016-06-07 19:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 25 | NA | NA | NA | KEPT OPEN AS PER INSTRUCTION OF NERLDC
56 | NER L217 | MARIANI_MOKUKCHUNG | 48.8 | North Eastern Region | --- | 2016-06-08 22:21 | 2016-06-13 11:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 16 | NA | NA | NA | Line H/T vide code 1565. |  | 100
57 | NER L401 | BALIPARA_BONGAIGAON 1 | 289.721 | North Eastern Region | --- | 2016-06-25 23:18 | 2016-06-25 23:28 | as given in (3) | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for taking out line reactor (L/R under Emergency S/D for replacement of B-ph Bushing). |  | 99.98
[5 empty] | --- | 2016-06-25 23:18 | 2016-06-29 19:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 20 | NA | NA | NA | Line kept open as per instructions of NERLDC.
58 | NER L402 | BALIPARA_BONGAIGAON 2 | 289.721 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
59 | NER L403 | MISA_BALIPARA 1 | 95.407 | North Eastern Region | --- | 2016-06-06 01:51 | 2016-06-06 02:23 | as given in (3) | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Bus bar protection operated at Balipara S/s. |  | 99.92
60 | NER L404 | MISA-BALIPARA 2 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
61 | NER L405 | BONGAIGAON-MALDA 1 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
62 | NER L406 | BONGAIGAON-MALDA 2 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
63 | NER L407 | BALIPARA-RANGANADI 1 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
64 | NER L408 | BALIPARA-RANGANADI 2 | 166.335 | North Eastern Region | --- | 2016-06-08 23:40 | 2016-06-09 19:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 28 | NA | NA | NA | LINE H/T VIDE CODE 1568 |  | 100
65 | NER L409 | PALLATANA-SURAJMANINAGAR 1 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
66 | NER L410 | PALLATANA-SURAJMANINAGAR 2 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
67 | NER L411 | BTPS-BONGAIGAON 1 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
68 | NER L412 | BTPS-BONGAIGAON 2 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
69 | NER L413 | BALIPARA-BONGAIGAON 3 | 309 | North Eastern Region | --- | 2016-06-15 00:01 | 2016-06-15 19:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | NA | NA | NA | H/T vide code 1664. |  | 99.99
[5 empty] | --- | 2016-06-17 01:16 | 2016-06-17 19:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 37 | NA | NA | NA | Line H/T vide code 1708.
[5 empty] | --- | 2016-06-13 09:43 | 2016-06-13 18:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 31 | NA | NA | NA | Line H/T vide code 1615.
[5 empty] | --- | 2016-06-20 15:49 | 2016-06-20 19:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 57 | NA | NA | NA | Line H/T vide code 1764.
[5 empty] | --- | 2016-06-23 05:20 | 2016-06-23 09:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 39 | NA | NA | NA | Line H/T vide code 1798.
[5 empty] | --- | 2016-06-24 12:32 | 2016-06-24 12:36 | as given in (3) | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped during system upgradation/NTAMC adoption works.
[5 empty] | --- | 2016-06-02 04:35 | 2016-06-03 20:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | NA | NA | NA | Line H/T as per instruction of NERLDC.
[5 empty] | --- | 2016-06-01 04:01 | 2016-06-01 23:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 52 | NA | NA | NA | Line H/T vide code 1431.
[5 empty] | --- | 2016-05-31 22:12 | 2016-06-01 01:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | NA | NA | NA | Line H/T vide code 1426.
[5 empty] | --- | 2016-05-31 22:12 | 2016-06-01 01:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | NA | NA | NA | Line H/T vide code 1426.
[5 empty] | --- | 2016-06-05 09:23 | 2016-06-05 20:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 9 | NA | NA | NA | LINE H/T VIDE CODE 1493
[5 empty] | --- | 2016-06-01 | 2016-06-01 01:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | NA | NA | NA | LINE H/T VIDE CODE 1426
[5 empty] | --- | 2016-05-31 22:12 | 2016-06-01 01:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | NA | NA | NA | Line H/T vide code 1426.
[5 empty] | --- | 2016-06-04 09:15 | 2016-06-04 19:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 55 | NA | NA | NA | Line H/T vide code 1477.
[5 empty] | --- | 2016-06-06 09:21 | 2016-06-06 19:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | NA | NA | NA | LI523NE H/T VIDE CODE 1
70 | NER L414 | BALIPARA-BONGAIGAON 4 | 309 | North Eastern Region | --- | 2016-06-24 06:09 | 2016-06-24 23:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | NA | NA | NA | Line H/T vide code 1816. |  | 99.79
[5 empty] | --- | 2016-06-22 00:54 | 2016-06-22 19:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | NA | NA | NA | Line H/T vide code 1784.
[5 empty] | --- | 2016-06-21 10:56 | 2016-06-21 19:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 24 | NA | NA | NA | Line H/T vide code 1775.
[5 empty] | --- | 2016-06-20 07:42 | 2016-06-20 12:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 51 | 0 | 0 | NA | NA | NA | Bad weather at Bongaigaon end.
[5 empty] | --- | 2016-06-09 07:52 | 2016-06-09 20:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 13 | NA | NA | NA | LINE H/T VIDE CODE 1570
[5 empty] | --- | 2016-06-06 20:29 | 2016-06-08 23:19 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | NA | NA | NA | LINE H/T VIDE CODE 1536
[5 empty] | --- | 2016-06-06 01:51 | 2016-06-06 03:20 | as given in (3) | 0 | 1 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Bus bar protecion operated at Balipara new.
[5 empty] | --- | 2016-06-20 06:56 | 2016-06-20 07:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | NA | NA | NA | Heavy thunderstorm reported at Bongaigaon end.
[5 empty] | --- | 2016-06-10 05:05 | 2016-06-10 18:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 34 | NA | NA | NA | Line H/T vide code 1589.
[5 empty] | --- | 2016-06-18 09:20 | 2016-06-18 19:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19 | NA | NA | NA | Line H/T vide code 1730.
[5 empty] | --- | 2016-06-14 08:57 | 2016-06-14 20:07 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | NA | NA | NA | Line H/T vide code 1641.
[5 empty] | --- | 2016-06-16 00:01 | 2016-06-16 20:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 13 | NA | NA | NA | Line H/T vide code 1684.
71 | NER L415 | SILCHAR-IMPHAL 1 | 167 | North Eastern Region | --- | 2016-06-17 07:59 | 2016-06-17 16:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 47 | NA | NA | NA | OPGW stringing works at loc198-200 & 213-218. |  | 100
[5 empty] | --- | 2016-06-20 08:05 | 2016-06-20 16:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 48 | NA | NA | NA | OPGW stringing at loc no. 198-200 & 213-218.
[5 empty] | --- | 2016-06-27 07:55 | 2016-06-27 16:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 53 | NA | NA | NA | OPGW STRINGING WORK AT LOC.NO.198-200 & 213-218.
[5 empty] | --- | 2016-06-29 08:26 | 2016-06-29 19:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38 | NA | NA | NA | S/D taken for OPGW stringing work at loc 198 - 200 and 213-218.
[5 empty] | --- | 2016-06-26 08:00 | 2016-06-26 16:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 42 | NA | NA | NA | OPGW STRINGING WORK AT LOC.NO.198-200 & 213-218.
72 | NER L416 | SILCHAR-IMPHAL 2 | 167 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
73 | NER L417 | BALIPARA_B.CHAIRALI 3 | 57.294 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
74 | NER L418 | BALIPARA_B.CHAIRALI 4 | 57.294 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
75 | NER L419 | B.CHAIRALI_RANGANADI 1 | 129.335 | North Eastern Region | --- | 2016-06-01 23:23 | 2016-06-02 17:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 59 | NA | NA | NA | Line H/T vide code 1448. |  | 100
[5 empty] | --- | 2016-06-04 08:43 | 2016-06-04 17:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | NA | NA | NA | Line H/T vide code 1475.
[5 empty] | --- | 2016-06-12 05:09 | 2016-06-12 17:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 46 | NA | NA | NA | Line H/T vide code 1604.
[5 empty] | --- | 2016-06-28 23:46 | 2016-06-29 16:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | NA | NA | NA | Line H/T vide code 1920.
[5 empty] | --- | 2016-06-20 01:04 | 2016-06-20 08:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 35 | NA | NA | NA | Line H/T vide code 1755.
[5 empty] | --- | 2016-06-26 23:21 | 2016-06-27 17:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | NA | NA | NA | LINE H/T VIDE CODE 1879.
[5 empty] | --- | 2016-06-27 23:27 | 2016-06-28 16:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | NA | NA | NA | Line H/T vide code 1908.
[5 empty] | --- | 2016-06-09 23:53 | 2016-06-10 18:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | NA | NA | NA | Line H/T vide code 1588.
[5 empty] | --- | 2016-06-04 23:57 | 2016-06-05 18:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | NA | NA | NA | LINE H/T VIDE CODE 1488
[5 empty] | --- | 2016-06-12 23:53 | 2016-06-13 11:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 23 | NA | NA | NA | Line H/T vide code 1612.
76 | NER L420 | B.CHAIRALI_RANGANADI 2 | 129.335 | North Eastern Region | --- | 2016-06-10 23:37 | 2016-06-11 18:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | NA | NA | NA | Line H/T vide code 1596. |  | 100
[5 empty] | --- | 2016-06-06 00:14 | 2016-06-06 14:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 42 | NA | NA | NA | LINE H/T VIDE CODE 1518
[5 empty] | --- | 2016-06-13 13:58 | 2016-06-13 17:17 | as given in (3) | 0 | 0 | 0 | 3 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | Reactor protection operated at Ranganadi S/s.
[5 empty] | --- | 2016-06-03 09:03 | 2016-06-03 17:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 13 | NA | NA | NA | Line H/T vide code 1462.
[5 empty] | --- | 2016-05-31 23:57 | 2016-06-01 17:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | NA | NA | NA | Line H/T vide code 1429.
[5 empty] | --- | 2016-06-01 | 2016-06-01 17:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | NA | NA | NA | H/T VIDE CODEE 1429
[5 empty] | --- | 2016-06-26 00:08 | 2016-06-26 18:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 51 | NA | NA | NA | LINE H/T VIDE CODE 1867.
[5 empty] | --- | 2016-06-19 01:12 | 2016-06-19 15:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 56 | NA | NA | NA | Line H/T vide code 1747.
77 | NER L421 | BALIPARA_B.CHAIRALI 1 | 59.54 | North Eastern Region | --- | 2016-06-25 15:33 | 2016-06-27 08:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 17 | NA | NA | NA | LINE H/T VIDE CODE 1856. |  | 100
78 | NER L422 | BALIPARA_B.CHAIRALI 2 | 59.54 | North Eastern Region | --- | 2016-06-27 06:09 | 2016-06-29 17:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 4 | NA | NA | NA | Line H/T vide code 1881. |  | 100
[5 empty] | --- | 2016-06-06 09:39 | 2016-06-23 09:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 3 | NA | NA | NA | Line H/T vide code 1524.
[5 empty] | --- | 2016-05-19 22:32 | 2016-06-04 10:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 23 | NA | NA | NA | Line H/T vide code 1210.
79 | NER L423 | SILCHAR-PURBAKANCHANBARI 1 | 127.2 | North Eastern Region | --- | 2016-06-05 09:08 | 2016-06-05 19:38 | as given in (3) | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY STATE AT PKBari |  | 100
80 | NER L424 | SILCHAR-PURBAKANCHANBARI 2 | 127.2 | North Eastern Region | --- | 2016-06-05 09:08 | 2016-06-05 19:39 | as given in (3) | 0 | 0 | 0 | 10 | 31 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY STATE AT PKBari |  | 100
81 | NER RBR2 | BR_BONGAIGAON (50MVAR) 2 | 50 | North Eastern Region | --- | 2016-06-14 10:18 | 2016-06-14 12:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 24 | NA | NA | NA | Reactor B/U Imp Relay testing. Defective CSD relays to be dismantled. |  | 100
82 | NER RBR3 | BR_BALIPARA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
83 | NER RBR4 | BR_MISA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
84 | NER RBR5 | BR_KUMARGHAT (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
85 | NER RBR6 | BR_AIZWAL (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
86 | NER RBR7 | BR_BONGAIGAON(80MVAR) 3 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
87 | NER RBR8 | BR_BALIPARA(80MVAR) 2 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
88 | NER RBR9 | BR_SILCHAR(63MVAR) 1 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
89 | NER RBR10 | BR_SILCHAR(63MVAR) 2 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
90 | NER RBR11 | BR_BONGAIGAON(80MVAR) 4 | 80 | North Eastern Region | --- | 2016-06-08 10:02 | 2016-06-08 12:54 | as given in (3) | 0 | 2 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | EMERGENCY S/D FOR TAKING Y-PH BUSHING OIL SAMPLE |  | 99.6
[5 empty] | --- | 2016-06-08 18:51 | 2016-06-30 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533 | 8 | NA | NA | NA | UPGRADATION OF BUSHING WITH RIP.
91 | NER TICT1 | ICT_SILCHAR (200MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
92 | NER TICT2 | ICT_BALIPARA (315MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
93 | NER ICT4 | ICT_SALAKATI (50 MVA) 1 | 50 | North Eastern Region | --- | 2016-06-28 10:40 | 2016-06-28 12:41 | as given in (3) | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken for connecting oil pipe from filtration machine to transformer conservator. |  | 99.72
94 | NER TICT5 | ICT_DIMAPUR (100 MVA) 1 | 100 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
95 | NER TICT6 | ICT_KUMARGHAT(5MVA) | 5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
96 | NER TICT7 | ICT_NIRJULI(16MVA) 1 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
97 | NER TICT8 | ICT_NIRJULI(10MVA) 2 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
98 | NER TICT10 | ICT_ZIRO (15MVA) | 15 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
99 | NER TICT11 | ICT_NIRJULI (16MVA) 2 | 16 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
100 | NER TICT12 | ICT_KOPILI (160 MVA) 2 | 160 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
101 | NER TICT14 | ICT_MISA 1 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
102 | NER TICT15 | ICT_SILCHAR(200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
103 | NER TICT16 | ICT_SILCHAR(200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
104 | NER TICT17 | ICT_BONGAIGAON(315MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
105 | NER TICT18 | ICT_MISA 2 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
106 | NER TICT19 | ICT_MOKOKCHUNG(30MVA) 1 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
107 | NER TICT20 | ICT_MOKOKCHUNG(30MVA) 2 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
108 | NER TICT21 | ICT_B'CHARIALI (200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
109 | NER ICT22 | ICT_B.CHAIRALI(200MVA) 2 | 200 | North Eastern Region | --- | 2016-06-23 00:41 | 2016-06-23 04:35 | as given in (3) | 0 | 3 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | OLTC - Yph Oil Surge relay operated. |  | 99.46
110 | NER TICT23 | ICT_NIRJULI(50MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
111 | NER ICT26 | ICT_NIRJULI(50MVA) 2 | 50 | North Eastern Region | --- | 2016-06-09 08:02 | 2016-06-09 20:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | NA | NA | NA | S/D TAKEN FOR ERECTION OF NEW 145KV ICT |  | 100
112 | NER ICT28 | ICT_IMPHAL(50MVA) 2 | 50 | North Eastern Region | --- | 2016-06-24 07:18 | 2016-06-24 08:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | NA | NA | NA | E/S/D taken for Checking of phase sequence for facilitating parallel operation of ICT-I and ICT-II. |  | 100

## JULY
S/No | Unique ID of Transmission Element | Element Name | Description (Length-km/Nos./MVA/ MVAr/MW/ etc. | Region | Type of failure | Outage Date & Time Hr Mn | Restoration Date & Time Hr Mn | Details of outage ( No. of Towers damaged, no. of insulators failed etc.) | Total Outage (in Days) (1) | Duration of Outage attribuatable to | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual & Norm (1 - 2) | Detailed Reason for Outage (3) | Outage certifying Agency & Reference Document | % Availability as certified by certifying agency
[10 empty] | ISTS Licensee Hr Min |  | Others Hr Min |  | System Constraint/ Natural calamity/ Milliitancy Hr Min |  | Deemed Available Hr Min
JULY' 2016
1 | NER L101 | RCN_AGARTALA 1 | 8.384 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | NERPC | 100
2 | NER L102 | RCN_AGARTALA 2 | 8.384 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
3 | NER L103 | BADARPUR_KOLASIB | 107.226 | North Eastern Region | --- | 2016-07-25 09:23 | 2016-07-25 17:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 7 | 43 | 0 | 0 | NA | NA | NA | S/D taken for tree cutting at loc. 343 to 344. |  | 100
[5 empty] | --- | 2016-07-15 17:31 | 2016-07-15 17:59 | as given in (3) | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-07-26 08:54 | 2016-07-26 19:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR TREE CUTTING AT LOC 343-344
4 | NER L104 | AIZWAL_KUMARGHAT | 131 | North Eastern Region | --- | 2016-07-31 14:57 | 2016-07-31 15:42 | as given in (3) | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 20MVAR BUS REACTOR B-PH LA FAILED AT KUMARGHAT |  | 99.9
5 | NER L105 | AIZWAL_ZEMEBAK 2 | 6.719 | North Eastern Region | --- | 2016-07-31 05:45 | 2016-07-31 06:21 | as given in (3) | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO SOWNSTREAM FAULT |  | 100
[5 empty] | --- | 2016-07-31 13:37 | 2016-07-31 14:06 | as given in (3) | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | NA | NA | NA | DOWNSTREAM FAULT
6 | NER L106 | BADARPUR-BADARPUR | 1.023 | North Eastern Region | --- | 2016-07-09 13:28 | 2016-07-09 13:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | NA | NA | NA | SPS OPERATED AT SILCHAR |  | 100
7 | NER L107 | BADARPUR_JIRIBAM | 67.21 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
8 | NER L108 | BADARPUR_KHLIERIAT | 76.646 | North Eastern Region | --- | 2016-07-09 13:19 | 2016-07-09 13:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | NA | NA | NA | POWER SWING NO TRIP AT BADARPUR |  | 100
9 | NER L109 | BADARPUR_KUMARGHAT | 118.513 | North Eastern Region | --- | 2016-07-31 14:57 | 2016-07-31 15:30 | as given in (3) | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 20 MVAR BUS REACTOR B-PH LA FAILED AT KUMARGHAT |  | 99.93
[5 empty] | --- | 2016-07-16 09:15 | 2016-07-16 15:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 6 | 9 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR CLEARING OF INFRINGEMENT IN ROW AREAS (LOC.144-172)
10 | NER L110 | DIMAPUR_IMPHAL | 168.865 | North Eastern Region | --- | 2016-07-09 13:19 | 2016-07-09 13:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | NA | NA | NA | POWER SWING NO TRIP AT DIMAPUR |  | 100
[5 empty] | --- | 2016-07-30 08:28 | 2016-07-30 08:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | NA | NA | NA | TRIP DUE TO FALLING OF BAMBOO FROM UPHILL SIDE UPON R-Y PH IN BETWEEN LOC 262-263
11 | NER L111 | DOYANG_DIMAPUR 1 | 92.526 | North Eastern Region | --- | 2016-07-27 10:54 | 2016-07-27 11:33 | as given in (3) | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | TRANSIENT E/F |  | 99.91
12 | NER L112 | DOYANG_DIMAPUR 2 | 92.526 | North Eastern Region | --- | 2016-07-31 11:35 | 2016-07-31 23:59 | as given in (3) | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY DOYANG (NEEPCO) |  | 99.85
[5 empty] | --- | 2016-07-31 11:19 | 2016-07-31 11:35 | as given in (3) | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Transient E/F
[5 empty] | --- | 2016-07-27 10:54 | 2016-07-27 11:45 | as given in (3) | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | TrANSIENT E/F
13 | NER L113 | GOHPUR_NIRJULI | 42.5 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 0 | 0 | NA | NA | NA | Hand tripped due to zero bus voltage at Ranganadi S/s. |  | 100
14 | NER L114 | IMPHAL_IMPHAL 1 | 1.5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
15 | NER L115 | JIRIBAM_AIZWAL | 172.315 | North Eastern Region | --- | 2016-07-30 12:04 | 2016-07-30 12:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | NA | NA | NA | BAMBOO FALLEN FROM UPHILL SIDE FOUND BURNT UNDER R& Y PH BETWEEN LOC 404 & 416 |  | 100
[5 empty] | --- | 2016-07-19 12:29 | 2016-07-19 12:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING
16 | NER L116 | JIRIBAM_HAFLONG | 100.63 | North Eastern Region | --- | 2016-07-21 13:25 | 2016-07-21 15:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 25 | 0 | 0 | NA | NA | NA | E/S/D taken for tree cutting at loc 201-202. |  | 100
[5 empty] | --- | 2016-07-09 11:00 | 2016-07-09 16:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOE CLEARING TREES BETWEEN LOC 133-134 WHICH CAME NEAR THE TOWER DUE TO SUDDEN LANDSLIDE
17 | NER L117 | JIRIBAM_LOKTAK 2 | 82.4 | North Eastern Region | --- | 2016-07-13 14:16 | 2016-07-13 16:27 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 11 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARING OF BAMBOOS LEANING TOWARDS THE LINE FROM OUTSIDE CORRIDOR AT LOC. 106 & 107 |  | 100
[5 empty] | --- | 2016-07-02 08:36 | 2016-07-02 19:19 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 10 | 43 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARIG OF TREES AND SOIL CAUSED BY LANDSLIDE IN BETWEEN LOC 206 & 207
18 | NER L118 | KHANDONG-HAFLONG | 63.166 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
19 | NER L119 | KHANDONG_KHLIERIAT 1 | 42.48 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
20 | NER L120 | KHANDONG_KHLIERIAT 2 | 40.933 | North Eastern Region | --- | 2016-07-21 12:03 | 2016-07-21 18:28 | as given in (3) | 0 | 6 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for replacement of Trip coil, Tan delta tests at Khangdong bay. |  | 99.14
21 | NER L121 | KHANDONG_KOPILI 1 | 10.914 | North Eastern Region | --- | 2016-07-23 17:32 | 2016-07-23 17:36 | as given in (3) | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY KHANGDONG (NEEPCO) |  | 100
22 | NER L122 | KHLIERIAT_KHLIERIAT | 7.801 | North Eastern Region | --- | 2016-07-31 12:08 | 2016-07-31 12:23 | as given in (3) | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNTREAM FAULT |  | 100
[5 empty] | --- | 2016-07-30 13:42 | 2016-07-30 14:17 | as given in (3) | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT
[5 empty] | --- | 2016-07-05 13:21 | 2016-07-05 13:47 | as given in (3) | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond jurisdiction.
23 | NER L123 | KUMARGHAT_R C NAGAR | 104.02 | North Eastern Region | --- | 2016-07-31 14:57 | 2016-07-31 15:39 | as given in (3) | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 20 MVAR BUS REACTOR B-PH LA FAILED AT KUMARGHAT |  | 99.91
[5 empty] | --- | 2016-07-09 13:19 | 2016-07-09 13:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO POWER SWING
24 | NER L124 | LOKTAK_IMPHAL 2 | 35.04 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
25 | NER L125 | SALAKATI-GELEPHUG | 49.217 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
26 | NER L126 | NIRJULI-RANGANADI | 22.29 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
27 | NER L128 | KOLASIB-AIZAWL | 66.098 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
28 | NER L129 | RANGANADI-ZIRO | 44.523 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
29 | NER L130 | KHANDONG_KOPILI 2 | 11.56 | North Eastern Region | --- | 2016-07-23 10:35 | 2016-07-23 16:24 | as given in (3) | 0 | 5 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP OF BAY EQUIPMENTS AT KHANGDONG HEP |  | 99.22
30 | NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) | 0.347 | North Eastern Region | --- | 2016-07-13 13:27 | 2016-07-13 14:22 | as given in (3) | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE SYSTEM. |  | 100
[5 empty] | --- | 2016-07-01 15:05 | 2016-07-03 19:06 | as given in (3) | 0 | 0 | 0 | 52 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION.CONDUCTOR SNAPPED IN STATE PORTION OF LINE
[5 empty] | --- | 2016-07-30 14:45 | 2016-07-30 14:55 | as given in (3) | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT
[5 empty] | --- | 2016-07-26 14:15 | 2016-07-26 14:37 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT IN STATE SYSTEM
[5 empty] | --- | 2016-07-12 12:17 | 2016-07-12 12:30 | as given in (3) | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE SYSTEM.
31 | NER L132 | DIMAPUR(PG)-DIMAPUR(LILO PORTION) | 0.347 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
32 | NER L133 | SILCHAR-BADARPUR 1 | 19.195 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
33 | NER L134 | SILCHAR-BADARPUR 2 | 19.195 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
34 | NER L135 | SILCHAR-SRIKONA 1 | 1.199 | North Eastern Region | --- | 2016-07-09 13:30 | 2016-07-09 14:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | NA | NA | NA | SPS I & II OPERATED IN SILCHAR |  | 100
35 | NER L136 | SILCHAR-SRIKONA 2 | 1.199 | North Eastern Region | --- | 2016-07-09 13:30 | 2016-07-09 14:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | NA | NA | NA | SPS I & II OPERATED IN SILCHAR |  | 100
36 | NER L137 | IMPHAL-IMPHAL 2 | 0.442 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
37 | NER L138 | SILCHAR-HAILAKANDI 1 | 17.3 | North Eastern Region | --- | 2016-07-09 13:30 | 2016-07-09 14:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | NA | NA | NA | SPS I& II OPERATED AT SILCHAR, TRIPPED AT SILCHAR END ONLY |  | 100
38 | NER L139 | SILCHAR-HAILAKANDI 2 | 17.3 | North Eastern Region | --- | 2016-07-09 13:19 | 2016-07-09 14:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO POWER SWING |  | 99.42
[5 empty] | --- | 2016-07-15 09:19 | 2016-07-15 13:37 | as given in (3) | 0 | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP OF BAY AT SILCHAR.
39 | NER L140 | MOKOCHUNG-MOKOKCHUNG 1 | 1.4 | North Eastern Region | --- | 2016-07-06 13:44 | 2016-07-06 17:45 | as given in (3) | 0 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CHECKING CONTACT RESISTANCE OF CB AND ISOLATOR |  | 99.46
40 | NER L141 | MOKOCHUNG-MOKOKCHUNG 2 | 1.4 | North Eastern Region | --- | 2016-07-07 10:40 | 2016-07-07 16:05 | as given in (3) | 0 | 5 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D FOR CHECKING CONTACT RESISTANCE OF CB AND ISOLATOR |  | 99.27
41 | NER L144 | NIRJULI-LEKHI | 9.7 | North Eastern Region | --- | 2016-07-28 11:20 | 2016-07-28 11:39 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO PROBLEM AT STATE END |  | 100
[5 empty] | --- | 2016-07-21 10:16 | 2016-07-21 11:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 0 | 0 | NA | NA | NA | Hand tripped due to zero bus voltage at Ranganadi S/s.
42 | NER L201 | BALIPARA_TEZPUR | 8.623 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
43 | NER L202 | KATHALGURI_MARIANI(OLD) | 162.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
44 | NER L203 | MISA_DIMAPUR 1 | 123.52 | North Eastern Region | insulator punctured | 2016-07-26 14:08 | 2016-07-26 14:32 | as given in (3) | 1 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1 | N | 0 | R-PH INSULATOR PUNCTURED AT LOC 315 |  | 100
[5 empty] | --- | 2016-07-27 09:54 | 2016-07-27 16:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 6 | 7 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR REPLACEMENT OF R-PH DAMAGED INSULATOR AT LOC 315 CAUSED BY LIGHTNING
45 | NER L204 | MISA_DIMAPUR 2 | 123.52 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
46 | NER L205 | MISA_KATHALGURI | 382.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
47 | NER L206 | MISA-KOPILI 1 | 72.791 | North Eastern Region | --- | 2016-07-07 13:46 | 2016-07-07 15:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 14 | 0 | 0 | NA | NA | NA | TrEE CUT BY MISCREANT WHICH WAS FALLEN ON CONDUCTOR BETWEEN LOC 258-259 |  | 100
48 | NER L207 | MISA_KOPILI 2 | 72.791 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
49 | NER L208 | MISA_KOPILI 3 | 75.788 | North Eastern Region | --- | 2016-07-01 | 2016-07-31 23:59 | as given in (3) | 0 | 0 | 0 | 743 | 59 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN BY KOPILI TO ATTEND CB PROBLEM (NEEPCO) |  | 100
50 | NER L209 | MISA_MARIANI(OLD) | 220 | North Eastern Region | --- | 2016-07-03 18:17 | 2016-07-03 18:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | NA | NA | NA | Thunderstorm and lightning reported in the area |  | 100
51 | NER L210 | MISA_SAMAGURI 1 | 34.439 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
52 | NER L211 | MISA_SAMAGURI 2 | 34.439 | North Eastern Region | --- | 2016-07-12 14:59 | 2016-07-12 15:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING REPORTED. FLASHOVER MARK FOUND ON R-PH ARCING HORN AT LOC 49 |  | 100
53 | NER L212 | SALAKATI_BTPS 2 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
54 | NER L213 | SALAKATI-BTPS 1 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
55 | NER L214 | MISA-MARIANI(NEW) | 222.682 | North Eastern Region | --- | 2016-07-30 03:01 | 2016-07-30 04:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 48 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING |  | 100
56 | NER L215 | KATHALGURI-MARIANI(NEW) | 160.536 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
57 | NER L216 | MARIANI_MOKUKCHUNG 1 | 48.8 | North Eastern Region | --- | 2016-07-09 05:30 | 2016-07-12 02:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 52 | NA | NA | NA | LINE H/T VIDE CODE 2038. |  | 100
[5 empty] | --- | 2016-07-01 | 2016-07-07 23:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 13 | NA | NA | NA | LINE KEPT OPEN AS PER INSTRUCTION OF NERLDC
[5 empty] | tower damage | 2016-07-12 02:22 | 2016-07-31 23:59 | as given in (3) | 19 | 0 | 0 | 0 | 0 | 477 | 37 | 0 | 0 | NA | NA | NA | AT LOC 56 & 57 TOWER DAMAGED, CAUSED BY HEAVY LANDSLIDE DUE TO CONTINOUS RAIN
58 | NER L217 | MARIANI_MOKUKCHUNG 2 | 48.8 | North Eastern Region | --- | 2016-07-04 20:44 | 2016-07-04 21:08 | as given in (3) | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to suspected downstream fault.At the same time Mokokchung-Mokokchung-1 & II also tripped |  | 100
[5 empty] | tower damage | 2016-07-12 01:11 | 2016-07-31 23:59 | as given in (3) | 19 | 0 | 0 | 0 | 0 | 478 | 48 | 0 | 0 | NA | NA | NA | AT LOC 56 & 57 TOWER DAMAGED, CAUSED BY HEAVY LANDSLIDE DUE TO CONTINUOUS RAIN
59 | NER L401 | BALIPARA_BONGAIGAON 1 | 289.721 | North Eastern Region | --- | 2016-07-14 17:35 | 2016-07-14 18:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | NA | NA | NA | KEPT OPEN ON NERLDC INSTRUCTIONS. |  | 99.72
[5 empty] | --- | 2016-07-21 10:16 | 2016-07-21 10:50 | as given in (3) | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA
[5 empty] | --- | 2016-07-21 10:50 | 2016-07-24 19:56 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | NA | NA | NA | KEPT OPEN DUE TO SYSTEM CONSTRAINT
[5 empty] | --- | 2016-07-14 16:03 | 2016-07-14 17:35 | as given in (3) | 0 | 1 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR DISMANTLING OF LR RADIATOR.
60 | NER L402 | BALIPARA_BONGAIGAON 2 | 289.721 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 10:42 | as given in (3) | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA |  | 99.94
61 | NER L403 | MISA_BALIPARA 1 | 95.407 | North Eastern Region | --- | 2016-07-06 19:27 | 2016-07-07 13:31 | as given in (3) | 0.5 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Y-PH LA BLASTED AT BALIPARA |  | 97.27
[5 empty] | --- | 2016-07-21 10:16 | 2016-07-21 10:53 | as given in (3) | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA
[5 empty] | --- | 2016-07-28 10:15 | 2016-07-28 11:56 | as given in (3) | 0 | 1 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | EMERGENCY S/D TAKEN TO ATTEND THE CURRENT IMBALANCE IN THE BAY AT BALIPARA
62 | NER L404 | MISA-BALIPARA 2 | 95.407 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:05 | as given in (3) | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA |  | 99.89
63 | NER L405 | BONGAIGAON-MALDA 1 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
64 | NER L406 | BONGAIGAON-MALDA 2 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
65 | NER L407 | BALIPARA-RANGANADI 1 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
66 | NER L408 | BALIPARA-RANGANADI 2 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
67 | NER L409 | PALLATANA-SURAJMANINAGAR 1 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
68 | NER L410 | PALLATANA-SURAJMANINAGAR 2 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
69 | NER L411 | BTPS-BONGAIGAON 1 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
70 | NER L412 | BTPS-BONGAIGAON 2 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
71 | NER L413 | BALIPARA-BONGAIGAON 3 | 309 | North Eastern Region | --- | 2016-07-21 05:55 | 2016-07-21 11:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51 | NA | NA | NA | Line H/t vide code 2185. |  | 100
[5 empty] | --- | 2016-07-04 00:05 | 2016-07-06 19:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 46 | NA | NA | NA | LINE H/T VIDE CODE 1993
[5 empty] | --- | 2016-07-26 02:06 | 2016-07-26 19:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 43 | NA | NA | NA | LINE H/T VIDE CODE 2229
[5 empty] | --- |  |  | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
[5 empty] | --- | 2016-07-28 06:06 | 2016-07-28 19:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 19 | NA | NA | NA | LINE H/T VIDE CODE 2262
[5 empty] | --- | 2016-07-30 08:27 | 2016-07-30 17:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | NA | NA | NA | LINE HT VIDE CODE 2276
[5 empty] | --- | 2016-07-16 23:46 | 2016-07-18 20:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 24 | NA | NA | NA | LINE H/T VIDE CODE 2142.
[5 empty] | --- | 2016-07-14 00:03 | 2016-07-14 15:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 52 | NA | NA | NA | LINE H/T VIDE CODE 2109.
[5 empty] | --- | 2016-07-11 23:19 | 2016-07-12 19:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | NA | NA | NA | LINE H/T VIDE CODE 2081.
[5 empty] | --- | 2016-07-01 07:39 | 2016-07-02 21:27 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 48 | NA | NA | NA | LINE H/T VIDE CODE 1957
[5 empty] | --- | 2016-07-09 07:52 | 2016-07-10 20:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 30 | NA | NA | NA | LINE H/T VIDE CODE 2039
72 | NER L414 | BALIPARA-BONGAIGAON 4 | 309 | North Eastern Region | --- | 2016-07-07 07:09 | 2016-07-08 19:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 33 | NA | NA | NA | LINE H/T VIDE CODE 2022 |  | 99.86
[5 empty] | --- | 2016-07-10 22:23 | 2016-07-11 19:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 46 | NA | NA | NA | LINE H/T VIDE CODE 2068.
[5 empty] | --- | 2016-07-13 04:42 | 2016-07-13 18:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | NA | NA | NA | LINE H/T VIDE CODE 2096.
[5 empty] | --- | 2016-07-15 04:41 | 2016-07-15 19:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | NA | NA | NA | LINE H/T VIDE CODE 2123.
[5 empty] | --- | 2016-07-16 01:29 | 2016-07-16 19:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 46 | NA | NA | NA | LINE H/T VIDE CODE 2138.
[5 empty] | --- | 2016-07-19 18:01 | 2016-07-20 19:12 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | NA | NA | NA | LINE H/T VIDE CODE 2169
[5 empty] | --- | 2016-07-21 10:16 | 2016-07-21 11:20 | as given in (3) | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA
[5 empty] | --- | 2016-07-25 06:26 | 2016-07-25 19:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 49 | NA | NA | NA | Line H/T vide code 2222.
[5 empty] | --- | 2016-07-27 07:41 | 2016-07-27 19:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 49 | NA | NA | NA | LINE H/T VIDE CODE 2242
[5 empty] | --- | 2016-07-02 23:34 | 2016-07-03 22:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 1 | NA | NA | NA | LINE H/T VIDE CODE 1981
[5 empty] | --- | 2016-07-29 05:07 | 2016-07-29 17:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 48 | NA | NA | NA | LINE H/T VIDE CODE 2268
73 | NER L415 | SILCHAR-IMPHAL 1 | 167 | North Eastern Region | --- | 2016-07-13 12:17 | 2016-07-13 13:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARING OF BAMBOOS LEANING TOWARDS THE LINE FROM OUTSIDE CORRIDOR AT LOC. 209 & 210 |  | 99.21
[5 empty] | jumper opened | 2016-07-30 12:39 | 2016-07-30 18:32 | as given in (3) | 0.24514 | 5 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.7549 | B-PH JUMPER OPENED AT LOC 346
74 | NER L416 | SILCHAR-IMPHAL 2 | 167 | North Eastern Region | --- | 2016-07-30 12:39 | 2016-07-30 13:06 | as given in (3) | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED ON OCCURRENCE OF 400 KV SIL-IMP CKT I |  | 99.65
[5 empty] | --- | 2016-07-03 11:59 | 2016-07-03 14:08 | as given in (3) | 0 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REPLACEMENT OF BOTTOM PHASE JUMPER AT LOC 55
75 | NER L417 | BALIPARA_B.CHAIRALI 3 | 57.294 | North Eastern Region | --- | 2016-07-09 08:57 | 2016-07-09 18:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | NA | NA | NA | LINE H/T VIDE CODE 2041 TAKEN BY FOREST DEPTT. |  | 99.88
[5 empty] | --- | 2016-07-10 09:13 | 2016-07-10 18:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 53 | NA | NA | NA | LINE H/T VIDE CODE 2063. S/D TAKEN BY FOREST DEPT
[5 empty] | --- | 2016-07-21 10:16 | 2016-07-21 11:10 | as given in (3) | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA
76 | NER L418 | BALIPARA_B.CHAIRALI 4 | 57.294 | North Eastern Region | --- | 2016-07-10 09:13 | 2016-07-10 18:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | NA | NA | NA | LINE H/T VIDE CODE 2064. S/D TAKEN BY FOREST DEPT |  | 99.65
[5 empty] | --- | 2016-07-21 10:16 | 2016-07-21 11:34 | as given in (3) | 0 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA
[5 empty] | --- | 2016-07-23 14:30 | 2016-07-23 20:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | NA | NA | NA | LINE KEPT OPEN AS PER INSTRUCTION OF NERLDC
[5 empty] | --- | 2016-07-23 13:12 | 2016-07-23 14:30 | as given in (3) | 0 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR ATTENDING CB PROBLEM IN BNC-IV TIE BAY AT BALIPARA
[5 empty] | --- | 2016-07-09 08:58 | 2016-07-09 18:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 40 | NA | NA | NA | LINE H/T VIDE CODE 2042 S/D TAKEN BY FOREST DEPTT
77 | NER L419 | B.CHAIRALI_RANGANADI 1 | 129.335 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:19 | as given in (3) | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA |  | 99.86
78 | NER L420 | B.CHAIRALI_RANGANADI 2 | 129.335 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:33 | as given in (3) | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA |  | 99.83
79 | NER L421 | BALIPARA_B.CHAIRALI 1 | 59.54 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:32 | as given in (3) | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA |  | 99.83
[5 empty] | --- | 2016-07-14 18:15 | 2016-07-20 19:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 20 | NA | NA | NA | LINE H/T VIDE CODE 2119
[5 empty] | --- | 2016-07-01 08:48 | 2016-07-09 08:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 57 | NA | NA | NA | LINE H/T VIDE CODE 1959
80 | NER L422 | BALIPARA_B.CHAIRALI 2 | 59.54 | North Eastern Region | --- | 2016-08-13 09:49 | 2016-08-17 12:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 49 | NA | NA | NA | LINE H/T VIDE CODE 2479. |  | 99.85
[5 empty] | --- | 2016-07-24 05:55 | 2016-07-31 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 4 | NA | NA | NA | LINE H/T VIDE CODE 2219
[5 empty] | --- | 2016-07-21 10:16 | 2016-07-21 11:24 | as given in (3) | 0 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 400 KV BUS DEAD AT BALIPARA
81 | NER L423 | SILCHAR-PURBAKANCHANBARI 1 | 127.2 | North Eastern Region | --- | 2016-07-12 09:23 | 2016-07-12 17:41 | as given in (3) | 0 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | LINE H/T TO FACILITATE BUS S/D AT P.K.BARI(STATE) END. |  | 100
[5 empty] | --- | 2016-07-09 13:19 | 2016-07-09 14:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO POWER SWING
82 | NER L424 | SILCHAR-PURBAKANCHANBARI 2 | 127.2 | North Eastern Region | --- | 2016-07-12 09:23 | 2016-07-12 18:06 | as given in (3) | 0 | 0 | 0 | 8 | 43 | 0 | 0 | 0 | 0 | NA | NA | NA | LINE H/T TO FACILITATE BUS S/D AT P.K.BARI(STATE) END. |  | 100
[5 empty] | --- | 2016-07-09 13:19 | 2016-07-09 14:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO POWER SWING
83 | NER RBR1 | BR_BONGAIGAON (50MVAR) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
84 | NER RBR2 | BR_BONGAIGAON (50MVAR) 2 | 50 | North Eastern Region | --- | 2016-07-01 | 2016-07-31 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743 | 59 | NA | NA | NA | E/S/D TAKEN FOR REPLACEMENT OF R-PH BUSHING |  | 100
85 | NER RBR3 | BR_BALIPARA (50MVAR) 1 | 50 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:07 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | NA | NA | NA | Hand tripped due to zero bus voltage at Balipara S/s. |  | 100
86 | NER RBR4 | BR_MISA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
87 | NER RBR5 | BR_KUMARGHAT (20MVAR) | 20 | North Eastern Region | --- | 2016-07-31 14:57 | 2016-07-31 16:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | NA | NA | NA | B-PH LA FAILED |  | 100
88 | NER RBR6 | BR_AIZWAL (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
89 | NER RBR7 | BR_BONGAIGAON(80MVAR) 3 | 80 | North Eastern Region | --- | 2016-07-01 | 2016-07-20 22:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478 | 45 | NA | NA | NA | B-PH BUSHING EXPLODED |  | 100
90 | NER RBR8 | BR_BALIPARA(80MVAR) 2 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
91 | NER RBR9 | BR_SILCHAR(63MVAR) 1 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
92 | NER RBR10 | BR_SILCHAR(63MVAR) 2 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
93 | NER RBR11 | BR_BONGAIGAON(80MVAR) 4 | 80 | North Eastern Region | --- | 2016-07-01 | 2016-07-03 20:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1 | NA | NA | NA | UPGRADATION OF BUSHING WITH RIP |  | 100
[5 empty] | --- | 2016-07-20 09:31 | 2016-07-20 21:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | NA | NA | NA | E/S/D TAKEN FOR CONNECTION OF B/R 3 JUMPER
[5 empty] | --- | 2016-07-20 21:55 | 2016-07-20 23:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 49 | NA | NA | NA | B/R KEPT OPEN DUE TO SYSTEM CONSTRAINT
94 | NER TICT1 | ICT_SILCHAR (200MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
95 | NET ICT2 | ICT_BALIPARA (315MVA) 1 | 315 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | NA | NA | NA | H/T DUE TO ZERO BUS VOLTAGE AT BALIPARA S/s. |  | 100
96 | NER ICT4 | ICT_SALAKATI (50 MVA) 1 | 50 | North Eastern Region | --- | 2016-07-17 18:46 | 2016-07-17 20:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 0 | NA | NA | NA | TRIPPED ON BACKUP E/F. |  | 100
97 | NER ICT5 | ICT_DIMAPUR (100 MVA) 1 | 100 | North Eastern Region | --- | 2016-07-22 08:02 | 2016-07-22 16:10 | as given in (3) | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken for AMP works. |  | 98.91
98 | NER TICT6 | ICT_KUMARGHAT(5MVA) | 5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
99 | NER TICT7 | ICT_NIRJULI(16MVA) 1 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
100 | NER TICT8 | ICT_NIRJULI(10MVA) 2 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
101 | NER TICT10 | ICT_ZIRO (15MVA) | 15 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
102 | NER TICT11 | ICT_NIRJULI (16MVA) 2 | 16 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
103 | NER TICT12 | ICT_KOPILI (160 MVA) 2 | 160 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
104 | NER TICT14 | ICT_MISA 1 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
105 | NER TICT15 | ICT_SILCHAR(200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
106 | NER ICT16 | ICT_SILCHAR(200MVA) 2 | 200 | North Eastern Region | --- | 2016-07-05 15:31 | 2016-07-05 16:55 | as given in (3) | 0 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D taken to attend hotspot in 132 kV side B-phase CT dropper. |  | 99.81
107 | NER TICT17 | ICT_BONGAIGAON(315MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
108 | NER TICT18 | ICT_MISA 2 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
109 | NER TICT19 | ICT_MOKOKCHUNG(30MVA) 1 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
110 | NER TICT20 | ICT_MOKOKCHUNG(30MVA) 2 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
111 | NER ICT21 | ICT_B.CHAIRALI(200MVA) 1 | 200 | North Eastern Region | --- | 2016-07-01 | 2016-07-03 16:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 26 | NA | NA | NA | FoR ATTENDING OLTC OIL LEAKAGE |  | 100
112 | NER ICT22 | ICT_B.CHAIRALI(200MVA) 2 | 200 | North Eastern Region | --- | 2016-07-29 05:51 | 2016-07-29 08:32 | as given in (3) | 0 | 2 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | OLTC SUREGE RELAY OPERATED |  | 99.64
113 | NER TICT23 | ICT_NIRJULI(50MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
114 | NER ICT25 | ICT_SALAKATI(50MVA) 2 | 50 | North Eastern Region | --- | 2016-07-17 19:01 | 2016-07-17 20:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 31 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERLOAD. |  | 100
115 | NER ICT28 | ICT_IMPHAL(50MVA) 2 | 50 | North Eastern Region | --- | 2016-07-19 10:07 | 2016-07-19 16:25 | as given in (3) | 0 | 6 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP. |  | 99.15
116 | NER ICT29 | ICT_NIRJULI(50MVA) 2 | 50 | North Eastern Region | --- | 2016-07-12 12:00 | 2016-07-12 13:36 | as given in (3) | 0 | 1 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN TO ARREST OIL LEAKAGE. |  | 99.78
117 | NER ICT30 | ICT_BALIPARA(315MVA) 2 | 315 | North Eastern Region | --- | 2016-07-21 10:16 | 2016-07-21 11:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 0 | 0 | NA | NA | NA | H/T DUE TO ZERO BUS VOLTAGE AT BALIPARA S/s. |  | 100

## AUGUST
S/No | Unique ID of Transmission Element | Element Name | Description (Length-km/Nos./MVA/ MVAr/MW/ etc. | Region | Type of failure | Outage Date & Time Hr Mn | Restoration Date & Time Hr Mn | Details of outage ( No. of Towers damaged, no. of insulators failed etc.) | Total Outage (in Days) (1) | Duration of Outage attribuatable to | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual & Norm (1 - 2) | Detailed Reason for Outage (3) | Outage certifying Agency & Reference Document | % Availability as certified by certifying agency
[10 empty] | ISTS Licensee Hr Min |  | Others Hr Min |  | System Constraint/ Natural calamity/ Milliitancy Hr Min |  | Deemed Available Hr Min
AUGUST' 2016
1 | NER L101 | RCN_AGARTALA 1 | 8.384 | North Eastern Region | --- | 2016-08-17 11:21 | 2016-08-17 13:41 | as given in (3) | 0 | 0 | 0 | 2 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY AGARTALA END (NEEPCO). | NERPC | 96.59
[5 empty] | Insulator failure | 2016-08-03 23:31 | 2016-08-04 12:38 | as given in (3) | 0.54653 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | N | -0.45347 | S/D TAKEN FOR RECTIFICATION OF INSULATOR AT LOC. 4
[5 empty] | insulator punctured | 2016-08-03 13:02 | 2016-08-03 13:52 | as given in (3) | 0.034722 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | N | -0.96528 | R-PH INSULATOR PUNCTURED AT LOC 4
[5 empty] | jumper opened | 2016-08-25 01:49 | 2016-08-25 13:14 | as given in (3) | 0.47569 | 11 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.5243 | Y ph. Jumper opened at loc.29.
2 | NER L102 | RCN_AGARTALA 2 | 8.384 | North Eastern Region | --- | 2016-08-31 23:44 | 2016-08-31 23:59 | as given in (3) | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Y-PH JUMPER OPEN AT LOC 15 |  | 99.97
[5 empty] | --- | 2016-08-13 11:17 | 2016-08-13 14:11 | as given in (3) | 0 | 0 | 0 | 2 | 54 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN BY NEEPCO.
[5 empty] | --- | 2016-08-03 13:06 | 2016-08-03 14:33 | as given in (3) | 0 | 0 | 0 | 1 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | PROBLEM AT RCNAGAR END
[5 empty] | jumper opened | 2016-08-31 23:44 | 2016-09-01 11:50 | as given in (3) | 0.50417 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.4958 | Y-PH JUMPER OPENED AT LOC 15.
3 | NER L103 | BADARPUR_KOLASIB | 107.226 | North Eastern Region | --- | 2016-08-25 16:43 | 2016-08-25 17:44 | as given in (3) | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION. |  | 100
[5 empty] | --- | 2016-08-15 01:15 | 2016-08-15 01:34 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT AT KOLASIB END.
4 | NER L104 | AIZWAL_KUMARGHAT | 131 | North Eastern Region | --- | 2016-08-25 17:07 | 2016-08-25 17:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE REGION DURING THE TIME OF TRIPPING. FLASHOVER MARK AT LOC 168 |  | 100
|  |  | 131 | North Eastern Region | --- | 2016-08-04 11:03 | 2016-08-04 11:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | NA | NA | NA | EVIDENCE OF INCLEMENT WEATHER CONFIRMED DURING THE TIME OF TRIPPING
5 | NER L105 | AIZWAL_ZEMEBAK 2 | 6.719 | North Eastern Region | --- | 2016-08-03 08:40 | 2016-08-03 09:04 | as given in (3) | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 100
6 | NER L106 | BADARPUR-BADARPUR | 1.023 | North Eastern Region | --- | 2016-08-30 14:44 | 2016-08-30 15:07 | as given in (3) | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH |  | 99.98
[5 empty] | --- | 2016-08-23 14:22 | 2016-08-23 14:30 | as given in (3) | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | (SPS SIGNAL RECEIVED AT BADARPUR).
7 | NER L107 | BADARPUR_JIRIBAM | 67.21 | North Eastern Region | --- | 2016-08-17 09:11 | 2016-08-17 17:21 | as given in (3) | 0 | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP OF BAY EQUIPMENTS. |  | 98.9
[5 empty] | --- | 2016-08-25 10:27 | 2016-08-25 10:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | NA | NA | NA | EVIDENCE OF INCLEMENT WEATHER IN ENTIRE NER AS SUPPORTED BY WEATHER REPORT
8 | NER L108 | BADARPUR_KHLIERIAT | 76.646 | North Eastern Region | --- | 2016-08-25 13:16 | 2016-08-25 13:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | NA | NA | NA | HEAVY LIGHTINING REPORTED. |  | 100
9 | NER L109 | BADARPUR_KUMARGHAT | 118.513 | North Eastern Region | --- | 2016-08-25 17:14 | 2016-08-25 17:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE REGION DURING THE TIME OF TRIPPING. |  | 100
[5 empty] | --- | 2016-08-27 05:33 | 2016-08-27 05:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING.BURNT BAMBOOS BETWEEN LOC 60-61
10 | NER L110 | DIMAPUR_IMPHAL | 168.865 | North Eastern Region | insulator damaged | 2016-08-14 07:00 | 2016-08-15 14:46 | as given in (3) | 1.3236 | 0 | 0 | 0 | 0 | 31 | 46 | 0 | 0 | 2 | N | -0.67639 | INSULATOR STRING AT LOC 210 DAMAGED DUE TO LIGHTENING STRIKE. |  | 96.78
[5 empty] | insulator damaged | 2016-08-03 16:58 | 2016-08-04 08:53 | as given in (3) | 0.66319 | 15 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.3368 | INSULATOR DAMAGED AT LOC 522.
[5 empty] | --- | 2016-08-25 14:56 | 2016-08-25 15:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO HEAVY THUNDERSTORM.
[5 empty] | --- | 2016-08-18 11:17 | 2016-08-18 11:26 | as given in (3) | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Transient E/F
[5 empty] | insulator damaged | 2016-08-04 10:59 | 2016-08-04 18:53 | as given in (3) | 0.32917 | 7 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | N | -1.6708 | INSULATOR DAMAGED AT LOC 173.
[5 empty] | insulator damaged | 2016-08-11 16:26 | 2016-08-11 16:45 | as given in (3) | 0.013194 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 2 | N | -1.9868 | INSULATOR STRING AT LOC 210 DAMAGED DUE TO LIGHTENING STRIKE.
[5 empty] | insulator damaged | 2016-08-12 12:18 | 2016-08-12 13:40 | as given in (3) | 0.056944 | 0 | 0 | 0 | 0 | 1 | 22 | 0 | 0 | 2 | N | -1.9431 | INSULATOR STRING AT LOC 210 DAMAGED DUE TO LIGHTENING STRIKE.
[5 empty] | insulator damaged | 2016-08-13 11:02 | 2016-08-13 18:24 | as given in (3) | 0.30694 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 2 | N | -1.6931 | INSULATOR STRING AT LOC 210 DAMAGED DUE TO LIGHTENING STRIKE.
11 | NER L111 | DOYANG_DIMAPUR 1 | 92.526 | North Eastern Region | --- | 2016-08-03 21:25 | 2016-08-03 21:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | NA | NA | NA | EVIDENCE OF INCLEMENT WEATHER PREVAILING DURING TIME OF TRIPPING |  | 100
[5 empty] | --- | 2016-08-15 06:04 | 2016-08-15 06:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
12 | NER L112 | DOYANG_DIMAPUR 2 | 92.526 | North Eastern Region | --- | 2016-07-31 11:35 | 2016-08-01 13:10 | as given in (3) | 0 | 0 | 0 | 25 | 35 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D taken by Doyang End.(NEEPCO). |  | 100
[5 empty] | --- | 2016-08-03 21:25 | 2016-08-03 22:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | NA | NA | NA | EVIDENCE OF INCLEMENT WEATHER PREVAILING DURING TIME OF TRIPPING
[5 empty] | --- | 2016-08-15 04:55 | 2016-08-15 05:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
[5 empty] | --- | 2016-08-15 06:04 | 2016-08-15 06:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
13 | NER L113 | GOHPUR_NIRJULI | 42.5 | North Eastern Region | --- | 2016-08-18 11:02 | 2016-08-18 11:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR CLEARING OF TREES AT LOC 131-132 LEANING TOWARDS DUE TO HEAVY RAIN AND THUNDERSTORM. |  | 100
[5 empty] | --- | 2016-08-27 11:07 | 2016-08-27 11:41 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | NA | NA | NA | ZERO BUS VOLTAGE AT RANGANADI.
14 | NER L114 | IMPHAL_IMPHAL | 1.5 | North Eastern Region | --- | 2016-08-19 09:07 | 2016-08-19 15:02 | as given in (3) | 0 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP OF BAY AT IMPHAL(PGCIL). |  | 99.2
15 | NER L115 | JIRIBAM_AIZWAL | 172.315 | North Eastern Region | --- | 2016-08-03 10:20 | 2016-08-03 12:36 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | NA | NA | NA | NO ABNORMALITY IN THE LINE FOUND ON PATROLLING WHICH MAY LEAD TO TRIPPING |  | 100
[5 empty] | --- | 2016-08-31 00:01 | 2016-08-31 00:19 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING AT JIRIBAM
[5 empty] | --- | 2016-08-14 23:17 | 2016-08-14 23:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING
[5 empty] | --- | 2016-08-18 13:00 | 2016-08-18 15:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 31 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REPLACING 3NOS. OF INSULATORS FAILED DUE TO LIGHTENING AT LOC 38.
[5 empty] | --- | 2016-08-25 10:27 | 2016-08-25 10:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | NA | NA | NA | EVIDENCE OF INCLEMENT WEATHER IN ENTIRE NER AS SUPPORTED BY WEATHER REPORT
[5 empty] | --- | 2016-08-25 16:02 | 2016-08-25 16:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE REGION DURING THE TIME OF TRIPPING.
[5 empty] | --- | 2016-08-25 19:32 | 2016-08-25 19:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE REGION DURING THE TIME OF TRIPPING.
[5 empty] | --- | 2016-08-25 21:20 | 2016-08-25 21:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE REGION DURING THE TIME OF TRIPPING.
[5 empty] | --- | 2016-08-14 18:41 | 2016-08-14 19:01 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING
16 | NER L116 | JIRIBAM_HAFLONG | 100.63 | North Eastern Region | --- | 2016-08-28 12:06 | 2016-08-28 12:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | NA | NA | NA | EVIDENCE OF INCLEMENT WEATHER & LIGHTNING AS SUPPORTED BY WEATHER REPORT & PATROL REPORT |  | 99.5
[5 empty] | --- | 2016-08-21 13:21 | 2016-08-21 13:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING
[5 empty] | --- | 2016-08-30 11:39 | 2016-08-30 15:20 | as given in (3) | 0 | 3 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D FOR RECTIFICATION OF JUMPER IN Y-PH AT LOC 81(A)
[5 empty] | --- | 2016-08-15 02:10 | 2016-08-15 02:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO THUNDERSTORM.
17 | NER L117 | JIRIBAM_LOKTAK 2 | 82.4 | North Eastern Region | --- | 2016-08-25 15:42 | 2016-08-25 15:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE REGION DURING THE TIME OF TRIPPING. |  | 99.98
|  |  | 82.4 | North Eastern Region | --- | 2016-08-16 15:57 | 2016-08-16 16:07 | as given in (3) | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Transient E/F
|  |  | 82.4 | North Eastern Region | --- | 2016-08-05 14:55 | 2016-08-05 15:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | NA | NA | NA | HEAVY LIGHTENING REPORTED FROM JIRIBAM END.
18 | NER L118 | KHANDONG-HAFLONG | 63.166 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
19 | NER L119 | KHANDONG_KHLIERIAT 1 | 42.48 | North Eastern Region | --- | 2016-08-24 15:50 | 2016-08-24 16:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING AT KHLIEHRIAT END |  | 100
[5 empty] | --- | 2016-08-15 03:21 | 2016-08-15 04:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO THUNDERSTORM.
[5 empty] | --- | 2016-08-08 09:23 | 2016-08-08 09:43 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | PROBLEM AT KHANGDONG END
20 | NER L120 | KHANDONG_KHLIERIAT 2 | 40.933 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
21 | NER L121 | KHANDONG_KOPILI 1 | 10.914 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
22 | NER L122 | KHLIERIAT_KHLIERIAT | 7.801 | North Eastern Region | --- | 2016-08-03 11:54 | 2016-08-03 20:48 | as given in (3) | 0 | 8 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR ATTENDING SPARKING AT Y-PH WAVETRAP. |  | 98.8
[5 empty] | --- | 2016-08-28 10:05 | 2016-08-28 11:58 | as given in (3) | 0 | 0 | 0 | 1 | 53 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
[5 empty] | --- | 2016-08-25 13:13 | 2016-08-25 13:34 | as given in (3) | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
[5 empty] | --- | 2016-08-25 09:23 | 2016-08-25 09:50 | as given in (3) | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
[5 empty] | --- | 2016-08-24 15:54 | 2016-08-24 16:01 | as given in (3) | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
[5 empty] | --- | 2016-08-18 23:39 | 2016-08-19 00:08 | as given in (3) | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
[5 empty] | --- | 2016-08-15 23:51 | 2016-08-16 00:21 | as given in (3) | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE JURISDICTION.
[5 empty] | --- | 2016-08-15 03:19 | 2016-08-15 04:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DIRECT LIGHTNING STROKE ON INSULATOR AT LOC 6-7
[5 empty] | --- | 2016-08-15 01:26 | 2016-08-15 02:39 | as given in (3) | 0 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
[5 empty] | --- | 2016-08-08 09:21 | 2016-08-08 10:02 | as given in (3) | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
[5 empty] | --- | 2016-08-05 21:06 | 2016-08-05 21:33 | as given in (3) | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
23 | NER L123 | KUMARGHAT_R C NAGAR | 104.02 | North Eastern Region | --- | 2016-08-20 09:35 | 2016-08-20 16:20 | as given in (3) | 0 | 6 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR JUMPER TIGHTENING AT LOC. 217. |  | 99.09
[5 empty] | jumper opened | 2016-08-31 07:51 | 2016-08-31 14:46 | as given in (3) | 0.28819 | 0 | 0 | 0 | 0 | 6 | 55 | 0 | 0 | 2 | N | -1.7118 | B-PH JUMPER OPENED AT LOC 263 DUE TO INCLEMENT WEATHER
24 | NER L124 | LOKTAK_IMPHAL 2 | 35.04 | North Eastern Region | --- | 2016-08-12 11:06 | 2016-08-12 11:20 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE END FEEDER. |  | 99.96
[5 empty] | --- | 2016-08-22 12:36 | 2016-08-22 12:55 | as given in (3) | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Transient E/F
25 | NER L125 | SALAKATI-GELEPHUG | 49.217 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
26 | NER L126 | NIRJULI-RANGANADI | 22.29 | North Eastern Region | --- | 2016-08-04 13:07 | 2016-08-04 13:34 | as given in (3) | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT. |  | 100
27 | NER L128 | KOLASIB-AIZAWL | 66.098 | North Eastern Region | --- | 2016-08-15 01:15 | 2016-08-15 01:42 | as given in (3) | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT AT KOLASIB END. |  | 100
[5 empty] | --- | 2016-08-25 16:43 | 2016-08-25 17:44 | as given in (3) | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION.
28 | NER L129 | RANGANADI-ZIRO | 44.523 | North Eastern Region | --- | 2016-08-13 06:45 | 2016-08-13 16:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 9 | 25 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF CONDUCTORS FROM EXISTING TO ERS TOWERS. DAMAGED BY LANDSLIDE. |  | 100
[5 empty] | --- | 2016-08-11 06:24 | 2016-08-11 17:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 10 | 51 | 0 | 0 | NA | NA | NA | SHIFTING OF CONDUCTOR FROM EXISTING TOWER TO ERS TOWER AT LOC. NO.12 (Damaged due to Landslide).
[5 empty] | --- | 2016-08-27 11:07 | 2016-08-27 11:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | NA | NA | NA | ZERO BUS VOLTAGE AT RANGANADI.
[5 empty] | --- | 2016-08-12 06:29 | 2016-08-12 15:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 9 | 23 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR SHIFTING OF CONDUCTORS FROM EXISTING TOWERS TO ERS TOWER AT LOC 12.
29 | NER L130 | KHANDONG_KOPILI 2 | 11.56 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
30 | NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) | 0.347 | North Eastern Region | --- | 2016-08-11 11:58 | 2016-08-11 12:05 | as given in (3) | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | NA | NA | NA | Problem at state end. |  | 100
[5 empty] | --- | 2016-08-21 11:33 | 2016-08-21 11:53 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-19 09:55 | 2016-08-19 10:02 | as given in (3) | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT AT STATE END.
[5 empty] | --- | 2016-08-17 07:37 | 2016-08-17 07:48 | as given in (3) | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-16 14:19 | 2016-08-16 14:23 | as given in (3) | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-15 15:29 | 2016-08-15 15:41 | as given in (3) | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-16 16:59 | 2016-08-16 17:33 | as given in (3) | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-08 14:36 | 2016-08-08 14:56 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-21 12:20 | 2016-08-21 12:33 | as given in (3) | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-03 16:58 | 2016-08-03 18:10 | as given in (3) | 0 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND POWERGRID'S JURISDICTION.
[5 empty] | --- | 2016-08-25 14:40 | 2016-08-25 14:55 | as given in (3) | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
[5 empty] | --- | 2016-08-25 15:40 | 2016-08-25 16:05 | as given in (3) | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT.
31 | NER L132 | DIMAPUR(PG)-DIMAPUR(LILO PORTION) | 0.347 | North Eastern Region | --- | 2016-08-25 15:50 | 2016-08-25 16:00 | as given in (3) | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to downstream fault. |  | 100
32 | NER L133 | SILCHAR-BADARPUR 1 | 19.195 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
33 | NER L134 | SILCHAR-BADARPUR 2 | 19.195 | North Eastern Region | --- | 2016-08-26 10:12 | 2016-08-26 11:33 | as given in (3) | 0 | 1 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | ESD TAKE FOR RECTIFICATION OF HOT SPOT IN Y-PHASE JUMPER AT LOC.68. |  | 99.82
34 | NER L135 | SILCHAR-SRIKONA 1 |  | North Eastern Region | --- | 2016-08-30 14:39 | 2016-08-30 14:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | SPS 1 & II OPERATED AT SILCHAR |  | 100
35 | NER L136 | SILCHAR-SRIKONA 2 |  | North Eastern Region | --- | 2016-08-30 14:39 | 2016-08-30 15:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | NA | NA | NA | SPS I & II OPERATED AT SILCHAR |  | 100
36 | NER L137 | IMPHAL-IMPHAL 2 | 0.442 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
37 | NER L138 | SILCHAR-HAILAKANDI 1 | 17.3 | North Eastern Region | --- | 2016-08-01 13:19 | 2016-08-01 18:53 | as given in (3) | 0 | 0 | 0 | 5 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | Fault beyond line length. |  | 100
[5 empty] | --- | 2016-08-15 21:15 | 2016-08-15 21:28 | as given in (3) | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT AT STATE END.
[5 empty] | --- | 2016-08-25 16:47 | 2016-08-25 17:01 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION.
[5 empty] | --- | 2016-08-27 04:38 | 2016-08-27 05:08 | as given in (3) | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE JURISDICTION FROM SILCHAR END.
[5 empty] | --- | 2016-08-30 14:39 | 2016-08-30 15:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | NA | NA | NA | SPS I & II OPERATED AT SILCHAR
38 | NER L139 | SILCHAR-HAILAKANDI 2 | 17.3 | North Eastern Region | --- | 2016-08-04 23:09 | 2016-08-04 23:23 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND POWERGRID'S JURISDICTION. |  | 100
[5 empty] | --- | 2016-08-31 00:51 | 2016-08-31 01:05 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURIDICTION
39 | NER L140 | MOKUKCHUNG_MOKUKCHUNG 1 | 1.4 | North Eastern Region | --- | 2016-08-29 09:17 | 2016-08-29 16:25 | as given in (3) | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP AT MOKOKCHUNG END |  | 99.04
40 | NER L141 | MOKOCHUNG-MOKOKCHUNG 2 | 1.4 | North Eastern Region | --- | 2016-08-30 09:55 | 2016-08-30 16:50 | as given in (3) | 0 | 6 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP IN BAY EQUIPMENT AT NAGALAND S/S |  | 99.07
41 | NER L142 | B.CHARAILI_PAVOI 1 | 12.93 | North Eastern Region | --- | 2016-08-09 12:29 | 2016-08-09 14:55 | as given in (3) | 0 | 0 | 0 | 2 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE END. |  | 100
[5 empty] | --- | 2016-08-24 11:26 | 2016-08-24 16:05 | as given in (3) | 0 | 0 | 0 | 4 | 39 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY PAVOI(AEGCL) S/S.
[5 empty] | --- | 2016-08-30 18:21 | 2016-08-30 18:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING AS RECORDED IN DR AGAINST TRIPPING
42 | NER L143 | B.CHARIALI_PAVOI 2 | 12.93 | North Eastern Region | --- | 2016-08-09 12:29 | 2016-08-09 14:55 | as given in (3) | 0 | 0 | 0 | 2 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE END. |  | 100
[5 empty] | --- | 2016-08-24 11:26 | 2016-08-24 16:05 | as given in (3) | 0 | 0 | 0 | 4 | 39 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY PAVOI(AEGCL) S/S.
43 | NER L148 | NIRJULI-RANGANADI | 22.29 |  | --- | 2016-08-27 11:07 | 2016-08-27 11:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | NA | NA | NA | ZERO BUS VOLTAGE AT RANGANADI. |  | 100
44 | NER L201 | BALIPARA_TEZPUR | 8.623 | North Eastern Region | --- | 2016-08-22 13:29 | 2016-08-22 14:09 | as given in (3) | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | NA | NA | NA | Tripped due to dwonstream fault. |  | 100
[5 empty] | --- | 2016-08-15 12:02 | 2016-08-15 12:22 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | AT SAME TIME SONABIL-SAMAGURI(STATE LINE)TRIPPED.
45 | NER L202 | KATHALGURI_MARIANI(OLD) | 162.864 |  | --- | 2016-08-30 09:37 | 2016-08-30 15:18 | as given in (3) | 0 | 5 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP OF BAY EQUIPMENT AT MARIANI AEGCL |  | 99.24
46 | NER L203 | MISA_DIMAPUR 1 | 123.52 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
47 | NER L204 | MISA_DIMAPUR 2 | 123.52 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
48 | NER L205 | MISA_KATHALGURI | 382.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
49 | NER L206 | MISA-KOPILI 1 | 72.791 | North Eastern Region | --- | 2016-08-24 08:19 | 2016-08-24 17:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 47 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR CLEARING JUNGLE LEANING FROM OUTSIDE CORRIDOR. |  | 100
|  |  | 72.791 | North Eastern Region | --- | 2016-08-23 15:06 | 2016-08-23 15:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | NA | NA | NA | SD TAKEN FOR INSTALLATION OF PMU AT KOPILI SS.
50 | NER L207 | MISA_KOPILI 2 | 72.791 | North Eastern Region | --- | 2016-08-23 15:31 | 2016-08-23 15:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | NA | NA | NA | SD TAKEN FOR INSTALLATION OF PMU AT KOPILI SS. |  | 100
51 | NER L208 | MISA_KOPILI 3 | 75.788 | North Eastern Region | --- | 2016-08-01 | 2016-08-11 23:09 | as given in (3) | 0 | 0 | 0 | 263 | 9 | 0 | 0 | 0 | 0 | NA | NA | NA | EMERGENCY S/D TAKEN BY KOPILI TO ATTEND CB PROBLEM (NEEPCO). |  | 100
[5 empty] | --- | 2016-08-17 12:54 | 2016-08-17 17:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 27 | 0 | 0 | NA | NA | NA | SUSPECTED DAMAGE CAUSED BY MISCREANTS.TREE FELLED AT LOC 178-179
[5 empty] | --- | 2016-08-23 15:46 | 2016-08-23 15:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | NA | NA | NA | SD TAKEN FOR INSTALLATION OF PMU AT KOPILI SS.
52 | NER L209 | MISA_MARIANI(OLD) | 220 | North Eastern Region | --- | 2016-08-30 01:12 | 2016-08-30 03:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 52 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTENING |  | 100
53 | NER L210 | MISA_SAMAGURI 1 | 34.439 | North Eastern Region | --- | 2016-08-17 08:49 | 2016-08-17 15:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 45 | NA | NA | NA | S/D TAKEN FOR REPLACEMENT OF CT AT SAMAGURI S/S IN LINE WITH DECISION OF 15TH NERPC MEETING |  | 100
54 | NER L211 | MISA_SAMAGURI 2 | 34.439 | North Eastern Region | --- | 2016-08-26 10:04 | 2016-08-26 14:45 | as given in (3) | 0 | 4 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP. |  | 99.37
55 | NER L212 | SALAKATI_BTPS 2 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
56 | NER L213 | SALAKATI-BTPS 1 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
57 | NER L214 | MISA-MARIANI(NEW) | 222.682 | North Eastern Region | --- | 2016-08-14 15:25 | 2016-08-14 15:55 | as given in (3) | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | Relay maloperation at Misa s/s |  | 99.93
58 | NER L215 | KATHALGURI-MARIANI(NEW) | 160.536 | North Eastern Region | --- | 2016-08-14 15:25 | 2016-08-14 16:03 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | NA | NA | NA | TRIPPED ON OVER VOLTAGE. |  | 100
[5 empty] | --- | 2016-08-18 08:51 | 2016-08-19 21:05 | as given in (3) | 0 | 0 | 0 | 36 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY KATHALIGURI END (NEEPCO).
59 | NER L216 | MARIANI_MOKUKCHUNG 1 | 48.8 | North Eastern Region | --- | 2016-08-09 04:10 | 2016-08-09 13:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 9 | 21 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE AT MOKOKCHUNG |  | 100
[5 empty] | --- | 2016-08-09 16:30 | 2016-08-09 16:41 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | NA | NA | NA | LINE H/T VIDE CODE 2419.
[5 empty] | --- | 2016-08-30 03:03 | 2016-08-30 13:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 10 | 44 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
[5 empty] | --- | 2016-08-25 13:54 | 2016-08-25 14:44 | as given in (3) | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | NA | NA | NA | AT THE SAME TIME 132 KV MOKOKCHUNG-DOYANG LINE TRIPPED.
[5 empty] | --- | 2016-08-16 03:26 | 2016-08-16 11:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 14 | 0 | 0 | NA | NA | NA | TRIPPED ON OVER-VOLTAGE.
[5 empty] | --- | 2016-08-14 15:25 | 2016-08-14 16:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO OVERVOLTAGE AT MOKOKCHUNG
[5 empty] | --- | 2016-08-12 17:52 | 2016-08-12 19:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 28 | NA | NA | NA | LINE H/T VIDE CODE 2472.
[5 empty] | --- | 2016-08-13 00:07 | 2016-08-13 00:39 | as given in (3) | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | NA | NA | NA | NO ABNORMALITY FOUND IN THE LINE
[5 empty] | Tower damaged | 2016-07-12 02:22 | 2016-08-03 14:52 | as given in (3) | 22.5208 | 0 | 0 | 0 | 0 | 540 | 30 | 0 | 0 | 50 | N | -27.4792 | TOWER DAMAGED AT LOC 56 & 57 CAUSED BY HEAVY LANDSLIDE DUE TO CONTINUOUS RAIN.
60 | NER L217 | MARIANI_MOKUKCHUNG 2 | 48.8 | North Eastern Region | Tower damaged | 2016-08-01 | 2016-08-31 23:59 | as given in (3) | 30.9993 | 0 | 0 | 0 | 0 | 743 | 59 | 0 | 0 | 50 | N | -19.0007 | AT LOC 56 & 57 TOWER DAMAGED |  | 100
61 | NER L401 | BALIPARA_BONGAIGAON 1 | 289.721 | North Eastern Region | --- | 2016-08-23 13:02 | 2016-08-23 13:36 | as given in (3) | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DURING MAINTENANCE OF NGR OF LINE REACTOR. |  | 99.7
[5 empty] | --- | 2016-08-07 05:08 | 2016-08-07 20:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | NA | NA | NA | LINE H/T VIDE CODE 2388.
[5 empty] | --- | 2016-08-11 16:09 | 2016-08-11 17:48 | as given in (3) | 0 | 1 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | RELAY MALOPERATION
[5 empty] | --- | 2016-08-14 04:09 | 2016-08-14 19:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | NA | NA | NA | LINE H/T VIDE CODE 2505.
[5 empty] | --- | 2016-08-30 19:45 | 2016-08-31 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 14 | NA | NA | NA | LINE H/T VIDE CODE 2854
62 | NER L402 | BALIPARA_BONGAIGAON 2 | 289.721 | North Eastern Region | --- | 2016-08-26 18:05 | 2016-08-26 18:27 | as given in (3) | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | LINE H/T FROM BONGAIGAON END DUE TO SPARKING OBSERVED AT Y-PH LINE ISOLATOR. |  | 99.95
[5 empty] | --- | 2016-08-09 02:12 | 2016-08-09 02:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | NA | NA | NA | FLASHOVER MARKS SEEN IN Y PHASE AT LOC 94 DUE TO HEAVY LIGHTNING
63 | NER L403 | MISA_BALIPARA 1 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
64 | NER L404 | MISA-BALIPARA 2 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
65 | NER L405 | BONGAIGAON-MALDA 1 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
66 | NER L406 | BONGAIGAON-MALDA 2 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
67 | NER L407 | BALIPARA-RANGANADI 1 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
68 | NER L408 | BALIPARA-RANGANADI 2 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
69 | NER L409 | PALLATANA-SURAJMANINAGAR 1 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
70 | NER L410 | PALLATANA-SURAJMANINAGAR 2 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
71 | NER L411 | BTPS-BONGAIGAON 1 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
72 | NER L412 | BTPS-BONGAIGAON 2 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
73 | NER L413 | BALIPARA-BONGAIGAON 3 | 309 | North Eastern Region | --- | 2016-08-24 07:57 | 2016-08-24 08:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO BAMBOOS TOUCHING LINE FROM OUTSIDE LINE CORRIDOR AT LOC 235-236 |  | 99.81
[5 empty] | --- | 2016-08-30 05:41 | 2016-08-30 18:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 13 | NA | NA | NA | LINE H/T VIDE CODE 2821
[5 empty] | --- | 2016-08-06 13:02 | 2016-08-06 18:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27 | NA | NA | NA | LINE H/T VIDE CODE 2379.
[5 empty] | --- | 2016-08-11 01:25 | 2016-08-11 02:49 | as given in (3) | 0 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPING INITIATED FROM L/R.
[5 empty] | --- | 2016-08-11 02:49 | 2016-08-11 11:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 36 | NA | NA | NA | LINE KEPT OPEN DUE TO SYSTEM CONSTRAINTS.
[5 empty] | --- | 2016-08-13 02:53 | 2016-08-13 20:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 37 | NA | NA | NA | LINE H/T VIDE CODE 2476.
[5 empty] | --- | 2016-08-17 09:35 | 2016-08-17 10:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | TRIPPED ON OVER-VOLTAGE.
[5 empty] | --- | 2016-08-20 15:15 | 2016-08-20 17:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 27 | NA | NA | NA | LINE H/T VIDE CODE 2672.
[5 empty] | --- | 2016-08-22 04:14 | 2016-08-22 18:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 26 | NA | NA | NA | LINE H/T VIDE CODE 2690.
[5 empty] | --- | 2016-08-05 07:05 | 2016-08-05 21:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 28 | NA | NA | NA | LINE H/T VIDE CODE 2367.
[5 empty] | --- | 2016-08-27 06:13 | 2016-08-27 10:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 44 | NA | NA | NA | LINE H/T VIDE CODE 2778.
[5 empty] | --- | 2016-08-09 13:35 | 2016-08-09 13:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | NA | NA | NA | S/D TAKEN FOR TAKING OUT L/R AT BALIPARA S/S.
[5 empty] | --- | 2016-08-03 04:44 | 2016-08-03 11:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 21 | NA | NA | NA | LINE H/T VIDE CODE 2320.
74 | NER L414 | BALIPARA-BONGAIGAON 4 | 309 | North Eastern Region | --- | 2016-08-04 04:02 | 2016-08-04 20:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | NA | NA | NA | LINE H/T VIDE CODE 2346. |  | 100
[5 empty] | --- | 2016-08-02 11:13 | 2016-08-02 19:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5 | NA | NA | NA | LINE H/T VIDE CODE 2310.
[5 empty] | --- | 2016-08-29 05:57 | 2016-08-29 13:12 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 15 | NA | NA | NA | LINE H/T VIDE CODE 2806
[5 empty] | --- | 2016-08-28 17:29 | 2016-08-28 19:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 36 | NA | NA | NA | LINE H.T VIDE CODE 2802.
[5 empty] | --- | 2016-08-10 00:48 | 2016-08-10 19:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | NA | NA | NA | LINE H/T VIDE CODE 2422.
[5 empty] | --- | 2016-08-13 10:49 | 2016-08-13 11:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | NA | NA | NA | SUSPECTED SABOTAGE BY MISCREANTS, FIR LODGED.
[5 empty] | --- | 2016-08-26 05:34 | 2016-08-26 18:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | NA | NA | NA | LINE H.T VIDE CODE 2757.
[5 empty] | --- | 2016-08-23 07:20 | 2016-08-23 13:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56 | NA | NA | NA | LINE H/T VIDE CODE 2699.
[5 empty] | --- | 2016-08-21 06:18 | 2016-08-21 19:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 44 | NA | NA | NA | LINE H/T VIDE CODE 2677.
[5 empty] | --- | 2016-08-11 00:10 | 2016-08-11 02:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 58 | NA | NA | NA | LINE H/T VIDE CODE 2432.
[5 empty] | --- | 2016-08-11 10:57 | 2016-08-12 14:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 27 | 25 | 0 | 0 | NA | NA | NA | SUSPECTED SABOTAGE BY MISCREANTS, FIR LODGED.
[5 empty] | --- | 2016-08-16 06:08 | 2016-08-16 19:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 26 | NA | NA | NA | LINE H/T VIDE CODE 2559.
[5 empty] | --- | 2016-08-14 23:09 | 2016-08-15 19:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | NA | NA | NA | LINE H/T VIDE CODE 2521.
[5 empty] | --- | 2016-08-16 23:11 | 2016-08-18 13:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 3 | NA | NA | NA | LINE H/T VIDE CODE 2577.
75 | NER L415 | SILCHAR-IMPHAL 1 | 167 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
76 | NER L416 | SILCHAR-IMPHAL 2 | 167 | North Eastern Region | --- | 2016-08-25 15:19 | 2016-08-25 15:30 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE REGION DURING THE TIME OF TRIPPING. |  | 100
77 | NER L417 | BALIPARA_B.CHAIRALI 3 | 57.294 | North Eastern Region | --- | 2016-08-11 16:26 | 2016-08-11 16:36 | as given in (3) | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | RELAY MALOPERATION |  | 99.98
78 | NER L418 | BALIPARA_B.CHAIRALI 4 | 57.294 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
79 | NER L419 | B.CHAIRALI_RANGANADI 1 | 129.335 | North Eastern Region | --- | 2016-08-27 11:15 | 2016-08-27 17:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | NA | NA | NA | LINE KEPT OPEN DUE TO SYSTEM CONSTRAINTS. |  | 100
[5 empty] | --- | 2016-08-27 11:07 | 2016-08-27 11:15 | as given in (3) | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | NA | NA | NA | NO ABNORMALITY OF THE LINE IS FOUND ON PATROLLING.
[5 empty] | --- | 2016-08-25 23:04 | 2016-08-26 16:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | NA | NA | NA | LINE H/T VIDE CODE 2755.
[5 empty] | --- | 2016-08-11 23:51 | 2016-08-12 15:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | NA | NA | NA | LINE H/T VIDE CODE 2448.
[5 empty] | --- | 2016-08-24 00:39 | 2016-08-24 18:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | NA | NA | NA | LINE H/T VIDE CODE 2711.
[5 empty] | --- | 2016-08-22 22:57 | 2016-08-23 17:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 53 | NA | NA | NA | LINE H/T VIDE CODE 2698.
[5 empty] | --- | 2016-08-15 23:48 | 2016-08-16 17:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | NA | NA | NA | LINE H/T VIDE CODE 2555.
[5 empty] | --- | 2016-08-17 01:09 | 2016-08-17 18:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | NA | NA | NA | LINE H/T VIDE CODE 2578.
[5 empty] | --- | 2016-08-18 20:58 | 2016-08-18 21:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | NA | NA | NA | TRIPPED ON OVER-VOLTAGE.
[5 empty] | --- | 2016-08-28 00:01 | 2016-08-28 16:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | NA | NA | NA | LINE H.T VIDE CODE 2787.
[5 empty] | --- | 2016-08-09 01:35 | 2016-08-09 18:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | NA | NA | NA | LINE H/T VIDE CODE 2404.
[5 empty] | --- | 2016-08-14 04:07 | 2016-08-14 18:14 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 7 | NA | NA | NA | LINE H/T VIDE CODE 2504.
80 | NER L420 | B.CHAIRALI_RANGANADI 2 | 129.335 | North Eastern Region | --- | 2016-08-14 22:56 | 2016-08-15 17:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 39 | NA | NA | NA | LINE H/T VIDE CODE 2520. |  | 100
[5 empty] | --- | 2016-08-13 10:54 | 2016-08-13 17:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 37 | NA | NA | NA | LINE H/T VIDE CODE 2482.
[5 empty] | --- | 2016-08-21 05:35 | 2016-08-21 17:32 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 57 | NA | NA | NA | LINE H/T VIDE CODE 2676.
[5 empty] | --- | 2016-08-21 21:40 | 2016-08-22 10:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | NA | NA | NA | Line H/T vide code 2687.
[5 empty] | --- | 2016-08-28 23:55 | 2016-08-29 17:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 45 | NA | NA | NA | LINE H/T VIDE CODE 2804
[5 empty] | --- | 2016-08-31 01:29 | 2016-08-31 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 30 | NA | NA | NA | LINE H/T VIDE CODE 2871
[5 empty] | --- | 2016-08-18 05:41 | 2016-08-18 09:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 37 | NA | NA | NA | LINE H/T VIDE CODE 2614.
[5 empty] | --- | 2016-08-29 21:04 | 2016-08-29 21:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTENING
[5 empty] | --- | 2016-08-27 00:10 | 2016-08-27 11:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | NA | NA | NA | LINE H/T VIDE CODE 2774.
[5 empty] | --- | 2016-08-25 00:38 | 2016-08-25 18:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | NA | NA | NA | LINE H/T VIDE CODE 2730.
[5 empty] | --- | 2016-08-29 23:36 | 2016-08-30 09:19 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 43 | NA | NA | NA | LINE H/T VIDE CODE 2819
81 | NER L421 | BALIPARA_B.CHAIRALI 1 | 59.54 | North Eastern Region | --- | 2016-08-18 20:58 | 2016-08-18 21:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | NA | NA | NA | TRIPPED ON OVER-VOLTAGE. |  | 100
82 | NER L422 | BALIPARA_B.CHAIRALI 2 | 59.54 | North Eastern Region | --- | 2016-08-09 00:12 | 2016-08-12 13:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 10 | NA | NA | NA | LINE H/T VIDE CODE 2403. |  | 99.97
[5 empty] | --- | 2016-08-08 06:23 | 2016-08-08 20:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | NA | NA | NA | LINE H/T VIDE 2390
[5 empty] | --- | 2016-08-06 02:30 | 2016-08-06 17:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | NA | NA | NA | LINE KEPT OPEN ON NERLDC INSTRUCTIONS.
[5 empty] | insulator decapped | 2016-08-06 02:15 | 2016-08-06 02:30 | as given in (3) | 0.010417 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | N | -0.98958 | DECAPPING OF INSULATORS
[5 empty] | --- | 2016-07-24 05:55 | 2016-08-06 01:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 3 | NA | NA | NA | LINE H/T VIDE CODE 2219
83 | NER L423 | SILCHAR-PURBAKANCHANBARI 1 | 127.2 | North Eastern Region | --- | 2016-08-31 09:18 | 2016-08-31 10:07 | as given in (3) | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | NA | NA | NA | LINE H/T AT PKBARI END ON RLDC INSTR. FOR RESYNCH. WITH RCNAGAR |  | 100
[5 empty] | --- | 2016-08-02 09:53 | 2016-08-02 17:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 12 | NA | NA | NA | S/D TAKEN FOR JUMPER TIGHTENING WITH SECURITY FORCES IN SECTION OF LINE AFFECTED BY ROW
[5 empty] | --- | 2016-08-27 14:41 | 2016-08-27 16:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 18 | NA | NA | NA | E/S/D TAKEN FOR REFIXING OF DETACHED JUMPER OF Y-PH AT LOC. NO 95 SEVERELY AFFECTED BY ROW ISSUES.
[5 empty] | --- | 2016-08-15 21:40 | 2016-08-15 22:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | NA | NA | NA | DR CONFIRMS TRIPPING DUE TO LIGHTNING
84 | NER L424 | SILCHAR-PURBAKANCHANBARI 2 | 127.2 | North Eastern Region | --- | 2016-08-31 09:18 | 2016-08-31 10:12 | as given in (3) | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | NA | NA | NA | LINE H/T AT PKBARI END ON RLDC INSTRCTION OF RESYNCH. WITH RCNAGAR |  | 100
[5 empty] | --- | 2016-08-30 15:44 | 2016-08-30 18:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 51 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REFIXING Y-PH JUMPER AT LOC 92; OPENED ON 27.8.16 ON A/C OF INCLEMENT WEATHER
[5 empty] | --- | 2016-08-29 12:41 | 2016-08-29 15:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 25 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REFIXING Y-PH JUMPER AT LOC 92; OPENED ON 27.8.16 ON A/C OF INCLEMENT WEATHER
[5 empty] | --- | 2016-08-27 21:13 | 2016-08-27 21:34 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING. ONE STRING JUMPR OPENED AT LOC 92 IN Y-PHASE
[5 empty] | --- | 2016-08-03 09:20 | 2016-08-03 17:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | NA | NA | NA | S/D TAKEN FOR JUMPER TIGHTENING IN LOCATIONS SEVERELY AFFECTED BY ROW
[5 empty] | --- | 2016-08-03 17:40 | 2016-08-03 19:00 | as given in (3) | 0 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | DELAY DUE TO PROBLEM AT P.K.BARI END.
[5 empty] | --- | 2016-08-05 11:00 | 2016-08-05 14:13 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 13 | NA | NA | NA | S/D TAKEN FOR JUMPER RECTIFICATION IN LOCATIONS SEVERELY AFFECTED BY ROW ISSUES
[5 empty] | --- | 2016-08-27 05:16 | 2016-08-27 05:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING. ONE STRING JUMPR OPENED AT LOC 92 IN Y-PHASE
85 | NER RBR1 | BR_BONGAIGAON (50MVAR) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
86 | NER RBR2 | BR_BONGAIGAON (50MVAR) 2 | 50 | North Eastern Region | --- | 2016-08-06 14:01 | 2016-08-06 22:38 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 37 | NA | NA | NA | B/R KEPT OPEN AS PER NERLDC INSTRUCTIONS. |  | 100
87 | NER RBR3 | BR_BALIPARA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
88 | NER RBR4 | BR_MISA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
89 | NER RBR5 | BR_KUMARGHAT (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
90 | NER RBR6 | BR_AIZWAL (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
91 | NER RBR7 | BR_BONGAIGAON(80MVAR) 3 | 80 | North Eastern Region | --- | 2016-08-18 18:19 | 2016-08-18 21:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 41 | NA | NA | NA | B/R H/T VIDE CODE 2646. |  | 100
92 | NER RBR8 | BR_BALIPARA(80MVAR) 2 | 80 | North Eastern Region | --- | 2016-08-18 14:36 | 2016-08-19 07:49 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | NA | NA | NA | B/R H/T VIDE CODE 2636. |  | 100
93 | NER RBR9 | BR_SILCHAR(63MVAR) 1 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
94 | NER RBR10 | BR_SILCHAR(63MVAR) 2 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
95 | NER RBR11 | BR_BONGAIGAON(80MVAR) 4 | 80 | North Eastern Region | --- | 2016-08-18 16:05 | 2016-08-20 06:09 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 4 | NA | NA | NA | B/R H/T VIDE CODE 2643. |  | 100
96 | NER RBR12 | BR_B'CHARIALI(80MVAR) 1 | 80 | North Eastern Region | --- | 2016-08-18 14:13 | 2016-08-18 20:51 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 38 | NA | NA | NA | B/R H/T VIDE CODE 2633 |  | 100
97 | NER RBR13 | BR_B'CHARIALI(80MVAR) 2 | 80 | North Eastern Region | --- | 2016-08-18 14:25 | 2016-08-18 20:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 32 | NA | NA | NA | B/R H/T VIDE CODE 2635 |  | 99.68
[5 empty] | --- | 2016-08-02 14:51 | 2016-08-02 17:14 | as given in (3) | 0 | 2 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR ATTENDING OIL LEAKAGE FROM REACTOR.
98 | NER TICT1 | ICT_SILCHAR (200MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
99 | NER TICT2 | ICT_BALIPARA (315MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
100 | NER TICT4 | ICT_SALAKATI (50 MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
101 | NER TICT5 | ICT_DIMAPUR (100 MVA) 1 | 100 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
102 | NER TICT6 | ICT_KUMARGHAT(5MVA) | 5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
103 | NER TICT7 | ICT_NIRJULI(16MVA) 1 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
104 | NER TICT8 | ICT_NIRJULI(10MVA) 2 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
105 | NER TICT10 | ICT_ZIRO (15MVA) | 15 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
106 | NER TICT11 | ICT_NIRJULI (16MVA) 2 | 16 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
107 | NER TICT12 | ICT_KOPILI (160 MVA) 2 | 160 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
108 | NER ICT13 | ICT_DIMAPUR (100 MVA) 2 | 100 | North Eastern Region | --- | 2016-08-30 08:16 | 2016-08-30 08:58 | as given in (3) | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP WORKS. S/D RETURNED EARLY DUE TO INCLEMENT WEATHER |  | 99.91
109 | NER TICT14 | ICT_MISA 1 | 315 | North Eastern Region | --- | 2016-08-19 11:34 | 2016-08-19 12:44 | as given in (3) | 0 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR CHANGE OVER OF UNITS. |  | 99.84
110 | NER TICT15 | ICT_SILCHAR(200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
111 | NER TICT16 | ICT_SILCHAR(200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
112 | NER TICT17 | ICT_BONGAIGAON(315MVA) | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
113 | NER TICT18 | ICT_MISA 2 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
114 | NER TICT19 | ICT_MOKOKCHUNG(30MVA) 1 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
115 | NER TICT20 | ICT_MOKOKCHUNG(30MVA) 2 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
116 | NER TICT21 | ICT_B'CHARIALI (200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
117 | NER TICT22 | ICT_B'CHARIALI (200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
118 | NER TICT23 | ICT_NIRJULI(50MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
119 | NER ICT27 | ICT_IMPHAL(50MVA) 1 | 50 | North Eastern Region | --- | 2016-08-17 09:17 | 2016-08-17 15:58 | as given in (3) | 0 | 6 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP OF ICT-1 AND IT'S BAY. |  | 99.1

## SEPT
S/No | Unique ID of Transmission Element | Element Name | Description (Length-km/Nos./MVA/ MVAr/MW/ etc. | Region | Type of failure | Outage Date & Time Hr Mn | Restoration Date & Time Hr Mn | Details of outage ( No. of Towers damaged, no. of insulators failed etc.) | Total Outage (in Days) (1) | Duration of Outage attribuatable to | [7 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual & Norm (1 - 2) | Detailed Reason for Outage (3) | Outage certifying Agency & Reference Document | % Availability as certified by certifying agency
[10 empty] | ISTS Licensee Hr Min |  | Others Hr Min |  | System Constraint/ Natural calamity/ Milliitancy Hr Min |  | Deemed Available Hr Min
SEPTEMBER' 2016 |  |  |  |  | ---
1 | NER L101 | RCN_AGARTALA 1 | 8.384 | North Eastern Region | --- | 2016-09-28 09:06 | 2016-09-28 16:58 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 7 | 52 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR MASS TIGHTENING OF JUMPERS | NERPC | 100
[5 empty] | --- | 2016-09-29 08:45 | 2016-09-29 13:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR TIGHTENING OF JUMPERS
[5 empty] | --- | 2016-09-03 10:09 | 2016-09-03 12:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR RECTIFICATION OF Y-PH CT DROPPER AT AGARTALA END.
[5 empty] | --- | 2016-09-10 10:05 | 2016-09-10 19:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR CONDUCTOR REPLACEMENT BETWEEN LOC 29-30
[5 empty] | --- | 2016-09-21 04:50 | 2016-09-21 12:36 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 7 | 46 | 0 | 0 | NA | NA | NA | LINE PUT UNDER S/D FOR RECTIFICATION WORK AT GANTRY TOWER AT RCNAGAR END(R-PH CVT DROPPER FAILED)
2 | NER L102 | RCN_AGARTALA 2 | 8.384 | North Eastern Region | --- | 2016-09-03 12:45 | 2016-09-03 15:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 39 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR RECTIFICATION OF Y-PH CT DROPPER AT AGARTALA END.. |  | 100
[5 empty] | --- | 2016-09-10 19:15 | 2016-09-10 20:03 | as given in (3) | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | NA | NA | NA | CHARGING DELAYED BY STATE & RCNAGAR END
[5 empty] | --- | 2016-09-30 08:14 | 2016-09-30 16:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 8 | 26 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR MASS TIGHTENING OF JUMPERS/ATTENDING OTHER CRITICAL HOTSPOTS
3 | NER L103 | BADARPUR_KOLASIB | 107.226 | North Eastern Region | --- | 2016-09-29 12:54 | 2016-09-29 19:33 | as given in (3) | 0 | 0 | 0 | 6 | 39 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE |  | 100
[5 empty] | jumper strand damage | 2016-09-21 18:30 | 2016-09-21 19:26 | as given in (3) | 0.038889 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 2 | N | -1.9611 | JUMPER STRAND DAMAGED IN R-Y-B PH AT LOC 124 DUE TO DIRECT LIGHTNING STROKE
[5 empty] | --- | 2016-09-23 11:20 | 2016-09-23 12:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 25 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR RECTIFICATION OF JUMPER AT LOC. 124.
[5 empty] | --- | 2016-09-23 12:45 | 2016-09-23 13:36 | as given in (3) | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | NA | NA | NA | DELAY IN RESTORATION DUE TO PROBLEM AT KOLASIB END.
4 | NER L104 | AIZWAL_KUMARGHAT | 131 | North Eastern Region | --- | 2016-09-23 17:14 | 2016-09-23 17:29 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | INSULATOR FLASHOVER MARK IN Y-PH AT LOC 33 DUE TO LIGHTNING |  | 99.27
[5 empty] | --- | 2016-09-23 12:31 | 2016-09-23 12:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED AT AIZAWL END.INSULATOR FLASHOVER MARK IN Y-PH AT LOC 33 DUE TO LIGHTNING
[5 empty] | --- | 2016-09-03 12:40 | 2016-09-03 12:45 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | NA | NA | NA | TREES SLIDED FROM UPHILL SIDE OUTSIDE LINE CORRIDOR DUE TO LANDSLIDE AT LOC 53-54
[5 empty] | --- | 2016-09-15 11:21 | 2016-09-15 16:30 | as given in (3) | 0 | 5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR JUMPER TIGHENING WORKS AT LOC 168/0,17/0 & 119/0
5 | NER L105 | AIZWAL_ZEMEBAK 2 | 6.719 | North Eastern Region | --- | 2016-09-16 23:36 | 2016-09-16 23:47 | as given in (3) | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT AT STATE END |  | 100
[5 empty] | --- | 2016-09-13 15:40 | 2016-09-13 15:56 | as given in (3) | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE END
6 | NER L106 | BADARPUR-BADARPUR | 1.023 | North Eastern Region | --- | 2016-09-29 11:04 | 2016-09-29 18:38 | as given in (3) | 0 | 0 | 0 | 7 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | 132KV MAIN BUS S/D TAKEN BY STATE END |  | 100
[5 empty] | --- | 2016-09-28 23:52 | 2016-09-29 00:19 | as given in (3) | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | PROBLEM AT STATE END
7 | NER L107 | BADARPUR_JIRIBAM | 67.21 | North Eastern Region | --- | 2016-09-25 01:59 | 2016-09-25 02:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM AT JIRIBAM END AT TIME OF TRIPPING. FLASHOVER MARKS FOUND IN LOC 189 (R-PH0 |  | 100
[5 empty] | --- | 2016-09-20 08:25 | 2016-09-20 08:40 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER DURING THE TIME OF TRIPPING.FLASH MARKS FOUND IN DISC 1,2,3 & 6 R-PH AT LOC 66
8 | NER L108 | BADARPUR_KHLIERIAT | 76.646 | North Eastern Region | --- | 2016-09-06 09:34 | 2016-09-06 13:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REPLACING INSULATOR STACK AT LOC. 206 DAMAMGED DUE TO HEAVY LIGHTENING. |  | 100
9 | NER L109 | BADARPUR_KUMARGHAT | 118.513 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
10 | NER L110 | DIMAPUR_IMPHAL | 168.865 | North Eastern Region | --- | 2016-09-28 10:36 | 2016-09-28 10:57 | as given in (3) | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | NA | NA | NA | NO ABNORMALITY FOUND IN THE LINE AS PER PATROL REPORT WHICH MAY HAVE LED TO TRIPPING |  | 99.74
[5 empty] | --- | 2016-09-11 05:59 | 2016-09-11 07:31 | as given in (3) | 0 | 1 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D OF 132 KV MAIN BUS AT IMPHAL FOR ATTENIND HOTSPOT IN MAIN BUS JUMPER (Y-PH) OF LOKTAK BAYS
11 | NER L111 | DOYANG_DIMAPUR 1 | 92.526 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
12 | NER L112 | DOYANG_DIMAPUR 2 | 92.526 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
13 | NER L113 | GOHPUR_NIRJULI | 42.5 | North Eastern Region | --- | 2016-09-08 19:50 | 2016-09-08 20:17 | as given in (3) | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO PROBLEM AT STATE END. |  | 100
14 | NER L114 | IMPHAL_IMPHAL 1 | 1.5 | North Eastern Region | --- | 2016-09-11 06:02 | 2016-09-11 07:38 | as given in (3) | 0 | 1 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D OF 132KV MAIN BUS AT IMPHAL FOR ATTENDING HOTSPOTS IN MAIN BUS JUMPER (Y-PH) OF LOKTAK BAYS |  | 99.79
[5 empty] | --- | 2016-09-14 11:02 | 2016-09-14 11:24 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE END
15 | NER L115 | JIRIBAM_AIZWAL | 172.315 | North Eastern Region | --- | 2016-09-17 01:08 | 2016-09-17 01:22 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED DURING THE TIME OF TRIPPING |  | 100
[5 empty] | disc insulator broken | 2016-09-28 23:36 | 2016-09-29 00:04 | as given in (3) | 0.019444 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 1 | N | -0.98056 | DISC INSULATOR FOUND BROKEN IN R-PH,LOC 185
16 | NER L116 | JIRIBAM_HAFLONG | 100.63 | North Eastern Region | --- | 2016-09-13 20:04 | 2016-09-13 20:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING DUE TO DR REPORT |  | 100
[5 empty] | --- | 2016-09-30 12:32 | 2016-09-30 12:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | BAMBOO CUT BY MISCREANTS AT LOC 275-276 FELL FROM OUTSIDE CORRIDOR ON Y PH
[5 empty] | conductor grounded | 2016-09-03 22:28 | 2016-09-04 17:45 | as given in (3) | 0.80347 | 0 | 0 | 0 | 0 | 19 | 17 | 0 | 0 | 1 | N | -0.19653 | AT LOC. 241, Y-PH INSULATOR DECAPPED AND CONDUCTOR GROUNDED DUE TO INCLEMENT WEATHER.
17 | NER L117 | JIRIBAM_LOKTAK 2 | 82.4 | North Eastern Region | --- | 2016-09-25 01:26 | 2016-09-25 01:54 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | NA | NA | NA | HEAVY THUNDERSTORM AT JIRIBAM END AT TIME OF TRIPPING. |  | 100
[5 empty] | --- | 2016-09-24 11:59 | 2016-09-24 12:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED AT JIRIBAM END AND SUPPORTED BY WEATHER REPORT
18 | NER L118 | KHANDONG-HAFLONG | 63.166 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
19 | NER L119 | KHANDONG_KHLIERIAT 1 | 42.48 | North Eastern Region | --- | 2016-09-26 13:14 | 2016-09-26 13:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING AS CONFIRMED BY DR REPORT |  | 100
[5 empty] | --- | 2016-09-23 08:02 | 2016-09-23 15:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 0 | NA | NA | NA | E S/D AVAILED FOR RECTIFICATION OF SNAPED EARTH WAIRE BETWN. LOC. NO. 100 TO 110.
[5 empty] | --- | 2016-09-22 12:28 | 2016-09-22 20:26 | as given in (3) | 0 | 0 | 0 | 7 | 58 | 0 | 0 | 0 | 0 | NA | NA | NA | CB RECLOSED AT KHL END. LATE INTIMATION BY KHANGDONG END REGARDING GEN.PROBLEM LEADING TO TRIPPING.
[5 empty] | --- | 2016-09-18 10:55 | 2016-09-18 11:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO HEAVY LIGHTNING
[5 empty] | --- | 2016-09-16 21:27 | 2016-09-17 00:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 2 | 37 | 0 | 0 | NA | NA | NA | E/S/D FOR REMOVAL OF DAMAGED EARTHWIRE, DUE TO LIGHTENING, FROM NEARBY DISTRIBUTION FEEDERS
[5 empty] | --- | 2016-09-16 14:57 | 2016-09-16 15:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED IN THE AREA
[5 empty] | --- | 2016-09-26 13:47 | 2016-09-26 13:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING AS CONFIRMED BY DR REPORT
[5 empty] | --- | 2016-09-30 13:54 | 2016-09-30 14:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | NA | NA | NA | BAD WEATHER & LIGHTNING PREVAILING IN REGION
[5 empty] | --- | 2016-09-27 13:55 | 2016-09-27 14:02 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | NA | NA | NA | AT LOC 39, Y-PH INSULATOR DECAPPED & CONDUCTOR GROUNDED AND E/W SNAPPED DUE TO HEAVY LIGHTNING.
[5 empty] | Insulator decapped, Conductor grounded, E/w snapped | 2016-09-27 14:17 | 2016-09-27 23:43 | as given in (3) | 0.39306 | 0 | 0 | 0 | 0 | 9 | 26 | 0 | 0 | 1 | N | -0.60694 | AT LOC 39, Y-PH INSULATOR DECAPPED & CONDUCTOR GROUNDED AND E/W SNAPPED DUE TO HEAVY LIGHTNING.
20 | NER L120 | KHANDONG_KHLIERIAT 2 | 40.933 | North Eastern Region | --- | 2016-09-17 14:21 | 2016-09-17 14:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING |  | 100
[5 empty] | --- | 2016-09-16 14:53 | 2016-09-16 15:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER DURING THE TIME OF TRIPPING
21 | NER L121 | KHANDONG_KOPILI 1 | 10.914 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
22 | NER L122 | KHLIERIAT_KHLIERIAT | 7.801 | North Eastern Region | --- | 2016-09-28 11:08 | 2016-09-28 11:31 | as given in (3) | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION |  | 100
[5 empty] | --- | 2016-09-29 01:54 | 2016-09-29 02:09 | as given in (3) | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND JURISDICTION
[5 empty] | --- | 2016-09-12 14:42 | 2016-09-12 15:04 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-09-15 13:56 | 2016-09-15 14:14 | as given in (3) | 0 | 0 |  | 0 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-09-19 13:02 | 2016-09-19 13:22 | as given in (3) | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-09-20 13:17 | 2016-09-20 13:54 | as given in (3) | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH
[5 empty] | --- | 2016-09-22 08:51 | 2016-09-22 12:15 | as given in (3) | 0 | 0 | 0 | 3 | 24 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY KHLIEHRIAT(STATE) END.
[5 empty] | --- | 2016-09-09 01:43 | 2016-09-09 02:09 | as given in (3) | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH.
23 | NER L123 | KUMARGHAT_R C NAGAR | 104.02 | North Eastern Region | --- | 2016-09-20 04:04 | 2016-09-20 04:31 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | HEAVY LIGHTNING AS CONFIRMED BY FLASHOVER MARKS AT LOC 213 |  | 100
24 | NER L124 | LOKTAK_IMPHAL 2 | 35.04 | North Eastern Region | --- | 2016-09-16 11:19 | 2016-09-16 11:28 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | NA | NA | NA | BROKEN TREE BRANCH FROM UPHILL SIDE WAS FOUND VERY NEAR TO B-CNDCTR AT LOC 23-24 |  | 99.73
[5 empty] | --- | 2016-09-11 06:04 | 2016-09-11 07:53 | as given in (3) | 0 | 1 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D OF 132KV MAIN BUS AT IMPHAL FOR ATTENDING HOTSPOTS IN MAIN BUS JUMOER (Y-PH) OF LOKTAK BAYS
25 | NER L126 | NIRJULI-RANGANADI | 22.29 | North Eastern Region | --- | 2016-09-19 09:09 | 2016-09-19 18:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 39 | NA | NA | NA | S/D TAKEN FOR REPLACEMENT OF PEAK AT LOC NO 48, 68 AND OPGW INSTALLATION AT LOC 31 TO 33 |  | 100
26 | NER L128 | KOLASIB-AIZAWL | 66.098 | North Eastern Region | --- | 2016-09-30 17:14 | 2016-09-30 18:34 | as given in (3) | 0 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR RECTIFICATION OF DAMAGED EARTHWIRE AT LOC 195 |  | 99.77
[5 empty] | --- | 2016-09-30 12:51 | 2016-09-30 13:11 | as given in (3) | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | T&P SLIPPED AND FELL ON CONDUCTOR DURING SHUTDOWN WORKS
27 | NER L129 | RANGANADI-ZIRO | 44.523 | North Eastern Region | --- | 2016-09-21 11:01 | 2016-09-21 15:35 | as given in (3) | 0 | 0 | 0 | 4 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY RANGANADI (NEEPCO) |  | 100
28 | NER L130 | KHANDONG_KOPILI 2 | 11.56 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
29 | NER L131 | DIMAPUR(PG)-KOHIMA(LILO PORTION) | 0.347 | North Eastern Region | --- | 2016-09-28 14:30 | 2016-09-28 14:40 | as given in (3) | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTRAM FAULT |  | 100
[5 empty] | --- | 2016-09-30 11:20 | 2016-09-30 11:30 | as given in (3) | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT
[5 empty] | --- | 2016-09-06 14:39 | 2016-09-06 14:53 | as given in (3) | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT IN STATE PORTION OF LINE.
[5 empty] | --- | 2016-09-19 17:17 | 2016-09-19 18:10 | as given in (3) | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE END.
[5 empty] | --- | 2016-09-27 16:09 | 2016-09-27 16:34 | as given in (3) | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT AT STATE END.
[5 empty] | --- | 2016-09-13 15:55 | 2016-09-14 15:10 | as given in (3) | 0 | 0 | 0 | 23 | 15 | 0 | 0 | 0 |  | NA | NA | NA | TRIPPED DUE TO FAULT AT STATE END
[5 empty] | --- | 2016-09-17 21:14 | 2016-09-17 21:23 | as given in (3) | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT AT STATE END
30 | NER L132 | DIMAPUR(PG)-DIMAPUR(LILO PORTION) | 0.347 | North Eastern Region | --- | 2016-09-19 17:48 | 2016-09-19 18:16 | as given in (3) | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO FAULT IN STATE END |  | 100
31 | NER L133 | SILCHAR-BADARPUR 1 | 19.195 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
32 | NER L134 | SILCHAR-BADARPUR 2 | 19.195 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
33 | NER L135 | SILCHAR-SRIKONA 1 | 1.199 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
34 | NER L136 | SILCHAR-SRIKONA 2 | 1.199 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
35 | NER L137 | IMPHAL-IMPHAL 2 | 0.442 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
36 | NER L138 | SILCHAR-HAILAKANDI 1 | 17.3 | North Eastern Region | --- | 2016-09-29 17:32 | 2016-09-29 18:53 | as given in (3) | 0 | 0 | 0 | 1 | 21 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT BEYOND LINE LENGTH |  | 100
[5 empty] | --- | 2016-09-22 09:42 | 2016-09-22 17:28 | as given in (3) | 0 | 0 | 0 | 7 | 46 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY HAILAKANDI(STATE) END.
[5 empty] | --- | 2016-09-26 10:18 | 2016-09-27 18:41 | as given in (3) | 0 | 0 | 0 | 32 | 23 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE(ASSAM)UP TO 27.09.16
[5 empty] | --- | 2016-09-30 09:52 | 2016-09-30 23:59 | as given in (3) | 0 | 0 | 0 | 14 | 7 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN BY STATE END
[5 empty] | --- | 2016-09-29 11:09 | 2016-09-29 15:36 | as given in (3) | 0 | 0 | 0 | 4 | 27 | 0 | 0 | 0 | 0 | NA | NA | NA | 132KV MAIN BUS S/D TAKEN BY STATE END
[5 empty] | --- | 2016-09-28 23:48 | 2016-09-29 00:19 | as given in (3) | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | NA | NA | NA | FAULT IN DOWNSTRAM END
37 | NER L139 | SILCHAR-HAILAKANDI 2 | 17.3 | North Eastern Region | --- | 2016-09-16 10:37 | 2016-09-18 15:15 | as given in (3) | 0 | 0 | 0 | 52 | 38 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE |  | 100
[5 empty] | --- | 2016-09-07 08:30 | 2016-09-07 18:04 | as given in (3) | 0 | 0 | 0 | 9 | 34 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE END.
[5 empty] | --- | 2016-09-06 09:41 | 2016-09-06 17:19 | as given in (3) | 0 | 0 | 0 | 7 | 38 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE END.
38 | NER L140 | MOKOCHUNG-MOKOKCHUNG 1 | 1.4 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
39 | NER L141 | MOKOCHUNG-MOKOKCHUNG 2 | 1.4 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
40 | NER L142 | B.CHARAILI_PAVOI 1 | 12.93 | North Eastern Region | --- | 2016-09-23 00:15 | 2016-09-23 01:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING AS SUPPORTED BY DR |  | 100
41 | NER L143 | B.CHARAILI_PAVOI 2 | 12.93 | North Eastern Region | --- | 2016-09-23 00:15 | 2016-09-23 01:08 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER REPORTED DURING THE TIME OF TRIPPING AS SUPPORTED BY DR |  | 100
42 | NER L144 | NIRJULI-LEKHI | 9.7 | North Eastern Region | --- | 2016-09-08 19:50 | 2016-09-08 20:17 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWN STREAM FAULT. |  | 100
[5 empty] | --- | 2016-09-23 04:01 | 2016-09-23 04:23 | as given in (3) | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT |  | 100
43 | NER L147 | HAFLONG-UMRANGSO |  |  | --- | 2016-09-22 13:07 | 2016-09-22 13:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER PREVAILED DURING TIME OF TRIPPING.FLASHOVER MARKS FOUND AT LOC 63 B-PH INSULATOR |  | 100
44 | NER L148 | NIRJULI-RANGANADI | 22.29 |  | --- | 2016-09-25 08:59 | 2016-09-25 12:15 | as given in (3) | 0 | 0 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY STATE END. |  | 100
45 | NER L201 | BALIPARA_TEZPUR | 8.623 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
46 | NER L202 | KATHALGURI_MARIANI(OLD) | 162.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
47 | NER L203 | MISA_DIMAPUR 1 | 123.52 | North Eastern Region | --- | 2016-09-12 12:30 | 2016-09-12 14:37 | as given in (3) | 0 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REMOVING R-PH CVT (FAULTY) AT DIMAPUR |  | 99.71
48 | NER L204 | MISA_DIMAPUR 2 | 123.52 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
49 | NER L205 | MISA_KATHALGURI | 382.864 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
50 | NER L206 | MISA-KOPILI 1 | 72.791 | North Eastern Region | --- | 2016-09-24 10:07 | 2016-09-24 10:50 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | NA | NA | NA | BAMBOO CAME DOWN FROM UPHILL SIDE DUE TO SOIL EROSION BY HEAVY RAIN & TOUCHED LINE AT LOC 311-312 |  | 100
51 | NER L207 | MISA_KOPILI 2 | 72.791 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
52 | NER L208 | MISA_KOPILI 3 | 75.788 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
53 | NER L209 | MISA_MARIANI(OLD) | 220 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
54 | NER L210 | MISA_SAMAGURI 1 | 34.439 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
55 | NER L211 | MISA_SAMAGURI 2 | 34.439 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
56 | NER L212 | SALAKATI_BTPS 2 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
57 | NER L213 | SALAKATI-BTPS 1 | 2.7 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
58 | NER L214 | MISA-MARIANI(NEW) | 222.682 | North Eastern Region | --- | 2016-09-06 15:31 | 2016-09-06 15:46 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | NA | NA | NA | TRIPPED ON OVER-VOLTAGE. |  | 100
[5 empty] | --- | 2016-09-05 22:06 | 2016-09-05 23:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | NA | NA | NA | PATROLLING DONE AND FLASHOVER MARK SEEN IN EARTHWIRE FITTING AT LOC 800-801 DUE TO LIGHTNING
59 | NER L215 | KATHALGURI-MARIANI(NEW) | 160.536 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
60 | NER L216 | MARIANI_MOKUKCHUNG 1 | 48.8 | North Eastern Region | --- | 2016-09-28 03:50 | 2016-09-28 04:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | NA | NA | NA | OVERVOLTAGE AT MOKOKCHUNG END |  | 100
[5 empty] | --- | 2016-09-17 14:24 | 2016-09-17 15:16 | as given in (3) | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | NA | NA | NA | AT SAME TIME 132KV DOYANG-MOKOKCHUNG (BELONG TO STATE) TRIPPED
[5 empty] | --- | 2016-09-11 11:30 | 2016-09-11 12:02 | as given in (3) | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO DOWNSTREAM FAULT
61 | NER L217 | MARIANI_MOKUKCHUNG 2 | 48.8 | North Eastern Region | --- | 2016-09-01 | 2016-09-30 23:59 | as given in (3) | 61 | 0 | 0 | 0 | 0 | 719 | 59 | 0 | 0 | 50 | N | 11 | AT LOC 56 & 57 TOWER DAMAGED CAUSED BY HEAVY LANDSLIDE DUE TO CONTINUOUS RAIN |  | 100
62 | NER L401 | BALIPARA_BONGAIGAON 1 | 289.721 | North Eastern Region | --- | 2016-09-21 09:15 | 2016-09-30 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 44 | NA | NA | NA | NGR BYPASS SCHEME-BAY MODIFICATION WORK AT BALIPARA SS. |  | 100
[5 empty] | --- | 2016-09-21 06:08 | 2016-09-21 09:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | NA | NA | NA | LINE H/T VIDE CODE 3120
[5 empty] | --- | 2016-08-30 19:45 | 2016-09-07 21:37 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 52 | NA | NA | NA | LINE H/T VIDE CODE 2854.
63 | NER L402 | BALIPARA_BONGAIGAON 2 | 289.721 | North Eastern Region | --- | 2016-09-19 01:21 | 2016-09-19 01:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO POWERSWING AS PER RELAY INDICATION |  | 100
64 | NER L403 | MISA_BALIPARA 1 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
65 | NER L404 | MISA-BALIPARA 2 | 95.407 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
66 | NER L405 | BONGAIGAON-MALDA 1 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
67 | NER L406 | BONGAIGAON-MALDA 2 | 432 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
68 | NER L407 | BALIPARA-RANGANADI 1 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
69 | NER L408 | BALIPARA-RANGANADI 2 | 166.335 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
70 | NER L409 | PALLATANA-SURAJMANINAGAR 1 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
71 | NER L410 | PALLATANA-SURAJMANINAGAR 2 | 37.2 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
72 | NER L411 | BTPS-BONGAIGAON 1 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
73 | NER L412 | BTPS-BONGAIGAON 2 | 3.119 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
74 | NER L413 | BALIPARA-BONGAIGAON 3 | 309 | North Eastern Region | --- | 2016-09-11 22:23 | 2016-09-12 18:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 57 | NA | NA | NA | LINE H/T VIDE CODE 2971 |  | 100
[5 empty] | --- | 2016-09-08 07:00 | 2016-09-08 18:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 47 | NA | NA | NA | LINE H/T VIDE CODE 2932.
[5 empty] | --- | 2016-09-15 00:24 | 2016-09-15 16:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 28 | NA | NA | NA | LINE H/T VIDE CODE 3001
[5 empty] | --- | 2016-09-17 16:13 | 2016-09-18 19:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 40 | NA | NA | NA | LINE H/T VIDE CODE 3051
[5 empty] | --- | 2016-09-20 02:55 | 2016-09-20 18:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | NA | NA | NA | LINE H/T VIDE CODE 3100
75 | NER L414 | BALIPARA-BONGAIGAON 4 | 309 | North Eastern Region | --- | 2016-09-10 06:37 | 2016-09-11 19:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 58 | NA | NA | NA | LINE H/T VIDE CODE 2951 |  | 100
[5 empty] | --- | 2016-09-18 22:04 | 2016-09-19 18:44 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | NA | NA | NA | LINE H/T VIDE CODE 3066
[5 empty] | --- | 2016-09-16 01:13 | 2016-09-17 13:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 34 | NA | NA | NA | LINE H/T VIDE CODE 3013
[5 empty] | --- | 2016-09-13 03:27 | 2016-09-13 18:42 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | NA | NA | NA | LINE H/T VIDE CODE 2984
76 | NER L415 | SILCHAR-IMPHAL 1 | 167 | North Eastern Region | --- | 2016-09-11 05:57 | 2016-09-11 07:35 | as given in (3) | 0 | 1 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D OF 132KV MAIN BUS AT IMPHAL FOR ATTENDING HOTSPOT IN MAIN BUS JUMPER (Y PH) OF LOKTAK BAYS |  | 99.77
77 | NER L416 | SILCHAR-IMPHAL 2 | 167 | North Eastern Region | --- | 2016-09-11 05:57 | 2016-09-11 07:36 | as given in (3) | 0 | 1 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D OF 132 KV MAIN BUS AT IMPHAL FOR ATTENDING HOTSPOTS IN MAIN BUS JUMPER (Y-PH) OF LOKTAK BAYS |  | 99.77
78 | NER L417 | BALIPARA_B.CHAIRALI 3 | 57.294 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
79 | NER L418 | BALIPARA_B.CHAIRALI 4 | 57.294 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
80 | NER L419 | B.CHAIRALI_RANGANADI 1 | 129.335 | North Eastern Region | --- | 2016-09-04 23:57 | 2016-09-05 16:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 46 | NA | NA | NA | LINE H/T VIDE CODE 2915. |  | 100
[5 empty] | --- | 2016-09-03 00:50 | 2016-09-03 17:16 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 26 | NA | NA | NA | LINE H/T VIDE CODE 2885.
[5 empty] | --- | 2016-09-19 04:38 | 2016-09-19 16:33 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 55 | NA | NA | NA | LINE H/T VIDE CODE 3069
[5 empty] | --- | 2016-09-07 22:36 | 2016-09-08 17:35 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 59 | NA | NA | NA | LINE H/T VIDE CODE 2931.
[5 empty] | --- | 2016-09-23 16:10 | 2016-09-23 16:26 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | NA | NA | NA | INCLEMENT WEATHER DURING THE TIME OF TRIPPING AS SUPPORTED BY WEATHER REPORT
[5 empty] | --- | 2016-09-09 23:24 | 2016-09-10 17:11 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 47 | NA | NA | NA | LINE H/T VIDE CODE 2949
[5 empty] | --- | 2016-09-15 22:14 | 2016-09-16 18:06 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 52 | NA | NA | NA | LINE H/T VIDE CODE 3010
[5 empty] | --- | 2016-09-13 23:00 | 2016-09-14 17:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | NA | NA | NA | LINE H/T VIDE CODE 2992
81 | NER L420 | B.CHAIRALI_RANGANADI 2 | 129.335 | North Eastern Region | --- | 2016-09-09 00:22 | 2016-09-09 09:24 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 2 | NA | NA | NA | Line H/T vide code 2943. |  | 100
[5 empty] | --- | 2016-09-11 06:16 | 2016-09-11 10:20 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | NA | NA | NA | LINE H/T VIDE CODE 2961
[5 empty] | --- | 2016-09-12 22:32 | 2016-09-13 16:39 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | NA | NA | NA | LINE H/T VIDE CODE 2983
[5 empty] | --- | 2016-09-14 23:46 | 2016-09-15 17:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | NA | NA | NA | LINE H/T VIDE CODE 3000
[5 empty] | --- | 2016-09-17 05:11 | 2016-09-17 17:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | NA | NA | NA | LINE H/T VIDE CODE 3041
[5 empty] | --- | 2016-09-18 00:16 | 2016-09-18 19:07 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 51 | NA | NA | NA | LINE H/T VIDE CODE 3055
[5 empty] | --- | 2016-09-19 22:32 | 2016-09-20 06:48 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | NA | NA | NA | LINE H/T VIDE CODE 3098
[5 empty] | --- | 2016-09-07 05:08 | 2016-09-07 17:43 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | NA | NA | NA | LINE H/T VIDE CODE 2925.
[5 empty] | --- | 2016-09-04 05:03 | 2016-09-04 17:18 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | NA | NA | NA | LINE H/T VIDE CODE 2898.
[5 empty] | --- | 2016-09-02 01:36 | 2016-09-02 17:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | NA | NA | NA | LINE H/T VIDE CODE 2882.
[5 empty] | --- | 2016-09-20 23:55 | 2016-09-21 11:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 26 | NA | NA | NA | LINE H/T VIDE CODE 3118
[5 empty] | --- | 2016-09-21 11:21 | 2016-09-21 16:04 | as given in (3) | 0 | 0 | 0 | 4 | 43 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN BY RANGANADI END (NEEPCO)
[5 empty] | --- | 2016-09-24 08:02 | 2016-09-30 23:59 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 57 | NA | NA | NA | SHIFTING OF CONDUCTOR FROM EXISTING TOWER TO NEWLY ERECTED TOWER AT LOC 17
[5 empty] | --- | 2016-09-01 01:29 | 2016-09-01 09:05 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 36 | NA | NA | NA | LINE H/T VIDE CODE 2871.
82 | NER L421 | BALIPARA_B.CHAIRALI 1 | 59.54 | North Eastern Region | --- | 2016-09-02 01:21 | 2016-09-05 19:47 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 26 | NA | NA | NA | LINE H/T VIDE CODE 2881. |  | 100
[5 empty] | --- | 2016-09-22 06:45 | 2016-09-22 18:21 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 36 | NA | NA | NA | LINE H/T VIDE CODE 3147.
83 | NER L422 | BALIPARA_B.CHAIRALI 2 | 59.54 | North Eastern Region | --- | 2016-09-22 23:16 | 2016-09-24 15:15 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 59 | NA | NA | NA | LINE H/T VIDE CODE 3175. |  | 100
[5 empty] | --- | 2016-09-06 05:29 | 2016-09-14 18:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 26 | NA | NA | NA | LINE H/T VIDE CODE 2915
[5 empty] | --- | 2016-09-18 07:00 | 2016-09-18 07:10 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERVOLTAGE
[5 empty] | --- | 2016-09-18 07:10 | 2016-09-19 12:04 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 54 | NA | NA | NA | LINE KEPT OPEN DUE TO SYSTEM CONSTRAINTS ON NERLDC INSTRUCTION
84 | NER L423 | SILCHAR-PURBAKANCHANBARI 2 | 127.2 | North Eastern Region | --- | 2016-09-10 09:26 | 2016-09-10 17:14 | as given in (3) | 0 | 0 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY PKBARI END |  | 99.97
[5 empty] | --- | 2016-09-19 09:35 | 2016-09-19 17:53 | as given in (3) | 0 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY PKBARI (STATE END)
[5 empty] | --- | 2016-09-22 09:24 | 2016-09-22 17:08 | as given in (3) | 0 | 0 | 0 | 7 | 44 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY P.K.BARI(STATE) END.
[5 empty] | --- | 2016-09-25 06:10 | 2016-09-25 10:55 | as given in (3) | 0 | 0 | 0 | 4 | 45 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN AT P.K.BARI END.
[5 empty] | --- | 2016-09-05 20:33 | 2016-09-05 21:00 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | NA | NA | NA | TRIPPED DUE TO LIGHTNING AS CONFIRMED BY DR REPORT
[5 empty] | --- | 2016-09-10 09:26 | 2016-09-10 17:15 | as given in (3) | 0 | 0 | 0 | 7 | 49 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY PKBARI
[5 empty] | --- | 2016-09-19 09:35 | 2016-09-19 17:55 | as given in (3) | 0 | 0 | 0 | 8 | 20 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY PKBARI STATE END
[5 empty] | --- | 2016-09-22 09:24 | 2016-09-22 17:23 | as given in (3) | 0 | 0 | 0 | 7 | 59 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN BY P.K.BARI(STATE) END.
[5 empty] | --- | 2016-09-25 06:10 | 2016-09-25 10:55 | as given in (3) | 0 | 0 | 0 | 4 | 45 | 0 | 0 | 0 | 0 | NA | NA | NA | BUS S/D TAKEN AT P.K.BARI END.
[5 empty] | --- | 2016-09-26 17:46 | 2016-09-26 17:58 | as given in (3) | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | TRIPPED DURING RTAMC TESTING.
85 | NER RBR1 | BR_BONGAIGAON (50MVAR) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
86 | NER RBR2 | BR_BONGAIGAON (50MVAR) 2 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
87 | NER RBR3 | BR_BALIPARA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
88 | NER RBR4 | BR_MISA (50MVAR) | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
89 | NER RBR5 | BR_KUMARGHAT (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
90 | NER RBR6 | BR_AIZWAL (20MVAR) | 20 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
91 | NER RBR7 | BR_BONGAIGAON(80MVAR) 3 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
92 | NER RBR8 | BR_BALIPARA(80MVAR) 2 | 80 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
93 | NER RBR9 | BR_SILCHAR(63MVAR) 1 | 63 | North Eastern Region | --- | 2016-09-19 13:06 | 2016-09-19 13:14 | as given in (3) | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR TESTING OF CSD |  | 99.98
94 | NER RBR10 | BR_SILCHAR(63MVAR) 2 | 63 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
95 | NER RBR11 | BR_BONGAIGAON(80MVAR) 4 | 80 | North Eastern Region | --- | 2016-09-03 19:03 | 2016-09-03 23:25 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 22 | NA | NA | NA | B/R HAND TRIPPED VIDE CODE 2895. |  | 100
96 | NER RBR12 | BR_B'CHARIALI(80MVAR) 1 | 80 | North Eastern Region | --- | 2016-09-06 14:41 | 2016-09-20 18:52 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 11 | NA | NA | NA | CONTINUOUS S/D TAKEN FOR REPLACEMENT OF OIP BUSHING AS PER APPROVAL IN 124TH OCC |  | 100
97 | NER RBR12 | BR_B'CHARIALI(80MVAR) 1 | 80 | North Eastern Region | --- | 2016-09-20 18:52 | 2016-09-20 22:55 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | NA | NA | NA | EQUIPMENT KEPT OPEN ON NERLDC ISNTRUCTION
98 | NER ICT1 | ICT_SILCHAR (200MVA) | 200 | North Eastern Region | --- | 2015-08-12 03:20 | 2015-08-12 04:29 | as given in (3) | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | NA | NA | NA | LBB optd. In Bus-II at Silchar during charging attempt of 132 KV Silchar-Dullabcherra feeder. |  | 100
99 | NER ICT2 | ICT_BALIPARA (315MVA) 1 | 315 | North Eastern Region | --- | 2016-09-29 09:24 | 2016-09-29 17:30 | as given in (3) | 0 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | S/D TAKEN FOR AMP |  | 98.88
100 | NER TICT4 | ICT_SALAKATI (50 MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
101 | NER TICT5 | ICT_DIMAPUR (100 MVA) 1 | 100 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
102 | NER TICT6 | ICT_KUMARGHAT(5MVA) | 5 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
103 | NER TICT7 | ICT_NIRJULI(16MVA) 1 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
104 | NER TICT8 | ICT_NIRJULI(10MVA) 2 | 10 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
105 | NER TICT10 | ICT_ZIRO (15MVA) | 15 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
106 | NER TICT11 | ICT_NIRJULI (16MVA) 2 | 16 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
107 | NER TICT12 | ICT_KOPILI (160 MVA) 2 | 160 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
108 | NER TICT14 | ICT_MISA 1 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
109 | NER TICT15 | ICT_SILCHAR(200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
110 | NER TICT16 | ICT_SILCHAR(200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
111 | NER ICT17 | ICT_BONGAIGAON(315MVA) | 315 | North Eastern Region | --- | 2016-09-29 11:07 | 2016-09-29 18:11 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR REPLACEMENT OF JUMPERS DAMAGED DUE TO EXCESS LAODING IN 220KV BAY |  | 100
112 | NER TICT18 | ICT_MISA 2 | 315 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
113 | NER TICT19 | ICT_MOKOKCHUNG(30MVA) 1 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
114 | NER TICT20 | ICT_MOKOKCHUNG(30MVA) 2 | 30 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
115 | NER TICT21 | ICT_B'CHARIALI (200MVA) 1 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
116 | NER TICT22 | ICT_B'CHARIALI (200MVA) 2 | 200 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
117 | NER TICT23 | ICT_NIRJULI(50MVA) 1 | 50 | North Eastern Region | --- | X | X | X | X | X | X | X | X | X | X | X | X | NA | NA | NA | X | X | 100
118 | NER ICT25 | ICT_SALAKATI(50MVA) 2 | 50 | North Eastern Region | --- | 2016-09-16 18:00 | 2016-09-16 18:57 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | NA | NA | NA | TRIPPED ON O/C |  | 100
119 | NER ICT25 | ICT_SALAKATI(50MVA) 2 | 50 | North Eastern Region | --- | 2016-09-16 21:07 | 2016-09-16 21:53 | as given in (3) | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | NA | NA | NA | TRIPPED ON OVERLOAD
120 | NER ICT30 | ICT_BALIPARA(315MVA) 2 | 315 | North Eastern Region | --- | 2016-09-15 11:04 | 2016-09-15 12:30 | as given in (3) | 0 | 1 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | E/S/D TAKEN FOR ARRESTING OIL LEAKAGE |  | 99.8