## SOP DATA NR1 FEB.-15
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.02.2015 to 28.02.2015
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | 23 | 24 | 25 | 26 | 27 | 21
A |  | 765 KV TRANS LINES | [17 empty] | NRPC | [6 empty] | 0
1 | NR176505 | 765 KV AGRA- MEERUT | 267.628 | NR1 | -- | 2015-02-08 07:52 | 2015-02-08 18:07 |  |  |  | 0 | 0 | 0 | 0.42708 |  |  |  | LCSD | S/D for strining work of 800 kV Agra-Bnc line. | [7 empty] | 672
|  |  |  | NR1 | -- | 2015-02-09 08:26 | 2015-02-09 17:48 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | -- | -- | -- | LCSD | S/D for strining work of 800 kV Agra-Bnc line.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.81736 | [6 empty] | 672 | 1779 | 267.628 | 476110.212 | 476110.212 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR1 | -- | 2015-02-03 03:21 | 2015-02-03 06:54 | -- | -- | -- | 0 | 0 | 0 | 0.14792 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-790kv
|  |  |  | NR1 |  | 2015-02-12 07:56 | 2015-02-12 19:38 |  |  |  | 0 | 0 | 0 | 0.4875 |  |  |  | LCSD | S/D for crossing of 800 kv Agra-BNC hvdc line
|  |  |  | NR1 | -- | 2015-02-13 07:56 | 2015-02-13 19:54 | -- | -- | -- | 0 | 0 | 0 | 0.49861 | -- | -- | -- | LCSD | S/D for X-ring of 800 kv HVDC agra-BNC line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 03:13 | [6 empty] | 672 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
5 | NR176503 | 765KV FATEHPUR-GAYA | 484.6 | NR1 | -- | [15 empty] | 672 | 1070 | 484.6 | 518522 | 518522 | 100
6 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 1067 | 355.008 | 378793.536 | 378793.536 | 100
7 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR1 | -- | 2015-02-14 09:36 | 2015-02-14 14:16 |  |  |  | 0.19444 | 0 | 0 | 0 |  |  |  | OSPT | S/D for oil sampling of bushing of L/R for DGA test at Ballia.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.19444 | 0 | 0 | 0 | [6 empty] | 672 | 1374 | 318.919 | 438194.706 | 435151.6872 | 99.3056
B |  | 400 KV TRANS LINES |  | NR1 | --
1 | NR140001 | 400KV AGRA-AGRA(UP)-I | 29.982 | NR1 | -- | 2015-02-15 05:17 | 2015-02-15 05:29 | -- | -- |  | 0 | 0.0083333 | 0 | 0 | -- | -- | -- | OMSU | Line tripped at Agra on Y-N fault in Z2 protection due to fault in UPPCL portion,FLR Agra-57km.
[6 empty] | 2015-02-18 08:14 | 2015-02-18 17:40 |  |  |  | 0.39306 | 0 | 0 | 0 |  |  |  | OSPT | S/D for executing AMP work
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0.39306 | 0.0083333 | 0 | 0 | [6 empty] | 672 | 515 | 29.982 | 15440.73 | 15223.9777 | 98.5962
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR1 | -- | 2015-02-15 05:17 | 2015-02-15 05:29 |  |  |  | 0 | 0.0083333 | 0 | 0 |  |  |  | OMSU | Line tripped at Agra on Y-N fault in Z2 protection due to fault in UPPCL portion.FLR Agra-57km.
[6 empty] | 2015-02-19 08:11 | 2015-02-19 18:29 |  |  |  | 0.42917 | 0 | 0 | 0 |  |  |  | OSPT | S/D by Agra-PG for line AMP work
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0.42917 | 0.0083333 | 0 | 0 | [6 empty] | 672 | 515 | 29.982 | 15440.73 | 15204.064 | 98.4673
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR1 | -- | 2015-02-16 10:18 | 2015-02-17 10:55 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 00:37 | -- | -- | -- | OPSD | S/D by NTPC for CT replacement work at Auraiya.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 00:37 | [6 empty] | 672 | 367 | 167.2 | 61362.4 | 61362.4 | 100
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR1 | -- | 2015-02-17 11:37 | 2015-02-17 20:02 |  |  |  | 0 | 0 | 0 | 0.35069 |  |  |  | OPSD | S/D by NTPC for CT replacement work at Auraiya.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.35069 | [6 empty] | 672 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 672 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR1 | -- | 2015-02-01 03:57 | 2015-02-01 06:53 | -- | -- | -- | 0 | 0 | 0 | 0.12222 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 |  | 2015-02-01 20:47 | 2015-02-02 07:12 |  |  |  | 0 | 0 | 0 | 0.43403 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 |  | 2015-02-03 21:44 | 2015-02-04 07:13 |  |  |  | 0 | 0 | 0 | 0.39514 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-04 21:03 | 2015-02-05 16:49 |  |  |  | 0 | 0 | 0 | 0.82361 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-05 21:04 | 2015-02-06 16:31 |  |  |  | 0 | 0 | 0 | 0.81042 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 |  | 2015-02-07 00:57 | 2015-02-08 09:29 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:32 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-428kv
|  |  |  | NR1 |  | 2015-02-08 21:04 | 2015-02-09 10:18 |  |  |  | 0 | 0 | 0 | 0.55139 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 |  | 2015-02-11 20:59 | 2015-02-12 07:03 |  |  |  | 0 | 0 | 0 | 0.41944 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-12 21:32 | 2015-02-13 07:12 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-13 21:27 | 2015-02-14 06:45 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-19 21:29 | 2015-02-20 06:28 |  |  |  | 0 | 0 | 0 | 0.37431 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-428kv
|  |  |  | NR1 |  | 2015-02-20 21:37 | 2015-02-21 06:09 |  |  |  | 0 | 0 | 0 | 0.35556 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-22 01:05 | 2015-02-22 08:41 |  |  |  | 0 | 0 | 0 | 0.31667 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-427kv
|  |  |  | NR1 |  | 2015-02-22 21:56 | 2015-02-23 09:01 |  |  |  | 0 | 0 | 0 | 0.46181 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-429kv
|  |  |  | NR1 |  | 2015-02-24 04:08 | 2015-02-24 06:39 |  |  |  | 0 | 0 | 0 | 0.10486 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-434kv
|  |  |  | NR1 |  | 2015-02-25 02:23 | 2015-02-25 06:22 |  |  |  | 0 | 0 | 0 | 0.16597 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-428 kv
|  |  |  | NR1 |  | 2015-02-28 21:46 | 2015-03-01 |  |  |  | 0 | 0 | 0 | 0.093056 |  |  |  | LVRD | Line hand tripped for voltage regulation.agra-430kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-06 13:47 | [6 empty] | 672 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 307 | 253.823 | 77923.661 | 77923.661 | 100
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2015-02-06 17:29 | 2015-02-06 18:52 | -- | -- | -- | 0.057639 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for attending hot spot in B-ph isolator at Agra end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.057639 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 307 | 253.823 | 77923.661 | 77763.2527 | 99.7941
11 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2015-02-01 | 2015-02-02 09:10 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:10 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Skr-434kv
|  |  |  | NR1 | -- | 2015-02-02 20:46 | 2015-02-03 09:16 | -- | -- | -- | 0 | 0 | 0 | 0.52083 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Skr-434kv
|  |  |  | NR1 | -- | 2015-02-03 20:39 | 2015-02-04 10:35 | -- | -- | -- | 0 | 0 | 0 | 0.58056 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Skr-432kv
[6 empty] | 2015-02-04 21:11 | 2015-02-05 09:08 |  |  |  | 0 | 0 | 0 | 0.49792 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
[6 empty] | 2015-02-05 21:06 | 2015-02-06 07:13 |  |  |  | 0 | 0 | 0 | 0.42153 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-432kv
[6 empty] | 2015-02-06 20:40 | 2015-02-08 09:36 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:56 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-426kv
[6 empty] | 2015-02-08 21:06 | 2015-02-09 07:17 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-432kv
[6 empty] | 2015-02-09 21:42 | 2015-02-10 07:24 |  |  |  | 0 | 0 | 0 | 0.40417 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 | -- | 2015-02-10 21:52 | 2015-02-11 07:54 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 | -- | 2015-02-11 20:53 | 2015-02-12 09:48 | -- | -- | -- | 0 | 0 | 0 | 0.53819 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 | -- | 2015-02-12 21:24 | 2015-02-13 11:54 | -- | -- | -- | 0 | 0 | 0 | 0.60417 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 | -- | 2015-02-15 21:34 | 2015-02-16 08:03 | -- | -- | -- | 0 | 0 | 0 | 0.43681 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-431kv
|  |  |  | NR1 |  | 2015-02-16 20:59 | 2015-02-17 06:38 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-431kv
|  |  |  | NR1 |  | 2015-02-17 21:05 | 2015-02-18 08:27 |  |  |  | 0 | 0 | 0 | 0.47361 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-431kv
|  |  |  | NR1 |  | 2015-02-19 21:01 | 2015-02-20 06:35 |  |  |  | 0 | 0 | 0 | 0.39861 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 01:00 | -- | -- | -- |  |  |  | 672 | 568 | 393.9 | 223735.2 | 223735.2 | 100
12 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2015-02-01 | 2015-02-01 07:02 | -- | -- | -- | 0 | 0 | 0 | 0.29306 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Skr-434kv
|  |  |  | NR1 | -- | 2015-02-01 20:51 | 2015-02-02 07:19 | -- | -- | -- | 0 | 0 | 0 | 0.43611 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 | -- | 2015-02-03 03:16 | 2015-02-03 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.14028 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 |  | 2015-02-08 21:54 | 2015-02-09 09:51 |  |  |  | 0 | 0 | 0 | 0.49792 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 |  | 2015-02-13 20:16 | 2015-02-14 10:02 |  |  |  | 0 | 0 | 0 | 0.57361 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
[6 empty] | 2015-02-14 21:36 | 2015-02-16 08:04 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:28 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-431kv
|  |  |  | NR1 |  | 2015-02-16 20:59 | 2015-02-17 06:38 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-431kv
|  |  |  | NR1 |  | 2015-02-20 21:35 | 2015-02-22 08:47 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:12 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-22 20:56 | 2015-02-23 22:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 01:48 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-24 04:06 | 2015-02-24 06:47 |  |  |  | 0 | 0 | 0 | 0.11181 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-434kv
|  |  |  | NR1 |  | 2015-02-25 02:05 | 2015-02-25 06:35 |  |  |  | 0 | 0 | 0 | 0.1875 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430 kv
|  |  |  | NR1 |  | 2015-02-27 20:38 | 2015-02-28 08:37 |  |  |  | 0 | 0 | 0 | 0.49931 |  |  |  | LVRD | Line hand tripped for voltage regulation.agra-429kv
|  |  |  | NR1 |  | 2015-02-28 20:48 | 2015-03-01 |  |  |  | 0 | 0 | 0 | 0.13333 |  |  |  | LVRD | Line hand tripped for voltage regulation.agra-430kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 06:04 | -- | -- | -- |  |  |  | 672 | 568 | 393.9 | 223735.2 | 223735.2 | 100
13 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR1 | -- | [15 empty] | 672 | 332 | 139.73 | 46390.36 | 46390.36 | 100
14 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR1 | -- | [15 empty] | 672 | 332 | 139.73 | 46390.36 | 46390.36 | 100
15 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 155.932 | 80304.98 | 80304.98 | 100
16 | NR140012 | 400KV ALLD-KNP-II | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 224 | 115360 | 115360 | 100
17 | NR140019 | 400KV BALIA-MAU-I | 13 | NR1 | -- | 2015-02-01 13:18 | 2015-02-01 13:44 | -- | -- |  | 0 | 0.018056 | 0 | 0 | -- | -- | -- | OMSU | Line tripped at Mau end only on CB auto trip due to some local problem at Mau/UPPCL.
[6 empty] | 2015-02-21 08:18 | 2015-02-21 20:31 |  |  |  | 0 | 0 | 0 | 0.50903 |  |  |  | LCSD | S/D for crossing of 765 kV Balia-Varanasi line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.018056 | 0 | 0.50903 | -- | -- | -- |  |  |  | 672 | 515 | 13 | 6695 | 6695 | 100
18 | NR140020 | 400KV BALIA-MAU-II | 13 | NR1 | -- | 2015-02-21 08:18 | 2015-02-21 20:21 | -- | -- | -- | 0 | 0 | 0 | 0.50208 | -- | -- | -- | LCSD | S/D for crossing of 765 kV Balia-Varanasi line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.50208 | -- | -- | -- |  |  |  | 672 | 515 | 13 | 6695 | 6695 | 100
19 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 227 | 229.163 | 52020.001 | 52020.001 | 100
20 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR1 | -- | [15 empty] | 672 | 227 | 229.163 | 52020.001 | 52020.001 | 100
21 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR1 | -- | [15 empty] | 672 | 687 | 1.559 | 1071.033 | 1071.033 | 100
22 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR1 | -- | 2015-02-12 16:39 | 2015-02-12 16:57 |  |  |  | 0 | 0.0125 | 0 | 0 |  |  |  | OMSU | Line tripped UPPCL end only during relay rectofitment work
[6 empty] | 2015-02-14 11:46 | 2015-02-14 14:57 |  |  |  | 0 | 0 | 0 | 0.13264 |  |  |  | OSPD | S/D by UPPCL for relay retrofitment work at Brly(up).
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.0125 | 0 | 0.13264 | -- | -- | -- |  |  |  | 672 | 515 | 9.2 | 4738 | 4738 | 100
23 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR1 | -- | 2015-02-14 16:45 | 2015-02-14 19:41 |  |  |  | 0 | 0 | 0 | 0.12222 |  |  |  | OSPD | S/D by UPPCL for relay retrofitment work at Brly(up).
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.12222 | 0 | 0 | 0 |  |  |  | 672 | 515 | 9.2 | 4738 | 4738 | 100
24 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR1 | -- | 2015-02-03 17:59 | 2015-02-03 18:40 | -- | -- | -- | 0 | 0.028472 | 0 | 0 | -- | -- | -- | OMSU | Line tripped Y&B fault, dist. Bareilly-7.4 kms, due to kite thread
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.028472 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 331 | 278.76 | 92269.56 | 92269.56 | 100
25 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 92.68 | 47730.2 | 47730.2 | 100
26 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 92.68 | 47730.2 | 47730.2 | 100
27 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR1 | -- | 2015-02-22 14:12 | 2015-02-22 14:57 | -- | -- | -- | 0 | 0.03125 | 0 | 0 | -- | -- | -- | OMSU | Tripped on Y-B phase due to kite thread. FLR, Brly-17.9 km, Rosa-105 km
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.03125 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 115.926 | 59701.89 | 59701.89 | 100
28 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 416 | 235 | 97760 | 97760 | 100
29 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 47.762 | 24597.43 | 24597.43 | 100
30 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 48.99 | 25229.85 | 25229.85 | 100
31 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- | 2015-02-21 13:12 | 2015-02-21 14:19 | -- | -- | -- | 0.046528 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for attending hot spot in Y-ph isolator at Jaipur end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.046528 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 37.164 | 19139.46 | 19107.6558 | 99.8338
32 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 37.164 | 19139.46 | 19139.46 | 100
33 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 247 | 106.153 | 26219.791 | 26219.791 | 100
34 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 48.432 | 33272.784 | 33272.784 | 100
35 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 48.432 | 33272.784 | 33272.784 | 100
36 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 82.8 | 42642 | 42642 | 100
37 | NR140033 | 400KV BHIWADI-HISAR | 211.547 | NR1 | -- | 2015-02-04 11:02 | 2015-02-04 18:33 | -- | -- | -- | 0 | 0 | 0 | 0.31319 | -- | -- | -- | OSPD | S/D by NR-II for line maint. Work
[6 empty] | 2015-02-19 09:13 | 2015-02-19 18:33 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | LCSD | S/D by NR-II for X-ring of HSR-Bhiwani line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.70208 | -- | -- | -- |  |  |  | 672 | 403 | 211.547 | 85253.441 | 85253.441 | 100
38 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 132.428 | 68200.42 | 68200.42 | 100
39 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2015-02-01 20:49 | 2015-02-02 07:11 | -- | -- |  | 0 | 0 | 0 | 0.43194 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-432kv
|  |  |  | NR1 | -- | 2015-02-03 21:45 | 2015-02-04 07:15 | -- | -- |  | 0 | 0 | 0 | 0.39583 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-04 21:05 | 2015-02-05 06:40 |  |  |  | 0 | 0 | 0 | 0.39931 |  |  |  | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 |  | 2015-02-05 21:05 | 2015-02-06 05:32 |  |  |  | 0 | 0 | 0 | 0.35208 |  |  |  | LVRD | Line hand tripped for voltage regulation.Nimr-427kv
|  |  |  | NR1 |  | 2015-02-07 00:55 | 2015-02-07 07:01 |  |  |  | 0 | 0 | 0 | 0.25417 |  |  |  | LVRD | Line hand tripped for voltage regulation.Nimr-425kv
|  |  |  | NR1 |  | 2015-02-11 21:00 | 2015-02-12 07:05 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-12 21:34 | 2015-02-13 07:14 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-13 21:27 | 2015-02-14 06:47 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-19 22:07 | 2015-02-20 09:05 |  |  |  | 0 | 0 | 0 | 0.45694 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-28 21:59 | 2015-03-01 |  |  |  | 0 | 0 | 0 | 0.084028 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-02 14:04 | -- | -- | -- |  |  |  | 672 | 515 | 48.428 | 24940.42 | 24940.42 | 100
40 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 48.428 | 24940.42 | 24940.42 | 100
41 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 42.7 | 21990.5 | 21990.5 | 100
42 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | 2015-02-11 10:52 | 2015-02-11 18:38 |  |  |  | 0.32361 | 0 | 0 | 0 |  |  |  | OSPT | S/D for replacement of Y phase CVT at Maharani bag
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0.32361 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 60.68 | 41929.88 | 41445.2737 | 98.8442
43 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR1 | -- | 2015-02-01 03:56 | 2015-02-01 06:59 | -- | -- | -- | 0 | 0 | 0 | 0.12708 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.12708 | -- | -- | -- |  |  |  | 672 | 515 | 235.952 | 121515.28 | 121515.28 | 100
44 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR1 | -- | 2015-02-01 23:48 | 2015-02-02 08:02 | -- | -- |  | 0 | 0 | 0 | 0.34306 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 | -- | 2015-02-03 01:16 | 2015-02-03 06:36 | -- | -- |  | 0 | 0 | 0 | 0.22222 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 | -- | 2015-02-05 22:03 | 2015-02-06 05:42 | -- | -- |  | 0 | 0 | 0 | 0.31875 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Mnp-433kv
|  |  |  | NR1 | -- | 2015-02-07 21:33 | 2015-02-08 08:41 | -- | -- |  | 0 | 0 | 0 | 0.46389 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 |  | 2015-02-08 21:11 | 2015-02-09 07:51 |  |  |  | 0 | 0 | 0 | 0.44444 |  |  |  | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 | -- | 2015-02-10 04:14 | 2015-02-10 08:37 | -- | -- |  | 0 | 0 | 0 | 0.18264 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 | -- | 2015-02-10 21:58 | 2015-02-11 07:58 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 |  | 2015-02-11 21:13 | 2015-02-12 07:29 |  |  |  | 0 | 0 | 0 | 0.42778 |  |  |  | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 |  | 2015-02-12 21:13 | 2015-02-13 09:57 |  |  |  | 0 | 0 | 0 | 0.53056 |  |  |  | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 |  | 2015-02-13 20:53 | 2015-02-14 08:50 |  |  |  | 0 | 0 | 0 | 0.49792 |  |  |  | LVRD | Line hand tripped for voltage regulation.Mnp-430kv
|  |  |  | NR1 |  | 2015-02-22 01:19 | 2015-02-22 08:47 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  | LVRD | Line hand tripped for voltage regulation.Mnp-429kv
|  |  |  | NR1 |  | 2015-02-25 02:07 | 2015-02-25 06:48 |  |  |  | 0 | 0 | 0 | 0.19514 |  |  |  | LVRD | Line hand tripped for voltage regulation.Blb-428 kv
|  |  |  | NR1 |  | 2015-02-26 01:12 | 2015-02-26 07:22 |  |  |  | 0 | 0 | 0 | 0.25694 |  |  |  | LVRD | Line hand tripped for voltage regulation.MNP-431kv
|  |  |  | NR1 |  | 2015-02-27 03:31 | 2015-02-27 07:47 |  |  |  | 0 | 0 | 0 | 0.17778 |  |  |  | LVRD | Line hand tripped for voltage regulation.MNP-431kv
|  |  |  | NR1 |  | 2015-02-28 00:27 | 2015-02-28 06:38 |  |  |  | 0 | 0 | 0 | 0.25764 |  |  |  | LVRD | Line hand tripped for voltage regulation.MNP-428kv
|  |  |  | NR1 |  | 2015-02-28 23:03 | 2015-03-01 |  |  |  | 0 | 0 | 0 | 0.039583 |  |  |  | LVRD | Line hand tripped for voltage regulation.MNP-428kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 02:04 | -- | -- | -- |  |  |  | 672 | 515 | 235.952 | 121515.28 | 121515.28 | 100
45 | NR140138 | 400KV BLBGRH-NAVADA | 12.55 | NR1 | -- | 2015-02-20 13:30 | 2015-02-20 13:45 | -- | -- |  | 0 | 0.010417 | 0 | 0 | -- | -- | -- | OMSU | Line tripped D/T received at BLB-PG end , fault in HVPNL end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0.010417 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 12.55 | 8672.05 | 8672.05 | 100
46 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- | 2015-02-20 11:13 | 2015-02-20 14:17 | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | OSPD | S/D by UPPCLfor relay rectofiitment work their end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 13.256 | 9159.896 | 9159.896 | 100
47 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 54.36 | 37562.76 | 37562.76 | 100
48 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | [15 empty] | 672 | 691 | 46.3 | 31993.3 | 31993.3 | 100
49 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | [15 empty] | 672 | 691 | 46.3 | 31993.3 | 31993.3 | 100
50 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2015-02-23 10:02 | 2015-03-01 | -- | -- |  | 0 | 0 | 0 | 1900-01-04 13:58 | -- | -- | -- | OSPD | S/D by NTPC for tower shifting work in Dadri stag-II reservoir area at Dadri.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-04 13:58 | -- | -- | -- |  |  |  | 672 | 515 | 33.098 | 17045.47 | 17045.47 | 100
51 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | 2015-02-01 02:55 | 2015-02-01 03:34 |  |  |  | 0 | 0.027083 | 0 | 0 |  |  |  | OMSU | Line A/R at Panipat & tripped at Dadri due to A/R relay prob at Dadri/NTPC on R-N,FLR Panipat-50.56km.
[6 empty] | 2015-02-23 10:43 | 2015-03-01 |  |  |  | 0 | 0 | 0 | 1900-01-04 13:17 |  |  |  | OSPD | S/D by NTPC for tower shifting work in Dadri stag-II reservoir area at Dadri.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0.027083 | 0 | 1900-01-04 13:17 | -- | -- | -- |  |  |  | 672 | 515 | 112.322 | 57845.83 | 57845.83 | 100
52 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 117 | 60255 | 60255 | 100
53 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 469 | 260.051 | 121963.919 | 121963.919 | 100
54 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 469 | 260.051 | 121963.919 | 121963.919 | 100
55 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR1 | -- | 2015-02-19 09:15 | 2015-02-19 17:04 | -- | -- | -- | 0 | 0 | 0 | 0.32569 | -- | -- | -- | OSPD | S/D by UPPCL for maint. Work their end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.32569 | -- | -- | -- |  |  |  | 672 | 515 | 45.94 | 23659.1 | 23659.1 | 100
56 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR1 | -- | 2015-02-20 11:33 | 2015-02-20 17:59 |  |  |  | 0 | 0 | 0 | 0.26806 |  |  |  | OSPD | S/D by UPPCL for maint. Work their end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.26806 | -- | -- | -- |  |  |  | 672 | 515 | 45.94 | 23659.1 | 23659.1 | 100
57 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 23.462 | 16118.394 | 16118.394 | 100
58 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 23.462 | 16118.394 | 16118.394 | 100
59 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 6.106 | 4194.822 | 4194.822 | 100
60 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 6.106 | 4194.822 | 4194.822 | 100
61 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 6.782 | 4659.234 | 4659.234 | 100
62 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 6.782 | 4659.234 | 4659.234 | 100
63 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- | 2015-02-27 21:06 | 2015-02-27 21:19 | -- | -- | -- | 0.0090278 | 0 | 0 | 0 | -- | -- | -- | LPPT | Line tripped Y&B fault, dist. Bhinmal-160.8 kms,KNK-30.0 kms
[6 empty] | 2015-02-28 13:46 | 2015-02-28 16:41 |  |  |  | 0.12153 | 0 | 0 | 0 |  |  |  | OSPT | S/D for rectification of jumper at loc no. 539 Y phase
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.13056 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 225 | 201.2 | 45270 | 45058.9196 | 99.5337
64 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2015-02-28 23:54 | 2015-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.0041667 | -- | -- | -- | OSPD | S/D by RRVPNL toattend hot spot their end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.0041667 | -- | -- | -- |  |  |  | 672 | 515 | 187.965 | 96801.975 | 96801.975 | 100
65 | NR140050 | 400KV KANKROLI-RAPPC-I | 198.54 | NR1 | -- | [15 empty] | 672 | 395 | 198.54 | 78423.3 | 78423.3 | 100
66 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 395 | 198.54 | 78423.3 | 78423.3 | 100
67 | NR140052 | 400KV KNP-AGRA | 240 | NR1 | -- | 2015-02-07 12:38 | 2015-02-07 12:50 |  |  |  | 0.0083333 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to abnormal sound in new reactor at kanpur.
[6 empty] | 2015-02-20 18:29 | 2015-02-20 18:44 |  |  |  | 0 | 0.010417 | 0 | 0 |  |  |  | OMSU | Line tripped on station DC E/fault during restoration work of 220kv control cable after major fire at KNP.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0.0083333 | 0.010417 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 291 | 240 | 69840 | 69819.2143 | 99.9702
68 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR1 | -- | [15 empty] | 672 | 515 | 72.6 | 37389 | 37389 | 100
69 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 73.2 | 37698 | 37698 | 100
70 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR1 | -- | 2015-02-03 03:18 | 2015-02-03 07:09 | -- | -- |  | 0 | 0 | 0 | 0.16042 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.BLB-429kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.16042 | -- | -- | -- |  |  |  | 672 | 342 | 385.69 | 131905.98 | 131905.98 | 100
71 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 361 | 370.772 | 133848.692 | 133848.692 | 100
72 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 361 | 370.772 | 133848.692 | 133848.692 | 100
73 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR1 | -- | 2015-02-28 08:12 | 2015-02-28 19:24 | -- | -- | -- | 0 | 0 | 0 | 0.46667 | -- | -- | -- | LCSD | S/D for X-ring of 400 KV D/C KNP-KNP line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.46667 | -- | -- | -- |  |  |  | 672 | 515 | 107.079 | 55145.685 | 55145.685 | 100
74 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR1 | -- | 2015-02-16 08:01 | 2015-02-16 18:01 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  | LCSD | S/D for X-ing work of 765 kV Varanasi-Knpr D/C line.
|  |  |  | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.41667 | -- | -- | -- |  |  |  | 672 | 515 | 107.1 | 55156.5 | 55156.5 | 100
75 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 5.922 | 3049.83 | 3049.83 | 100
76 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR1 | -- | [15 empty] | 672 | 515 | 5.86 | 3017.9 | 3017.9 | 100
77 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 179.711 | 92551.165 | 92551.165 | 100
78 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 309 | 255.56 | 78968.04 | 78968.04 | 100
79 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | 2015-02-16 09:34 | 2015-02-16 13:28 |  |  |  | 0.1625 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for attending hot spot in Y-ph line isolator at Kota.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.1625 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 50.5 | 26007.5 | 25856.5636 | 99.4196
80 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 2.7 | 1390.5 | 1390.5 | 100
81 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 2.7 | 1390.5 | 1390.5 | 100
82 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 633 | 14.463 | 9155.079 | 9155.079 | 100
83 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 633 | 16.49 | 10438.17 | 10438.17 | 100
84 | NR140151 | 400KV LUCKNOW-BAREILLY (765) | 251.613 | NR1 | -- | 2015-02-09 13:16 | 2015-02-09 18:57 | -- | -- | -- | 0 | 0 | 0 | 0.23681 | -- | -- | -- | LCSD | Erection of new Gantry Tower in 765kv BLY Stn.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.23681 | -- | -- | -- |  |  |  | 672 | 633 | 251.613 | 159271.029 | 159271.029 | 100
85 | NR140069 | 400KV LUCKNOW-BAREILLY-II | 255.5 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 425 | 255.5 | 108587.5 | 108587.5 | 100
86 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 289 | 263.933 | 76276.637 | 76276.637 | 100
87 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 289 | 263.933 | 76276.637 | 76276.637 | 100
88 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR1 | -- | [15 empty] | 672 | 687 | 2.86 | 1964.82 | 1964.82 | 100
89 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR1 | -- | [15 empty] | 672 | 687 | 2.86 | 1964.82 | 1964.82 | 100
90 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 41.743 | 21497.645 | 21497.645 | 100
91 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 371 | 169.785 | 62990.235 | 62990.235 | 100
92 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 98.281 | 50614.715 | 50614.715 | 100
93 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR1 | -- | [15 empty] | 672 | 515 | 98.281 | 50614.715 | 50614.715 | 100
94 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 41.743 | 21497.645 | 21497.645 | 100
95 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR1 | -- | [15 empty] | 672 | 515 | 73.826 | 38020.39 | 38020.39 | 100
96 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 73.826 | 38020.39 | 38020.39 | 100
97 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 133.5 | 68752.5 | 68752.5 | 100
98 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- | 2015-02-26 02:11 | 2015-02-26 07:46 | -- | -- | -- | 0 | 0 | 0 | 0.23264 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.BLY-428kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.23264 | -- | -- | -- |  |  |  | 672 | 616 | 66.009 | 40661.544 | 40661.544 | 100
99 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 616 | 66.009 | 40661.544 | 40661.544 | 100
100 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 672 | 678 | 178.69 | 121151.82 | 121151.82 | 100
101 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 672 | 673 | 175.63 | 118198.99 | 118198.99 | 100
102 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | [15 empty] | 672 | 515 | 59.868 | 30832.02 | 30832.02 | 100
103 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | [15 empty] | 672 | 515 | 59.868 | 30832.02 | 30832.02 | 100
104 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 672 | 515 | 54.298 | 27963.47 | 27963.47 | 100
105 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 672 | 515 | 54.298 | 27963.47 | 27963.47 | 100
106 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | [15 empty] | 672 | 515 | 37.38 | 19250.7 | 19250.7 | 100
107 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 76.018 | 39149.27 | 39149.27 | 100
108 | NR140139 | 400KV NAVADA-GR.NOIDA | 30.15 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 30.15 | 20833.65 | 20833.65 | 100
109 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 67.041 | 34526.115 | 34526.115 | 100
110 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 67.041 | 34526.115 | 34526.115 | 100
111 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- | 2015-02-03 21:47 | 2015-02-04 07:13 | -- | -- |  | 0 | 0 | 0 | 0.39306 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 | -- | 2015-02-04 21:04 | 2015-02-05 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Agra-430kv
|  |  |  | NR1 | -- | 2015-02-05 21:04 | 2015-02-06 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Nimr-427kv
|  |  |  | NR1 | -- | 2015-02-07 00:57 | 2015-02-07 06:58 | -- | -- | -- | 0 | 0 | 0 | 0.25069 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Nimr-425kv
|  |  |  | NR1 |  | 2015-02-11 21:02 | 2015-02-12 07:02 |  |  |  | 0 | 0 | 0 | 0.41667 | -- | -- | -- | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-12 21:36 | 2015-02-13 07:18 |  |  |  | 0 | 0 | 0 | 0.40417 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-13 21:24 | 2015-02-14 06:45 |  |  |  | 0 | 0 | 0 | 0.38958 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-19 22:13 | 2015-02-20 09:08 |  |  |  | 0 | 0 | 0 | 0.45486 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  |  |  | NR1 |  | 2015-02-28 21:57 | 2015-03-01 |  |  |  | 0 | 0 | 0 | 0.085417 |  |  |  | LVRD | Line hand tripped for voltage regulation.Neem-428kv
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 03:29 | -- | -- | -- |  |  |  | 672 | 515 | 175.859 | 90567.385 | 90567.385 | 100
112 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 175.859 | 90567.385 | 90567.385 | 100
113 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 433 | 279.245 | 120913.085 | 120913.085 | 100
114 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR1 | -- | [15 empty] | 672 | 433 | 279.245 | 120913.085 | 120913.085 | 100
115 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 2.1 | 1081.5 | 1081.5 | 100
116 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 2.1 | 1081.5 | 1081.5 | 100
117 | NR140091 | 400KV SING-ALLD-I | 224 | NR1 | -- | 2015-02-21 10:45 | 2015-02-21 12:54 |  |  |  | 0 | 0 | 0 | 0.089583 |  |  |  | LCSD | S/D for PLCC retrofitment at Allahabad end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.089583 | -- | -- | -- |  |  |  | 672 | 332 | 224 | 74368 | 74368 | 100
118 | NR140092 | 400KV SING-ALLD-II | 202 | NR1 | -- | 2015-02-22 10:09 | 2015-02-22 11:35 |  |  |  | 0 | 0 | 0 | 0.059722 |  |  |  | LCSD | S/D for PLCC retrofitment at both end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.059722 | 0 | 0 | 0 |  |  |  | 672 | 306 | 202 | 61812 | 61812 | 100
119 | NR140093 | 400KV SING-ANPARA | 25.057 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 25.057 | 12904.355 | 12904.355 | 100
120 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 236 | 330.953 | 78104.908 | 78104.908 | 100
121 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 337 | 408.6 | 137698.2 | 137698.2 | 100
122 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR1 | -- | [15 empty] | 672 | 515 | 42.026 | 21643.39 | 21643.39 | 100
123 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR1 | -- | [15 empty] | 672 | 515 | 43.952 | 22635.28 | 22635.28 | 100
124 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR1 | -- | [15 empty] | 672 | 515 | 3.341 | 1720.615 | 1720.615 | 100
125 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 3.317 | 1708.255 | 1708.255 | 100
126 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 236 | 233.707 | 55154.852 | 55154.852 | 100
127 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 272 | 142.8 | 38841.6 | 38841.6 | 100
|  |  |  | NR1 | -- | [17 empty] | 17663.733
C |  | 220 KV TRANS LINES |  | NR1 | --
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR1 | -- | [15 empty] | 672 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR1 | -- | 2015-02-21 05:53 | 2015-02-21 06:50 |  |  |  | 0 | 0.039583 | 0 | 0 |  |  |  | OMSU | Tripped B-N fault, Z-3, All-5.353 kms, UPPCL portion
[6 empty] | 2015-02-24 13:07 | 2015-02-24 13:20 |  |  |  | 0 | 0.0090278 | 0 | 0 |  |  |  | SEFU | Line tripped on R-N fault due to LA damaged at Rewa Rd/UPPCL.
[6 empty] | 2015-02-24 13:20 | 2015-02-24 17:08 |  |  |  | 0 | 0 | 0 | 0.15833 |  |  |  | OSFD | Forced S/D by UPPCL to attend damaged LA prob at Rewa Rd.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0.048611 | 0 | 0.15833 | 0 | 0 | 0 |  |  |  | 672 | 132 | 3 | 396 | 396 | 100
5 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 3 | 396 | 396 | 100
6 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 186.667 | 24640.044 | 24640.044 | 100
7 | NR122038 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 180.287 | 23797.884 | 23797.884 | 100
8 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 87.544 | 11468.264 | 11468.264 | 100
9 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | 2015-02-28 18:22 | 2015-02-28 21:02 |  |  |  | 0 | 0.11111 | 0 | 0 |  |  |  | OMSU | A/R from Anta tripped at S. modhopur.RRVPNL end only , R-N fault, dist. Anta-52.3 kms delay charging due to CB problem at RRVPNL end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0.11111 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 102.164 | 13485.648 | 13485.648 | 100
10 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR1 | -- | [15 empty] | 672 | 132 | 182.176 | 24047.232 | 24047.232 | 100
11 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 182.176 | 24047.232 | 24047.232 | 100
12 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 35.353 | 4631.243 | 4631.243 | 100
13 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | [15 empty] | 672 | 131 | 20.109 | 2634.279 | 2634.279 | 100
14 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | [15 empty] | 672 | 131 | 20.109 | 2634.279 | 2634.279 | 100
15 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | [15 empty] | 672 | 131 | 22.478 | 2944.618 | 2944.618 | 100
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 109 | 234.59 | 25570.31 | 25570.31 | 100
17 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 156 | 59.01 | 9205.56 | 9205.56 | 100
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR1 | -- | 2015-02-12 16:04 | 2015-02-12 16:10 | -- | -- |  | 0 | 0.0041667 | 0 | 0 | -- | -- | -- | OMSU | Line tripped Y-N fault, dist. Fatehpur-PG-10.7 kms UPPCL portion
[6 empty] | 2015-02-12 16:10 | 2015-02-13 12:39 |  |  |  | 0 | 0 | 0 | 0.85347 |  |  |  | OSPD | S/D by UPPCL to attend broken jumper in UPPCL yard
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.0041667 | 0 | 0.85347 | -- | -- | -- |  |  |  | 672 | 131 | 5.284 | 692.204 | 692.204 | 100
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR1 | -- | 2015-02-13 16:32 | 2015-02-13 19:39 | -- | -- |  | 0 | 0 | 0 | 0.12986 | -- | -- | -- | OSPD | S/D by UPPCL maint. Work their end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.12986 | -- | -- | -- |  |  |  | 672 | 131 | 5.284 | 692.204 | 692.204 | 100
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 6.17 | 808.27 | 808.27 | 100
21 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 6.17 | 808.27 | 808.27 | 100
22 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 15.69 | 2055.39 | 2055.39 | 100
23 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 15.69 | 2055.39 | 2055.39 | 100
24 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 17.691 | 2317.521 | 2317.521 | 100
25 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 17.691 | 2317.521 | 2317.521 | 100
26 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | [15 empty] | 672 | 131 | 24.875 | 3258.625 | 3258.625 | 100
27 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [15 empty] | 672 | 131 | 12 | 1572 | 1572 | 100
28 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR1 | -- | 2015-02-13 22:02 | 2015-02-13 22:45 | -- | -- | -- | 0 | 0.029861 | 0 | 0 | -- | -- | -- | OMSU | Line tripped B-N fault, dist. KNP-63.7 kms, UPPCL portion
[6 empty] | 2015-02-19 19:42 | 2015-02-22 23:47 |  |  |  | 0 | 0 | 1900-01-02 04:05 | 0 |  |  |  | LNCC | Tripped due to massive fire in 220KV cable trench at Knp. Line hand tripped from other end vide NRLDC code-1520.
[6 empty] | 2015-02-28 08:37 | 2015-02-28 20:14 |  |  |  | 0 | 0 | 0 | 0.48403 |  |  |  | LCSD | S/D for X-ring of 400 KV D/C KNP-KNP line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.029861 | 1900-01-02 04:05 | 0.48403 | -- | -- | -- |  |  |  | 595.9167 | 131 | 10.4 | 1362.4 | 1362.4 | 100
29 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR1 | -- | 2015-02-28 08:57 | 2015-02-28 20:12 |  |  |  | 0 | 0 | 0 | 0.46875 |  |  |  | LCSD | S/D for X-ring of 400 KV D/C KNP-KNP line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.46875 | -- | -- | -- |  |  |  | 672 | 131 | 14.86 | 1946.66 | 1946.66 | 100
30 | NR122018 | 220KV KNP-PANKI-I | 10.4 | NR1 | -- | 2015-02-28 08:51 | 2015-02-28 21:01 | -- | -- | -- | 0 | 0 | 0 | 0.50694 | -- | -- | -- | LCSD | S/D for X-ring of 400 KV D/C KNP-KNP line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.50694 | -- | -- | -- |  |  |  | 672 | 131 | 10.4 | 1362.4 | 1362.4 | 100
31 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR1 | -- | 2015-02-19 19:42 | 2015-02-23 01:19 | -- | -- | -- | 0 | 0 | 1900-01-02 05:37 | 0 | -- | -- | -- | LNCC | Tripped due to massive fire in 220KV cable trench at Knp. Line hand tripped from other end vide NRLDC code-1520.
[6 empty] | 2015-02-28 08:51 | 2015-02-28 21:03 |  |  |  | 0 | 0 | 0 | 0.50833 |  |  |  | LCSD | S/D for X-ring of 400 KV D/C KNP-KNP line
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 1900-01-02 05:37 | 0.50833 | -- | -- | -- |  |  |  | 594.3833 | 131 | 14.86 | 1946.66 | 1946.66 | 100
32 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR1 | -- | 2015-02-26 06:52 | 2015-02-26 07:03 |  |  |  | 0 | 0.0076389 | 0 | 0 |  |  |  | OMSU | Trip from KNP on B-N, Z-II protn opted due to fault beyond UCR.FLR: KNP=UCR-I=162km, UCR-II=177km whereas Line length=144km.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.0076389 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 143.553 | 18805.443 | 18805.443 | 100
33 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR1 | -- | 2015-02-19 19:42 | 2015-02-23 00:53 | -- | -- | -- | 0 | 0 | 1900-01-02 05:11 | 0 | -- | -- | -- | LNCC | Tripped due to massive fire in 220KV cable trench at Knp. Line hand tripped from other end vide NRLDC code-1520.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 1900-01-02 05:11 | 0 | -- | -- | -- |  |  |  | 594.8167 | 131 | 143.553 | 18805.443 | 18805.443 | 100
34 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR1 | -- | 2015-02-19 19:42 | 2015-02-23 00:56 |  |  |  | 0 | 0 | 1900-01-02 05:14 | 0 |  |  |  | LNCC | Tripped due to massive fire in 220KV cable trench at Knp. Line hand tripped from other end vide NRLDC code-1520.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 1900-01-02 05:14 | 0 | -- | -- | -- |  |  |  | 594.7667 | 131 | 144.63 | 18946.53 | 18946.53 | 100
35 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR1 | -- | 2015-02-19 16:24 | 2015-02-19 16:47 |  |  |  | 0.015972 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped R-N fault,dist. KNp-118.0 kms
[6 empty] | 2015-02-26 06:52 | 2015-02-26 07:03 |  |  |  | 0 | 0.0076389 | 0 | 0 |  |  |  | OMSU | Trip from KNP on B-N, Z-II protn opted due to fault beyond UCR.FLR: KNP=UCR-I=162km, UCR-II=177km whereas Line length=144km.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0.015972 | 0.0076389 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 144.63 | 18946.53 | 18935.7222 | 99.943
36 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 28.02 | 3698.64 | 3698.64 | 100
37 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- | 2015-02-02 06:21 | 2015-02-02 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.020833 | -- | -- | -- | LPRD | Line hand tripped for Power regulation.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.020833 | -- | -- | -- |  |  |  | 672 | 132 | 2.316 | 305.712 | 305.712 | 100
38 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- | 2015-02-22 14:43 | 2015-02-22 16:19 | -- | -- | -- | 0 | 0 | 0 | 0.066667 | -- | -- | -- | OSPD | S/D by UPPCL for attending CT problem at Modipuram end
[6 empty] | 2015-02-25 16:20 | 2015-02-25 19:50 |  |  |  | 0 | 0 | 0 | 0.14583 |  |  |  | OSPD | S/D by UPPCL for maintenance work at M,puram.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.2125 | -- | -- | -- |  |  |  | 672 | 132 | 9.254 | 1221.528 | 1221.528 | 100
39 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  | N-1392
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 2.316 | 305.712 | 305.712 | 100
40 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 8.234 | 1086.888 | 1086.888 | 100
41 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 9.254 | 1221.528 | 1221.528 | 100
42 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR1 | -- | [15 empty] | 672 | 156 | 177.88 | 27749.28 | 27749.28 | 100
43 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 1.19 | 157.08 | 157.08 | 100
44 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 1.19 | 157.08 | 157.08 | 100
45 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | 2015-02-01 13:05 | 2015-02-01 22:10 |  |  |  | 0 | 0 | 0 | 0.37847 |  |  |  | OSPD | S/D by RRVPNL for Y-ph CVT replacement at Chittorgarh,charging delay by RAPPB ,charging code issued at 1859hrs.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.37847 | -- | -- | -- |  |  |  | 672 | 131 | 128.833 | 16877.123 | 16877.123 | 100
46 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | [15 empty] | 672 | 131 | 128.833 | 16877.123 | 16877.123 | 100
47 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | [15 empty] | 672 | 131 | 0.175 | 22.925 | 22.925 | 100
48 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- | 2015-02-02 04:57 | 2015-02-02 05:58 | -- | -- |  | 0 | 0.042361 | 0 | 0 | -- | -- | -- | OMSU | Line A/R at Udaipur & tripped at RAPPB due to auto reclose relay prob at RAPPB on B-N,FLR Udaipur-31.05km,RAPPB-243.6km.
[6 empty] | 2015-02-04 09:47 | 2015-02-04 16:03 |  |  |  | 0 | 0 | 0 | 0.26111 |  |  |  | LCSD | S/D for polymer insulator replacement work
[6 empty] | 2015-02-04 16:03 | 2015-02-04 18:50 |  |  |  | 0 | 0 | 0 | 0.11597 |  |  |  | OSPD | S/D extendedby Rapp-Bend charging code issued at 16.03 hrs
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.042361 | 0 | 0.37708 | -- | -- | -- |  |  |  | 672 | 131 | 230.297 | 30168.907 | 30168.907 | 100
49 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 106.243 | 14024.076 | 14024.076 | 100
50 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- | 2015-02-01 | 2015-02-02 06:52 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:52 | -- | -- | -- | LPRD | Line hand tripped for Power regulation.
[6 empty] | 2015-02-23 10:59 | 2015-02-25 11:15 |  |  |  | 0 | 0 | 0 | 1900-01-01 00:16 |  |  |  | OSPD | S/D by RRVPNL for maintenance work at Ratangarh.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 07:08 | -- | -- | -- |  |  |  | 672 | 132 | 2.83 | 373.56 | 373.56 | 100
51 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | 2015-02-27 11:32 | 2015-02-27 21:32 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  | OSPD | S/d by RRVPNL for maint. Work their end
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.41667 | -- | -- | -- |  |  |  | 672 | 132 | 2.83 | 373.56 | 373.56 | 100
52 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- | 2015-02-10 17:02 | 2015-02-10 18:26 | -- | -- |  | 0.058333 | 0 | 0 | 0 | -- | -- | -- | OSFT | Forcely open from Sikar(PG) end due to sparking in Yph line isolator.
[6 empty] | 2015-02-11 11:07 | 2015-02-11 15:06 |  |  |  | 0.16597 | 0 | 0 | 0 |  |  |  | OSPT | S/D for damaged Yphase line isolator replacement at Sikar
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.22431 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 3 | 396 | 392.8277 | 99.1989
53 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 3 | 396 | 396 | 100
54 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR1 | -- | 2015-02-21 17:30 | 2015-02-21 18:04 | -- | -- | -- | 0 | 0.023611 | 0 | 0 | -- | -- | -- | OMSU | Tripped on R-Y phase due to kite thread. FLR, Strgnj-56.7km, Brly-48.5km
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0.023611 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 105.72 | 13955.04 | 13955.04 | 100
55 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 106 | 13992 | 13992 | 100
56 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 42.55 | 5616.6 | 5616.6 | 100
57 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR1 | -- | 2015-02-02 08:55 | 2015-02-03 17:12 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:17 | -- | -- | -- | OSPD | S/D by UCR/NTPC for mntc work at their end.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:17 | -- | -- | -- |  |  |  | 672 | 132 | 0.92 | 121.44 | 121.44 | 100
58 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR1 | -- | 2015-02-04 09:06 | 2015-02-05 19:39 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 10:33 | -- | -- | -- | OSPD | S/D by NTPC for bay AMP work
[6 empty] | 2015-02-26 06:52 | 2015-02-26 07:03 |  |  |  | 0 | 0.0076389 | 0 | 0 |  |  |  | OMSU | CB autotrip at UCR/NTPC on Z-II protn opted due to fault beyond UCR.Remain charge from Raibly.
[6 empty] | 2015-02-26 07:03 | 2015-02-26 10:00 |  |  |  | 0 | 0 | 0 | 0.12292 |  |  |  | OSPD | S/D by UCR/NTPC for protn testing.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0.0076389 | 0 | 1899-12-31 13:30 | -- | -- | -- |  |  |  | 672 | 132 | 0.92 | 121.44 | 121.44 | 100
59 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR1 | -- | 2015-02-06 09:23 | 2015-02-07 18:24 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:01 | -- | -- | -- | OSPD | S/D by NTPC for bay AMP work at Unchr end.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:01 | -- | -- | -- |  |  |  | 672 | 132 | 42.5 | 5610 | 5610 | 100
|  |  |  | NR1 | -- | [17 empty] | 3236.293
D |  | 132 KV TRANS LINES |  | NR1 | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR1 | -- | [15 empty] | 672 | 50 | 58 | 2900 | 2900 | 100
NR1
| Lines | TOTAL FOR T/LS |  | NR1 | [6 empty] | 1900-01-02 23:20 | 0.875 | 1900-01-24 16:14 | 1900-05-12 04:50 | [8 empty] | 20958.026 | 10132764.827 | 10128194.7886 | 99.9549 | %
|  | OVERALL SYSTEM AVAILABILITY= |  | NR1 | [7 empty] | 99.9732 | % (AC) | 99.6562 | [6 empty] | %'(HVDC)
E |  | 765/400 KV ICT'S |  | NR1 | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 400/765KV ICT-I AGRA | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1500 |  | 1500 | 1500 | 100
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | 2015-02-13 11:01 | 2015-02-13 11:15 |  |  |  | 0.0097222 | 0 | 0 | 0 |  |  |  | OMST | Tripped during replacement of differential relay at jhatikra
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.0097222 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1500 |  | 1500 | 1499.4792 | 99.9653
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
13 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
14 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [15 empty] | 672 | 1500 |  | 1500 | 1500 | 100
F |  | 400/220 KV ICT'S |  | NR1 | --
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
3 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
4 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
5 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
6 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
7 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
8 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
9 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
10 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
11 | NR1ICT10 | 315MVA ICT-I BLBGARH | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
12 | NR1ICT11 | 315MVA ICT-II BLBGARH | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
13 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | 2015-02-16 12:12 | 2015-02-16 13:29 |  |  |  | 0.053472 | 0 | 0 | 0 |  |  |  | OSPT | S/D for oil top up work.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.053472 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 314.3984 | 99.809
14 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
15 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
16 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
17 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
18 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
19 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
20 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
21 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
22 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
23 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
24 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
25 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
26 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
27 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
28 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
29 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
30 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
31 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
32 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
33 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
34 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
35 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
36 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
37 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
38 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
39 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
40 | NR1ICT28 | 315MVA ICT-I MANDOLA | 315 | NR1 | -- | 2015-02-16 10:22 | 2015-02-16 13:25 |  |  |  | 0 | 0 | 0 | 0.12708 |  |  |  | OSPD | S/D for attending DTL 220kv side Y-ph isolator hot spot.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.12708 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
41 | NR1ICT29 | 315MVA ICT-II MANDOLA | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
42 | NR1ICT30 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
43 | NR1ICT31 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
44 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
45 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
46 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 316 |  | 316 | 316 | 100
47 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
48 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
49 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
50 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [15 empty] | 672 | 500 |  | 500 | 500 | 100
51 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
52 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
53 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
54 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
55 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
56 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100
57 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [15 empty] | 672 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR1 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 | -- | [15 empty] | 672 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR1 | -- | [15 empty] | 672 | 100 |  | 100 | 100 | 100
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR1 | -- | [15 empty] | 672 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR1 | -- | [15 empty] | 672 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR1 | -- | [15 empty] | 672 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR1 | -- | [15 empty] | 672 | 100 |  | 100 | 100 | 100
|  |  |  | NR1 | --
78 |  | TOTAL FOR ICTs |  | NR1 | -- | [5 empty] | 0.12639 | 0 | 0 | 0.25417 | [7 empty] | 41136 |  | 41136 | 41134.8776 | 99.9973 | %
H |  | HVDC RIHAND-DADRI |  | NR1 | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR1 | -- | 2015-02-18 12:06 | 2015-02-18 17:34 |  |  |  | 0.22778 | 0 | 0 | 0 |  |  |  | OSFT | S/D for rectification of conductor in its earth-electrode line at loc.63 at Rihand end.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.22778 | 0 | 0 | 0 | [6 empty] | 672 | 750 | 815 | 611250 | 606277.5298 | 99.1865
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR1 | -- | 2015-02-18 10:51 | 2015-02-18 11:30 | -- | -- | -- | 0 | 0.027083 | 0 | 0 | N/A | N/A | N/A | OMSU | Tripped on valve cooling problem due to aux supply fluctuation at Balia
|  |  |  | NR1 |  | 2015-02-19 12:11 | 2015-02-19 12:17 |  |  |  | 0.0041667 | 0 | 0 | 0 |  |  |  | OMST | tripped due to station ground over curent protection failed at Bhiwadi
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.0041667 | 0.027083 | 0 | 0 | [6 empty] | 672 | 1250 | 789.786 | 987232.5 | 987085.5904 | 99.9851
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR1 | -- | 2015-02-18 10:51 | 2015-02-18 11:30 | -- | -- | -- | 0 | 0.027083 | 0 | 0 | N/A | N/A | N/A | OMSU | Tripped on valve cooling problem due to aux supply fluctuation at Balia
|  |  |  | NR1 |  | 2015-02-19 12:11 | 2015-02-19 12:17 |  |  |  | 0.0041667 | 0 | 0 | 0 |  |  |  | OMST | tripped due to station ground over curent protection failed at Bhiwadi
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.0041667 | 0.027083 | 0 | 0 | [6 empty] | 672 | 1250 | 789.786 | 987232.5 | 987085.5904 | 99.9851
|  | TOTAL FOR HVDC line |  | NR1 | -- | [5 empty] | 0.23611 | 0.054167 | 0 | 0 | [8 empty] | 3209.572 | 3196965 | 3191698.7106 | 99.8353 | %
J |  | HVDC BTB VINDH |  | NR1 | -- | [16 empty] | RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I | 250 | NR1 | -- | 2015-02-13 16:40 | 2015-02-14 02:06 |  |  |  | 0.39306 | 0 | 0 | 0 |  |  |  | OMST | Blocked tripped on DC over curent protection operated
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0.39306 | 0 | 0 | 0 | [6 empty] | 672 | 250 |  | 250 | 246.4906 | 98.5962
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 250 |  | 250 | 250 | 100
|  | TOTAL FOR HVDC VINDHYACHAL |  | NR1 | -- | [5 empty] | 0.39306 | 0 | 0 | 0 | [9 empty] | 500 | 496.4906 | 99.2981 | %
L |  | SVC, KANPUR |  | NR1 | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 280 | 280 | 100 | %
M |  | Bus & Switch Line Reactor |  | NR1 | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-II AGRA | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-III AGRA | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 50MVAR B/Reactor-I BAREILLY | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
16 | NR1BRT04 | 50MVAR B/Reactor BASSI | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
17 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 80 |  | 80 | 80 | 100
18 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
19 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
20 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
21 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
22 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
23 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR1 | -- | [15 empty] | 672 | 330 |  | 330 | 330 | 100
24 | NR1BRT39 | 125MVAR B/Reactor GORAKHPUR | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
25 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
26 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
27 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
28 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
29 | NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
30 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
31 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
32 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
33 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
34 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
35 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
36 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
37 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
38 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100
39 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
40 | NR1BRT40 | 125MVAR B/Reactor Roorki | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100
41 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100
42 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR1 | -- | [15 empty] | 672 | 93.2 |  | 93.2 | 93.2 | 100
43 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR1 | -- | [15 empty] | 672 | 93.2 |  | 93.2 | 93.2 | 100
44 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
45 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100
46 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
47 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
48 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
49 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
50 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
51 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
52 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
53 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
54 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
55 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR1 | -- | [15 empty] | 672 | 330 |  | 330 | 330 | 100
56 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
57 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
58 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR1 | -- | [15 empty] | 672 | 63 |  | 63 | 63 | 100
59 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR1 | -- | [15 empty] | 672 | 63 |  | 63 | 63 | 100
60 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
61 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR1 | -- | [15 empty] | 672 | 63 |  | 63 | 63 | 100
62 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR1 | -- | [15 empty] | 672 | 63 |  | 63 | 63 | 100
63 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
64 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
65 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
66 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR1 | -- | [15 empty] | 672 | 240 |  | 240 | 240 | 100
67 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
68 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 0 | [9 empty] | 8248.4 | 8248.4 | 100 | %
|  | TOTAL | [8 empty] | 1900-01-03 17:28 | 0.92917 | 1900-01-24 16:14 | 1900-05-12 10:56
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L15:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M15:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N15:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O15:[Deemed Available, row above])
Note on C421: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14