## SOP DATA NR1 Feb-16
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.06.2015 to 30.06.2015
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [24 empty] | 0
1 | NR176505 | 765 KV AGRA- MEERUT | 267.628 | NR1 | -- | 2016-02-01 09:53 | 2016-02-01 20:52 |  |  |  | 0 | 0 | 0 | 0.45764 |  |  |  | OSPD | S/D by UPPCL for crossing of 765 kV Mainpuri-Hapur Line | [7 empty] | 696
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.45764 | [6 empty] | 696 | 1779 | 267.628 | 476110.212 | 476110.212 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR1 | -- | 2016-02-01 | 2016-02-01 07:19 |  |  |  | 0 | 0 | 0 | 0.30486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790kV. Open since 31.01.16 at 2014hrs
[6 empty] | 2016-02-02 21:00 | 2016-02-03 08:17 |  |  |  | 0 | 0 | 0 | 0.47014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790kV
[6 empty] | 2016-02-04 21:55 | 2016-02-05 06:23 |  |  |  | 0 | 0 | 0 | 0.35278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-801kV
[6 empty] | 2016-02-12 21:39 | 2016-02-13 08:37 |  |  |  | 0 | 0 | 0 | 0.45694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-787kV
[6 empty] | 2016-02-27 10:58 | 2016-02-27 14:04 |  |  |  | 0.12917 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R out of service for its bushing gasket replacement at Agra.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.12917 | 0 | 0 | 1899-12-31 14:02 | [6 empty] | 696 | 1779 | 267.628 | 476110.212 | 473989.6062 | 99.5546
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR1 | -- | 2016-02-01 21:29 | 2016-02-02 07:01 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790kV
[6 empty] | 2016-02-07 21:26 | 2016-02-08 09:17 |  |  |  | 0 | 0 | 0 | 0.49375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-791kV
[6 empty] | 2016-02-09 01:06 | 2016-02-09 05:51 |  |  |  | 0 | 0 | 0 | 0.19792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790kV
[6 empty] | 2016-02-10 01:26 | 2016-02-10 06:45 |  |  |  | 0 | 0 | 0 | 0.22153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-786kV
[6 empty] | 2016-02-11 04:35 | 2016-02-11 07:46 |  |  |  | 0 | 0 | 0 | 0.13264 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-795kV
[6 empty] | 2016-02-11 21:09 | 2016-02-12 07:45 |  |  |  | 0 | 0 | 0 | 0.44167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-785kV
[6 empty] | 2016-02-14 21:36 | 2016-02-15 06:08 |  |  |  | 0 | 0 | 0 | 0.35556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-787kV
[6 empty] | 2016-02-15 21:18 | 2016-02-16 08:14 |  |  |  | 0 | 0 | 0 | 0.45556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-782kV
[6 empty] | 2016-02-16 22:02 | 2016-02-17 06:54 |  |  |  | 0 | 0 | 0 | 0.36944 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789kV
[6 empty] | 2016-02-18 01:17 | 2016-02-18 06:08 |  |  |  | 0 | 0 | 0 | 0.20208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789kV
[6 empty] | 2016-02-20 22:03 | 2016-02-21 07:46 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  | LVRD | Line hand tripped for Voltage regulation.AGRA-786kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 16:08 | [6 empty] | 696 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
5 | NR176503 | 765KV FATEHPUR-GAYA | 484.6 | NR1 | -- | 2016-02-04 16:21 | 2016-02-04 18:19 |  |  |  | 0.081944 | 0 | 0 | 0 |  |  |  | OSPT | S/D for topping of oil in L/Reactor at Fatehpur.
[5 empty] | -- | 2016-02-09 07:17 | 2016-02-09 07:45 |  |  |  | 0 | 0 | 0.019444 | 0 |  |  |  | LNCC | Tripped on Y-B fault during dense fog. FLR:Fthpr-60 km, Gaya-441.7km.
[5 empty] | -- | 2016-02-16 08:38 | 2016-02-16 18:31 |  |  |  | 0 | 0 | 0 | 0.41181 |  |  |  | LCSD | S/D for stringing of 400kV D/C quad Varansi-Sarnath line.
[5 empty] | -- | 2016-02-17 08:10 | 2016-02-17 18:54 |  |  |  | 0 | 0 | 0 | 0.44722 |  |  |  | LCSD | S/D for stringing of 400kV D/C quad Varansi-Sarnath line.
[5 empty] | -- | 2016-02-19 14:15 | 2016-02-19 19:20 |  |  |  | 0.21181 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend L/R R-ph oil leakage at Fatehpur.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.29375 | 0 | 0.019444 | 0.85903 | [6 empty] | 695.5333 | 1070 | 484.6 | 518522 | 513266.2057 | 98.9864
6 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 1067 | 355.008 | 378793.536 | 378793.536 | 100
7 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR1 | -- | 2016-02-21 11:07 | 2016-02-21 16:53 |  |  |  | 0.24028 | 0 | 0 | 0 |  |  |  | OSPT | S/D for polluted insulator cleaning work.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.24028 | 0 | 0 | 0 | [6 empty] | 696 | 1374 | 318.919 | 438194.706 | 434564.0698 | 99.1715
8 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR1 | -- | 2016-02-01 12:16 | 2016-02-01 18:05 |  |  |  | 0.24236 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending hot spot on wave trap at Bareily end.
[5 empty] | -- | 2016-02-02 15:48 | 2016-02-02 16:31 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-B fault due to Kite thread, FLR:Brly-30km, Lko-229.29km.
[5 empty] | -- | 2016-02-16 13:27 | 2016-02-16 17:19 |  |  |  | 0.16111 | 0 | 0 | 0 |  |  |  | OSFT | S/D for cleaning of polluted insulator strings.
[5 empty] | -- | 2016-02-26 11:41 | 2016-02-26 18:19 |  |  |  | 0.27639 | 0 | 0 | 0 |  |  |  | OSPT | S/D for R-ph pilot string replacement at loc no-162.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.67986 | 0.029861 | 0 | 0 | [6 empty] | 720 | 1019 | 251.613 | 256393.647 | 250583.2447 | 97.7338
9 | NR176508 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 1155 | 271.571 | 313664.505 | 313664.505 | 100
B |  | 400 KV TRANS LINES |  |  | --
1 | NR140001 | 400KV AGRA-AGRA(UP)-I | 29.982 | NR1 | -- | 2016-02-15 10:18 | 2016-02-15 11:05 | -- | -- |  | 0 | 0.032639 | 0 | 0 | -- | -- | -- | OMSU | CB A/trip only at Agra (UP) and remain charged from PG end. No flag / facia reported.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.032639 | 0 | 0 | [6 empty] | 696 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 696 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR1 | -- | 2016-02-01 | 2016-02-01 08:26 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434kV. Open since 31.01.16 at 2152hrs.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.35139 | [6 empty] | 696 | 367 | 167.2 | 61362.4 | 61362.4 | 100
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR1 | -- | 2016-02-01 | 2016-02-01 06:34 | -- | -- | -- | 0 | 0 | 0 | 0.27361 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV. Open since 31.01.16 at 2126hrs
[5 empty] | -- | 2016-02-01 20:59 | 2016-02-01 21:04 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | -- | -- | -- | GOVC | Tripped on O/Voltage protection oprtd at Agra>436 kV
[6 empty] | 2016-02-01 21:04 | 2016-02-02 06:32 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | -- | -- | -- | LVRD | Line kept open for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-06 21:37 | 2016-02-07 07:28 | -- | -- | -- | 0 | 0 | 0 | 0.41042 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-07 20:50 | 2016-02-08 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.42014 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-16 05:03 | 2016-02-16 07:14 | -- | -- | -- | 0 | 0 | 0 | 0.090972 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-435kV
[6 empty] | 2016-02-20 21:47 | 2016-02-21 07:36 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.AGRA-436kV
[6 empty] | 2016-02-21 21:23 | 2016-02-22 07:04 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.AGRA-436kV
[6 empty] | 2016-02-23 01:12 | 2016-02-23 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.22708 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.0034722 | 1900-01-01 15:06 | [6 empty] | 695.9167 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR1 | -- | 2016-02-12 20:53 | 2016-02-13 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-428kV
[5 empty] | -- | 2016-02-22 21:54 | 2016-02-23 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.36042 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[5 empty] | -- | 2016-02-23 21:34 | 2016-02-24 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.35069 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[5 empty] | -- | 2016-02-24 20:54 | 2016-02-25 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[5 empty] | -- | 2016-02-25 21:49 | 2016-02-26 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.33333 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[5 empty] | -- | 2016-02-26 20:57 | 2016-02-27 09:05 | -- | -- | -- | 0 | 0 | 0 | 0.50556 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[5 empty] | -- | 2016-02-28 21:42 | 2016-02-29 09:41 | -- | -- | -- | 0 | 0 | 0 | 0.49931 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 19:53 | [6 empty] | 696 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR1 | -- | 2016-02-01 | 2016-02-01 09:06 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434kv. Open since 31.01.16 at 1737hrs
[6 empty] | 2016-02-01 21:46 | 2016-02-02 09:10 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-02 20:30 | 2016-02-03 07:18 |  |  |  | 0 | 0 | 0 | 0.45 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[6 empty] | 2016-02-03 21:15 | 2016-02-04 09:57 |  |  |  | 0 | 0 | 0 | 0.52917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-04 21:08 | 2016-02-05 07:46 |  |  |  | 0 | 0 | 0 | 0.44306 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-05 20:54 | 2016-02-06 07:09 |  |  |  | 0 | 0 | 0 | 0.42708 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-06 19:36 | 2016-02-07 07:49 |  |  |  | 0 | 0 | 0 | 0.50903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-07 20:51 | 2016-02-08 07:00 |  |  |  | 0 | 0 | 0 | 0.42292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-08 20:17 | 2016-02-09 11:04 |  |  |  | 0 | 0 | 0 | 0.61597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-09 19:45 | 2016-02-10 08:52 |  |  |  | 0 | 0 | 0 | 0.54653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-425kV
[6 empty] | 2016-02-10 20:55 | 2016-02-11 07:11 |  |  |  | 0 | 0 | 0 | 0.42778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-11 18:22 | 2016-02-12 07:48 |  |  |  | 0 | 0 | 0 | 0.55972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-13 21:08 | 2016-02-14 08:30 |  |  |  | 0 | 0 | 0 | 0.47361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-429kV
[6 empty] | 2016-02-14 20:27 | 2016-02-15 08:18 |  |  |  | 0 | 0 | 0 | 0.49375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-432kV
[6 empty] | 2016-02-16 20:57 | 2016-02-17 08:04 |  |  |  | 0 | 0 | 0 | 0.46319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-17 20:47 | 2016-02-18 11:11 |  |  |  | 0 | 0 | 0 | 0.6 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-20 01:14 | 2016-02-20 08:35 |  |  |  | 0 | 0 | 0 | 0.30625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-21 17:12 | 2016-02-22 06:58 |  |  |  | 0 | 0 | 0 | 0.57361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-07 16:42 | [6 empty] | 696 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2016-02-01 | 2016-02-01 09:11 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432kV. Open since 31.01.16 at 2104hrs
[6 empty] | 2016-02-01 20:59 | 2016-02-01 21:04 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | -- | -- | -- | GOVC | Tripped on O/Voltage protection oprtd at Agra>436 kV
[6 empty] | 2016-02-01 21:04 | 2016-02-02 07:05 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | -- | -- | -- | LVRD | Line kept open for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-02 21:14 | 2016-02-03 07:35 |  |  |  | 0 | 0 | 0 | 0.43125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-05 20:58 | 2016-02-06 07:14 |  |  |  | 0 | 0 | 0 | 0.42778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-06 19:38 | 2016-02-07 07:18 |  |  |  | 0 | 0 | 0 | 0.48611 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-07 16:41 | 2016-02-08 06:58 |  |  |  | 0 | 0 | 0 | 0.59514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-14 21:05 | 2016-02-15 06:55 |  |  |  | 0 | 0 | 0 | 0.40972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-20 01:12 | 2016-02-20 08:44 |  |  |  | 0 | 0 | 0 | 0.31389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-20 21:51 | 2016-02-21 07:31 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line hand tripped for Voltage regulation.AGRA-436kV
[6 empty] | 2016-02-21 21:28 | 2016-02-22 07:04 |  |  |  | 0 | 0 | 0 | 0.4 |  |  |  | LVRD | Line hand tripped for Voltage regulation.AGRA-436kV
[6 empty] | 2016-02-23 01:13 | 2016-02-23 06:41 |  |  |  | 0 | 0 | 0 | 0.22778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.0034722 | 1900-01-03 11:52 | -- | -- | -- |  |  |  | 695.9167 | 307 | 253.823 | 77923.661 | 77923.661 | 100
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2016-02-03 21:22 | 2016-02-04 09:52 | -- | -- | -- | 0 | 0 | 0 | 0.52083 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-08 20:15 | 2016-02-09 07:33 |  |  |  | 0 | 0 | 0 | 0.47083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[5 empty] | -- | 2016-02-09 19:46 | 2016-02-10 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.45903 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-425kV
[6 empty] | 2016-02-10 20:57 | 2016-02-11 07:09 |  |  |  | 0 | 0 | 0 | 0.425 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-11 21:35 | 2016-02-12 07:43 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 07:09 | -- | -- | -- |  |  |  | 696 | 307 | 253.823 | 77923.661 | 77923.661 | 100
11 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2016-02-01 20:59 | 2016-02-02 10:08 | -- | -- | -- | 0 | 0 | 0 | 0.54792 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-436kV
[6 empty] | 2016-02-02 20:26 | 2016-02-03 08:24 |  |  |  | 0 | 0 | 0 | 0.49861 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[6 empty] | 2016-02-05 18:22 | 2016-02-06 07:25 |  |  |  | 0 | 0 | 0 | 0.54375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-07 15:31 | 2016-02-08 09:35 |  |  |  | 0 | 0 | 0 | 0.75278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-11 00:56 | 2016-02-11 07:15 |  |  |  | 0 | 0 | 0 | 0.26319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428kV
[6 empty] | 2016-02-12 21:44 | 2016-02-13 06:44 |  |  |  | 0 | 0 | 0 | 0.375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428V
[6 empty] | 2016-02-14 17:37 | 2016-02-15 09:05 |  |  |  | 0 | 0 | 0 | 0.64444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432kV
[6 empty] | 2016-02-15 21:08 | 2016-02-16 07:27 |  |  |  | 0 | 0 | 0 | 0.42986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432kV
[6 empty] | 2016-02-16 20:52 | 2016-02-17 09:05 |  |  |  | 0 | 0 | 0 | 0.50903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-17 20:45 | 2016-02-18 11:02 |  |  |  | 0 | 0 | 0 | 0.59514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-19 21:27 | 2016-02-20 08:50 |  |  |  | 0 | 0 | 0 | 0.47431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[5 empty] | -- | 2016-02-20 21:50 | 2016-02-22 10:15 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:25 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.AGRA-436kV
[6 empty] | 2016-02-22 14:10 | 2016-02-23 08:56 |  |  |  | 0 | 0 | 0 | 0.78194 |  |  |  | LVRD | Line hand tripped for Voltage regulation.MERTA-421kV
[6 empty] | 2016-02-23 21:35 | 2016-02-24 06:05 |  |  |  | 0 | 0 | 0 | 0.35417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-24 20:50 | 2016-02-25 11:48 |  |  |  | 0 | 0 | 0 | 0.62361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[6 empty] | 2016-02-25 21:22 | 2016-02-26 09:29 |  |  |  | 0 | 0 | 0 | 0.50486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-26 21:19 | 2016-02-27 09:14 |  |  |  | 0 | 0 | 0 | 0.49653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[6 empty] | 2016-02-28 21:45 | 2016-03-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:15 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 00:09 | -- | -- | -- |  |  |  | 696 | 568 | 393.9 | 223735.2 | 223735.2 | 100
12 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2016-02-01 | 2016-02-01 09:22 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434kV . Open since 31.01.16 at 1741hrs
[5 empty] | -- | 2016-02-03 21:21 | 2016-02-04 10:26 | -- | -- | -- | 0 | 0 | 0 | 0.54514 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[5 empty] | -- | 2016-02-04 21:15 | 2016-02-05 07:55 | -- | -- | -- | 0 | 0 | 0 | 0.44444 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[5 empty] | -- | 2016-02-05 21:49 | 2016-02-07 07:55 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:06 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[5 empty] | -- | 2016-02-08 20:15 | 2016-02-09 11:10 | -- | -- | -- | 0 | 0 | 0 | 0.62153 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[5 empty] | -- | 2016-02-09 19:46 | 2016-02-10 09:02 | -- | -- | -- | 0 | 0 | 0 | 0.55278 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-425kV
[5 empty] | -- | 2016-02-10 20:59 | 2016-02-11 07:15 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[5 empty] | -- | 2016-02-11 21:36 | 2016-02-12 07:56 | -- | -- | -- | 0 | 0 | 0 | 0.43056 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[5 empty] | -- | 2016-02-12 20:55 | 2016-02-14 08:35 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:40 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-428kV
[5 empty] | -- | 2016-02-18 21:48 | 2016-02-19 09:07 | -- | -- | -- | 0 | 0 | 0 | 0.47153 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 18:59 | -- | -- | -- |  |  |  | 696 | 568 | 393.9 | 223735.2 | 223735.2 | 100
13 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 332 | 139.73 | 46390.36 | 46390.36 | 100
14 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 332 | 139.73 | 46390.36 | 46390.36 | 100
15 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 155.932 | 80304.98 | 80304.98 | 100
16 | NR140012 | 400KV ALLD-KNP-II | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 224 | 115360 | 115360 | 100
17 | NR140019 | 400KV BALIA-MAU-I | 13 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 13 | 6695 | 6695 | 100
18 | NR140020 | 400KV BALIA-MAU-II | 13 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 13 | 6695 | 6695 | 100
19 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR1 | -- | 2016-02-04 16:13 | 2016-02-04 16:57 |  |  |  | 0.030556 | 0 | 0 | 0 |  |  |  | OMST | Tripped only from Balia end on protn malopted during fault in Balia-Bsariff-II line.
[5 empty] | -- | 2016-02-27 13:24 | 2016-02-27 13:27 |  |  |  | 0.0020833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R out, at Sohawal for LA replacement.
[6 empty] | 2016-02-29 13:14 | 2016-02-29 13:17 |  |  |  | 0.0020833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R in at Sohawal after replacing LA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.034722 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 227 | 229.163 | 52020.001 | 51957.7165 | 99.8803
20 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR1 | -- | 2016-02-24 09:24 | 2016-02-24 09:28 |  |  |  | 0.0027778 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/Reactor out for its LA replacenmet at Sohawal end.
[5 empty] | -- | 2016-02-27 12:44 | 2016-02-27 12:47 |  |  |  | 0.0020833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R in, at Sohawal after LA replacement.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.0048611 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 227 | 229.163 | 52020.001 | 52011.2812 | 99.9832
21 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 687 | 1.559 | 1071.033 | 1071.033 | 100
22 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 687 | 1.559 | 1071.033 | 1071.033 | 100
23 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR1 | -- | 2016-02-12 15:42 | 2016-02-12 16:38 |  |  |  | 0 | 0.038889 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-B fault due to kite thread. Brly-0.5km
[6 empty] | 2016-02-18 16:45 | 2016-02-18 17:17 |  |  |  | 0 | 0.022222 | 0 | 0 |  |  |  | OMSU | Line tripped due to Kite thread on Y-B fault. FLR:Brly-4km.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.061111 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 9.2 | 4738 | 4738 | 100
24 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR1 | -- | 2016-02-12 15:42 | 2016-02-12 16:17 |  |  |  | 0 | 0.024306 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-B fault only from Brly (PG) due to kite thread. FLR:Brly-0.5km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.024306 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 9.2 | 4738 | 4738 | 100
25 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR1 | -- | 2016-02-10 10:14 | 2016-02-10 19:27 | -- | -- | -- | 0 | 0 | 0 | 0.38403 | -- | -- | -- | LCSD | S/D for isolator retrofitment work under AddCap at Lko.
[5 empty] | -- | 2016-02-11 09:36 | 2016-02-11 19:45 | -- | -- | -- | 0 | 0 | 0 | 0.42292 | -- | -- | -- | LCSD | S/D for isolator retrofitment work under AddCap at Lko.
[5 empty] | -- | 2016-02-12 09:19 | 2016-02-12 19:18 | -- | -- | -- | 0 | 0 | 0 | 0.41597 | -- | -- | -- | LCSD | S/D for isolator retrofitment work under AddCap at Lko.
[5 empty] | -- | 2016-02-17 10:20 | 2016-02-17 18:48 | -- | -- | -- | 0 | 0 | 0 | 0.35278 | -- | -- | -- | LCSD | S/D for isolator retrofitment work under AddCap at Lko.
[5 empty] | -- | 2016-02-18 13:35 | 2016-02-18 14:13 | -- | -- | -- | 0 | 0.026389 | 0 | 0 | -- | -- | -- | OMSU | Line tripped due to kite thread, on Y-N fault. Brly-170.6km.
[5 empty] | -- | 2016-02-22 12:29 | 2016-02-22 13:06 | -- | -- | -- | 0 | 0 | 0 | 0.025694 | -- | -- | -- | OSFD | Line hand tripped by Lko-UPPCL on carrier failure alarm. D/T signal received at Bareilly(PG).
[5 empty] | -- | 2016-02-24 13:51 | 2016-02-24 18:40 | -- | -- | -- | 0 | 0.20069 | 0 | 0 | -- | -- | -- | OMSU | Tripped on R-N fault due to kite thread. FLR, Brly-167.4km. Charging Delayed for clearance by UP end.
[6 empty] | 2016-02-25 13:28 | 2016-02-25 14:48 |  |  |  | 0.055556 | 0 | 0 | 0 |  |  |  | OSFT | Hand tripped due to heavy sparking in R-ph line isolator at Bareily end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.055556 | 0.22708 | 0 | 1899-12-31 14:26 | -- | -- | -- |  |  |  | 696 | 331 | 278.76 | 92269.56 | 92092.7984 | 99.8084
26 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR1 | -- | 2016-02-12 15:43 | 2016-02-12 16:00 |  |  |  | 0 | 0.011806 | 0 | 0 |  |  |  | OMSU | Line tripped due to fire in Y-ph isolator at Moradabad-UP S/yard.
[5 empty] | -- | 2016-02-12 16:00 | 2016-02-12 18:39 |  |  |  | 0 | 0 | 0 | 0.11042 |  |  |  | OSFD | Forced S/D by UPPCL to attend isolator, damaged by fire.
[6 empty] | 2016-02-19 10:02 | 2016-02-19 10:52 |  |  |  | 0 | 0.034722 | 0 | 0 |  |  |  | OMSU | Line tripped due to kite thread on R-B fault. Brly-18.18km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.046528 | 0 | 0.11042 | -- | -- | -- |  |  |  | 696 | 515 | 92.68 | 47730.2 | 47730.2 | 100
27 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 92.68 | 47730.2 | 47730.2 | 100
28 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR1 | -- | 2016-02-02 11:32 | 2016-02-02 11:59 | -- | -- | -- | 0 | 0.01875 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on Y-B fault due to Kite thread. FLR:Brly-13.7km,Rosa-110km.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.01875 | 0 | 0 | [6 empty] | 696 | 515 | 115.926 | 59701.89 | 59701.89 | 100
29 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 515 | 116.03 | 59755.45 | 59755.45 | 100
30 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 101.841 | 69964.767 | 69964.767 | 100
31 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 696 | 687 | 101.841 | 69964.767 | 69964.767 | 100
32 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 416 | 235 | 97760 | 97760 | 100
33 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- | 2016-02-14 13:56 | 2016-02-14 17:07 | -- | -- | -- | 0.13264 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D to attend snapped Earth wire due to failure of midspan joint between loc no.593-594.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.13264 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 47.762 | 24597.43 | 24484.9274 | 99.5426
34 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 48.99 | 25229.85 | 25229.85 | 100
35 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 37.164 | 19139.46 | 19139.46 | 100
36 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 37.164 | 19139.46 | 19139.46 | 100
37 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- | 2016-02-10 12:37 | 2016-02-10 17:50 | -- | -- | -- | 0 | 0 | 0 | 0.21736 | -- | -- | -- | LPRD | Line hand tripped for Power regulation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.21736 | -- | -- | -- |  |  |  | 696 | 247 | 106.153 | 26219.791 | 26219.791 | 100
38 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- | 2016-02-10 12:37 | 2016-02-10 13:40 | -- | -- | -- | 0 | 0.04375 | 0 | 0 | -- | -- | -- | OMSU | Operational delay by RRVPNL in line isolation and issue of PTW for maintenance work.
[5 empty] | -- | 2016-02-10 13:40 | 2016-02-10 16:16 | -- | -- | -- | 0.10833 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for attending Y-ph jumper connection problem at Bassi.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10833 | 0.04375 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 48.432 | 33272.784 | 33148.4891 | 99.6264
39 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 48.432 | 33272.784 | 33272.784 | 100
40 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 82.8 | 42642 | 42642 | 100
41 | NR140033 | 400KV BHIWADI-HISAR-I | 211.547 | NR1 | -- | 2016-02-01 | 2016-02-01 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.28125 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bwd-432kV. Open since 31.01.16 at 2150hrs
[6 empty] | 2016-02-02 21:14 | 2016-02-03 07:21 |  |  |  | 0 | 0 | 0 | 0.42153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-12 22:04 | 2016-02-13 08:40 |  |  |  | 0 | 0 | 0 | 0.44167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-419kV
[6 empty] | 2016-02-13 21:38 | 2016-02-14 08:06 |  |  |  | 0 | 0 | 0 | 0.43611 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-428kV
[6 empty] | 2016-02-16 21:33 | 2016-02-17 08:12 |  |  |  | 0 | 0 | 0 | 0.44375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-429kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 00:35 | -- | -- | -- |  |  |  | 696 | 403 | 211.547 | 85253.441 | 85253.441 | 100
42 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 132.428 | 68200.42 | 68200.42 | 100
43 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2016-02-01 | 2016-02-01 08:02 | -- | -- |  | 0 | 0 | 0 | 0.33472 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Nmrn-432kV . Open since 31.01.16 at 1747hrs
[6 empty] | 2016-02-02 20:29 | 2016-02-03 07:30 |  |  |  | 0 | 0 | 0 | 0.45903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
[6 empty] | 2016-02-03 21:25 | 2016-02-04 10:42 |  |  |  | 0 | 0 | 0 | 0.55347 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-04 21:05 | 2016-02-05 07:50 |  |  |  | 0 | 0 | 0 | 0.44792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-05 21:01 | 2016-02-06 07:16 |  |  |  | 0 | 0 | 0 | 0.42708 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431kV
[6 empty] | 2016-02-06 21:40 | 2016-02-08 09:32 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:52 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-431kV
[6 empty] | 2016-02-11 00:54 | 2016-02-11 07:13 |  |  |  | 0 | 0 | 0 | 0.26319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428kV
[6 empty] | 2016-02-11 18:20 | 2016-02-12 07:51 |  |  |  | 0 | 0 | 0 | 0.56319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-12 21:52 | 2016-02-13 06:43 |  |  |  | 0 | 0 | 0 | 0.36875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-428kV
[6 empty] | 2016-02-13 21:11 | 2016-02-14 08:25 |  |  |  | 0 | 0 | 0 | 0.46806 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-429kV
[6 empty] | 2016-02-14 20:31 | 2016-02-15 06:31 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-432kV
[6 empty] | 2016-02-16 21:03 | 2016-02-17 08:08 |  |  |  | 0 | 0 | 0 | 0.46181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431kV
[6 empty] | 2016-02-17 20:48 | 2016-02-18 07:55 |  |  |  | 0 | 0 | 0 | 0.46319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-430kV
[6 empty] | 2016-02-20 01:15 | 2016-02-20 08:49 |  |  |  | 0 | 0 | 0 | 0.31528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433kV
[6 empty] | 2016-02-21 21:30 | 2016-02-22 07:02 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LVRD | Line hand tripped for Voltage regulation.BWD-435kV
[6 empty] | 2016-02-22 21:47 | 2016-02-23 06:30 |  |  |  | 0 | 0 | 0 | 0.36319 |  |  |  | LVRD | Line hand tripped for Voltage regulation.BWD-435kV
[6 empty] | 2016-02-23 21:40 | 2016-02-24 06:09 |  |  |  | 0 | 0 | 0 | 0.35347 |  |  |  | LVRD | Line hand tripped for Voltage regulation.BWD-428kV
[6 empty] | 2016-02-24 20:47 | 2016-02-25 05:52 |  |  |  | 0 | 0 | 0 | 0.37847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431kV
[6 empty] | 2016-02-25 21:54 | 2016-02-26 05:51 |  |  |  | 0 | 0 | 0 | 0.33125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434kV
[6 empty] | 2016-02-26 20:56 | 2016-02-29 09:43 |  |  |  | 0 | 0 | 0 | 1900-01-01 12:47 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-10 09:26 | -- | -- | -- |  |  |  | 696 | 515 | 48.428 | 24940.42 | 24940.42 | 100
44 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 48.428 | 24940.42 | 24940.42 | 100
45 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 42.7 | 21990.5 | 21990.5 | 100
46 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 691 | 60.68 | 41929.88 | 41929.88 | 100
47 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR1 | -- | 2016-02-01 | 2016-02-01 06:57 | -- | -- | -- | 0 | 0 | 0 | 0.28958 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-430kV. Open since 31.01.16 at 2103hrs
[5 empty] | -- | 2016-02-01 23:28 | 2016-02-02 09:12 | -- | -- | -- | 0 | 0 | 0 | 0.40556 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Mnp-428kV
[5 empty] | -- | 2016-02-03 01:22 | 2016-02-03 09:46 | -- | -- | -- | 0 | 0 | 0 | 0.35 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-432kV
[5 empty] | -- | 2016-02-06 21:49 | 2016-02-08 09:39 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:50 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP=429kv.
[5 empty] | -- | 2016-02-08 08:15 | 2016-02-08 20:41 | -- | -- | -- | 0 | 0 | 0 | 0.51806 | -- | -- | -- | LCSD | S/D for stringing of 800kv HVDC Champa-Kuruchetra line
[5 empty] | -- | 2016-02-09 08:31 | 2016-02-09 19:50 | -- | -- | -- | 0 | 0 | 0 | 0.47153 | -- | -- | -- | LCSD | S/D for stringing of 800kv HVDC Champa-Kuruchetra line
[5 empty] | -- | 2016-02-14 21:07 | 2016-02-15 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.4 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-426kV
[5 empty] | -- | 2016-02-16 01:43 | 2016-02-16 07:41 | -- | -- | -- | 0 | 0 | 0 | 0.24861 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP-427kV
[5 empty] | -- | 2016-02-21 16:10 | 2016-02-22 10:22 | -- | -- | -- | 0 | 0 | 0 | 0.75833 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.MNP-430kv.
[5 empty] | -- | 2016-02-23 01:08 | 2016-02-23 07:00 | -- | -- | -- | 0 | 0 | 0 | 0.24444 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP-431kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-04 04:18 | -- | -- | -- |  |  |  | 696 | 515 | 235.952 | 121515.28 | 121515.28 | 100
48 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR1 | -- | 2016-02-17 02:09 | 2016-02-17 07:48 | -- | -- |  | 0 | 0 | 0 | 0.23542 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP-430kV
[5 empty] | -- | 2016-02-18 01:15 | 2016-02-18 08:01 | -- | -- |  | 0 | 0 | 0 | 0.28194 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-429kV
[5 empty] | -- | 2016-02-05 01:10 | 2016-02-05 07:49 | -- | -- |  | 0 | 0 | 0 | 0.27708 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP=429kv.
[5 empty] | -- | 2016-02-05 21:50 | 2016-02-06 07:17 | -- | -- |  | 0 | 0 | 0 | 0.39375 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP=429kv.
[5 empty] | -- | 2016-02-07 17:11 | 2016-02-08 07:02 | -- | -- |  | 0 | 0 | 0 | 0.57708 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP=429kv.
[5 empty] | -- | 2016-02-08 08:15 | 2016-02-08 20:40 | -- | -- |  | 0 | 0 | 0 | 0.51736 | -- | -- | -- | LCSD | S/D for stringing of 800kv HVDC Champa-Kuruchetra line
[5 empty] | -- | 2016-02-08 21:33 | 2016-02-09 06:44 | -- | -- |  | 0 | 0 | 0 | 0.38264 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-429kv.
[6 empty] | 2016-02-09 08:31 | 2016-02-09 19:51 |  |  |  | 0 | 0 | 0 | 0.47222 |  |  |  | LCSD | S/D for stringing of 800kv HVDC Champa-Kuruchetra line
[6 empty] | 2016-02-11 00:57 | 2016-02-11 07:20 |  |  |  | 0 | 0 | 0 | 0.26597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428kV
[6 empty] | 2016-02-11 21:40 | 2016-02-12 07:53 |  |  |  | 0 | 0 | 0 | 0.42569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-426kV
[6 empty] | 2016-02-20 01:22 | 2016-02-20 09:08 |  |  |  | 0 | 0 | 0 | 0.32361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428kV
[6 empty] | 2016-02-20 17:13 | 2016-02-21 07:52 |  |  |  | 0 | 0 | 0 | 0.61042 |  |  |  | LVRD | Line hand tripped for Voltage regulation.MNP-430kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 18:19 | -- | -- | -- |  |  |  | 696 | 515 | 235.952 | 121515.28 | 121515.28 | 100
49 | NR140138 | 400KV BLBGRH-NAVADA | 12.55 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 691 | 12.55 | 8672.05 | 8672.05 | 100
50 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 691 | 13.256 | 9159.896 | 9159.896 | 100
51 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- | 2016-02-11 16:46 | 2016-02-11 17:53 | -- | -- |  | 0.046528 | 0 | 0 | 0 | -- | -- | -- | OSFT | Line hand tripped at Maharanibagh end only due to abnormal sound in R-ph CVT.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.046528 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 691 | 54.36 | 37562.76 | 37502.4941 | 99.8396
52 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | 2016-02-12 12:17 | 2016-03-01 |  |  |  | 0 | 0 | 0 | 1900-01-16 11:43 |  |  |  | LCSD | S/D for tower erection and diversion work of line due to construction of EPE highway by NHAI.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-16 11:43 | -- | -- | -- |  |  |  | 696 | 691 | 46.3 | 31993.3 | 31993.3 | 100
53 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | 2016-02-13 08:40 | 2016-03-01 |  |  |  | 0 | 0 | 0 | 1900-01-15 15:20 |  |  |  | LCSD | S/D for tower erection and diversion work of line due to construction of EPE highway by NHAI.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-15 15:20 | -- | -- | -- |  |  |  | 696 | 691 | 46.3 | 31993.3 | 31993.3 | 100
54 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2016-02-18 12:27 | 2016-02-18 17:41 | -- | -- |  | 0 | 0 | 0 | 0.21806 | -- | -- | -- | OSPD | S/D by UPPCL for construction work at Muradnagar.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.21806 | -- | -- | -- |  |  |  | 696 | 515 | 33.098 | 17045.47 | 17045.47 | 100
55 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 696 | 515 | 112.322 | 57845.83 | 57845.83 | 100
56 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- | 2016-02-05 09:47 | 2016-02-05 19:03 | -- | -- |  | 0 | 0 | 0 | 0.38611 | -- | -- | -- | OSPD | S/D by UPPCL for stringing of their Hapur-Ataur line.
[6 empty] | 2016-02-26 10:18 | 2016-02-26 13:22 |  |  |  | 0 | 0 | 0 | 0.12778 |  |  |  | OSPD | S/D by BBMB for attending hot spot at Panipat.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.51389 | -- | -- | -- |  |  |  | 696 | 515 | 117 | 60255 | 60255 | 100
57 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR1 | -- | 2016-02-03 01:21 | 2016-02-03 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.26875 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-432kV
[6 empty] | 2016-02-03 07:48 | 2016-02-04 18:45 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:57 |  |  |  | LCSD | S/D for stringing of D/C 400 Knp-Knp line.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 17:24 | -- | -- | -- |  |  |  | 696 | 469 | 260.051 | 121963.919 | 121963.919 | 100
58 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR1 | -- | 2016-02-01 01:18 | 2016-02-01 06:58 | -- | -- | -- | 0 | 0 | 0 | 0.23611 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Mnp-430kV
[6 empty] | 2016-02-06 20:57 | 2016-02-07 08:14 |  |  |  | 0 | 0 | 0 | 0.47014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP=429kv.
[6 empty] | 2016-02-07 21:12 | 2016-02-08 07:02 |  |  |  | 0 | 0 | 0 | 0.40972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP=429kv.
[6 empty] | 2016-02-20 01:25 | 2016-02-20 09:06 |  |  |  | 0 | 0 | 0 | 0.32014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428kV
[6 empty] | 2016-02-21 01:58 | 2016-02-21 07:49 |  |  |  | 0 | 0 | 0 | 0.24375 |  |  |  | LVRD | Line hand tripped for Voltage regulation.MNP-427kV
[6 empty] | 2016-02-23 01:09 | 2016-02-23 07:05 |  |  |  | 0 | 0 | 0 | 0.24722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-431kV
[6 empty] | 2016-02-03 07:58 | 2016-02-04 18:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:46 |  |  |  | LCSD | S/D for stringing of D/C 400 Knp-Knp line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 09:01 | -- | -- | -- |  |  |  | 696 | 469 | 260.051 | 121963.919 | 121963.919 | 100
59 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 45.94 | 23659.1 | 23659.1 | 100
60 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 45.94 | 23659.1 | 23659.1 | 100
61 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 23.462 | 16118.394 | 16118.394 | 100
62 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 23.462 | 16118.394 | 16118.394 | 100
63 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 6.106 | 4194.822 | 4194.822 | 100
64 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 6.106 | 4194.822 | 4194.822 | 100
65 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- | 2016-02-19 12:08 | 2016-02-19 16:41 | -- | -- | -- | 0 | 0 | 0 | 0.18958 | -- | -- | -- | OSPD | S/D by DTL for replacement of R-ph wave trap clamp at Mundka.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.18958 | -- | -- | -- |  |  |  | 696 | 687 | 6.782 | 4659.234 | 4659.234 | 100
66 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | 2016-02-01 07:57 | 2016-02-01 09:34 |  |  |  | 0 | 0.067361 | 0 | 0 |  |  |  | OMSU | A/R from Jhatikla but tripped from Mundka(DTL) on R-N fault in DTL portion.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.067361 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 6.782 | 4659.234 | 4659.234 | 100
67 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 225 | 201.2 | 45270 | 45270 | 100
68 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2016-02-04 16:54 | 2016-02-04 17:25 | -- | -- | -- | 0 | 0.021528 | 0 | 0 | -- | -- | -- | OMSU | Tripped only at Jodhpur-RRVPNL end during protn testing.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.021528 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 187.965 | 96801.975 | 96801.975 | 100
69 | NR140050 | 400KV KANKROLI-RAPPC-I | 198.54 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 395 | 198.54 | 78423.3 | 78423.3 | 100
70 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- | 2016-02-11 16:49 | 2016-02-11 17:12 | -- | -- |  | 0.015972 | 0 | 0 | 0 | -- | -- | -- | SRET | Line tripped due to L/R backup relay malfunction at Kankroli.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.015972 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 395 | 198.54 | 78423.3 | 78380.1071 | 99.9449
71 | NR140052 | 400KV KNP-AGRA | 240 | NR1 | -- | 2016-02-19 08:22 | 2016-02-19 20:08 |  |  |  | 0 | 0 | 0 | 0.49028 |  |  |  | LCSD | S/D for stringing work of 800kv Champa-Kurukshetra line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.49028 | -- | -- | -- |  |  |  | 696 | 291 | 240 | 69840 | 69840 | 100
72 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 72.6 | 37389 | 37389 | 100
73 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 73.2 | 37698 | 37698 | 100
74 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR1 | -- | 2016-02-14 21:33 | 2016-02-15 06:35 | -- | -- |  | 0 | 0 | 0 | 0.37639 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-426kV
[5 empty] | -- | 2016-02-20 01:19 | 2016-02-20 09:13 | -- | -- |  | 0 | 0 | 0 | 0.32917 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-428kV
[5 empty] | -- | 2016-02-22 07:59 | 2016-02-22 17:43 | -- | -- |  | 0 | 0 | 0 | 0.40556 | -- | -- | -- | LCSD | S/D for stringing of 765KV KNP-Jhatikara Line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 02:40 | -- | -- | -- |  |  |  | 696 | 342 | 385.69 | 131905.98 | 131905.98 | 100
75 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR1 | -- | 2016-02-01 01:21 | 2016-02-01 07:27 | -- | -- |  | 0 | 0 | 0 | 0.25417 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-430kV
[5 empty] | -- | 2016-02-05 11:08 | 2016-02-05 15:34 | -- | -- |  | 0.18472 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D to attend isolator hotspot at BLB.
[5 empty] | -- | 2016-02-09 03:07 | 2016-02-09 08:21 | -- | -- |  | 0 | 0 | 0 | 0.21806 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-431kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.18472 | 0 | 0 | 0.47222 | -- | -- | -- |  |  |  | 696 | 361 | 370.772 | 133848.692 | 132996.1117 | 99.363
76 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR1 | -- | 2016-02-06 01:58 | 2016-02-06 08:12 | -- | -- | -- | 0 | 0 | 0 | 0.25972 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB=430kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.25972 | -- | -- | -- |  |  |  | 696 | 361 | 370.772 | 133848.692 | 133848.692 | 100
77 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 107.079 | 55145.685 | 55145.685 | 100
78 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 107.1 | 55156.5 | 55156.5 | 100
79 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 5.922 | 3049.83 | 3049.83 | 100
80 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 5.86 | 3017.9 | 3017.9 | 100
81 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 515 | 179.711 | 92551.165 | 92551.165 | 100
82 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- | 2016-02-01 20:53 | 2016-02-01 22:48 | -- | -- | -- | 0 | 0 | 0 | 0.079861 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Merta-423kV
[6 empty] | 2016-02-02 20:14 | 2016-02-03 06:25 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-423kV
[6 empty] | 2016-02-03 20:30 | 2016-02-04 06:56 |  |  |  | 0 | 0 | 0 | 0.43472 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-423kV
[6 empty] | 2016-02-05 21:56 | 2016-02-06 06:41 |  |  |  | 0 | 0 | 0 | 0.36458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Kota=427kv.
[6 empty] | 2016-02-06 20:52 | 2016-02-07 06:36 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta=427kv.
[6 empty] | 2016-02-07 18:02 | 2016-02-07 18:05 |  |  |  | 0 | 0 | 0.0020833 | 0 |  |  |  | GOVC | Tripped on O/voltage from Merta. DT received at Kota.
[6 empty] | 2016-02-07 18:05 | 2016-02-08 06:16 |  |  |  | 0 | 0 | 0 | 0.50764 |  |  |  | LVRD | Line kept open for Voltage regulation.
[6 empty] | 2016-02-08 18:21 | 2016-02-09 06:15 |  |  |  | 0 | 0 | 0 | 0.49583 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Kota-424kV
[6 empty] | 2016-02-12 18:01 | 2016-02-13 06:30 |  |  |  | 0 | 0 | 0 | 0.52014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-14 18:00 | 2016-02-14 18:23 |  |  |  | 0 | 0 | 0 | 0.015972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-14 21:14 | 2016-02-15 06:08 |  |  |  | 0 | 0 | 0 | 0.37083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-15 18:09 | 2016-02-16 06:20 |  |  |  | 0 | 0 | 0 | 0.50764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-16 20:21 | 2016-02-17 00:08 |  |  |  | 0 | 0 | 0 | 0.15764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-17 20:55 | 2016-02-18 00:20 |  |  |  | 0 | 0 | 0 | 0.14236 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-18 03:42 | 2016-02-18 05:57 |  |  |  | 0 | 0 | 0 | 0.09375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-428kV
[6 empty] | 2016-02-18 20:58 | 2016-02-19 06:26 |  |  |  | 0 | 0 | 0 | 0.39444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-19 19:41 | 2016-02-20 07:11 |  |  |  | 0 | 0 | 0 | 0.47917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427kV
[6 empty] | 2016-02-20 20:39 | 2016-02-21 05:57 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-420kV
[6 empty] | 2016-02-21 21:36 | 2016-02-22 06:56 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-429kV
[6 empty] | 2016-02-22 21:27 | 2016-02-23 06:19 |  |  |  | 0 | 0 | 0 | 0.36944 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-421kV
[6 empty] | 2016-02-26 19:33 | 2016-02-27 06:12 |  |  |  | 0 | 0 | 0 | 0.44375 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-428kV
[6 empty] | 2016-02-27 19:52 | 2016-02-28 06:32 |  |  |  | 0 | 0 | 0 | 0.44444 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-428kV
[6 empty] | 2016-02-28 21:15 | 2016-02-29 06:41 |  |  |  | 0 | 0 | 0 | 0.39306 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-428kV
[6 empty] | 2016-02-29 18:39 | 2016-03-01 |  |  |  | 0 | 0 | 0 | 0.22292 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-428kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.0020833 | 1900-01-07 01:04 | -- | -- | -- |  |  |  | 695.95 | 309 | 255.56 | 78968.04 | 78968.04 | 100
83 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | 2016-02-12 15:49 | 2016-02-12 16:43 |  |  |  | 0 | 0.0375 | 0 | 0 |  |  |  | OMSU | Line tripped on R-N fault caused during new bay construction work by RAPP in their s/yard. FLR:Kota-50.5km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.0375 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 50.5 | 26007.5 | 26007.5 | 100
84 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 2.7 | 1390.5 | 1390.5 | 100
85 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 2.7 | 1390.5 | 1390.5 | 100
86 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 633 | 14.463 | 9155.079 | 9155.079 | 100
87 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 696 | 633 | 16.49 | 10438.17 | 10438.17 | 100
88 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 289 | 263.933 | 76276.637 | 76276.637 | 100
89 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 289 | 263.933 | 76276.637 | 76276.637 | 100
90 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 2.86 | 1964.82 | 1964.82 | 100
91 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 2.86 | 1964.82 | 1964.82 | 100
92 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR1 | -- | 2016-02-26 00:13 | 2016-02-26 00:37 |  |  |  | 0.016667 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on R-N fault in reclaim time. FLR:Lko(pg)-2.82km, Lko(up)-57km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.016667 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 41.743 | 21497.645 | 21485.29 | 99.9425
93 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 371 | 169.785 | 62990.235 | 62990.235 | 100
94 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR1 | Conductor failure | 2016-02-26 15:11 | 2016-02-28 12:31 |  |  | 1.8889 | 1899-12-31 21:20 | 0 | 0 | 0 | 2 | N | -0.11111 | LHWT | Line tripped on R-Y fault. FLR:Shahjahanpur-43km. Y-ph conductor mid span joint failed between Loc. 345-346.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 1899-12-31 21:20 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 169.729 | 87410.435 | 81717.035 | 93.4866
95 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 98.281 | 50614.715 | 50614.715 | 100
96 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 515 | 98.281 | 50614.715 | 50614.715 | 100
97 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 41.743 | 21497.645 | 21497.645 | 100
98 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 73.826 | 38020.39 | 38020.39 | 100
99 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 73.826 | 38020.39 | 38020.39 | 100
100 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | 2016-02-29 16:34 | 2016-02-29 20:10 |  |  |  | 0 | 0 | 0 | 0.15 |  |  |  | OSFD | S/D by UPPCL to attend hotspot in R-ph CT terminal at MBD.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.15 | -- | -- | -- |  |  |  | 696 | 515 | 133.5 | 68752.5 | 68752.5 | 100
101 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 616 | 66.009 | 40661.544 | 40661.544 | 100
102 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | 2016-02-13 18:46 | 2016-02-13 19:02 |  |  |  | 0 | 0.011111 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-B fault due to kite thread, in Power Link portion. BLY=29.8km.
[6 empty] | 2016-02-16 15:37 | 2016-02-16 16:09 |  |  |  | 0 | 0.022222 | 0 | 0 |  |  |  | OMSU | Tripped on R-B fault due to kite thread. FLR:Brly-4.8 km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.033333 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 616 | 66.009 | 40661.544 | 40661.544 | 100
103 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 678 | 178.69 | 121151.82 | 121151.82 | 100
104 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 673 | 175.63 | 118198.99 | 118198.99 | 100
105 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 696 | 515 | 59.868 | 30832.02 | 30832.02 | 100
106 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 515 | 59.868 | 30832.02 | 30832.02 | 100
107 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 696 | 515 | 54.298 | 27963.47 | 27963.47 | 100
108 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 696 | 515 | 54.298 | 27963.47 | 27963.47 | 100
109 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 515 | 37.38 | 19250.7 | 19250.7 | 100
110 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- | 2016-02-07 03:49 | 2016-02-07 04:00 | -- | -- | -- | 0 | 0 | 0.0076389 | 0 | -- | -- | -- | GOVC | Tripped only from Muzafrngr-UP on O/V protn malfunction.
[5 empty] | -- | 2016-02-07 04:00 | 2016-02-07 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.068056 | -- | -- | -- | LVRD | Line kept open for Voltage regulation.
[5 empty] | -- | 2016-02-07 06:16 | 2016-02-07 06:32 | -- | -- | -- | 0 | 0 | 0.011111 | 0 | -- | -- | -- | GOVC | Tripped only from Muzafrngr-UP on O/V protn malfunction.
[5 empty] | -- | 2016-02-07 17:20 | 2016-02-07 17:39 | -- | -- | -- | 0 | 0.013194 | 0 | 0 | -- | -- | -- | OMSU | Tripped only from Muzafrngr-UP on O/V protn malfunction.
[6 empty] | 2016-02-16 10:05 | 2016-02-16 16:29 |  |  |  | 0 | 0 | 0 | 0.26667 |  |  |  | OSPD | S/D by UPPCL for replacement of faulty CVT at Mzfrngr.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.013194 | 0.01875 | 0.33472 | -- | -- | -- |  |  |  | 695.55 | 515 | 76.018 | 39149.27 | 39149.27 | 100
111 | NR140139 | 400KV NAVADA-GR.NOIDA | 30.15 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 691 | 30.15 | 20833.65 | 20833.65 | 100
112 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 67.041 | 34526.115 | 34526.115 | 100
113 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 67.041 | 34526.115 | 34526.115 | 100
114 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- | 2016-02-01 | 2016-02-01 08:01 | -- | -- |  | 0 | 0 | 0 | 0.33403 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Nmrn-432kV. Open since 31.01.16 at 2101hrs
[6 empty] | 2016-02-21 21:31 | 2016-02-22 07:03 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LVRD | Line hand tripped for Voltage regulation.BWD-435kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.73125 | -- | -- | -- |  |  |  | 696 | 515 | 175.859 | 90567.385 | 90567.385 | 100
115 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- | 2016-02-16 20:55 | 2016-02-17 07:44 | -- | -- | -- | 0 | 0 | 0 | 0.45069 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Nmrn-429kV
[5 empty] | -- | 2016-02-17 20:51 | 2016-02-18 07:52 | -- | -- | -- | 0 | 0 | 0 | 0.45903 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Skr-431kV
[5 empty] | -- | 2016-02-24 20:45 | 2016-02-25 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Nmrn-429kV
[5 empty] | -- | 2016-02-25 21:47 | 2016-02-26 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.33403 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Nmrn-431kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:03 | -- | -- | -- |  |  |  | 696 | 515 | 175.859 | 90567.385 | 90567.385 | 100
116 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 433 | 279.245 | 120913.085 | 120913.085 | 100
117 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 433 | 279.245 | 120913.085 | 120913.085 | 100
118 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 2.1 | 1081.5 | 1081.5 | 100
119 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 2.1 | 1081.5 | 1081.5 | 100
120 | NR140161 | 400KV ROORKI-KASHIPUR-I | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 150.832 | 103621.584 | 103621.584 | 100
121 | NR140162 | 400KV ROORKI-KASHIPUR-II | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 687 | 150.832 | 103621.584 | 103621.584 | 100
122 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 |  | 2016-02-01 | 2016-02-01 06:18 |  |  |  | 0 | 0 | 0 | 0.2625 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV . Open since 31.01.16 at 1815hrs
[6 empty] | 2016-02-01 18:10 | 2016-02-02 06:20 |  |  |  | 0 | 0 | 0 | 0.50694 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-02 20:12 | 2016-02-03 06:17 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-03 21:04 | 2016-02-04 06:28 |  |  |  | 0 | 0 | 0 | 0.39167 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-04 20:44 | 2016-02-05 07:41 |  |  |  | 0 | 0 | 0 | 0.45625 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-06 21:22 | 2016-02-07 06:45 |  |  |  | 0 | 0 | 0 | 0.39097 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-07 18:09 | 2016-02-08 06:12 |  |  |  | 0 | 0 | 0 | 0.50208 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-08 18:20 | 2016-02-09 06:11 |  |  |  | 0 | 0 | 0 | 0.49375 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426kV
[6 empty] | 2016-02-09 21:55 | 2016-02-10 06:50 |  |  |  | 0 | 0 | 0 | 0.37153 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-10 20:27 | 2016-02-11 06:56 |  |  |  | 0 | 0 | 0 | 0.43681 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-11 18:10 | 2016-02-12 06:23 |  |  |  | 0 | 0 | 0 | 0.50903 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-12 20:15 | 2016-02-13 06:21 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-13 20:50 | 2016-02-14 06:30 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-14 20:27 | 2016-02-15 06:27 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
[6 empty] | 2016-02-15 20:06 | 2016-02-16 06:14 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428kV
[6 empty] | 2016-02-16 20:16 | 2016-02-17 06:00 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426kV
[6 empty] | 2016-02-17 18:13 | 2016-02-18 06:02 |  |  |  | 0 | 0 | 0 | 0.49236 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426kV
[6 empty] | 2016-02-18 20:02 | 2016-02-19 06:29 |  |  |  | 0 | 0 | 0 | 0.43542 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426kV
[6 empty] | 2016-02-19 20:48 | 2016-02-20 07:13 |  |  |  | 0 | 0 | 0 | 0.43403 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426kV
[6 empty] | 2016-02-20 20:18 | 2016-02-21 05:58 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421kV
[6 empty] | 2016-02-21 18:40 | 2016-02-22 06:40 |  |  |  | 0 | 0 | 0 | 0.5 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421kV
[6 empty] | 2016-02-22 18:26 | 2016-02-23 06:27 |  |  |  | 0 | 0 | 0 | 0.50069 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421kV
[6 empty] | 2016-02-23 18:08 | 2016-02-24 06:06 |  |  |  | 0 | 0 | 0 | 0.49861 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426 kV
[6 empty] | 2016-02-24 18:21 | 2016-02-25 06:07 |  |  |  | 0 | 0 | 0 | 0.49028 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426 kV
[6 empty] | 2016-02-25 20:09 | 2016-02-26 05:52 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-426 kV
[6 empty] | 2016-02-26 19:34 | 2016-02-27 06:10 |  |  |  | 0 | 0 | 0 | 0.44167 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428kV
[6 empty] | 2016-02-27 19:47 | 2016-02-28 06:30 |  |  |  | 0 | 0 | 0 | 0.44653 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428kV
[6 empty] | 2016-02-28 18:15 | 2016-02-29 06:39 |  |  |  | 0 | 0 | 0 | 0.51667 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428kV
[6 empty] | 2016-02-29 18:41 | 2016-03-01 |  |  |  | 0 | 0 | 0 | 0.22153 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-11 14:17 | -- | -- | -- |  |  |  | 696 | 515 | 76.48 | 39387.2 | 39387.2 | 100
122 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 |  | 2016-02-05 18:15 | 2016-02-06 06:47 |  |  |  | 0 | 0 | 0 | 0.52222 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-425kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.52222 | -- | -- | -- |  |  |  | 696 | 515 | 76.48 | 39387.2 | 39387.2 | 100
123 | NR140091 | 400KV SING-ALLD-I | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 332 | 224 | 74368 | 74368 | 100
124 | NR140092 | 400KV SING-ALLD-II | 202 | NR1 | -- | [15 empty] | 696 | 306 | 202 | 61812 | 61812 | 100
125 | NR140093 | 400KV SING-ANPARA | 25.057 | NR1 | -- | 2016-02-04 15:30 | 2016-02-04 19:00 | -- | -- | -- | 0 | 0 | 0 | 0.14583 | -- | -- | -- | OSPD | S/D by UPPCL to attend hotspot in Trans Bus isolator at Anpara.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.14583 | -- | -- | -- |  |  |  | 696 | 515 | 25.057 | 12904.355 | 12904.355 | 100
126 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 236 | 330.953 | 78104.908 | 78104.908 | 100
127 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 337 | 408.6 | 137698.2 | 137698.2 | 100
128 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 42.026 | 21643.39 | 21643.39 | 100
129 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 696 | 515 | 43.952 | 22635.28 | 22635.28 | 100
130 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 3.341 | 1720.615 | 1720.615 | 100
131 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 515 | 3.317 | 1708.255 | 1708.255 | 100
132 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 236 | 233.707 | 55154.852 | 55154.852 | 100
133 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 272 | 142.8 | 38841.6 | 38841.6 | 100
[5 empty] | -- | [17 empty] | 18701.336
|  | 220 KV TRANS LINES |  |  | --
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR1 | -- | 2016-02-12 10:05 | 2016-02-12 18:20 | -- | -- |  | 0 | 0 | 0 | 0.34375 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.34375 | -- | -- | -- |  |  |  | 696 | 132 | 21.879 | 2888.028 | 2888.028 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR1 | -- | 2016-02-08 08:45 | 2016-02-08 20:27 | -- | -- |  | 0 | 0 | 0 | 0.4875 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
[5 empty] | -- | 2016-02-08 20:40 | 2016-02-08 21:00 | -- | -- |  | 0 | 0.013889 | 0 | 0 | -- | -- | -- | SEFU | Tripped due to B-ph LA blast at Rewa Road(UPPCL) S/S.
[6 empty] | 2016-02-08 21:00 | 2016-02-09 19:57 |  |  |  | 0 | 0 | 0 | 0.95625 |  |  |  | OSFD | Forced S/D by UPPCL for replacement of B-ph damaged LA at Rewa Road end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.013889 | 0 | 1899-12-31 10:39 | -- | -- | -- |  |  |  | 696 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR1 | -- | 2016-02-08 20:40 | 2016-02-08 21:15 |  |  |  | 0 | 0.024306 | 0 | 0 |  |  |  | SBBU | Tripped on Bus Bar protn oprn at Rewa Road-UPPCL during tripping of Ckt-I.
[5 empty] | -- | 2016-02-10 09:05 | 2016-02-10 18:59 |  |  |  | 0 | 0 | 0 | 0.4125 |  |  |  | LCSD | S/D for Polymer insulator installation for system strenthening.
[5 empty] | -- | 2016-02-11 08:46 | 2016-02-11 18:06 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | LCSD | S/D for Polymer insulator installation for system strenthening.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.024306 | 0 | 0.80139 | [6 empty] | 696 | 132 | 3 | 396 | 396 | 100
5 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 186.667 | 24640.044 | 24640.044 | 100
6 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 186.667 | 24640.044 | 24640.044 | 100
7 | NR122038 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 180.287 | 23797.884 | 23797.884 | 100
8 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- | 2016-02-01 08:56 | 2016-02-01 19:05 | -- | -- |  | 0 | 0 | 0 | 0.42292 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
[5 empty] | -- | 2016-02-02 08:06 | 2016-02-02 19:38 | -- | -- |  | 0 | 0 | 0 | 0.48056 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
[5 empty] | -- | 2016-02-03 08:03 | 2016-02-03 18:55 | -- | -- |  | 0 | 0 | 0 | 0.45278 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
[5 empty] | -- | 2016-02-04 08:42 | 2016-02-04 18:24 | -- | -- |  | 0 | 0 | 0 | 0.40417 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
[6 empty] | 2016-02-27 02:27 | 2016-02-27 02:58 | -- | -- |  | 0 | 0.021528 | 0 | 0 | -- | -- | -- | OMSU | Line A/R at Anta but tripped from RappC on Y-N fault due to A/R problem. FLR:RappC-73.76km, Anta-10.38km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.021528 | 0 | 1899-12-31 18:15 | -- | -- | -- |  |  |  | 696 | 131 | 87.544 | 11468.264 | 11468.264 | 100
9 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 102.164 | 13485.648 | 13485.648 | 100
10 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR1 | -- | 2016-02-27 09:08 | 2016-02-27 19:10 |  |  |  | 0 | 0 | 0 | 0.41806 |  |  |  | LCSD | S/D for stringing work of 800kV Champa-Kurukshtera line.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.41806 | [6 empty] | 696 | 132 | 182.176 | 24047.232 | 24047.232 | 100
11 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR1 | -- | 2016-02-27 09:08 | 2016-02-27 19:12 |  |  |  | 0 | 0 | 0 | 0.41944 |  |  |  | LCSD | S/D for stringing work of 800kV Champa-Kurukshtera line.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.41944 | -- | -- | -- |  |  |  | 696 | 132 | 182.176 | 24047.232 | 24047.232 | 100
12 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | 2016-02-04 11:36 | 2016-02-04 16:46 |  |  |  | 0 | 0 | 0 | 0.21528 |  |  |  | OSFD | S/D by RRVPNL to attend damage isolator at Bagru.
[6 empty] | 2016-02-10 13:16 | 2016-02-10 17:03 |  |  |  | 0 | 0 | 0 | 0.15764 |  |  |  | LPRD | Line hand tripped for Power regulation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.37292 | -- | -- | -- |  |  |  | 696 | 131 | 35.353 | 4631.243 | 4631.243 | 100
13 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 20.109 | 2634.279 | 2634.279 | 100
14 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 20.109 | 2634.279 | 2634.279 | 100
15 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 22.478 | 2944.618 | 2944.618 | 100
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 109 | 234.59 | 25570.31 | 25570.31 | 100
17 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR1 | -- | 2016-02-09 13:11 | 2016-02-09 14:18 | -- | -- | -- | 0.046528 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for attending hot spot in Y-ph isolator at Pthrgrh end.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.046528 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 156 | 59.01 | 9205.56 | 9190.7905 | 99.8396
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR1 | -- | 2016-02-04 12:17 | 2016-02-04 15:05 | -- | -- |  | 0 | 0 | 0 | 0.11667 | -- | -- | -- | OSFD | Forced S/D by UPPCL to attend isolator hotspot in their s/y.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.11667 | -- | -- | -- |  |  |  | 696 | 131 | 5.284 | 692.204 | 692.204 | 100
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 5.284 | 692.204 | 692.204 | 100
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 6.17 | 808.27 | 808.27 | 100
21 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 6.17 | 808.27 | 808.27 | 100
22 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 15.69 | 2055.39 | 2055.39 | 100
23 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- | 2016-02-18 11:30 | 2016-02-18 18:57 | -- | -- |  | 0 | 0 | 0 | 0.31042 | -- | -- | -- | OSPD | S/D by HVPNL to attend Bus-II isolator hot spot at Palla.
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.31042 | -- | -- | -- |  |  |  | 696 | 131 | 15.69 | 2055.39 | 2055.39 | 100
24 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 17.691 | 2317.521 | 2317.521 | 100
25 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 17.691 | 2317.521 | 2317.521 | 100
26 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 131 | 24.875 | 3258.625 | 3258.625 | 100
27 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 131 | 12 | 1572 | 1572 | 100
28 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 10.4 | 1362.4 | 1362.4 | 100
29 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 14.86 | 1946.66 | 1946.66 | 100
30 | NR122018 | 220KV KNP-PANKI-I | 10.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 10.4 | 1362.4 | 1362.4 | 100
31 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 14.86 | 1946.66 | 1946.66 | 100
32 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR1 | -- | 2016-02-03 23:13 | 2016-02-03 23:48 |  |  |  | 0 | 0.024306 | 0 | 0 |  |  |  | OMSU | Line A/R at Kanpur but tripped from Unchahar/NTPC due to A/R problem on R-N fault. FLR:Unchahar-125.5km.
[5 empty] | -- | 2016-02-08 08:53 | 2016-02-08 21:04 |  |  |  | 0 | 0 | 0 | 0.50764 |  |  |  | LCSD | S/D for Polymer insulator installation for system strenthening.
[5 empty] | -- | 2016-02-09 09:19 | 2016-02-09 18:07 |  |  |  | 0 | 0 | 0 | 0.36667 |  |  |  | LCSD | S/D for Polymer insulator installation for system strenthening.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.024306 | 0 | 0.87431 | -- | -- | -- |  |  |  | 696 | 131 | 143.553 | 18805.443 | 18805.443 | 100
33 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR1 | -- | 2016-02-10 08:48 | 2016-02-10 18:05 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
[5 empty] | -- | 2016-02-10 22:20 | 2016-02-10 22:42 | -- | -- | -- | 0 | 0.015278 | 0 | 0 | -- | -- | -- | OMSU | A/R at Knp but tripped only from Unchahar, NTPC due to A/R problem on B-N fault. Unchr-125.6km.
[5 empty] | -- | 2016-02-11 08:34 | 2016-02-11 18:24 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strenthening.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.015278 | 0 | 0.79653 | -- | -- | -- |  |  |  | 696 | 131 | 143.553 | 18805.443 | 18805.443 | 100
34 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR1 | -- | 2016-02-03 07:46 | 2016-02-03 19:00 |  |  |  | 0.46806 | 0 | 0 | 0 |  |  |  | OSPT | S/D for annual maintenance work of line.
[5 empty] | -- | 2016-02-04 08:24 | 2016-02-04 20:13 |  |  |  | 0.49236 | 0 | 0 | 0 |  |  |  | OSPT | S/D for annual maintenance work of line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.96042 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 144.63 | 18946.53 | 18319.0623 | 96.6882
35 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR1 | -- | 2016-02-05 08:24 | 2016-02-05 18:20 |  |  |  | 0.41389 | 0 | 0 | 0 |  |  |  | OSPT | S/D for annual maintenance work of line.
[5 empty] | -- | 2016-02-06 09:16 | 2016-02-06 18:44 |  |  |  | 0.39444 | 0 | 0 | 0 |  |  |  | OSPT | S/D for annual maintenance work of line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.80833 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 144.63 | 18946.53 | 18418.4227 | 97.2126
36 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 28.02 | 3698.64 | 3698.64 | 100
37 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 2.316 | 305.712 | 305.712 | 100
38 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 9.254 | 1221.528 | 1221.528 | 100
39 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 2.316 | 305.712 | 305.712 | 100
40 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 8.234 | 1086.888 | 1086.888 | 100
41 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 9.254 | 1221.528 | 1221.528 | 100
42 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR1 | -- | 2016-02-16 08:02 | 2016-02-16 09:01 |  |  |  | 0 | 0.040972 | 0 | 0 |  |  |  | OMSU | Tripped on R-B fault due to kite thread. FLR:Brly-1.9km, Pthgrh-167.5km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.040972 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 156 | 177.88 | 27749.28 | 27749.28 | 100
43 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 1.19 | 157.08 | 157.08 | 100
44 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 1.19 | 157.08 | 157.08 | 100
45 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 128.833 | 16877.123 | 16877.123 | 100
46 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 128.833 | 16877.123 | 16877.123 | 100
47 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 0.175 | 22.925 | 22.925 | 100
48 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 131 | 230.297 | 30168.907 | 30168.907 | 100
49 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 106.243 | 14024.076 | 14024.076 | 100
50 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 2.83 | 373.56 | 373.56 | 100
51 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 2.83 | 373.56 | 373.56 | 100
52 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 3 | 396 | 396 | 100
53 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 3 | 396 | 396 | 100
54 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR1 | -- | 2016-02-18 17:40 | 2016-02-18 19:04 | -- | -- | -- | 0 | 0.058333 | 0 | 0 | -- | -- | -- | OMSU | CB A/trip at Brly(UP) only during testing work. Line remain charged from Sitarganj.
[5 empty] | -- | 2016-02-21 14:47 | 2016-02-21 15:30 | -- | -- | -- | 0 | 0.029861 | 0 | 0 | -- | -- | -- | OMSU | Trip due to R-ph jumper burnt at CB Ganj/UPPCL end.
[5 empty] | -- | 2016-02-21 15:30 | 2016-02-21 20:16 | -- | -- | -- | 0 | 0 | 0 | 0.19861 | -- | -- | -- | OSFD | Forced S/D by UPPCL for restoration of R-ph jumper.
[5 empty] | -- | 2016-02-22 09:58 | 2016-02-22 10:26 | -- | -- | -- | 0 | 0.019444 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on R-Y fault due to kite thread. Strgnj-56.9km.
[5 empty] | -- | 2016-02-22 16:27 | 2016-02-22 19:58 | -- | -- | -- | 0 | 0 | 0 | 0.14653 | -- | -- | -- | OSPD | S/D by UPPCL for Bus maintenance work at Brly(UP).
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.10764 | 0 | 0.34514 | -- | -- | -- |  |  |  | 696 | 132 | 105.72 | 13955.04 | 13955.04 | 100
55 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR1 | -- | 2016-02-21 14:44 | 2016-02-21 16:54 |  |  |  | 0 | 0 | 0.090278 | 0 |  |  |  | GOVC | Line tripped on O/voltage protn operation at Tanakpur.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.090278 | 0 | -- | -- | -- |  |  |  | 693.8333 | 132 | 106 | 13992 | 13992 | 100
56 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 42.55 | 5616.6 | 5616.6 | 100
57 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 0.92 | 121.44 | 121.44 | 100
58 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 0.92 | 121.44 | 121.44 | 100
59 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 132 | 42.5 | 5610 | 5610 | 100
[5 empty] | -- | [17 empty] | 3446.824
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 | 58 | 2900 | 2900 | 100
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-10 07:04 | 1899-12-31 19:26 | 0.275 | 1900-10-17 04:28 | [8 empty] | 22206.16 | 11103384.426 | 11078250.2855 | 99.7736 | %
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | #VALUE! | % (AC) | 97.6533 | [6 empty] | %'(HVDC)
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 400/765KV ICT-I AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | 2016-02-09 12:37 | 2016-02-09 18:44 |  |  |  | 0.25486 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for attending tension insulator string due to flashover.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.25486 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1486.8175 | 99.1212
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | 2016-02-08 07:42 | 2016-02-08 16:36 |  |  |  | 0.37083 | 0 | 0 | 0 | -- | -- | -- | SICT | Tripped on differential protection operation due to flashover in 400KV gantry insulator string during heavy fog.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.37083 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1480.819 | 98.7213
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
13 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
14 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 1500 |  | 1500 | 1500 | 100
F |  | 400/220 KV ICT'S |  | NR1 | --
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
3 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
4 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
5 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
6 | NR1ICT68 | 500MVA ICT-III BASSI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 500 |  | 500 | 500 | 100
7 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
8 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
9 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
10 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
11 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
12 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
13 | NR1ICT10 | 315MVA ICT-I BLBGARH | 315 | NR1 | -- | 2016-02-12 12:40 | 2016-03-01 |  |  |  | 0 | 0 | 0 | 1900-01-16 11:20 |  |  |  | LCSD | S/D for retrofitment with New 500MVA ICT approved under system strengthening scheme.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-16 11:20 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
14 | NR1ICT11 | 315MVA ICT-II BLBGARH | 315 | NR1 | -- | 2016-02-17 15:48 | 2016-02-17 18:06 |  |  |  | 0.095833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for Y-ph isolator contact replacement work.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.095833 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 313.9591 | 99.6695
15 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
16 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- | 2016-02-04 11:40 | 2016-02-04 15:15 | -- | -- | -- | 0 | 0 | 0 | 0.14931 | -- | -- | -- | OSFD | S/D by BBMB to attend Y-ph Stuck isolator in their S/yard.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.14931 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
17 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
18 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
19 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
20 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
21 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
22 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
23 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
24 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 500 |  | 500 | 500 | 100
25 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
26 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
27 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
28 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
29 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
30 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
31 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
32 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
33 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
34 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
35 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
36 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
37 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
38 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 500 |  | 500 | 500 | 100
39 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 500 |  | 500 | 500 | 100
40 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
41 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
42 | NR1ICT28 | 315MVA ICT-I MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
43 | NR1ICT29 | 315MVA ICT-II MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
44 | NR1ICT30 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
45 | NR1ICT31 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
46 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
47 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
48 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 316 |  | 316 | 316 | 100
49 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
50 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
51 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | [7 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
52 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
53 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
54 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
55 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
56 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | 2016-02-11 10:22 | 2016-02-11 18:51 |  |  |  | 0.35347 | 0 | 0 | 0 |  |  |  | OSPT | S/D for annual maintenance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.35347 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 311.1606 | 98.7811
57 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
58 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 500 |  | 500 | 500 | 100
59 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
60 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
61 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 315 |  | 315 | 315 | 100
62 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR1 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR1 | -- | [15 empty] | 696 | 100 |  | 100 | 100 | 100
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 100 |  | 100 | 100 | 100
--
83 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 1900-01-01 03:36 | 0 | 0 | 1900-02-03 05:50 | [7 empty] | 46451 |  | 46451 | 46413.7561 | 99.9198 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR1 | -- | 2016-02-26 06:24 | 2016-02-27 03:02 |  |  |  | 0.85972 | 0 | 0 | 0 |  |  |  | OSPT | S/D for replacement of damaged Air core reactor at Rihand.
[6 empty] | 2016-02-27 15:30 | 2016-02-27 18:16 |  |  |  | 0.11528 | 0 | 0 | 0 |  |  |  | OSFT | S/D for replacement of damage conductor of E/electrode line at Rihand end.
[6 empty] | 2016-02-29 03:40 | 2016-02-29 09:15 |  |  |  | 0.23264 | 0 | 0 | 0 |  |  |  | OSFT | Force S/D due to smoke detected in valvehall. Charged after replacing burnt capacitors.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 04:59 | 0 | 0 | 0 | [6 empty] | 696 | 750 | 815 | 611250 | 585795.8872 | 95.8357
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR1 | -- | 2016-02-06 08:49 | 2016-02-06 19:54 |  |  |  | 0.46181 | 0 | 0 | 0 |  |  |  | OSPT | S/D for RTV coating over smoothing reactor at BWD.
[5 empty] | -- | 2016-02-11 16:29 | 2016-02-11 16:38 |  |  |  | 0.00625 | 0 | 0 | 0 |  |  |  | OMST | Pole tripped on DC line earth fault at Bhiwadi.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.46806 | 0 | 0 | 0 | [6 empty] | 696 | 1250 | 789.786 | 987232.5 | 971298.7187 | 98.386
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR1 | -- | 2016-02-07 08:35 | 2016-02-07 19:28 |  |  |  | 0.45347 | 0 | 0 | 0 |  |  |  | OSPT | S/D for RTV coating over smoothing reactor at BWD.
[6 empty] | 2016-02-11 16:29 | 2016-02-11 16:45 |  |  |  | 0.011111 | 0 | 0 | 0 |  |  |  | OMST | Pole tripped on DC line earth fault at Bhiwadi.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.46458 | 0 | 0 | 0 | [6 empty] | 696 | 1250 | 789.786 | 987232.5 | 971416.9219 | 98.398
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 1900-01-01 03:22 | 0 | 0 | 0 | [8 empty] | 3209.572 | 3196965 | 3139761.5278 | 98.2107 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I | 250 | NR1 | -- | 2016-02-27 23:49 | 2016-03-01 |  |  | 2 | 1900-01-01 00:11 | 0 | 0 | 0 | 120 | N | 118 | OMST | Tripped on DC over currnet protection. Large no of thyrestor failed in valve hall.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-01 00:11 | 0 | 0 | 0 | [6 empty] | 696 | 250 |  | 250 | 232.6928 | 93.0771
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 250 |  | 250 | 250 | 100
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-01 00:11 | 0 | 0 | 0 | [9 empty] | 500 | 482.6928 | 96.5386 | %
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 696 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 280 | 280 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR1 | -- | 2016-02-01 | 2016-02-02 01:40 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 01:40 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<748kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 01:40 | -- | -- | -- |  |  |  | 696 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 50MVAR B/Reactor-I BAREILLY | 50 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
16 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR1 | -- | 2016-02-06 11:14 | 2016-02-06 15:15 |  |  |  | 0 | 0 | 0 | 0.16736 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.16736 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
17 | NR1BRT53 | 50MVAR B/Reactor-II BASSI | 50 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
18 | NR1BRT54 | 50MVAR B/Reactor-III BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
19 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- | 2016-02-17 09:09 | 2016-02-17 19:10 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[11 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.41736 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
20 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 80 |  | 80 | 80 | 100
21 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 80 |  | 80 | 80 | 100
22 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
23 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 125 |  | 125 | 125 | 100
24 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 125 |  | 125 | 125 | 100
25 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 330 |  | 330 | 330 | 100
26 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
27 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
29 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) | 125 | NR1 | -- | 2016-02-06 10:34 | 2016-02-06 15:18 |  |  |  | 0 | 0 | 0 | 0.19722 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[5 empty] | -- | 2016-02-10 09:07 | 2016-02-10 21:26 |  |  |  | 0 | 0 | 0 | 0.51319 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[5 empty] | -- | 2016-02-16 11:48 | 2016-02-16 19:04 |  |  |  | 0 | 0 | 0 | 0.30278 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 00:19 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
30 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 | 240 | NR1 | -- | [15 empty] | 696 | 240 |  | 240 | 240 | 100
31 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
32 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
33 | NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- | [15 empty] | 696 | 80 |  | 80 | 80 | 100
34 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | 2016-02-17 07:44 | 2016-02-17 18:12 |  |  |  | 0 | 0 | 0 | 0.43611 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.43611 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
35 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
36 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
37 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR1 | -- | [15 empty] | 696 | 125 |  | 125 | 125 | 100
38 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 240 |  | 240 | 240 | 100
39 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
40 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
41 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 125 |  | 125 | 125 | 100
42 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
43 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
44 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
45 | NR1BRT48 | 125MVAR B/Reactor-I RATANGARH(RJ) | 125 | NR1 | -- | [15 empty] | 696 | 125 |  | 125 | 125 | 100
46 | NR1BRT40 | 125MVAR B/Reactor Roorki | 125 | NR1 | -- | 2016-02-08 09:12 | 2016-02-08 18:17 | -- | -- | -- | 0 | 0 | 0 | 0.37847 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[5 empty] | -- | 2016-02-16 11:48 | 2016-02-16 17:28 | -- | -- | -- | 0 | 0 | 0 | 0.23611 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2016-02-17 09:09 | 2016-02-17 19:08 |  |  |  | 0 | 0 | 0 | 0.41597 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2016-02-18 14:42 | 2016-02-18 18:08 |  |  |  | 0 | 0 | 0 | 0.14306 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:10 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
47 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJAHANPUR | 125 | NR1 | -- | 2016-02-16 10:10 | 2016-02-16 17:35 |  |  |  | 0 | 0 | 0 | 0.30903 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[5 empty] | -- | 2016-02-19 10:08 | 2016-02-19 13:09 |  |  |  | 0 | 0 | 0 | 0.12569 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.43472 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
48 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 80 |  | 80 | 80 | 100
49 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 93.2 |  | 93.2 | 93.2 | 100
50 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 93.2 |  | 93.2 | 93.2 | 100
51 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR1 | -- | 2016-02-01 | 2016-02-01 11:36 | -- | -- | -- | 0 | 0 | 0 | 0.48333 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.48333 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
52 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR1 | -- | 2016-02-01 | 2016-03-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-28 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-28 | -- | -- | -- |  |  |  | 696 | 125 |  | 125 | 125 | 100
53 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
54 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
55 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
56 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
57 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
58 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
59 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
60 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
61 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
62 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 330 |  | 330 | 330 | 100
63 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
64 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
65 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 63 |  | 63 | 63 | 100
66 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 63 |  | 63 | 63 | 100
67 | NR1SRT24 | GORAKH 80MVAR S/R BARH-I LINE | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 80 |  | 80 | 80 | 100
68 | NR1SRT25 | GORAKH 80MVAR S/R BARH-II LINE | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 80 |  | 80 | 80 | 100
69 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
70 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 63 |  | 63 | 63 | 100
71 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 63 |  | 63 | 63 | 100
72 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
73 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
74 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 50 |  | 50 | 50 | 100
75 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
76 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
77 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
78 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 50 |  | 50 | 50 | 100
79 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 240 |  | 240 | 240 | 100
80 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 696 | 240 |  | 240 | 240 | 100
81 | NR1SRT27 | PHAGI(JPR)240MVAR S/R BHIWANI-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 696 | 240 |  | 240 | 240 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 1900-03-08 09:22 | [9 empty] | 9923.4 | 9923.4 |  | %
|  | TOTAL | [8 empty] | 1900-01-16 14:13 | 1899-12-31 19:26 | 0.275 | 1901-01-28 19:40
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L15:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M15:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N15:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O15:[Deemed Available, row above])
Note on C212: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C577: DOC-11-02-15
Note on C711: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14
Note on C927: DOC-15/06/14
Note on C928: DOC-26/09/14