## SOP DATA NR1 Nov-15
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.06.2015 to 30.06.2015
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [24 empty] | 0
1 | NR176505 | 765 KV AGRA- MEERUT | 267.628 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 720
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1779 | 267.628 | 476110.212 | 476110.212 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR1 | -- | 2015-11-02 21:15 | 2015-11-04 07:45 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:30 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-802 kV
[6 empty] | 2015-11-14 20:53 | 2015-11-15 07:40 |  |  |  | 0 | 0 | 0 | 0.44931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-792 kV
[6 empty] | 2015-11-15 20:41 | 2015-11-16 06:20 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-792 kV
[6 empty] | 2015-11-18 21:04 | 2015-11-19 11:29 |  |  |  | 0 | 0 | 0 | 0.60069 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-793 kV
[6 empty] | 2015-11-20 20:03 | 2015-11-21 07:14 |  |  |  | 0 | 0 | 0 | 0.46597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-800 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 08:32 | [6 empty] | 720 | 1779 | 267.628 | 476110.212 | 476110.212 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR1 | -- | 2015-11-01 | 2015-11-02 07:06 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:06 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-795 kV. Out since 2014hrs 28.10.15
[6 empty] | 2015-11-05 22:00 | 2015-11-06 05:42 |  |  |  | 0 | 0 | 0 | 0.32083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-794 kV
[6 empty] | 2015-11-06 21:57 | 2015-11-07 08:00 |  |  |  | 0 | 0 | 0 | 0.41875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-794 kV
[6 empty] | 2015-11-07 21:18 | 2015-11-08 14:57 |  |  |  | 0 | 0 | 0 | 0.73542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-794 kV
[6 empty] | 2015-11-12 01:33 | 2015-11-13 07:34 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:01 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-792 kV
[6 empty] | 2015-11-16 22:01 | 2015-11-17 07:06 |  |  |  | 0 | 0 | 0 | 0.37847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-792 kV
[6 empty] | 2015-11-17 21:50 | 2015-11-18 09:32 |  |  |  | 0 | 0 | 0 | 0.4875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-803 kV
[6 empty] | 2015-11-19 20:39 | 2015-11-20 09:24 |  |  |  | 0 | 0 | 0 | 0.53125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-792 kV
[6 empty] | 2015-11-21 20:19 | 2015-11-22 05:52 |  |  |  | 0 | 0 | 0 | 0.39792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789kV
[6 empty] | 2015-11-22 20:25 | 2015-11-23 08:12 |  |  |  | 0 | 0 | 0 | 0.49097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789kV
[6 empty] | 2015-11-23 20:46 | 2015-11-24 06:55 |  |  |  | 0 | 0 | 0 | 0.42292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789kV
[6 empty] | 2015-11-25 03:22 | 2015-11-25 06:20 |  |  |  | 0 | 0 | 0 | 0.12361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-800kV
[6 empty] | 2015-11-25 20:02 | 2015-11-26 07:56 |  |  |  | 0 | 0 | 0 | 0.49583 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-800kV
[6 empty] | 2015-11-26 21:09 | 2015-11-27 07:13 |  |  |  | 0 | 0 | 0 | 0.41944 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-792
[6 empty] | 2015-11-27 21:01 | 2015-11-28 06:51 |  |  |  | 0 | 0 | 0 | 0.40972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-792
[6 empty] | 2015-11-28 20:07 | 2015-11-29 07:05 |  |  |  | 0 | 0 | 0 | 0.45694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-795 kV
[6 empty] | 2015-11-30 20:56 | 2015-12-01 06:35 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 00:55 | [6 empty] | 720 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
5 | NR176503 | 765KV FATEHPUR-GAYA | 484.6 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1070 | 484.6 | 518522 | 518522 | 100
6 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR1 | -- | 2015-11-05 07:57 | 2015-11-05 18:49 |  |  |  | 0 | 0 | 0 | 0.45278 |  |  |  | LCSD | S/D for stringing of 765KV Gaya-Varanasi line.
[5 empty] | -- | 2015-11-06 09:50 | 2015-11-06 19:50 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | -- | -- | -- | LCSD | S/D for stringing of 765KV Gaya-Varanasi line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.86944 | [6 empty] | 720 | 1067 | 355.008 | 378793.536 | 378793.536 | 100
7 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
8 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR1 | -- | 2015-11-02 10:38 | 2015-11-02 13:38 |  |  |  | 0.125 | 0 | 0 | 0 |  |  |  | OSFT | Forced s/d due to abnormal sound on L/R at Bareilly end.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.125 | 0 | 0 | 0 | [6 empty] | 720 | 1019 | 251.613 | 256393.647 | 255325.3401 | 99.5833
9 | NR176508 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1155 | 271.571 | 313664.505 | 313664.505 | 100
B |  | 400 KV TRANS LINES |  |  | --
1 | NR140001 | 400KV AGRA-AGRA(UP)-I | 29.982 | NR1 | -- | 2015-11-18 20:08 | 2015-11-18 20:24 | -- | -- |  | 0 | 0 | 0.011111 | 0 | -- | -- | -- | GOVC | Tripped on Over Voltage protection at Agra(UP)> 436kv.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.011111 | 0 | [6 empty] | 719.7333 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR1 | -- | 2015-11-21 08:34 | 2015-11-21 18:12 | -- | -- | -- | 0.40139 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for dismantling of faulty L/R bushing at Agra end.
[5 empty] | -- | 2015-11-24 12:33 | 2015-11-24 17:45 | -- | -- | -- | 0 | 0 | 0 | 0.21667 | -- | -- | -- | OSFD | S/D by NTPC to attend hot spot in Y-ph isolator at Auraiya.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.40139 | 0 | 0 | 0.21667 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 60541.3938 | 98.662
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR1 | -- | 2015-11-01 21:23 | 2015-11-02 07:54 | -- | -- | -- | 0 | 0 | 0 | 0.43819 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[5 empty] | -- | 2015-11-03 21:43 | 2015-11-04 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.36319 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-06 21:52 | 2015-11-06 23:30 | -- | -- | -- | 0 | 0 | 0 | 0.068056 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-13 21:05 | 2015-11-14 09:09 | -- | -- | -- | 0 | 0 | 0 | 0.50278 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2015-11-17 20:42 | 2015-11-18 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.40139 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-18 08:17 | 2015-11-18 20:13 | -- | -- | -- | 0.49722 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-19 09:12 | 2015-11-19 18:44 | -- | -- | -- | 0.39722 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-20 21:15 | 2015-11-21 10:21 | -- | -- | -- | 0 | 0 | 0 | 0.54583 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-438 kV
[6 empty] | 2015-11-21 21:19 | 2015-11-23 06:52 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:33 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2015-11-26 20:13 | 2015-11-27 07:00 | -- | -- | -- | 0 | 0 | 0 | 0.44931 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-27 12:44 | 2015-11-27 15:38 | -- | -- | -- | 0 | 0 | 0 | 0.12083 | -- | -- | -- | LCSD | S/D for isolator retrofitment work under addcap at Agra.
[6 empty] | 2015-11-27 20:20 | 2015-11-28 06:57 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-28 21:53 | 2015-11-29 10:27 | -- | -- | -- | 0 | 0 | 0 | 0.52361 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-29 21:49 | 2015-11-30 08:16 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.89444 | 0 | 0 | 1900-01-04 16:32 | [6 empty] | 720 | 245 | 211.433 | 51801.085 | 50256.6452 | 97.0185
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR1 | -- | 2015-11-27 12:16 | 2015-11-27 12:48 | -- | -- | -- | 0 | 0.022222 | 0 | 0 | -- | -- | -- | OMSU | Line tripped due to fault by broken steal wire rope of crane, lifting material at nearby building construction, which swang to charged area. Site pictures and report already e-mailled.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.022222 | 0 | 0 | [6 empty] | 720 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR1 | -- | 2015-11-01 | 2015-11-06 07:04 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 07:04 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV. Out since 2030hrs 29.10.15
[6 empty] | 2015-11-06 20:13 | 2015-11-07 07:27 |  |  |  | 0 | 0 | 0 | 0.46806 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-07 21:13 | 2015-11-08 07:08 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-08 17:12 | 2015-11-09 06:12 |  |  |  | 0 | 0 | 0 | 0.54167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-10 02:06 | 2015-11-14 09:44 |  |  |  | 0 | 0 | 0 | 1900-01-03 07:38 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-14 16:12 | 2015-11-15 06:27 |  |  |  | 0 | 0 | 0 | 0.59375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-15 16:40 | 2015-11-18 06:13 |  |  |  | 0 | 0 | 0 | 1900-01-01 13:33 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-18 20:22 | 2015-11-19 09:07 |  |  |  | 0 | 0 | 0 | 0.53125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-20 20:52 | 2015-11-22 09:19 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:27 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-22 20:22 | 2015-11-23 06:33 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-23 20:06 | 2015-11-24 06:35 |  |  |  | 0 | 0 | 0 | 0.43681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-24 19:37 | 2015-11-25 06:56 |  |  |  | 0 | 0 | 0 | 0.47153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-25 18:48 | 2015-11-26 09:33 |  |  |  | 0 | 0 | 0 | 0.61458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-437 kV
[6 empty] | 2015-11-26 20:50 | 2015-11-27 06:08 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-27 20:22 | 2015-11-28 06:40 |  |  |  | 0 | 0 | 0 | 0.42917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-28 20:15 | 2015-11-30 08:56 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:41 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-30 21:07 | 2015-12-01 |  |  |  | 0 | 0 | 0 | 0.12014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-437 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-19 15:45 | [6 empty] | 720 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR1 | -- | 2015-11-14 20:53 | 2015-11-14 21:48 |  |  |  | 0.038194 | 0 | 0 | 0 |  |  |  | OSFT | Forced s/d- hand tripped from BLB end due to sparking in -ph CVT LMU connector.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.038194 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 382 | 181.137 | 69194.334 | 69106.2394 | 99.8727
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2015-11-01 | 2015-11-01 08:01 | -- | -- | -- | 0 | 0 | 0 | 0.33403 | -- | -- | -- | LVRD | Kept open on V/Regulation.Out since 2151hrs 31.10.15
[6 empty] | 2015-11-02 19:59 | 2015-11-03 09:48 | -- | -- | -- | 0 | 0 | 0 | 0.57569 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2015-11-03 20:50 | 2015-11-06 10:57 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 14:07 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2015-11-08 21:03 | 2015-11-09 06:03 |  |  |  | 0 | 0 | 0 | 0.375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-10 01:59 | 2015-11-10 09:42 |  |  |  | 0 | 0 | 0 | 0.32153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-10 21:00 | 2015-11-12 17:52 |  |  |  | 0 | 0 | 0 | 1899-12-31 20:52 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2015-11-13 20:20 | 2015-11-14 09:29 |  |  |  | 0 | 0 | 0 | 0.54792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2015-11-14 20:47 | 2015-11-15 06:36 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2015-11-15 20:52 | 2015-11-16 06:24 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-16 20:47 | 2015-11-17 10:19 |  |  |  | 0 | 0 | 0 | 0.56389 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-434 kV
[6 empty] | 2015-11-18 20:00 | 2015-11-19 09:36 |  |  |  | 0 | 0 | 0 | 0.56667 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-19 19:58 | 2015-11-20 09:05 |  |  |  | 0 | 0 | 0 | 0.54653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-20 21:15 | 2015-11-20 21:20 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on O/Voltage protection at Agra>438kv. DT received at Jaipr.
[6 empty] | 2015-11-20 21:20 | 2015-11-21 10:12 |  |  |  | 0 | 0 | 0 | 0.53611 |  |  |  | LVRD | Line kept open for Voltage regulation. Agra-438 kV
[6 empty] | 2015-11-22 21:07 | 2015-11-23 08:45 |  |  |  | 0 | 0 | 0 | 0.48472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-23 08:45 | 2015-11-23 18:00 |  |  |  | 0.38542 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-23 19:54 | 2015-11-24 08:53 |  |  |  | 0 | 0 | 0 | 0.54097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-24 08:53 | 2015-11-24 17:17 | -- | -- | -- | 0.35 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-24 20:46 | 2015-11-25 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.40139 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-25 19:38 | 2015-11-26 09:21 | -- | -- | -- | 0 | 0 | 0 | 0.57153 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-437 kV
[6 empty] | 2015-11-26 20:36 | 2015-11-27 06:58 |  |  |  | 0 | 0 | 0 | 0.43194 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-27 21:27 | 2015-11-28 06:24 |  |  |  | 0 | 0 | 0 | 0.37292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-29 19:47 | 2015-11-30 08:50 |  |  |  | 0 | 0 | 0 | 0.54375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.73542 | 0 | 0.0034722 | 1900-01-11 23:29 | -- | -- | -- |  |  |  | 719.9167 | 307 | 253.823 | 77923.661 | 76013.2279 | 97.5483
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2015-11-01 21:06 | 2015-11-02 07:51 | -- | -- | -- | 0 | 0 | 0 | 0.44792 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2015-11-06 21:24 | 2015-11-07 07:16 |  |  |  | 0 | 0 | 0 | 0.41111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-07 21:11 | 2015-11-08 07:17 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-12 21:35 | 2015-11-13 11:19 |  |  |  | 0 | 0 | 0 | 0.57222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-25 09:00 | 2015-11-25 18:08 | -- | -- | -- | 0.38056 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-26 10:24 | 2015-11-26 17:35 | -- | -- | -- | 0.29931 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-28 20:13 | 2015-11-29 11:13 | -- | -- | -- | 0 | 0 | 0 | 0.625 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.67986 | 0 | 0 | 1900-01-01 11:27 | -- | -- | -- |  |  |  | 720 | 307 | 253.823 | 77923.661 | 76157.7521 | 97.7338
11 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2015-11-01 | 2015-11-01 08:40 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV. Out since 0205hrs 28.10.15
[6 empty] | 2015-11-01 21:03 | 2015-11-02 11:16 |  |  |  | 0 | 0 | 0 | 0.59236 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2015-11-03 20:08 | 2015-11-05 06:50 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:42 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2015-11-05 21:47 | 2015-11-06 05:49 |  |  |  | 0 | 0 | 0 | 0.33472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-438 kV
[6 empty] | 2015-11-06 21:23 | 2015-11-08 08:31 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:08 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-08 21:02 | 2015-11-09 05:55 |  |  |  | 0 | 0 | 0 | 0.37014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-10 02:11 | 2015-11-10 06:29 |  |  |  | 0 | 0 | 0 | 0.17917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-10 20:59 | 2015-11-12 18:01 |  |  |  | 0 | 0 | 0 | 1899-12-31 21:02 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2015-11-13 02:09 | 2015-11-13 06:56 |  |  |  | 0 | 0 | 0 | 0.19931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-13 21:01 | 2015-11-14 09:22 |  |  |  | 0 | 0 | 0 | 0.51458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2015-11-14 21:02 | 2015-11-15 06:46 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[5 empty] | -- | 2015-11-15 20:49 | 2015-11-17 09:28 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:39 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-17 17:24 | 2015-11-18 06:57 |  |  |  | 0 | 0 | 0 | 0.56458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-18 20:07 | 2015-11-19 09:50 |  |  |  | 0 | 0 | 0 | 0.57153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-19 19:41 | 2015-11-20 09:14 |  |  |  | 0 | 0 | 0 | 0.56458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2015-11-20 20:02 | 2015-11-23 06:59 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:57 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-23 20:48 | 2015-11-24 10:05 |  |  |  | 0 | 0 | 0 | 0.55347 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-24 19:58 | 2015-11-25 07:01 |  |  |  | 0 | 0 | 0 | 0.46042 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-25 19:37 | 2015-11-26 08:15 |  |  |  | 0 | 0 | 0 | 0.52639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-437 kV
[6 empty] | 2015-11-26 20:00 | 2015-11-27 07:24 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-27 20:19 | 2015-11-30 09:01 |  |  |  | 0 | 0 | 0 | 1900-01-01 12:42 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2015-11-30 21:09 | 2015-12-01 |  |  |  | 0 | 0 | 0 | 0.11875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-437 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-17 02:10 | -- | -- | -- |  |  |  | 720 | 568 | 393.9 | 223735.2 | 223735.2 | 100
12 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2015-11-01 | 2015-11-03 06:49 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 06:49 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV. Out since 2053hrs 27.10.15
[5 empty] | -- | 2015-11-05 01:29 | 2015-11-07 07:34 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 06:05 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[5 empty] | -- | 2015-11-07 21:12 | 2015-11-08 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[5 empty] | -- | 2015-11-08 19:57 | 2015-11-10 09:52 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 13:55 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[5 empty] | -- | 2015-11-12 00:33 | 2015-11-14 09:55 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:22 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[5 empty] | -- | 2015-11-14 16:14 | 2015-11-16 15:52 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 23:38 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[5 empty] | -- | 2015-11-16 21:33 | 2015-11-17 11:11 | -- | -- | -- | 0 | 0 | 0 | 0.56806 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[5 empty] | -- | 2015-11-17 20:59 | 2015-11-18 09:12 | -- | -- | -- | 0 | 0 | 0 | 0.50903 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-20 21:39 | 2015-11-21 10:55 |  |  |  | 0 | 0 | 0 | 0.55278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-439 kV
[6 empty] | 2015-11-22 22:04 | 2015-11-23 10:31 |  |  |  | 0 | 0 | 0 | 0.51875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-24 20:43 | 2015-11-25 06:30 |  |  |  | 0 | 0 | 0 | 0.40764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-25 21:40 | 2015-11-26 10:01 |  |  |  | 0 | 0 | 0 | 0.51458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV
[6 empty] | 2015-11-30 01:34 | 2015-11-30 08:24 |  |  |  | 0 | 0 | 0 | 0.28472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-13 06:34 | -- | -- | -- |  |  |  | 720 | 568 | 393.9 | 223735.2 | 223735.2 | 100
13 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 332 | 139.73 | 46390.36 | 46390.36 | 100
14 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 332 | 139.73 | 46390.36 | 46390.36 | 100
15 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 155.932 | 80304.98 | 80304.98 | 100
16 | NR140012 | 400KV ALLD-KNP-II | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 224 | 115360 | 115360 | 100
17 | NR140019 | 400KV BALIA-MAU-I | 13 | NR1 | -- | 2015-11-06 11:42 | 2015-11-06 17:13 | -- | -- |  | 0 | 0 | 0 | 0.22986 | -- | -- | -- | OSPD | S/D by UPPCL to attend hot spot at Mau end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.22986 | -- | -- | -- |  |  |  | 720 | 515 | 13 | 6695 | 6695 | 100
18 | NR140020 | 400KV BALIA-MAU-II | 13 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 13 | 6695 | 6695 | 100
19 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 227 | 229.163 | 52020.001 | 52020.001 | 100
20 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 227 | 229.163 | 52020.001 | 52020.001 | 100
21 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 1.559 | 1071.033 | 1071.033 | 100
22 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 1.559 | 1071.033 | 1071.033 | 100
23 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 9.2 | 4738 | 4738 | 100
24 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 9.2 | 4738 | 4738 | 100
25 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR1 | -- | 2015-11-07 08:59 | 2015-11-07 19:07 | -- | -- | -- | 0.42222 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-08 08:21 | 2015-11-08 18:03 |  |  |  | 0.40417 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.82639 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 331 | 278.76 | 92269.56 | 89727.8754 | 97.2454
26 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR1 | -- | 2015-11-05 08:04 | 2015-11-05 11:12 |  |  |  | 0.13056 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-06 08:03 | 2015-11-06 18:56 |  |  |  | 0.45347 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-09 08:04 | 2015-11-09 17:27 |  |  |  | 0.39097 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.975 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 92.68 | 47730.2 | 46178.9685 | 96.75
27 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR1 | -- | 2015-11-04 10:00 | 2015-11-04 18:27 |  |  |  | 0.35208 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.35208 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 92.68 | 47730.2 | 47170.0331 | 98.8264
28 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 115.926 | 59701.89 | 59701.89 | 100
29 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 116.03 | 59755.45 | 59755.45 | 100
30 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 101.841 | 69964.767 | 69964.767 | 100
31 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 101.841 | 69964.767 | 69964.767 | 100
32 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 416 | 235 | 97760 | 97760 | 100
33 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 47.762 | 24597.43 | 24597.43 | 100
34 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 48.99 | 25229.85 | 25229.85 | 100
35 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 37.164 | 19139.46 | 19139.46 | 100
36 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 37.164 | 19139.46 | 19139.46 | 100
37 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 247 | 106.153 | 26219.791 | 26219.791 | 100
38 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.432 | 33272.784 | 33272.784 | 100
39 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.432 | 33272.784 | 33272.784 | 100
40 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | 2015-11-19 14:33 | 2015-11-19 19:01 |  |  |  | 0.18611 | 0 | 0 | 0 |  |  |  | OSFT | Forced s/d to attend R-ph loose jumper at loc no.12 by Bhw.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.18611 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 82.8 | 42642 | 42377.4617 | 99.3796
41 | NR140033 | 400KV BHIWADI-HISAR | 211.547 | NR1 | -- | 2015-11-10 02:16 | 2015-11-18 09:43 | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 07:27 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434 kV
[6 empty] | 2015-11-20 21:27 | 2015-11-21 05:54 |  |  |  | 0 | 0 | 0 | 0.35208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-429 kV
[6 empty] | 2015-11-21 21:49 | 2015-11-23 10:18 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:29 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV
[6 empty] | 2015-11-24 20:48 | 2015-11-25 10:53 |  |  |  | 0 | 0 | 0 | 0.58681 |  |  |  | LVRD | Line hand tripped for V/regulation. Bhiwadi-430 kV
[6 empty] | 2015-11-25 21:06 | 2015-11-27 07:30 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:24 |  |  |  | LVRD | Line hand tripped for V/ regulation. Bhiwadi-430 kV
[6 empty] | 2015-11-29 21:43 | 2015-11-30 06:23 |  |  |  | 0 | 0 | 0 | 0.36111 |  |  |  | LVRD | Line hand tripped for V/ regulation. Bhiwadi-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-11 13:32 | -- | -- | -- |  |  |  | 720 | 403 | 211.547 | 85253.441 | 85253.441 | 100
42 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 132.428 | 68200.42 | 68200.42 | 100
43 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2015-11-01 | 2015-11-01 07:54 | -- | -- |  | 0 | 0 | 0 | 0.32917 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BWD-431 kV. Out since 2156hrs 31.10.15
[6 empty] | 2015-11-01 21:07 | 2015-11-02 07:57 |  |  |  | 0 | 0 | 0 | 0.45139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-431 kV
[6 empty] | 2015-11-02 20:49 | 2015-11-03 09:14 |  |  |  | 0 | 0 | 0 | 0.51736 |  |  |  | LVRD | Line hand tripped for Voltage regulation.NEEM-428 kV
[6 empty] | 2015-11-08 20:59 | 2015-11-09 06:09 |  |  |  | 0 | 0 | 0 | 0.38194 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nimrana=427kv
[6 empty] | 2015-11-10 02:02 | 2015-11-10 09:37 |  |  |  | 0 | 0 | 0 | 0.31597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nimrana=427kv
[6 empty] | 2015-11-12 21:32 | 2015-11-13 07:00 |  |  |  | 0 | 0 | 0 | 0.39444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-433kV
[6 empty] | 2015-11-13 21:03 | 2015-11-14 05:50 |  |  |  | 0 | 0 | 0 | 0.36597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NEEM-428 kV
[6 empty] | 2015-11-14 21:01 | 2015-11-15 07:02 |  |  |  | 0 | 0 | 0 | 0.41736 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NEEM-428 kV
[6 empty] | 2015-11-16 20:49 | 2015-11-17 06:19 |  |  |  | 0 | 0 | 0 | 0.39583 |  |  |  | LVRD | Line hand tripped for Voltage regulation.BWD-427. kV
[6 empty] | 2015-11-17 21:08 | 2015-11-18 06:44 |  |  |  | 0 | 0 | 0 | 0.4 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nimrana=427kv
[6 empty] | 2015-11-20 20:50 | 2015-11-21 06:53 |  |  |  | 0 | 0 | 0 | 0.41875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmr-431 kV
[6 empty] | 2015-11-21 21:48 | 2015-11-22 06:50 |  |  |  | 0 | 0 | 0 | 0.37639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmr-431 kV
[6 empty] | 2015-11-22 20:23 | 2015-11-23 06:31 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmr-431 kV
[6 empty] | 2015-11-24 20:39 | 2015-11-25 06:55 |  |  |  | 0 | 0 | 0 | 0.42778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bhiwadi-430 kV
[6 empty] | 2015-11-25 21:05 | 2015-11-26 07:46 |  |  |  | 0 | 0 | 0 | 0.44514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bhiwadi-430 kV
[6 empty] | 2015-11-26 21:03 | 2015-11-27 06:04 |  |  |  | 0 | 0 | 0 | 0.37569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-428 kV
[6 empty] | 2015-11-27 20:20 | 2015-11-28 06:38 |  |  |  | 0 | 0 | 0 | 0.42917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-428 kV
[6 empty] | 2015-11-28 20:52 | 2015-11-29 10:34 |  |  |  | 0 | 0 | 0 | 0.57083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-427 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-06 10:27 | -- | -- | -- |  |  |  | 720 | 515 | 48.428 | 24940.42 | 24940.42 | 100
44 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- | 2015-11-18 20:20 | 2015-11-19 09:54 | -- | -- |  | 0 | 0 | 0 | 0.56528 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bhi-428 kV
[5 empty] | -- | 2015-11-19 20:00 | 2015-11-20 09:08 | -- | -- |  | 0 | 0 | 0 | 0.54722 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bhi-428 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 02:42 | -- | -- | -- |  |  |  | 720 | 515 | 48.428 | 24940.42 | 24940.42 | 100
45 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 42.7 | 21990.5 | 21990.5 | 100
46 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 60.68 | 41929.88 | 41929.88 | 100
47 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR1 | -- | 2015-11-16 09:14 | 2015-11-16 17:54 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | -- | -- | -- | OSPD | S/D by UPPCL for stringing of their 765kv MNP-Hapur line.
[5 empty] | -- | 2015-11-15 09:53 | 2015-11-15 19:25 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | -- | -- | -- | OSPD | S/D by UPPCL for stringing of their 765kv MNP-Hapur line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.75833 | -- | -- | -- |  |  |  | 720 | 515 | 235.952 | 121515.28 | 121515.28 | 100
48 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR1 | -- | 2015-11-16 09:14 | 2015-11-16 17:57 | -- | -- |  | 0 | 0 | 0 | 0.36319 | -- | -- | -- | OSPD | S/D by UPPCL for stringing of their 765kv MNP-Hapur line.
[6 empty] | 2015-11-06 21:21 | 2015-11-07 08:23 |  |  |  | 0 | 0 | 0 | 0.45972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV
[6 empty] | 2015-11-07 21:14 | 2015-11-08 06:21 |  |  |  | 0 | 0 | 0 | 0.37986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV
[6 empty] | 2015-11-12 00:37 | 2015-11-12 09:17 |  |  |  | 0 | 0 | 0 | 0.36111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-430 kV
[6 empty] | 2015-11-12 15:17 | 2015-11-13 07:03 |  |  |  | 0 | 0 | 0 | 0.65694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2015-11-15 09:52 | 2015-11-15 19:26 |  |  |  | 0 | 0 | 0 | 0.39861 |  |  |  | OSPD | S/D by UPPCL for stringing of their 765kv MNP-Hapur line.
[6 empty] | 2015-11-17 21:36 | 2015-11-18 06:04 |  |  |  | 0 | 0 | 0 | 0.35278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-427. kV
[6 empty] | 2015-11-20 21:23 | 2015-11-22 09:36 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:13 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV
[6 empty] | 2015-11-22 18:25 | 2015-11-22 21:00 |  |  |  | 0.10764 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to B-ph LA failure at MNP end. Ready for charging.
[6 empty] | 2015-11-22 21:00 | 2015-11-22 22:28 |  |  |  | 0 | 0 | 0 | 0.061111 |  |  |  | LVRD | Line kept open for Voltage regulation. Mnp-430 kV.
[5 empty] | -- | 2015-11-23 11:56 | 2015-11-23 15:55 | -- | -- |  | 0.16597 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for B-ph faulty LA replacement work at MNP.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.27361 | 0 | 0 | 1900-01-03 13:01 | -- | -- | -- |  |  |  | 720 | 515 | 235.952 | 121515.28 | 120407.0156 | 99.088
49 | NR140138 | 400KV BLBGRH-NAVADA | 12.55 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 12.55 | 8672.05 | 8672.05 | 100
50 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 13.256 | 9159.896 | 9159.896 | 100
51 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 54.36 | 37562.76 | 37562.76 | 100
52 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 46.3 | 31993.3 | 31993.3 | 100
53 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 46.3 | 31993.3 | 31993.3 | 100
54 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 33.098 | 17045.47 | 17045.47 | 100
55 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 112.322 | 57845.83 | 57845.83 | 100
56 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 117 | 60255 | 60255 | 100
57 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR1 | -- | 2015-11-15 14:06 | 2015-11-15 15:25 | -- | -- | -- | 0.054861 | 0 | 0 | 0 | -- | -- | -- | OSFT | Forced S/D due to Fire in S/yard near Gantry tower at Mnp.
[5 empty] | -- | 2015-11-22 18:25 | 2015-11-22 18:25 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | LART | A/reclosed at Fatehpur during LA blast of Blb-II at MNP.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.054861 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 469 | 260.051 | 121963.919 | 121740.8831 | 99.8171
58 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR1 | -- | 2015-11-02 21:29 | 2015-11-03 07:37 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.MNp-428 kV
[6 empty] | 2015-11-06 21:23 | 2015-11-07 07:23 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV
[6 empty] | 2015-11-12 15:18 | 2015-11-13 07:10 |  |  |  | 0 | 0 | 0 | 0.66111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2015-11-15 14:06 | 2015-11-15 15:25 |  |  |  | 0.054861 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to Fire in S/yard near Gantry tower at Mnp.
[6 empty] | 2015-11-29 14:09 | 2015-11-29 14:15 |  |  |  | 0.0041667 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R out of service for topping up of oil.
[6 empty] | 2015-11-29 15:48 | 2015-11-29 15:54 |  |  |  | 0.0041667 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R in service after topping up of oil.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.063194 | 0 | 0 | 1899-12-31 12:00 | -- | -- | -- |  |  |  | 720 | 469 | 260.051 | 121963.919 | 121707.0043 | 99.7894
59 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 45.94 | 23659.1 | 23659.1 | 100
60 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 45.94 | 23659.1 | 23659.1 | 100
61 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 23.462 | 16118.394 | 16118.394 | 100
62 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 23.462 | 16118.394 | 16118.394 | 100
63 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | 2015-11-01 | 2015-11-04 18:46 |  |  |  | 0 | 0 | 0 | 1900-01-02 18:46 |  |  |  | OSPD | S/D by DTL for maintenance work at Bmnoli end. Open since 16.03.15 at 13:04hrs.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 18:46 | -- | -- | -- |  |  |  | 720 | 687 | 6.106 | 4194.822 | 4194.822 | 100
64 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | 2015-11-06 10:08 | 2015-11-06 17:53 |  |  |  | 0 | 0 | 0 | 0.32292 |  |  |  | OSPD | S/D by DTL for maintanance work at their end.
[6 empty] | 2015-11-16 11:10 | 2015-11-16 20:53 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  | OSPD | S/D by DTL for new cable testing work.
[6 empty] | 2015-11-20 10:55 | 2015-11-20 18:51 |  |  |  | 0 | 0 | 0 | 0.33056 |  |  |  | OSPD | S/D by DTL for conductor dismentling work.
[6 empty] | 2015-11-29 14:57 | 2015-11-30 20:31 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:34 |  |  |  | OSPD | S/D taken by DTL for testing of relays at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 06:58 | -- | -- | -- |  |  |  | 720 | 687 | 6.106 | 4194.822 | 4194.822 | 100
65 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.782 | 4659.234 | 4659.234 | 100
66 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.782 | 4659.234 | 4659.234 | 100
67 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 225 | 201.2 | 45270 | 45270 | 100
68 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2015-11-17 20:37 | 2015-11-17 23:37 | -- | -- | -- | 0 | 0 | 0 | 0.125 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Jodhpur=439kv.
[6 empty] | 2015-11-18 21:04 | 2015-11-18 21:16 |  |  |  | 0 | 0 | 0 | 0.0083333 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jodhpur-430 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.13333 | -- | -- | -- |  |  |  | 720 | 515 | 187.965 | 96801.975 | 96801.975 | 100
69 | NR140050 | 400KV KANKROLI-RAPPC-I | 198.54 | NR1 | -- | 2015-11-26 08:50 | 2015-11-26 19:32 |  |  |  | 0.44583 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.44583 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 395 | 198.54 | 78423.3 | 77257.8426 | 98.5139
70 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- | 2015-11-27 08:04 | 2015-11-27 20:22 | -- | -- |  | 0.5125 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.5125 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 395 | 198.54 | 78423.3 | 77083.5686 | 98.2917
71 | NR140052 | 400KV KNP-AGRA | 240 | NR1 | -- | 2015-11-04 09:04 | 2015-11-08 15:57 |  |  |  | 0 | 0 | 0 | 1900-01-03 06:53 |  |  |  | LCSD | S/D for tower erection and restringing for diversion of line to facilitate construction of Railway-DFCC project.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 06:53 | -- | -- | -- |  |  |  | 720 | 291 | 240 | 69840 | 69840 | 100
72 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR1 | -- | 2015-11-24 08:37 | 2015-11-24 19:13 |  |  |  | 0 | 0 | 0 | 0.44167 |  |  |  | LCSD | S/D for shifting of line on ERS to facilitate erection of new tower for line diversion due to DFCC-project.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.44167 | -- | -- | -- |  |  |  | 720 | 515 | 72.6 | 37389 | 37389 | 100
73 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR1 | -- | 2015-11-25 10:00 | 2015-11-25 21:33 | -- | -- |  | 0 | 0 | 0 | 0.48125 | -- | -- | -- | LCSD | S/D for shifting of line on ERS to facilitate erection of new tower for line diversion due to DFCC-project.
[6 empty] | 2015-11-30 07:30 | 2015-12-01 |  |  |  | 0 | 0 | 0 | 0.6875 |  |  |  | LCSD | S/D for diversion work for facilitate DFCC project. S/D by 01.12.15
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 04:03 | -- | -- | -- |  |  |  | 720 | 515 | 73.2 | 37698 | 37698 | 100
74 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR1 | -- | 2015-11-01 | 2015-11-01 07:33 | -- | -- |  | 0 | 0 | 0 | 0.31458 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB=428kv.Out since 2110hrs 31.10.15
[5 empty] | -- | 2015-11-01 07:33 | 2015-11-01 18:45 | -- | -- |  | 0 | 0 | 0 | 0.46667 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-01 21:20 | 2015-11-02 08:31 | -- | -- |  | 0 | 0 | 0 | 0.46597 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB=428kv.
[5 empty] | -- | 2015-11-02 08:31 | 2015-11-02 18:49 | -- | -- |  | 0 | 0 | 0 | 0.42917 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-03 08:15 | 2015-11-03 18:06 | -- | -- |  | 0 | 0 | 0 | 0.41042 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-04 08:02 | 2015-11-04 20:53 | -- | -- |  | 0 | 0 | 0 | 0.53542 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-05 08:52 | 2015-11-05 19:32 | -- | -- |  | 0 | 0 | 0 | 0.44444 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-06 09:11 | 2015-11-06 18:11 | -- | -- |  | 0 | 0 | 0 | 0.375 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-06 21:27 | 2015-11-07 07:19 | -- | -- |  | 0 | 0 | 0 | 0.41111 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV
[5 empty] | -- | 2015-11-07 12:48 | 2015-11-07 18:28 | -- | -- |  | 0 | 0 | 0 | 0.23611 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-07 21:16 | 2015-11-08 06:03 | -- | -- |  | 0 | 0 | 0 | 0.36597 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV
[5 empty] | -- | 2015-11-08 08:50 | 2015-11-08 18:31 | -- | -- |  | 0 | 0 | 0 | 0.40347 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-16 21:26 | 2015-11-17 06:17 | -- | -- |  | 0 | 0 | 0 | 0.36875 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-427. kV
[5 empty] | -- | 2015-11-17 21:17 | 2015-11-18 06:11 | -- | -- |  | 0 | 0 | 0 | 0.37083 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-427. kV
[5 empty] | -- | 2015-11-26 21:49 | 2015-11-27 07:17 | -- | -- |  | 0 | 0 | 0 | 0.39444 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-428 kV
[5 empty] | -- | 2015-11-27 21:23 | 2015-11-28 06:42 | -- | -- |  | 0 | 0 | 0 | 0.38819 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-428 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-05 09:08 | -- | -- | -- |  |  |  | 720 | 342 | 385.69 | 131905.98 | 131905.98 | 100
75 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 361 | 370.772 | 133848.692 | 133848.692 | 100
76 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 361 | 370.772 | 133848.692 | 133848.692 | 100
77 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 107.079 | 55145.685 | 55145.685 | 100
78 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 107.1 | 55156.5 | 55156.5 | 100
79 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR1 | -- | 2015-11-26 11:33 | 2015-11-26 12:16 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | OMSU | DT received at KNP due to wrong operation by Panki UPPCL during shifting on transfer bus at panki.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.029861 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 5.922 | 3049.83 | 3049.83 | 100
80 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 5.86 | 3017.9 | 3017.9 | 100
81 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- | 2015-11-28 12:35 | 2015-11-28 18:58 | -- | -- | -- | 0.26597 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.26597 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 179.711 | 92551.165 | 91730.6304 | 99.1134
82 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- | 2015-11-01 | 2015-11-01 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.30417 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Merta-425 kV
[6 empty] | 2015-11-01 20:12 | 2015-11-02 08:23 |  |  |  | 0 | 0 | 0 | 0.50764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-425 kV
[6 empty] | 2015-11-02 20:00 | 2015-11-02 22:40 |  |  |  | 0 | 0 | 0 | 0.11111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-426 kV
[6 empty] | 2015-11-05 20:20 | 2015-11-05 20:25 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on O/Voltage protn operated at Merta>436kv. D/T received at Kota.
[6 empty] | 2015-11-05 20:25 | 2015-11-06 00:19 |  |  |  | 0 | 0 | 0 | 0.1625 |  |  |  | LVRD | Line kept open for Voltage regulation. Kota>428kv.
[6 empty] | 2015-11-06 20:55 | 2015-11-06 21:00 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on O/Voltage protn operated at Merta>438kv. D/T received at Kota.
[6 empty] | 2015-11-06 21:00 | 2015-11-07 06:40 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line kept open for Voltage regulation. Kota>429kv.
[6 empty] | 2015-11-07 20:16 | 2015-11-08 05:50 |  |  |  | 0 | 0 | 0 | 0.39861 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-428 kV
[6 empty] | 2015-11-08 19:34 | 2015-11-09 06:42 |  |  |  | 0 | 0 | 0 | 0.46389 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-428 kV
[6 empty] | 2015-11-09 16:10 | 2015-11-10 07:27 |  |  |  | 0 | 0 | 0 | 0.63681 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-428 kV
[6 empty] | 2015-11-10 19:34 | 2015-11-11 06:28 |  |  |  | 0 | 0 | 0 | 0.45417 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-421 kV
[6 empty] | 2015-11-11 14:09 | 2015-11-12 06:54 |  |  |  | 0 | 0 | 0 | 0.69792 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-421 kV
[6 empty] | 2015-11-12 19:36 | 2015-11-13 07:04 |  |  |  | 0 | 0 | 0 | 0.47778 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-423 kV
[6 empty] | 2015-11-13 20:58 | 2015-11-14 06:04 |  |  |  | 0 | 0 | 0 | 0.37917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-432 kV
[6 empty] | 2015-11-14 20:03 | 2015-11-15 06:12 |  |  |  | 0 | 0 | 0 | 0.42292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta=427kv.
[6 empty] | 2015-11-15 19:41 | 2015-11-16 06:11 |  |  |  | 0 | 0 | 0 | 0.4375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta=427kv.
[6 empty] | 2015-11-16 19:20 | 2015-11-17 06:12 |  |  |  | 0 | 0 | 0 | 0.45278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta=427kv.
[6 empty] | 2015-11-17 19:59 | 2015-11-18 06:24 |  |  |  | 0 | 0 | 0 | 0.43403 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta=429kv.
[6 empty] | 2015-11-18 19:30 | 2015-11-19 06:27 |  |  |  | 0 | 0 | 0 | 0.45625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. merta-430 kV
[6 empty] | 2015-11-19 19:58 | 2015-11-19 22:40 |  |  |  | 0 | 0 | 0 | 0.1125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-430 kV
[6 empty] | 2015-11-20 05:01 | 2015-11-20 05:05 |  |  |  | 0 | 0 | 0.0027778 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection at Merta>437kv.
[6 empty] | 2015-11-20 05:05 | 2015-11-20 05:41 |  |  |  | 0 | 0 | 0 | 0.025 |  |  |  | LVRD | Line kept open for Voltage regulation. Merta-430 kV
[6 empty] | 2015-11-20 19:23 | 2015-11-20 22:32 |  |  |  | 0 | 0 | 0 | 0.13125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-430 kV
[6 empty] | 2015-11-21 19:42 | 2015-11-21 22:40 |  |  |  | 0 | 0 | 0 | 0.12361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-430 kV
[6 empty] | 2015-11-22 19:39 | 2015-11-23 06:56 |  |  |  | 0 | 0 | 0 | 0.47014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-430 kV
[6 empty] | 2015-11-23 20:49 | 2015-11-24 06:45 |  |  |  | 0 | 0 | 0 | 0.41389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-430 kV
[6 empty] | 2015-11-24 19:45 | 2015-11-24 22:48 |  |  |  | 0 | 0 | 0 | 0.12708 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-430 kV
[6 empty] | 2015-11-25 19:53 | 2015-11-26 06:00 |  |  |  | 0 | 0 | 0 | 0.42153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-423 kV
[6 empty] | 2015-11-26 19:44 | 2015-11-27 05:39 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-423 kV
[6 empty] | 2015-11-27 19:35 | 2015-11-28 06:49 |  |  |  | 0 | 0 | 0 | 0.46806 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-423 kV
[6 empty] | 2015-11-28 21:20 | 2015-11-29 07:14 |  |  |  | 0 | 0 | 0 | 0.4125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427 kV
[6 empty] | 2015-11-29 19:36 | 2015-11-30 06:26 |  |  |  | 0 | 0 | 0 | 0.45139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-427 kV
[6 empty] | 2015-11-30 09:29 | 2015-11-30 18:27 |  |  |  | 0.37361 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-30 20:51 | 2015-11-30 22:55 |  |  |  | 0 | 0 | 0 | 0.086111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-426kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.37361 | 0 | 0.0097222 | 1900-01-09 20:33 | -- | -- | -- |  |  |  | 719.7667 | 309 | 255.56 | 78968.04 | 77984.2766 | 98.7542
83 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | 2015-11-25 07:48 | 2015-11-25 19:19 |  |  |  | 0.47986 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.47986 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 50.5 | 26007.5 | 25591.5004 | 98.4005
84 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.7 | 1390.5 | 1390.5 | 100
85 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.7 | 1390.5 | 1390.5 | 100
86 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | 2015-11-21 09:58 | 2015-11-21 16:11 |  |  |  | 0 | 0 | 0 | 0.25903 |  |  |  | OSPD | S/D by THDC for their GIS maintenance work at Tehri.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.25903 | -- | -- | -- |  |  |  | 720 | 633 | 14.463 | 9155.079 | 9155.079 | 100
87 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 633 | 16.49 | 10438.17 | 10438.17 | 100
88 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 289 | 263.933 | 76276.637 | 76276.637 | 100
89 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 289 | 263.933 | 76276.637 | 76276.637 | 100
90 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR1 | -- | [15 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 | 100
91 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR1 | -- | [15 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 | 100
92 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR1 | -- | 2015-11-18 13:36 | 2015-11-18 21:47 |  |  |  | 0 | 0 | 0 | 0.34097 |  |  |  | OSPD | S/D by UPPCL for maintinance work at their end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.34097 | -- | -- | -- |  |  |  | 720 | 515 | 41.743 | 21497.645 | 21497.645 | 100
93 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 371 | 169.785 | 62990.235 | 62990.235 | 100
94 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 169.729 | 87410.435 | 87410.435 | 100
95 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 98.281 | 50614.715 | 50614.715 | 100
96 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.281 | 50614.715 | 50614.715 | 100
97 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 41.743 | 21497.645 | 21497.645 | 100
98 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 73.826 | 38020.39 | 38020.39 | 100
99 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 73.826 | 38020.39 | 38020.39 | 100
100 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | 2015-11-04 09:32 | 2015-11-04 14:35 |  |  |  | 0 | 0 | 0 | 0.21042 |  |  |  | OSPD | S/D by UPPCL for ICT-II commissioning work at Mrdbd.
[6 empty] | 2015-11-07 09:15 | 2015-11-08 19:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:45 |  |  |  | LCSD | S/D for stringing of 800kv HVDC champa-Kuruchetra line
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 14:48 | -- | -- | -- |  |  |  | 720 | 515 | 133.5 | 68752.5 | 68752.5 | 100
101 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- | 2015-11-02 08:35 | 2015-11-02 23:44 | -- | -- | -- | 0 | 0 | 0 | 0.63125 | -- | -- | -- | LCSD | S/D for stringing of 800kv HVDC champa-Kuruchetra line
[6 empty] | 2015-11-03 11:07 | 2015-11-03 19:29 |  |  |  | 0 | 0 | 0 | 0.34861 |  |  |  | LCSD | S/D for stringing of 800kv HVDC champa-Kuruchetra line
[6 empty] | 2015-11-17 08:56 | 2015-11-17 17:37 | -- | -- | -- | 0 | 0 | 0 | 0.36181 | -- | -- | -- | OSPD | S/D by Power Link for annual line maintenance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:12 | -- | -- | -- |  |  |  | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
102 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | 2015-11-02 08:35 | 2015-11-02 23:44 |  |  |  | 0 | 0 | 0 | 0.63125 |  |  |  | LCSD | S/D for stringing of 800kv HVDC champa-Kuruchetra line
[6 empty] | 2015-11-03 11:07 | 2015-11-03 19:30 |  |  |  | 0 | 0 | 0 | 0.34931 |  |  |  | LCSD | S/D for stringing of 800kv HVDC champa-Kuruchetra line
[6 empty] | 2015-11-18 08:30 | 2015-11-18 16:46 |  |  |  | 0 | 0 | 0 | 0.34444 |  |  |  | OSPD | S/D by Power Link for annual line maintenance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:48 | -- | -- | -- |  |  |  | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
103 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 678 | 178.69 | 121151.82 | 121151.82 | 100
104 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 673 | 175.63 | 118198.99 | 118198.99 | 100
105 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 59.868 | 30832.02 | 30832.02 | 100
106 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 59.868 | 30832.02 | 30832.02 | 100
107 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | 2015-11-24 09:27 | 2015-11-25 19:58 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:31 |  |  |  | OSPD | S/D by UPPCL for stringing of 400kv Hapur-Ataur Line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:31 | 0 | 0 | 0 |  |  |  | 720 | 515 | 54.298 | 27963.47 | 27963.47 | 100
108 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | 2015-11-24 09:29 | 2015-11-25 19:55 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:26 |  |  |  | OSPD | S/D by UPPCL for stringing of 400kv Hapur-Ataur Line.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:26 | 0 | 0 | 0 |  |  |  | 720 | 515 | 54.298 | 27963.47 | 27963.47 | 100
109 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 37.38 | 19250.7 | 19250.7 | 100
110 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 76.018 | 39149.27 | 39149.27 | 100
111 | NR140139 | 400KV NAVADA-GR.NOIDA | 30.15 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 30.15 | 20833.65 | 20833.65 | 100
112 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 67.041 | 34526.115 | 34526.115 | 100
113 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 67.041 | 34526.115 | 34526.115 | 100
114 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- | 2015-11-02 20:52 | 2015-11-03 09:22 | -- | -- |  | 0 | 0 | 0 | 0.52083 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.NEEM-428 kV
[6 empty] | 2015-11-17 09:43 | 2015-11-17 17:48 |  |  |  | 0.33681 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-18 21:42 | 2015-11-19 06:00 |  |  |  | 0 | 0 | 0 | 0.34584 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428 kV
[6 empty] | 2015-11-20 20:55 | 2015-11-21 06:58 |  |  |  | 0 | 0 | 0 | 0.41875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmr-431 kV
[6 empty] | 2015-11-22 21:04 | 2015-11-23 06:35 |  |  |  | 0 | 0 | 0 | 0.39653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmr-431 kV
[6 empty] | 2015-11-27 21:29 | 2015-11-28 06:16 |  |  |  | 0 | 0 | 0 | 0.36597 |  |  |  | LVRD | Line hand tripped for Voltage regulation.NMR -428 kV
[5 empty] | -- | 2015-11-28 21:26 | 2015-11-29 10:31 | -- | -- | -- | 0 | 0 | 0 | 0.54514 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.NMR -428 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.33681 | 0 | 0 | 1900-01-01 14:14 | -- | -- | -- |  |  |  | 720 | 515 | 175.859 | 90567.385 | 89550.5984 | 98.8773
115 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- | 2015-11-18 09:19 | 2015-11-18 18:19 | -- | -- | -- | 0.375 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-21 21:47 | 2015-11-22 06:48 |  |  |  | 0 | 0 | 0 | 0.37569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmr-431 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.375 | 0 | 0 | 0.37569 | -- | -- | -- |  |  |  | 720 | 515 | 175.859 | 90567.385 | 89435.2927 | 98.75
116 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR1 | -- | 2015-11-18 16:38 | 2015-11-18 17:21 | -- | -- | -- | 0.029861 | 0 | 0 | 0 | -- | -- | -- | OSFT | Forced s/d to attend heavy oil leakage in L/R safty valve at Allahabad end.
[5 empty] | -- | 2015-11-18 18:19 | 2015-11-18 18:40 | -- | -- | -- | 0.014583 | 0 | 0 | 0 | -- | -- | -- | OSFT | Force S/D due to low oil level alarm in L/R at Allahabad.
[5 empty] | -- | 2015-11-26 09:12 | 2015-11-27 20:34 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:22 | -- | -- | -- | OSPD | S/D by Rhd NTPC for Numerical relay installation work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.044444 | 0 | 0 | 1899-12-31 11:22 | -- | -- | -- |  |  |  | 720 | 433 | 279.245 | 120913.085 | 120733.9545 | 99.8519
117 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 433 | 279.245 | 120913.085 | 120913.085 | 100
118 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.1 | 1081.5 | 1081.5 | 100
119 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.1 | 1081.5 | 1081.5 | 100
120 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 |  | 2015-11-01 | 2015-11-01 05:59 |  |  |  | 0 | 0 | 0 | 0.24931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. ratangarh-432 kV. Out since 2032hrs 31.10.15
[6 empty] | 2015-11-01 20:46 | 2015-11-02 06:13 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. ratangarh-432 kV
[6 empty] | 2015-11-02 19:57 | 2015-11-03 06:34 |  |  |  | 0 | 0 | 0 | 0.44236 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-432 kV
[6 empty] | 2015-11-03 20:31 | 2015-11-04 06:09 |  |  |  | 0 | 0 | 0 | 0.40139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-428 kV
[6 empty] | 2015-11-05 21:27 | 2015-11-06 06:05 |  |  |  | 0 | 0 | 0 | 0.35972 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-423 kV
[6 empty] | 2015-11-06 20:05 | 2015-11-07 06:34 |  |  |  | 0 | 0 | 0 | 0.43681 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-423 kV
[6 empty] | 2015-11-07 20:04 | 2015-11-08 05:54 |  |  |  | 0 | 0 | 0 | 0.40972 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-423 kV
[6 empty] | 2015-11-09 20:12 | 2015-11-10 06:34 |  |  |  | 0 | 0 | 0 | 0.43194 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-423 kV
[6 empty] | 2015-11-10 20:02 | 2015-11-11 06:32 |  |  |  | 0 | 0 | 0 | 0.4375 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-420 kV
[6 empty] | 2015-11-11 17:05 | 2015-11-12 06:12 |  |  |  | 0 | 0 | 0 | 0.54653 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-420 kV
[6 empty] | 2015-11-12 20:52 | 2015-11-13 07:07 |  |  |  | 0 | 0 | 0 | 0.42708 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421 kV
[6 empty] | 2015-11-13 20:05 | 2015-11-14 06:00 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-432 kV
[6 empty] | 2015-11-14 16:18 | 2015-11-15 06:03 |  |  |  | 0 | 0 | 0 | 0.57292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-432 kV
[6 empty] | 2015-11-15 18:06 | 2015-11-16 07:29 |  |  |  | 0 | 0 | 0 | 0.55764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-432 kV
[6 empty] | 2015-11-16 19:10 | 2015-11-17 06:13 |  |  |  | 0 | 0 | 0 | 0.46042 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-432 kV
[6 empty] | 2015-11-17 21:24 | 2015-11-18 06:24 |  |  |  | 0 | 0 | 0 | 0.375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. R,garh=429kv.
[6 empty] | 2015-11-18 19:55 | 2015-11-19 06:01 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428 kV
[6 empty] | 2015-11-19 19:40 | 2015-11-19 22:41 |  |  |  | 0 | 0 | 0 | 0.12569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. sikar-421 kV
[6 empty] | 2015-11-20 09:37 | 2015-11-20 16:25 |  |  |  | 0.28333 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-20 19:32 | 2015-11-20 22:42 |  |  |  | 0 | 0 | 0 | 0.13194 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-421 kV
[6 empty] | 2015-11-21 19:31 | 2015-11-21 22:49 |  |  |  | 0 | 0 | 0 | 0.1375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-421 kV
[6 empty] | 2015-11-22 19:32 | 2015-11-23 06:56 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-421 kV
[6 empty] | 2015-11-23 19:15 | 2015-11-24 07:10 |  |  |  | 0 | 0 | 0 | 0.49653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-421 kV
[6 empty] | 2015-11-25 19:49 | 2015-11-26 06:03 |  |  |  | 0 | 0 | 0 | 0.42639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-423 kV
[6 empty] | 2015-11-26 19:48 | 2015-11-27 05:43 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. R/garh-423 kV
[6 empty] | 2015-11-27 19:34 | 2015-11-28 06:13 |  |  |  | 0 | 0 | 0 | 0.44375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. R/GARH-423 kV
[6 empty] | 2015-11-28 19:44 | 2015-11-29 06:46 |  |  |  | 0 | 0 | 0 | 0.45972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-421 kV
[6 empty] | 2015-11-29 19:04 | 2015-11-30 06:28 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-427 kV
[6 empty] | 2015-11-30 19:02 | 2015-11-30 22:46 |  |  |  | 0 | 0 | 0 | 0.15556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Skr-427kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.28333 | 0 | 0 | 1900-01-10 01:50 | -- | -- | -- |  |  |  | 720 | 515 | 76.48 | 39387.2 | 39015.2098 | 99.0556
121 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 |  | 2015-11-04 21:20 | 2015-11-05 05:27 |  |  |  | 0 | 0 | 0 | 0.33819 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421 kV
[6 empty] | 2015-11-08 17:08 | 2015-11-09 06:34 |  |  |  | 0 | 0 | 0 | 0.55972 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-423 kV
[6 empty] | 2015-11-12 19:32 | 2015-11-12 22:25 |  |  |  | 0 | 0 | 0 | 0.12014 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-418 kV
[6 empty] | 2015-11-19 09:24 | 2015-11-19 18:16 |  |  |  | 0.36944 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-24 19:35 | 2015-11-24 22:33 |  |  |  | 0 | 0 | 0 | 0.12361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-421 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.36944 | 0 | 0 | 1899-12-31 03:24 | -- | -- | -- |  |  |  | 720 | 515 | 76.48 | 39387.2 | 38902.1539 | 98.7685
122 | NR140091 | 400KV SING-ALLD-I | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 332 | 224 | 74368 | 74368 | 100
123 | NR140092 | 400KV SING-ALLD-II | 202 | NR1 | -- | [15 empty] | 720 | 306 | 202 | 61812 | 61812 | 100
124 | NR140093 | 400KV SING-ANPARA | 25.057 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 25.057 | 12904.355 | 12904.355 | 100
125 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 236 | 330.953 | 78104.908 | 78104.908 | 100
126 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 337 | 408.6 | 137698.2 | 137698.2 | 100
127 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 42.026 | 21643.39 | 21643.39 | 100
128 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 43.952 | 22635.28 | 22635.28 | 100
129 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 3.341 | 1720.615 | 1720.615 | 100
130 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 3.317 | 1708.255 | 1708.255 | 100
131 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | 2015-11-16 10:20 | 2015-11-16 20:19 |  |  |  | 0 | 0 | 0 | 0.41597 |  |  |  | OSPD | S/D by for replacement of faulty CVT at Zerda by Gridco.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.41597 | -- | -- | -- |  |  |  | 720 | 236 | 233.707 | 55154.852 | 55154.852 | 100
132 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 272 | 142.8 | 38841.6 | 38841.6 | 100
[5 empty] | -- | [17 empty] | 18399.672
|  | 220 KV TRANS LINES |  |  | --
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR1 | -- | [15 empty] | 720 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR1 | -- | 2015-11-22 13:15 | 2015-11-22 15:27 | -- | -- |  | 0 | 0 | 0 | 0.091667 | -- | -- | -- | OSPD | S/D by UPPCL to attend hotspot at RewaRd end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.091667 | -- | -- | -- |  |  |  | 720 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 3 | 396 | 396 | 100
5 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | 2015-11-04 08:16 | 2015-11-04 19:32 |  |  |  | 0.46944 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.46944 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 186.667 | 24640.044 | 24254.4729 | 98.4352
6 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | 2015-11-05 08:22 | 2015-11-05 19:29 |  |  |  | 0.46319 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.46319 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 186.667 | 24640.044 | 24259.6063 | 98.456
7 | NR122038 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- | 2015-11-01 08:33 | 2015-11-01 19:23 | -- | -- | -- | 0 | 0 | 0 | 0.45139 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[6 empty] | 2015-11-02 08:23 | 2015-11-02 19:09 |  |  |  | 0 | 0 | 0 | 0.44861 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
[6 empty] | 2015-11-07 13:35 | 2015-11-07 18:30 |  |  |  | 0 | 0 | 0 | 0.20486 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 02:31 | -- | -- | -- |  |  |  | 720 | 132 | 180.287 | 23797.884 | 23797.884 | 100
8 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- | 2015-11-20 08:12 | 2015-11-20 18:14 | -- | -- |  | 0.41806 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.41806 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 87.544 | 11468.264 | 11308.4516 | 98.6065
9 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | 2015-11-03 08:30 | 2015-11-03 19:39 |  |  |  | 0.46458 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.46458 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 102.164 | 13485.648 | 13276.8078 | 98.4514
10 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 182.176 | 24047.232 | 24047.232 | 100
11 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR1 | -- | 2015-11-29 06:13 | 2015-11-29 07:23 |  |  |  | 0 | 0.048611 | 0 | 0 |  |  |  | OMSU | Line tripped on Z-2 protn 3-ph fault beyond Auraiya. FLR-Sikand-186km.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.048611 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 182.176 | 24047.232 | 24047.232 | 100
12 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 35.353 | 4631.243 | 4631.243 | 100
13 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100
14 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100
15 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | 2015-11-25 10:45 | 2015-11-26 19:42 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:57 |  |  |  | LPRD | Line hand tripped on Power regulation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:57 | -- | -- | -- |  |  |  | 720 | 131 | 22.478 | 2944.618 | 2944.618 | 100
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 109 | 234.59 | 25570.31 | 25570.31 | 100
17 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 156 | 59.01 | 9205.56 | 9205.56 | 100
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 5.284 | 692.204 | 692.204 | 100
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 5.284 | 692.204 | 692.204 | 100
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 6.17 | 808.27 | 808.27 | 100
21 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR1 | -- | 2015-11-19 11:52 | 2015-11-19 13:51 |  |  |  | 0 | 0.082639 | 0 | 0 |  |  |  | OMSU | Line tripped on R&B phase fault in UPPCL portion. FLR: Fatehpur-49.5km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.082639 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 6.17 | 808.27 | 808.27 | 100
22 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 15.69 | 2055.39 | 2055.39 | 100
23 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 15.69 | 2055.39 | 2055.39 | 100
24 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 17.691 | 2317.521 | 2317.521 | 100
25 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 17.691 | 2317.521 | 2317.521 | 100
26 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 24.875 | 3258.625 | 3258.625 | 100
27 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 12 | 1572 | 1572 | 100
28 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR1 | -- | 2015-11-21 10:40 | 2015-11-30 17:56 | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 07:16 | -- | -- | -- | OSPD | S/D by UPPCL for diversion of the line due to Lucknow-Agra express way construction.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 07:16 | -- | -- | -- |  |  |  | 720 | 131 | 10.4 | 1362.4 | 1362.4 | 100
29 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR1 | -- | 2015-11-06 15:28 | 2015-11-06 17:57 |  |  |  | 0 | 0 | 0 | 0.10347 |  |  |  | OSFD | S/D by UPPCL for maintanance work at Naubasta end.
[6 empty] | 2015-11-25 12:50 | 2015-11-25 13:17 |  |  |  | 0 | 0.01875 | 0 | 0 |  |  |  | OMSU | Line A/R at KNP but tripped from Naubasta due to non auto reclose on B-N fault in UP portion. FLR:15km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.01875 | 0 | 0.10347 | -- | -- | -- |  |  |  | 720 | 131 | 14.86 | 1946.66 | 1946.66 | 100
30 | NR122018 | 220KV KNP-PANKI-I | 10.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 10.4 | 1362.4 | 1362.4 | 100
31 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 14.86 | 1946.66 | 1946.66 | 100
32 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 143.553 | 18805.443 | 18805.443 | 100
33 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 143.553 | 18805.443 | 18805.443 | 100
34 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 144.63 | 18946.53 | 18946.53 | 100
35 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 144.63 | 18946.53 | 18946.53 | 100
36 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | 2015-11-03 09:32 | 2015-11-03 19:05 |  |  |  | 0 | 0 | 0 | 0.39792 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
[6 empty] | 2015-11-04 08:22 | 2015-11-04 10:49 |  |  |  | 0 | 0 | 0 | 0.10208 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.5 | -- | -- | -- |  |  |  | 720 | 132 | 28.02 | 3698.64 | 3698.64 | 100
37 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- | 2015-11-21 10:14 | 2015-11-21 10:35 | -- | -- | -- | 0 | 0 | 0 | 0.014583 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
[6 empty] | 2015-11-30 07:46 | 2015-11-30 17:53 |  |  |  | 0 | 0 | 0 | 0.42153 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.43611 | -- | -- | -- |  |  |  | 720 | 132 | 2.316 | 305.712 | 305.712 | 100
38 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- | 2015-11-21 10:14 | 2015-11-21 10:35 | -- | -- | -- | 0 | 0 | 0 | 0.014583 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
[5 empty] | -- | 2015-11-25 09:41 | 2015-11-25 18:38 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[6 empty] | 2015-11-25 18:38 | 2015-11-25 21:41 |  |  |  | 0 | 0 | 0 | 0.12708 |  |  |  | OSFD | S/D continued by UPPCL due to isolator problem at Modipr.
[5 empty] | -- | 2015-11-26 08:17 | 2015-11-26 13:00 | -- | -- | -- | 0 | 0.19653 | 0 | 0 | -- | -- | -- | OMSU | Line opened for S/D but PTW not issued by UPPC. Restored back due to proposed SPS testing, without any work.
[5 empty] | -- | 2015-11-27 08:20 | 2015-11-27 18:26 | -- | -- | -- | 0 | 0 | 0 | 0.42083 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
[6 empty] | 2015-11-28 09:39 | 2015-11-28 18:19 |  |  |  | 0 | 0 | 0 | 0.36111 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-29 08:06 | 2015-11-29 16:56 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | -- | -- | -- | LCSD | S/D for Polymer insulator installation for system strengthning.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.19653 | 0 | 1899-12-31 15:57 | -- | -- | -- |  |  |  | 720 | 132 | 9.254 | 1221.528 | 1221.528 | 100
39 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- | 2015-11-06 14:24 | 2015-11-06 18:17 | -- | -- | -- | 0 | 0 | 0 | 0.16181 | -- | -- | -- | OSFD | S/D by UPPCL to attend hot spot at Nara end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.16181 | -- | -- | -- |  |  |  | 720 | 132 | 2.316 | 305.712 | 305.712 | 100
40 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- | 2015-11-21 10:20 | 2015-11-21 11:08 | -- | -- | -- | 0 | 0 | 0 | 0.033333 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.033333 | -- | -- | -- |  |  |  | 720 | 132 | 8.234 | 1086.888 | 1086.888 | 100
41 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 9.254 | 1221.528 | 1221.528 | 100
42 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 156 | 177.88 | 27749.28 | 27749.28 | 100
43 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR1 | -- | 2015-11-25 01:22 | 2015-11-25 17:08 | -- | -- | -- | 0 | 0 | 0 | 0.65694 | -- | -- | -- | OSFD | Forced s/d by UPPCL to attend Y-N fault in their portion after tripping at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.65694 | -- | -- | -- |  |  |  | 720 | 132 | 1.19 | 157.08 | 157.08 | 100
44 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 1.19 | 157.08 | 157.08 | 100
45 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | 2015-11-23 11:58 | 2015-11-23 18:33 |  |  |  | 0.27431 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-23 18:33 | 2015-11-24 04:46 |  |  |  | 0 | 0 | 0 | 0.42569 |  |  |  | OSFD | Forced S/D by RAPPB due to sparking in isolator.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.27431 | 0 | 0 | 0.42569 | -- | -- | -- |  |  |  | 720 | 131 | 128.833 | 16877.123 | 16722.8067 | 99.0856
46 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | 2015-11-24 08:55 | 2015-11-24 19:42 |  |  |  | 0.44931 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter maintinance and AMP works.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.44931 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 128.833 | 16877.123 | 16624.3568 | 98.5023
47 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 0.175 | 22.925 | 22.925 | 100
48 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- | 2015-11-21 08:49 | 2015-11-21 17:47 | -- | -- |  | 0.37361 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
[6 empty] | 2015-11-21 17:47 | 2015-11-21 20:29 |  |  |  | 0 | 0.1125 | 0 | 0 |  |  |  | OMSU | Operational delay in charging due to problem at RVPNL.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.37361 | 0.1125 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 230.297 | 30168.907 | 29793.1924 | 98.7546
49 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | 2015-11-04 11:22 | 2015-11-04 19:45 |  |  |  | 0 | 0 | 0 | 0.34931 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-05 08:32 | 2015-11-05 17:33 |  |  |  | 0 | 0 | 0 | 0.37569 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
[6 empty] | 2015-11-06 08:45 | 2015-11-06 18:38 |  |  |  | 0 | 0 | 0 | 0.41181 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
[5 empty] | -- | 2015-11-07 08:55 | 2015-11-07 13:10 |  |  |  | 0 | 0 | 0 | 0.17708 |  |  |  | LCSD | S/D for Polymer insulator installation for system strengthning.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:32 | -- | -- | -- |  |  |  | 720 | 132 | 106.243 | 14024.076 | 14024.076 | 100
50 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 2.83 | 373.56 | 373.56 | 100
51 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 2.83 | 373.56 | 373.56 | 100
52 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 3 | 396 | 396 | 100
53 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- | 2015-11-22 05:55 | 2015-11-22 07:00 | -- | -- | -- | 0 | 0.045139 | 0 | 0 | -- | -- | -- | OMSU | Tripped due to B-ph Jumper snaping in RRVPNL portion.
[5 empty] | -- | 2015-11-22 07:00 | 2015-11-22 14:51 | -- | -- | -- | 0 | 0 | 0 | 0.32708 | -- | -- | -- | OSFD | Forced S/D by RRVPNL for restoration of B-ph jumper.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.045139 | 0 | 0.32708 | -- | -- | -- |  |  |  | 720 | 132 | 3 | 396 | 396 | 100
54 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR1 | -- | 2015-11-03 08:06 | 2015-11-03 18:31 | -- | -- | -- | 0.43403 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for pre winter maintinance and AMP works.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.43403 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 105.72 | 13955.04 | 13753.1442 | 98.5532
55 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR1 | -- | 2015-11-23 08:34 | 2015-11-23 09:02 |  |  |  | 0 | 0.019444 | 0 | 0 |  |  |  | OMSU | CB autotrip at Tanakpur end due to local problem. Line remain charged from Bly(UP) end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.019444 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 106 | 13992 | 13992 | 100
56 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR1 | -- | 2015-11-02 08:27 | 2015-11-02 18:20 |  |  |  | 0.41181 | 0 | 0 | 0 |  |  |  | OSPT | S/D for pre winter and AMP works.
[6 empty] | 2015-11-23 08:34 | 2015-11-23 09:28 |  |  |  | 0 | 0.0375 | 0 | 0 |  |  |  | OMSU | CB autotrip at Tanakpur end due to local problem. Line remain charged from Sitarganj end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.41181 | 0.0375 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 42.55 | 5616.6 | 5539.5018 | 98.6273
57 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 0.92 | 121.44 | 121.44 | 100
58 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 0.92 | 121.44 | 121.44 | 100
59 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 42.5 | 5610 | 5610 | 100
[5 empty] | -- | [17 empty] | 3441.839
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 | 58 | 2900 | 2900 | 100
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-24 16:50 | 1899-12-31 05:26 | 0.048611 | 1901-01-08 21:48 | [8 empty] | 21899.511 | 10895483.238 | 10871672.2276 | 99.7815 | %
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | #VALUE! | % (AC) | 88.8815 | [6 empty] | %'(HVDC)
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 400/765KV ICT-I AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
13 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
14 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
F |  | 400/220 KV ICT'S |  | NR1 | --
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
3 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
4 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
5 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
6 | NR1ICT68 | 500MVA ICT-III BASSI | 315 | NR1 |  | 2015-11-25 11:01 | 2015-11-26 19:01 |  |  |  | 1899-12-31 08:00 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for replacement of its radiator bank fins.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 08:00 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 477.7778 | 95.5556
7 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
8 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
9 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
10 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
11 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
12 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
13 | NR1ICT10 | 315MVA ICT-I BLBGARH | 315 | NR1 | -- | 2015-11-18 14:38 | 2015-11-18 18:14 |  |  |  | 0 | 0 | 0 | 0.15 |  |  |  | SCSD | S/D for isolator retrofitment work at BLB under Addcap. Dejumpering.
[6 empty] | 2015-11-30 11:11 | 2015-11-30 14:07 |  |  |  | 0 | 0 | 0 | 0.12222 |  |  |  | SCSD | S/D for isolator retrofitment work under Addcap. Re-jumpering.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.27222 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
14 | NR1ICT11 | 315MVA ICT-II BLBGARH | 315 | NR1 | -- | 2015-11-04 11:19 | 2015-11-04 12:54 |  |  |  | 0 | 0 | 0 | 0.065972 |  |  |  | SCSD | S/D for isolator retrofitment work at BLB under Addcap. Dejumpering.
[5 empty] | -- | 2015-11-10 11:09 | 2015-11-10 13:46 |  |  |  | 0 | 0 | 0 | 0.10903 |  |  |  | SCSD | S/D for isolator retrofitment work under Addcap. Re-jumpering.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.175 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
15 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
16 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
17 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
18 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
19 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
20 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
21 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
22 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
23 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
24 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
25 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
26 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
27 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
28 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
29 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
30 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
31 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
32 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
33 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
34 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
35 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
36 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
37 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
38 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
39 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
40 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
41 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR1 | -- | 2015-11-13 11:30 | 2015-11-13 14:18 |  |  |  | 0.11667 | 0 | 0 | 0 |  |  |  | OSFT | Force S/D for attend hot spot in 220KV side R-ph isolator.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.11667 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 313.775 | 99.6111
42 | NR1ICT28 | 315MVA ICT-I MANDOLA | 315 | NR1 | -- | 2015-11-04 06:58 | 2015-11-04 11:54 |  |  |  | 0 | 0 | 0 | 0.20556 |  |  |  | SCSD | S/D for main CB retrofitment work at MND under Addcap. Dejumpering.
[6 empty] | 2015-11-05 07:28 | 2015-11-05 17:09 |  |  |  | 0 | 0 | 0 | 0.40347 |  |  |  | SCSD | S/D for main CB retrofitment work at MND under Addcap. Rejumpering.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.60903 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
43 | NR1ICT29 | 315MVA ICT-II MANDOLA | 315 | NR1 | -- | 2015-11-23 07:46 | 2015-11-23 12:04 |  |  |  | 0 | 0 | 0 | 0.17917 |  |  |  | SCSD | S/D for main CB retrofitment work at MND under Addcap. Dejumpering.
[5 empty] | -- | 2015-11-24 07:40 | 2015-11-24 12:45 |  |  |  | 0 | 0 | 0 | 0.21181 |  |  |  | SCSD | S/D for main CB retrofitment work at MND under Addcap. Rejumpering.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.39097 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
44 | NR1ICT30 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
45 | NR1ICT31 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | 2015-11-07 05:35 | 2015-11-07 08:07 |  |  |  | 0.10556 | 0 | 0 | 0 |  |  |  | SICT | ICT tripped on Differential protection operation.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10556 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 313.8917 | 99.6481
46 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
47 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
48 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 316 |  | 316 | 316 | 100
49 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
50 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
51 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | [7 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
52 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
53 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
54 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
55 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
56 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
57 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
58 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
59 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
60 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
61 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
62 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR1 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 | -- | 2015-11-01 | 2015-11-20 14:02 |  |  | 20 | 0 | 0 | 1900-01-18 14:02 | 0 | 52 | N | -32 | LNCC | Differential, REF, PRD, Buchholz & other ICT protn trip due to striking of lightning surge on Y-ph unit near LV bushing during strong thunderstorm. Out since 1720hrs of 22-08-15.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1900-01-18 14:02 | 0 | -- | -- | -- |  |  |  | 249.9667 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR1 | -- | [15 empty] | 720 | 100 |  | 100 | 100 | 100
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR1 | -- | 2015-11-11 11:05 | 2015-11-11 13:54 |  |  |  | 0 | 0 | 0 | 0.11736 |  |  |  | OSFD | S/D by UPPCL for attending hot spot on B-ph CT in their 132 KV S/Yard.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.11736 | -- | -- | -- |  |  |  | 720 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR1 | -- | 2015-11-16 09:39 | 2015-11-16 19:09 |  |  |  | 0.39583 | 0 | 0 | 0 |  |  |  | OSPT | S/D for annual mailtanance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.39583 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 100 |  | 100 | 98.6806 | 98.6806
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR1 | -- | 2015-11-17 09:36 | 2015-11-17 18:46 |  |  |  | 0.38194 | 0 | 0 | 0 |  |  |  | OSPT | S/D for annual mailtanance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.38194 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 100 |  | 100 | 98.7269 | 98.7269
--
83 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 1900-01-03 16:00 | 0 | 1900-02-07 04:04 | 1900-01-02 03:06 | [7 empty] | 46451 |  | 46451 | 46423.8519 | 99.9416 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR1 | -- | 2015-11-25 14:19 | 2015-11-25 19:01 |  |  |  | 0.19583 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for replacement of snubber capacitor at Rh end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.19583 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 607259.8958 | 99.3472
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR1 | -- | 2015-11-20 08:22 | 2015-11-20 19:47 |  |  |  | 0.47569 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance
[5 empty] | -- | 2015-11-21 08:18 | 2015-11-21 21:19 |  |  |  | 0.54236 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line AMP & terminal equipment maintenance.
[5 empty] | -- | 2015-11-24 08:22 | 2015-11-24 22:36 |  |  |  | 0.59306 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance work.
[5 empty] | -- | 2015-11-30 08:25 | 2015-11-30 19:04 |  |  |  | 0.44375 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-01 01:19 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 919611.6443 | 93.1505
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR1 | -- | 2015-11-22 08:12 | 2015-11-22 21:36 |  |  |  | 0.55833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance
[6 empty] | 2015-11-23 08:15 | 2015-11-23 19:55 |  |  |  | 0.48611 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance.
[6 empty] | 2015-11-25 08:35 | 2015-11-25 20:30 |  |  |  | 0.49653 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance work.
[6 empty] | 2015-11-26 08:25 | 2015-11-26 19:13 |  |  |  | 0.45 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance
[6 empty] | 2015-11-27 08:24 | 2015-11-27 19:20 |  |  |  | 0.45556 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance work.
[6 empty] | 2015-11-28 08:55 | 2015-11-28 19:50 |  |  |  | 0.45486 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance work.
[6 empty] | 2015-11-29 08:44 | 2015-11-29 19:29 |  |  |  | 0.44792 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & terminal equipment maintenance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-02 08:23 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 877014.3901 | 88.8356
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 1900-01-04 14:24 | 0 | 0 | 0 | [8 empty] | 3209.572 | 3196965 | 3015135.9302 | 94.3124 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I | 250 | NR1 | -- | 2015-11-01 | 2015-11-13 17:44 |  |  | 13 | 1900-01-11 17:44 | 0 | 0 | 0 | 35 | N | -22 | OMST | Tripped on DC over curent protection. Out due to major components failure in valve hall since 6/8/15-1242hrs. Expected by 15-11-15.
[6 empty] | 2015-11-18 16:19 | 2015-11-18 19:20 |  |  |  | 0 | 0.12569 | 0 | 0 |  |  |  | OMSU | Power loss due to tripping of both 400KV AC-HVDC feeder of NTPC from VSTPP end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-11 17:44 | 0.12569 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 143.8426 | 57.537
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR1 | -- | 2015-11-06 16:25 | 2015-11-07 03:12 |  |  |  | 0.44931 | 0 | 0 | 0 |  |  |  | OSFT | Force S/D due to thyrister Failure alarm in valve hall.
[5 empty] | -- | 2015-11-18 16:19 | 2015-11-18 19:20 |  |  |  | 0 | 0.12569 | 0 | 0 |  |  |  | OMSU | Power loss due to tripping of both 400KV AC-HVDC feeder of NTPC from VSTPP end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.44931 | 0.12569 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 246.2558 | 98.5023
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-12 04:31 | 0.12569 | 0 | 0 | [9 empty] | 500 | 390.0984 | 78.0197 | %
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 280 | 280 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 50MVAR B/Reactor-I BAREILLY | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
16 | NR1BRT04 | 50MVAR B/Reactor BASSI | 50 | NR1 | -- | 2015-11-24 10:20 | 2015-11-24 19:31 |  |  |  | 0 | 0 | 0 | 0.38264 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[6 empty] | 2015-11-25 09:23 | 2015-11-25 19:43 |  |  |  | 0 | 0 | 0 | 0.43056 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2015-11-26 08:05 | 2015-11-26 21:01 |  |  |  | 0 | 0 | 0 | 0.53889 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2015-11-27 10:06 | 2015-11-27 21:20 |  |  |  | 0 | 0 | 0 | 0.46806 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 19:41 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
17 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- | 2015-11-26 10:37 | 2015-11-26 19:32 | -- | -- | -- | 0 | 0 | 0 | 0.37153 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.37153 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
18 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
19 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
20 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
21 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
22 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
23 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 330 |  | 330 | 330 | 100
24 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
25 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
26 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | 2015-11-24 10:21 | 2015-11-24 19:38 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[5 empty] | -- | 2015-11-25 10:31 | 2015-11-25 19:38 |  |  |  | 0 | 0 | 0 | 0.37986 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[5 empty] | -- | 2015-11-26 08:16 | 2015-11-26 21:01 |  |  |  | 0 | 0 | 0 | 0.53125 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[5 empty] | -- | 2015-11-27 10:06 | 2015-11-27 21:20 |  |  |  | 0 | 0 | 0 | 0.46806 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[5 empty] | -- | 2015-11-30 09:06 | 2015-11-30 09:10 |  |  |  | 0 | 0 | 0 | 0.0027778 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 18:27 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
27 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 | 240 | NR1 | -- | [15 empty] | 720 | 240 |  | 240 | 240 | 100
28 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
29 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
30 | NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- | [15 empty] | 720 | 80 |  | 80 | 80 | 100
31 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | 2015-11-24 09:38 | 2015-11-24 19:50 |  |  |  | 0 | 0 | 0 | 0.425 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[6 empty] | 2015-11-25 09:19 | 2015-11-25 13:24 |  |  |  | 0 | 0 | 0 | 0.17014 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2015-11-26 09:11 | 2015-11-26 13:17 |  |  |  | 0 | 0 | 0 | 0.17083 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2015-11-30 06:56 | 2015-11-30 13:12 |  |  |  | 0 | 0 | 0 | 0.26111 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 00:39 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
32 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
33 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
34 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR1 | -- | [15 empty] | 720 | 125 |  | 125 | 125 | 100
35 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
36 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
37 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
38 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
39 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
40 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
41 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
42 | NR1BRT48 | 125MVAR B/Reactor-I RATANGARH(RJ) | 125 | NR1 | -- | [15 empty] | 720 | 125 |  | 125 | 125 | 100
43 | NR1BRT40 | 125MVAR B/Reactor Roorki | 125 | NR1 | -- | 2015-11-02 07:09 | 2015-11-05 02:57 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 19:48 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2015-11-06 05:30 | 2015-11-13 00:30 |  |  |  | 0 | 0 | 0 | 1900-01-05 19:00 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[6 empty] | 2015-11-13 07:24 | 2015-11-20 21:15 |  |  |  | 0 | 0 | 0 | 1900-01-06 13:51 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2015-11-21 11:29 | 2015-11-28 21:18 |  |  |  | 0 | 0 | 0 | 1900-01-06 09:49 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[6 empty] | 2015-11-30 06:53 | 2015-12-01 |  |  |  | 0 | 0 | 0 | 0.71319 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-24 07:35 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
44 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJAHANPUR | 125 | NR1 | -- | [15 empty] | 720 | 125 |  | 125 | 125 | 100
45 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
46 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 93.2 |  | 93.2 | 93.2 | 100
47 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 93.2 |  | 93.2 | 93.2 | 100
48 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
49 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
50 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
51 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
52 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
53 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
54 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
55 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
56 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
57 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
58 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
59 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
60 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
61 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
62 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
63 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
64 | NR1SRT24 | GORAKH 80MVAR S/R BARH-I LINE | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
65 | NR1SRT25 | GORAKH 80MVAR S/R BARH-II LINE | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
66 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
67 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
68 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
69 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
70 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
71 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
72 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
73 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
74 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
75 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
76 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
77 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
78 | NR1SRT27 | PHAGI(JPR)240MVAR S/R BHIWANI-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 1900-02-28 14:34 | [9 empty] | 9823.4 | 9823.4 |  | %
|  | TOTAL | [8 empty] | 1900-02-17 03:45 | 1899-12-31 08:27 | 1900-02-07 05:14 | 1901-03-13 15:28
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L15:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M15:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N15:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O15:[Deemed Available, row above])
Note on C219: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C576: DOC-11-02-15
Note on C699: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14
Note on C907: DOC-15/06/14
Note on C908: DOC-26/09/14