## OUTAGE_April_13
POWER GRID CORPORATION OF INDIA LTD.
NORTHERN REGION - 1
CPCC, N. DELHI
DOC No: NR-I/CPCC/II
MONTH – APRIL'2013 LINE/ ICT OUTAGE DETAILS
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Classification/ Category Code | REASON OF OUTAGE | NRLDC CODE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Code
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12
NEDCB01 | 404009 | +/-500MW HVDC B/B SASARAM | 2013-04-02 07:08 | 2013-04-02 12:22 | 0.21806 | 0 | 0 | 0 | OMST | TRIPPED DUE TO EAST SIDE PROTECTION FAILURE CAUSED BY BIRD STRIKE.
NEDCB01 | 404079 | +/-500MW HVDC B/B SASARAM | 2013-04-07 17:26 | 2013-04-07 22:19 | 0.20347 | 0 | 0 | 0 | OMST | TRIPPED DUE TO OPRATION OF FILTER PROTECTION CAUSED BY BIRDS STRIKES
NEDCB01 | 404094 | +/-500MW HVDC B/B SASARAM | 2013-04-08 20:42 | 2013-04-08 23:15 | 0 | 0.10625 | 0 | 0 | OMSU | TRIPPED DUE TO AUXILIARY SUPPLY FAILURE AT BSEB SYSTEM.
|  | SUB TOTAL |  |  | 0.42153 | 0.10625 | 0 | 0
NWDCB01 | 104039 | VINDH HVDC B/B BLOCK-I | 2013-04-04 16:06 | 2013-04-04 18:10 | 0 | 0 | 0 | 0.086111 | SCSD | S/D for Erection work of future Bay equipment at Vindh. | N-333
NWDCB01 | 104193 | VINDH HVDC B/B BLOCK-I | 2013-04-20 12:00 | 2013-04-20 14:13 | 0.092361 | 0 | 0 | 0 | OSPT | S/D for inspection and assessment of Valve hall upgradation work by M/s ABB Engineer. | N-1565
NWDCB01 | 104214 | VINDH HVDC B/B BLOCK-I | 2013-04-23 09:06 | 2013-04-26 20:54 | 1900-01-02 11:48 | 0 | 0 | 0 | OSPT | S/D for annual maintenance work. | N-1752
NWDCB01 | 104254 | VINDH HVDC B/B BLOCK-I | 2013-04-28 13:15 | 2013-04-28 17:43 | 0.18611 | 0 | 0 | 0 | OSFT | S/D to attend R-ph west isolator sprking problem. | N-2089
|  | SUB TOTAL |  |  | 1900-01-02 18:29 | 0 | 0 | 0.086111
NWDCB02 | 104190 | VINDH HVDC B/B BLOCK-II | 2013-04-20 09:12 | 2013-04-20 11:52 | 0.11111 | 0 | 0 | 0 | OSPT | S/D for inspection and assessment of Valve hall upgradation work by M/s ABB Engineer. | N-1548
NWDCB02 | 104222 | VINDH HVDC B/B BLOCK-II | 2013-04-24 11:24 | 2013-04-24 14:33 | 0 | 0 | 0 | 0.13125 | SCSD | S/D for Gantry tower insulator replacement with Polymer. | N-1815
NWDCB02 | 104246 | VINDH HVDC B/B BLOCK-II | 2013-04-27 09:46 | 2013-04-29 20:57 | 1900-01-01 11:11 | 0 | 0 | 0 | OSPT | S/D for annual maintenance work. | N-2009
|  | SUB TOTAL |  |  | 1900-01-01 13:51 | 0 | 0 | 0.13125
NR1DCP01 | 104159 | HVDC R-D POLE-I | 2013-04-17 09:00 | 2013-04-17 11:26 | 0.10139 | 0 | 0 | 0 | OSPT | S/D for inspection and assessment of Valve hall upgradation work by M/s ABB Engineer. | N-1322
NR1DCP01 | 104176 | HVDC R-D POLE-I | 2013-04-19 04:00 | 2013-04-19 07:00 | 0.125 | 0 | 0 | 0 | OSFT | H/tripped by Dadri due to spark seen in B-ph Valve hall.
NR1DCP01 | 104177 | HVDC R-D POLE-I | 2013-04-19 07:00 | 2013-04-19 19:28 | 0 | 0 | 0 | 0.51944 | LCSD | S/D for stringing work of 765kv Agra-Fatehpur line. | N-1482
NR1DCP01 | 104178 | HVDC R-D POLE-I | 2013-04-19 07:00 | 2013-04-19 19:09 | 0 | 0 | 0 | 0.50625 | LCSD | S/D for stringing work of 765kv Agra-Fatehpur line. | N-1482
NR1DCP01 | 104206 | HVDC R-D POLE-I | 2013-04-21 08:10 | 2013-04-22 20:05 | 1899-12-31 11:55 | 0 | 0 | 0 | OSPT | S/D for replacement of R-ph X-1 Bushing at Dadri end. | N-1636
|  | SUB TOTAL |  |  | 1899-12-31 17:21 | 0 | 0 | 1899-12-31 00:37
NR1DCP02 | 104066 | HVDC R-D POLE-II | 2013-04-06 16:18 | 2013-04-06 19:29 | 0.13264 | 0 | 0 | 0 | OSPT | S/D for V-string restoration at Loc.1658 by Mainpuri. | N-513
NR1DCP02 | 104161 | HVDC R-D POLE-II | 2013-04-17 11:35 | 2013-04-17 13:55 | 0.097222 | 0 | 0 | 0 | OSPT | S/D for inspection and assessment of Valve hall upgradation work by M/s ABB Engineer. | N-1343
|  | SUB TOTAL |  |  | 0.22986 | 0 | 0 | 0
NR1DCP04 | 104174 | HVDC BALIA-BHWD POLE-II | 2013-04-18 17:47 | 2013-04-18 18:05 | 0 | 0.0125 | 0 | 0 | OMSU | Tripped due to disturbance in Aux supply at Balia during fault in UPPCL system.
|  | SUB TOTAL |  |  | 0 | 0.0125 | 0 | 0
NR176502 | 104170 | 765KV AGRA-FATEHPUR | 2013-04-18 15:09 | 2013-04-18 18:46 | 0 | 0 | 0 | 0.15069 | LCSD | S/D for jumpering work of 765 KV Jhatikra line at agra | N-1431
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.15069
NR176501 | 104204 | 765KV LUCKNOW-BALIA | 2013-04-21 04:17 | 2013-04-21 04:23 | 0 | 0 | 0.0041667 | 0 | GOVC | Trip on O/VOL protn at Balia.
NR176501 | 104205 | 765KV LUCKNOW-BALIA | 2013-04-21 04:23 | 2013-04-21 07:10 | 0 | 0 | 0 | 0.11597 | LVRD | Kept open for V/Regulation. Balia-430kv. | N-1619
|  | SUB TOTAL |  |  | 0 | 0 | 0.0041667 | 0.11597
NR140003 | 104247 | 400KV AGRA-AURAIYA-I | 2013-04-27 11:06 | 2013-04-27 14:58 | 0 | 0 | 0 | 0.16111 | OSPD | S/D by NTPC for attending DR problem at Auraiya end. | N-2017
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.16111
NR140005 | 104020 | 400KV AGRA-BASSI-I | 2013-04-03 03:04 | 2013-04-03 06:47 | 0 | 0 | 0 | 0.15486 | LVRD | Hand tripped for voltage regulation. Agra-432 KV | N/176
NR140005 | 104160 | 400KV AGRA-BASSI-I | 2013-04-17 11:03 | 2013-04-17 12:58 | 0 | 0 | 0 | 0.079861 | LCSD | S/D for installation of Polymer Insulator string at loc-99. | N-1333
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.23472
NR140008 | 104015 | 400KV AGRA-BHIWADI-I | 2013-04-02 21:40 | 2013-04-03 06:45 | 0 | 0 | 0 | 0.37847 | LVRD | Hand tripped for voltage regulation. BWD=437kv. | N/156
NR140008 | 104074 | 400KV AGRA-BHIWADI-I | 2013-04-07 15:10 | 2013-04-08 05:57 | 0 | 0 | 0 | 0.61597 | LVRD | Hand tripped for voltage regulation. Bhw-434kv. | N-580
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.99444
NR140009 | 104085 | 400KV AGRA-BHIWADI-II | 2013-04-08 14:02 | 2013-04-08 15:19 | 0.053472 | 0 | 0 | 0 | OSPT | S/D for lopping of Trees by BWD-TL. | N-672
|  | SUB TOTAL |  |  | 0.053472 | 0 | 0 | 0
NR140116 | 104030 | 400KV AGRA-JAIPUR(S)-I | 2013-04-03 09:48 | 2013-04-03 18:08 | 0 | 0 | 0 | 0.34722 | LCSD | S/D for testing of s/station automation system at Jpr-S | N/214
NR140116 | 104038 | 400KV AGRA-JAIPUR(S)-I | 2013-04-04 12:12 | 2013-04-04 15:43 | 0 | 0 | 0 | 0.14653 | LCSD | S/D for testing of s/station automation system at Jpr-S | N-317
NR140116 | 104261 | 400KV AGRA-JAIPUR(S)-I | 2013-04-30 03:48 | 2013-04-30 06:05 | 0 | 0 | 0 | 0.095139 | LVRD | H/Tripped for voltage regulation. Bassi-430kv | N-2191
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.58889
NR140126 | 104135 | 400KV AGRA-JAIPUR(S)-II | 2013-04-14 01:32 | 2013-04-14 06:41 | 0 | 0 | 0 | 0.21458 | LVRD | H/Triped for voltage regulation. Jpr-434kv | N-1109
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.21458
NR140122 | 104006 | 400KV ALLD-FATEHPUR-I | 2013-04-02 08:12 | 2013-04-02 17:16 | 0 | 0 | 0 | 0.37778 | LCSD | S/D for installation of polymer insulator string. | N/96
NR140122 | 104034 | 400KV ALLD-FATEHPUR-I | 2013-04-04 07:43 | 2013-04-05 19:22 | 0 | 0 | 0 | 1899-12-31 11:39 | LCSD | S/D for installation of polymer insulator string. | N-293
NR140122 | 104109 | 400KV ALLD-FATEHPUR-I | 2013-04-11 08:39 | 2013-04-11 17:59 | 0 | 0 | 0 | 0.38889 | LCSD | S/D for installation of polymer insulator string. | N/906
NR140122 | 104218 | 400KV ALLD-FATEHPUR-I | 2013-04-24 08:19 | 2013-04-24 19:50 | 0 | 0 | 0 | 0.47986 | LCSD | S/D for installation of polymer insulator strings. | N-1801
NR140122 | 104227 | 400KV ALLD-FATEHPUR-I | 2013-04-25 07:12 | 2013-04-25 19:38 | 0 | 0 | 0 | 0.51806 | LCSD | S/D for installation of polymer insulator strings. | N-1854
NR140122 | 104236 | 400KV ALLD-FATEHPUR-I | 2013-04-26 07:41 | 2013-04-26 17:33 | 0 | 0 | 0 | 0.41111 | LCSD | S/D for installation of polymer insulator strings. | N-1926
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-02 15:52
NR140123 | 104239 | 400KV ALLD-FATEHPUR-II | 2013-04-27 07:02 | 2013-04-27 19:37 | 0 | 0 | 0 | 0.52431 | LCSD | S/D for installation of polymer insulator strings. | N-1992
NR140123 | 104249 | 400KV ALLD-FATEHPUR-II | 2013-04-28 07:57 | 2013-04-28 18:59 | 0 | 0 | 0 | 0.45972 | LCSD | S/D for installation of polymer insulator strings. | N-2076
NR140123 | 104262 | 400KV ALLD-FATEHPUR-II | 2013-04-30 08:38 | 2013-04-30 20:04 | 0 | 0 | 0 | 0.47639 | LCSD | S/D for installation of polymer insulator strings. | N-2203
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 11:03
NR140015 | 104167 | 400KV ALLD-SARNATH | 2013-04-18 08:51 | 2013-04-18 21:59 | 0 | 0 | 0 | 0.54722 | LCSD | S/D for stringing of 765 KV SSRM-fatehpur line. | N-1405
NR140015 | 104244 | 400KV ALLD-SARNATH | 2013-04-27 09:01 | 2013-04-27 18:50 | 0 | 0 | 0 | 0.40903 | LCSD | S/D for stringing work of 765kv Sasaram-Fatehpur line. | N-2003
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.95625
NR140016 | 104166 | 400KV ALLD-SASARAM | 2013-04-18 08:34 | 2013-04-18 21:44 | 0 | 0 | 0 | 0.54861 | LCSD | S/D for stringing of 765 KV SSRM-fatehpur line. | N-1405
NR140016 | 104243 | 400KV ALLD-SASARAM | 2013-04-27 08:25 | 2013-04-27 18:37 | 0 | 0 | 0 | 0.425 | LCSD | S/D for stringing work of 765kv Sasaram-Fatehpur line. | N-2000
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.97361
NR140018 | 104008 | 400KV BALIA-BIHARSHRF-II | 2013-04-02 10:53 | 2013-04-02 17:33 | 0.27778 | 0 | 0 | 0 | OSPT | S/D by ER-1 for line maint. work | N/109
|  | SUB TOTAL |  |  | 0.27778 | 0 | 0 | 0
NR140019 | 104172 | 400KV BALIA-MAU-I | 2013-04-18 17:42 | 2013-04-18 18:24 | 0 | 0.029167 | 0 | 0 | SBBU | Tripped on Bus bar protn operation at Mau-UP S/S.
NR140019 | 104238 | 400KV BALIA-MAU-I | 2013-04-26 15:37 | 2013-04-26 19:39 | 0 | 0 | 0 | 0.16806 | OSPD | S/D by UPPCL to attend Bus jumper hotspot at Mau. | N-1954
|  | SUB TOTAL |  |  | 0 | 0.029167 | 0 | 0.16806
NR140020 | 104173 | 400KV BALIA-MAU-II | 2013-04-18 17:42 | 2013-04-18 18:29 | 0 | 0.032639 | 0 | 0 | SBBU | Tripped on Bus bar protn operation at Mau-UP S/S.
NR140020 | 104231 | 400KV BALIA-MAU-II | 2013-04-25 10:39 | 2013-04-25 16:40 | 0 | 0 | 0 | 0.25069 | OSPD | S/D by UPPCL to attend Bus jumper hotspot at Mau. | N-1870
|  | SUB TOTAL |  |  | 0 | 0.032639 | 0 | 0.25069
NR140021 | 104014 | 400KV BALIA-PATNA-I | 2013-04-02 21:27 | 2013-04-05 19:54 | 0 | 0 | 0 | 1900-01-01 22:27 | LVRD | Hand tripped for voltage regulation. Balia-430kv. | N/154
NR140021 | 104083 | 400KV BALIA-PATNA-I | 2013-04-08 13:33 | 2013-04-08 13:35 | 0 | 0 | 0.0013889 | 0 | GOVC | Tripped on O/VOL protn at Patna. D/T recd at Balia.
NR140021 | 104084 | 400KV BALIA-PATNA-I | 2013-04-08 13:35 | 2013-04-11 15:11 | 0 | 0 | 0 | 1900-01-02 01:36 | LVRD | Kept open for VOL/Regulation. Balia-429kv. | N-703
NR140021 | 104175 | 400KV BALIA-PATNA-I | 2013-04-18 22:04 | 2013-04-19 10:12 | 0 | 0 | 0 | 0.50556 | LVRD | H/Tripped for voltage regulation. Balia-430KV | N/1474
|  | SUB TOTAL |  |  | 0 | 0 | 0.0013889 | 1900-01-05 12:11
NR140022 | 104048 | 400KV BALIA-PATNA-II | 2013-04-05 13:25 | 2013-04-08 08:14 | 0 | 0 | 0 | 1900-01-01 18:49 | LVRD | Hand tripped for voltage regulation. Balia-430kv. | N-412
NR140022 | 104152 | 400KV BALIA-PATNA-II | 2013-04-16 08:52 | 2013-04-18 09:27 | 0 | 0 | 0 | 1900-01-01 00:35 | LVRD | H/Tripped for voltage regulation. Balia-430KV | N-1229
NR140022 | 104182 | 400KV BALIA-PATNA-II | 2013-04-19 13:25 | 2013-04-20 18:36 | 0 | 0 | 0 | 1899-12-31 05:11 | LVRD | H/Tripped for voltage regulation. Balia-430KV | N-1499
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-05 00:35
NR140136 | 103137 | 400KV BALIA-PATNA-III | 2013-04-01 | 2013-04-02 10:34 | 0 | 0 | 0 | 1899-12-31 10:34 | LVRD | Hand tripped for voltage regulation. Balia-428 KV. Out since 0241hrs of 20/03/13. | N-1462
NR140136 | 104065 | 400KV BALIA-PATNA-III | 2013-04-06 13:11 | 2013-04-08 10:21 | 0 | 0 | 0 | 1899-12-31 21:10 | LVRD | Hand tripped for voltage regulation. Balia-430kv. | N-504
NR140136 | 104198 | 400KV BALIA-PATNA-III | 2013-04-20 21:14 | 2013-04-27 19:08 | 0 | 0 | 0 | 1900-01-05 21:54 | LVRD | H/Tripped for voltage regulation. Balia-430KV | N-1607
NR140136 | 104265 | 400KV BALIA-PATNA-III | 2013-04-30 13:59 | 2013-04-30 16:13 | 0.093056 | 0 | 0 | 0 | LEFT | Line trip on Y-N fault in reclaim time. FLR:Balia-117.4km, Patna-136km.
|  | SUB TOTAL |  |  | 0.093056 | 0 | 0 | 1900-01-09 05:38
NR140137 | 104114 | 400KV BALIA-PATNA-IV | 2013-04-11 16:03 | 2013-04-16 09:53 | 0 | 0 | 0 | 1900-01-03 17:50 | LVRD | Hand tripped for voltage regulation. Balia-430kv. | N/944
NR140137 | 104164 | 400KV BALIA-PATNA-IV | 2013-04-17 18:25 | 2013-04-18 09:58 | 0 | 0 | 0 | 0.64792 | LVRD | H/Tripped for voltage regulation. Balia-430KV | N-1659
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-04 09:23
NR140140 | 104050 | 400KV BALIA-SOHAWAL-I | 2013-04-05 13:32 | 2013-04-05 13:50 | 0 | 0 | 0.0125 | 0 | GOVC | Tripped on Over Voltage protection. DT received at Balia.
NR140140 | 104139 | 400KV BALIA-SOHAWAL-I | 2013-04-14 15:14 | 2013-04-14 19:26 | 0 | 0 | 0 | 0.175 | LVRD | H/Tripped for voltage regulation. Balia-430KV | N-1139
|  | SUB TOTAL |  |  | 0 | 0 | 0.0125 | 0.175
NR140120 | 104007 | 400KV BALIA-SOHAWAL-II | 2013-04-02 10:39 | 2013-04-02 18:06 | 0 | 0 | 0 | 0.31042 | LCSD | S/D for remote commissioning of isolators at Sohawal. | N/107
NR140120 | 104031 | 400KV BALIA-SOHAWAL-II | 2013-04-03 09:57 | 2013-04-03 17:52 | 0 | 0 | 0 | 0.32986 | LCSD | S/D for remote commissioning of isolators at Sohawal. | N/213
NR140120 | 104051 | 400KV BALIA-SOHAWAL-II | 2013-04-05 13:32 | 2013-04-05 13:35 | 0 | 0 | 0.0020833 | 0 | GOVC | Tripped on Over Voltage protection. DT recvd at Balia.
NR140120 | 104053 | 400KV BALIA-SOHAWAL-II | 2013-04-05 13:35 | 2013-04-05 18:55 | 0 | 0 | 0 | 0.22222 | LVRD | Kept open for voltage regulation. Balia-432kv. | N-417
NR140120 | 104168 | 400KV BALIA-SOHAWAL-II | 2013-04-18 09:40 | 2013-04-18 19:52 | 0 | 0 | 0 | 0.425 | LCSD | S/D for remote commissioning of isolators at Sohawal. | N-1405
NR140120 | 104191 | 400KV BALIA-SOHAWAL-II | 2013-04-20 09:40 | 2013-04-20 18:54 | 0 | 0 | 0 | 0.38472 | LCSD | S/D for remote commissioning of isolators at Sohawal. | N-1551
NR140120 | 104215 | 400KV BALIA-SOHAWAL-II | 2013-04-23 14:10 | 2013-04-23 16:14 | 0.086111 | 0 | 0 | 0 | OSFT | S/D to attend isolator jumper Hot spot at Balia end. | N-1766
|  | SUB TOTAL |  |  | 0.086111 | 0 | 0.0020833 | 1899-12-31 16:08
NR140025 | 104016 | 400KV BAREILLY-LKO(UP) | 2013-04-02 22:41 | 2013-04-03 00:03 | 0 | 0.056944 | 0 | 0 | SBBU | Tripped on Bus bar protn at Lko-UP S/S due to blasting of their transfer Bus CT.
|  | SUB TOTAL |  |  | 0 | 0.056944 | 0 | 0
NR140026 | 104032 | 400KV BAREILLY-MBAD-I | 2013-04-03 15:44 | 2013-04-03 15:56 | 0 | 0.0083333 | 0 | 0 | OMSU | Line A/R and tripped on R-N fault due to kite thread, FLR:BLY-28.9 kms
NR140026 | 104157 | 400KV BAREILLY-MBAD-I | 2013-04-16 18:15 | 2013-04-16 18:38 | 0 | 0.015972 | 0 | 0 | OMSU | A/R & Trip on Y-N fault due to Kite Thread, BLY=4.3km.
|  | SUB TOTAL |  |  | 0 | 0.024306 | 0 | 0
NR140115 | 104022 | 400KV BAREILLY-ROSA-I | 2013-04-03 03:05 | 2013-04-03 03:07 | 0 | 0 | 0.0013889 | 0 | GOVC | Tripped on Over Voltage protection at Rosa.
NR140115 | 104025 | 400KV BAREILLY-ROSA-I | 2013-04-03 03:07 | 2013-04-03 05:36 | 0 | 0 | 0 | 0.10347 | LVRD | Kept open for voltage regulation. BLY-435 KV | N/178
NR140115 | 104259 | 400KV BAREILLY-ROSA-I | 2013-04-29 16:14 | 2013-04-29 16:46 | 0 | 0.022222 | 0 | 0 | OMSU | Tripped on R-Y fault due to Kite Thread, FLR:Brly-114.7km Rosa-13.45 km.
|  | SUB TOTAL |  |  | 0 | 0.022222 | 0.0013889 | 0.10347
NR140028 | 104005 | 400KV BASSI-BHIWADI-I | 2013-04-02 04:12 | 2013-04-03 08:42 | 0 | 0 | 0 | 1899-12-31 04:30 | LVRD | Hand tripped for voltage regulation. BWD=438kv. | N-82
NR140028 | 104033 | 400KV BASSI-BHIWADI-I | 2013-04-04 03:38 | 2013-04-04 07:35 | 0 | 0 | 0 | 0.16458 | LVRD | Hand tripped for voltage regulation. BWD=435kv. | N/280
NR140028 | 104123 | 400KV BASSI-BHIWADI-I | 2013-04-13 00:08 | 2013-04-13 10:57 | 0 | 0 | 0 | 0.45069 | LVRD | H/Tripped for voltage regulation. BHI-432 KV | N-1054
NR140028 | 104129 | 400KV BASSI-BHIWADI-I | 2013-04-13 21:13 | 2013-04-15 09:46 | 0 | 0 | 0 | 1899-12-31 12:33 | LVRD | H/Triped for voltage regulation. BWD-433 KV | N-1101
NR140028 | 104226 | 400KV BASSI-BHIWADI-I | 2013-04-25 02:32 | 2013-04-25 12:15 | 0 | 0 | 0 | 0.40486 | LVRD | H/Tripped for voltage regulation. BWD=427kv. | N-1852
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-02 17:32
NR140129 | 104040 | 400KV BASSI-BHIWADI-II | 2013-04-05 00:26 | 2013-04-05 05:40 | 0 | 0 | 0 | 0.21806 | LVRD | Hand tripped for voltage regulation. BWD=435kv. | N-361
NR140129 | 104055 | 400KV BASSI-BHIWADI-II | 2013-04-05 23:01 | 2013-04-06 05:56 | 0 | 0 | 0 | 0.28819 | LVRD | Hand tripped for voltage regulation. BWD=435kv. | N-453
NR140129 | 104078 | 400KV BASSI-BHIWADI-II | 2013-04-07 21:56 | 2013-04-08 06:11 | 0 | 0 | 0 | 0.34375 | LVRD | Hand tripped for voltage regulation. Bhw-426kv. | N-613
NR140129 | 104151 | 400KV BASSI-BHIWADI-II | 2013-04-16 02:47 | 2013-04-16 07:06 | 0 | 0 | 0 | 0.17986 | LVRD | H/Tripped for voltage regulation. BWD-433 KV | N-1224
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 00:43
NR140030 | 104208 | 400KV BASSI-HIRAPURA-I | 2013-04-22 08:26 | 2013-04-22 20:53 | 0 | 0 | 0 | 0.51875 | LCSD | S/D for installation of polymer insulator strings. | N-1683
NR140030 | 104213 | 400KV BASSI-HIRAPURA-I | 2013-04-23 07:56 | 2013-04-23 20:07 | 0 | 0 | 0 | 0.50764 | LCSD | S/D for installation of polymer insulator strings. | N-1751
NR140030 | 104219 | 400KV BASSI-HIRAPURA-I | 2013-04-24 08:52 | 2013-04-24 20:08 | 0 | 0 | 0 | 0.46944 | LCSD | S/D for installation of polymer insulator strings. | N-1803
NR140030 | 104228 | 400KV BASSI-HIRAPURA-I | 2013-04-25 09:18 | 2013-04-25 19:51 | 0 | 0 | 0 | 0.43958 | LCSD | S/D for installation of polymer insulator strings. | N-1866
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 22:27
NR140031 | 104237 | 400KV BASSI-HIRAPURA-II | 2013-04-26 08:37 | 2013-04-26 20:09 | 0 | 0 | 0 | 0.48056 | LCSD | S/D for installation of polymer insulator strings. | N-1930
NR140031 | 104245 | 400KV BASSI-HIRAPURA-II | 2013-04-27 09:08 | 2013-04-27 19:21 | 0 | 0 | 0 | 0.42569 | LCSD | S/D for installation of polymer insulator strings. | N-2004
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.90625
NR140117 | 104037 | 400KV BASSI-JAIPUR(S)-I | 2013-04-04 11:28 | 2013-04-04 12:31 | 0.04375 | 0 | 0 | 0 | SBBT | Tripped due to Bus-Bar protection operated at Jpr (S).
NR140117 | 104103 | 400KV BASSI-JAIPUR(S)-I | 2013-04-10 11:33 | 2013-04-10 19:55 | 0 | 0 | 0 | 0.34861 | LCSD | S/D for bay eqpt erection Work at Jaipur( S). | N-845
NR140117 | 104171 | 400KV BASSI-JAIPUR(S)-I | 2013-04-18 15:45 | 2013-04-18 17:35 | 0 | 0 | 0 | 0.076389 | LCSD | S/D for erection of Bus pipe for CB & Isolator at Bassi. | N-1405
NR140117 | 104258 | 400KV BASSI-JAIPUR(S)-I | 2013-04-29 09:58 | 2013-04-29 19:22 | 0 | 0 | 0 | 0.39167 | LCSD | S/D for construction of Faggi bay at Bassi. | N-2146
NR140117 | 104260 | 400KV BASSI-JAIPUR(S)-I | 2013-04-30 03:46 | 2013-04-30 06:02 | 0 | 0 | 0 | 0.094444 | LVRD | H/Tripped for voltage regulation. Bassi-430kv | N-2191
|  | SUB TOTAL |  |  | 0.04375 | 0 | 0 | 0.91111
NR140127 | 104134 | 400KV BASSI-JAIPUR(S)-II | 2013-04-14 01:25 | 2013-04-14 06:45 | 0 | 0 | 0 | 0.22222 | LVRD | H/Triped for voltage regulation. Jpr-434kv | N-1109
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.22222
NR140106 | 104011 | 400KV BHIWADI-NIMRANA-I | 2013-04-02 17:25 | 2013-04-03 08:46 | 0 | 0 | 0 | 0.63958 | LVRD | Hand tripped for voltage regulation. BWD=437kv. | N/138
NR140106 | 104042 | 400KV BHIWADI-NIMRANA-I | 2013-04-05 00:28 | 2013-04-05 05:38 | 0 | 0 | 0 | 0.21528 | LVRD | Hand tripped for voltage regulation. BWD=435kv. | N-362
NR140106 | 104075 | 400KV BHIWADI-NIMRANA-I | 2013-04-07 16:13 | 2013-04-08 06:18 | 0 | 0 | 0 | 0.58681 | LVRD | Hand tripped for voltage regulation. Bhw-434kv. | N-586
NR140106 | 104093 | 400KV BHIWADI-NIMRANA-I | 2013-04-09 23:35 | 2013-04-10 10:19 | 0 | 0 | 0 | 0.44722 | LVRD | H/Triped for voltage regulation. Bhwd-432 KV | N-800
NR140106 | 104108 | 400KV BHIWADI-NIMRANA-I | 2013-04-11 03:04 | 2013-04-12 07:41 | 0 | 0 | 0 | 1899-12-31 04:37 | LVRD | H/Triped for voltage regulation. BHI-432 KV | N/892
NR140106 | 104124 | 400KV BHIWADI-NIMRANA-I | 2013-04-13 00:09 | 2013-04-13 10:59 | 0 | 0 | 0 | 0.45139 | LVRD | H/Tripped for voltage regulation. BHI-432 KV | N-1053
NR140106 | 104130 | 400KV BHIWADI-NIMRANA-I | 2013-04-13 21:15 | 2013-04-16 09:27 | 0 | 0 | 0 | 1900-01-01 12:12 | LVRD | H/Triped for voltage regulation. BWD-433 KV | N-1100
NR140106 | 104183 | 400KV BHIWADI-NIMRANA-I | 2013-04-19 16:44 | 2013-04-20 08:42 | 0 | 0 | 0 | 0.66528 | LVRD | H/Tripped for voltage regulation. BHI-432 KV | N-1508
NR140106 | 104202 | 400KV BHIWADI-NIMRANA-I | 2013-04-21 03:28 | 2013-04-22 10:07 | 0 | 0 | 0 | 1899-12-31 06:39 | LVRD | H/Tripped for voltage regulation. Nim-434kv. | N-1615
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-06 23:36
NR140107 | 104056 | 400KV BHIWADI-NIMRANA-II | 2013-04-05 23:02 | 2013-04-06 05:59 | 0 | 0 | 0 | 0.28958 | LVRD | Hand tripped for voltage regulation. BWD=435kv. | N-454
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.28958
NR140037 | 104001 | 400KV BLBGRH-MAINPURI-I | 2013-04-01 02:40 | 2013-04-01 06:25 | 0 | 0 | 0 | 0.15625 | LVRD | Hand Tripped for VOL/Regulation. Mnp=434kv. | N-11
NR140037 | 104043 | 400KV BLBGRH-MAINPURI-I | 2013-04-05 03:01 | 2013-04-05 05:39 | 0 | 0 | 0 | 0.10972 | LVRD | Hand tripped for voltage regulation. Mnpr-433kv. | N-370
NR140037 | 104058 | 400KV BLBGRH-MAINPURI-I | 2013-04-06 01:27 | 2013-04-06 06:14 | 0 | 0 | 0 | 0.19931 | LVRD | Hand tripped for voltage regulation. Mnpr-433kv. | N-463
NR140037 | 104079 | 400KV BLBGRH-MAINPURI-I | 2013-04-08 01:33 | 2013-04-08 05:45 | 0 | 0 | 0 | 0.175 | LVRD | Hand tripped for voltage regulation. Blb-426kv. | N-616
NR140037 | 104126 | 400KV BLBGRH-MAINPURI-I | 2013-04-13 01:29 | 2013-04-13 11:28 | 0 | 0 | 0 | 0.41597 | LVRD | H/Tripped for voltage regulation. BLB-432 KV | N-1058
NR140037 | 104132 | 400KV BLBGRH-MAINPURI-I | 2013-04-13 21:25 | 2013-04-14 09:28 | 0 | 0 | 0 | 0.50208 | LVRD | H/Triped for voltage regulation. BLB-429 KV | N-1103
NR140037 | 104150 | 400KV BLBGRH-MAINPURI-I | 2013-04-16 02:45 | 2013-04-16 07:09 | 0 | 0 | 0 | 0.18333 | LVRD | H/Tripped for voltage regulation. Mnpr-432KV | N-1223
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 17:48
NR140038 | 104004 | 400KV BLBGRH-MAINPURI-II | 2013-04-02 02:31 | 2013-04-02 06:50 | 0 | 0 | 0 | 0.17986 | LVRD | Hand tripped for voltage regulation. BLB=432kv. | N-76
NR140038 | 104138 | 400KV BLBGRH-MAINPURI-II | 2013-04-14 13:54 | 2013-04-15 11:47 | 0 | 0 | 0 | 0.91181 | LVRD | H/Tripped for voltage regulation. BLB-436KV | N-1134
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 02:12
NR140043 | 104232 | 400KV DAD-MURADNGR | 2013-04-25 13:51 | 2013-04-25 17:51 | 0.16667 | 0 | 0 | 0 | OSPT | S/D for Jumper replacement at loc-35. | N-1888
NR140043 | 104234 | 400KV DAD-MURADNGR | 2013-04-25 17:51 | 2013-04-25 19:26 | 0 | 0 | 0 | 0.065972 | OSPD | S/D by UPPCL to attend E/Switch problem at Mnagar.
|  | SUB TOTAL |  |  | 0.16667 | 0 | 0 | 0.065972
NR140044 | 104165 | 400KV DAD-PANIPAT-I | 2013-04-18 05:11 | 2013-04-18 05:37 | 0 | 0.018056 | 0 | 0 | OMSU | A/R at DDR but tripped from PPT-BBMB end due to relay problem on Y-N, Z-I fault. PPT=22km. DDR=78.4km.
|  | SUB TOTAL |  |  | 0 | 0.018056 | 0 | 0
NR140045 | 104021 | 400KV DAD-PANIPAT-II | 2013-04-03 03:04 | 2013-04-03 03:07 | 0 | 0 | 0.0020833 | 0 | GOVC | Tripped on Over Voltage protection at Panipat.
NR140045 | 104024 | 400KV DAD-PANIPAT-II | 2013-04-03 03:07 | 2013-04-03 06:14 | 0 | 0 | 0 | 0.12986 | LVRD | Kept open for voltage regulation.Dadri-434 Kv | N/177
|  | SUB TOTAL |  |  | 0 | 0 | 0.0020833 | 0.12986
NR140124 | 104100 | 400KV FATEHPUR-MAINPURI-I | 2013-04-10 07:58 | 2013-04-10 20:22 | 0 | 0 | 0 | 0.51667 | LCSD | S/D for stringing of 765 KV Agra-Fatehpur line | N-819
NR140124 | 104143 | 400KV FATEHPUR-MAINPURI-I | 2013-04-14 16:39 | 2013-04-14 19:26 | 0 | 0 | 0 | 0.11597 | LVRD | H/Tripped for voltage regulation. Mnpr-436KV | N-1146
NR140124 | 104153 | 400KV FATEHPUR-MAINPURI-I | 2013-04-16 13:02 | 2013-04-16 16:24 | 0 | 0 | 0 | 0.14028 | LVRD | H/Tripped for voltage regulation. MNP=438kv. | N-1263
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.77292
NR140125 | 104101 | 400KV FATEHPUR-MAINPURI-II | 2013-04-10 07:58 | 2013-04-10 19:51 | 0 | 0 | 0 | 0.49514 | LCSD | S/D for stringing of 765 KV Agra-Fatehpur line | N-819
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.49514
NR140046 | 104046 | 400KV GORAKH-GORAKH-I | 2013-04-05 13:01 | 2013-04-05 13:05 | 0 | 0 | 0.0027778 | 0 | GOVC | Tripped on Over Voltage protn at UP. DT received at PG.
NR140046 | 104047 | 400KV GORAKH-GORAKH-I | 2013-04-05 13:05 | 2013-04-05 15:55 | 0 | 0 | 0 | 0.11806 | LVRD | Kept open for voltage regulation. Gkp-435kv. | N-411
|  | SUB TOTAL |  |  | 0 | 0 | 0.0027778 | 0.11806
NR140128 | 103056 | 400KV GURGAON-MANESAR-I | 2013-04-01 | 2013-05-01 | 0 | 0 | 0 | 1900-01-29 | LCSD | S/D for Gurgaon GIS Bus-I extention work. Out since 1242hrs of 06/03/13. | N-520
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-29
NR140129 | 104140 | 400KV GURGAON-MANESAR-II | 2013-04-14 15:24 | 2013-04-14 15:44 | 0.013889 | 0 | 0 | 0 | LEFT | Tripped on R-N fault in reclaim time during wind storm. FLR:Ggn-16km.
|  | SUB TOTAL |  |  | 0.013889 | 0 | 0 | 0
NR140132 | 104255 | 400KV JHATIKALA-BAMNOLI-I | 2013-04-29 01:43 | 2013-04-29 02:14 | 0 | 0.021528 | 0 | 0 | OMSU | Tripped on R-N fault in DTL portion. FLR:Jhtk-13.4km
|  | SUB TOTAL |  |  | 0 | 0.021528 | 0 | 0
NR140133 | 104256 | 400KV JHATIKALA-BAMNOLI-II | 2013-04-29 01:43 | 2013-04-29 02:14 | 0 | 0.021528 | 0 | 0 | OMSU | Tripped on R-N fault in DTL portion. FLR:Jhtk-14.5km
|  | SUB TOTAL |  |  | 0 | 0.021528 | 0 | 0
NR140049 | 104185 | 400KV KANKROLI-JODHPUR | 2013-04-19 21:29 | 2013-04-19 21:33 | 0 | 0 | 0.0027778 | 0 | GOVC | Trip on O/VOL protn at Jodhpur>440kv. D/T recd at Kank.
NR140049 | 104186 | 400KV KANKROLI-JODHPUR | 2013-04-19 21:33 | 2013-04-19 22:11 | 0 | 0 | 0 | 0.026389 | LVRD | Kept open for voltage regulation. Kank-429kv. | N-1525
NR140049 | 104188 | 400KV KANKROLI-JODHPUR | 2013-04-20 02:11 | 2013-04-20 05:47 | 0 | 0 | 0 | 0.15 | LVRD | H/Tripped for voltage regulation. Kank-430kv | N-1533
NR140049 | 104207 | 400KV KANKROLI-JODHPUR | 2013-04-22 03:32 | 2013-04-22 06:11 | 0 | 0 | 0 | 0.11042 | LVRD | H/Tripped for voltage regulation. Kank-430kv | N-1667
NR140049 | 104211 | 400KV KANKROLI-JODHPUR | 2013-04-23 02:04 | 2013-04-23 05:54 | 0 | 0 | 0 | 0.15972 | LVRD | H/Tripped for voltage regulation. Kank-427kv | N-1741
|  | SUB TOTAL |  |  | 0 | 0 | 0.0027778 | 0.44653
NR140052 | 104029 | 400KV KNP-AGRA | 2013-04-03 07:05 | 2013-04-03 20:30 | 0 | 0 | 0 | 0.55903 | LCSD | S/D for stringing of 765KV Agra-Mrt and Agra-Fthpr lines. | N/194
NR140052 | 104036 | 400KV KNP-AGRA | 2013-04-04 10:45 | 2013-04-04 17:48 | 0 | 0 | 0 | 0.29375 | OSPD | S/D by UPPCL for stringing work of their new line. | N-302
NR140052 | 104082 | 400KV KNP-AGRA | 2013-04-08 11:25 | 2013-04-08 11:45 | 0.013889 | 0 | 0 | 0 | OSFT | Forced S/D due to sparking in R-ph Bus Isolator at KNP.
|  | SUB TOTAL |  |  | 0.013889 | 0 | 0 | 0.85278
NR140055 | 104002 | 400KV KNP-BLBGARH-I | 2013-04-01 02:47 | 2013-04-01 06:28 | 0 | 0 | 0 | 0.15347 | LVRD | Hand Tripped for VOL/Regulation. Blb=430kv. | N-12
NR140055 | 104003 | 400KV KNP-BLBGARH-I | 2013-04-02 02:29 | 2013-04-02 07:08 | 0 | 0 | 0 | 0.19375 | LVRD | Hand tripped for voltage regulation. BLB=432kv. | N-77
NR140055 | 104080 | 400KV KNP-BLBGARH-I | 2013-04-08 08:07 | 2013-04-08 19:00 | 0 | 0 | 0 | 0.45347 | OSPD | S/D by UPPCL for stringing work of their line. | N-636
NR140055 | 104142 | 400KV KNP-BLBGARH-I | 2013-04-14 16:29 | 2013-04-15 09:30 | 0 | 0 | 0 | 0.70903 | LVRD | H/Tripped for voltage regulation. Blb-430KV | N-1144
NR140055 | 104154 | 400KV KNP-BLBGARH-I | 2013-04-16 14:09 | 2013-04-16 14:31 | 0.015278 | 0 | 0 | 0 | LEFT | A/R and Tripped on B-N fault. BLB=62.45km.
NR140055 | 104155 | 400KV KNP-BLBGARH-I | 2013-04-16 16:00 | 2013-04-16 16:52 | 0.036111 | 0 | 0 | 0 | LEFT | A/R and trip on B-N fault. BLB=62.99km. KNP=300.6km.
NR140055 | 104158 | 400KV KNP-BLBGARH-I | 2013-04-16 19:47 | 2013-04-16 20:24 | 0.025694 | 0 | 0 | 0 | OSPT | S/D for removing of Tree encroachment at loc. 842-843. | N-1310
NR140055 | 104197 | 400KV KNP-BLBGARH-I | 2013-04-20 16:08 | 2013-04-20 18:21 | 0 | 0 | 0 | 0.092361 | LCSD | S/D for retrofitment of M-I protection relay at BLB. | N-1580
|  | SUB TOTAL |  |  | 0.077083 | 0 | 0 | 1899-12-31 14:27
NR140056 | 104119 | 400KV KNP-BLBGARH-II | 2013-04-12 07:09 | 2013-04-12 19:10 | 0 | 0 | 0 | 0.50069 | LCSD | S/D for stringing work of 765kv Agra-Meerut line. | N-991
NR140056 | 104240 | 400KV KNP-BLBGARH-II | 2013-04-27 08:06 | 2013-04-27 20:11 | 0 | 0 | 0 | 0.50347 | OSPD | S/D by UPPCL for Xing of 400kv MNP-Orai line. | N-1994
NR140056 | 104250 | 400KV KNP-BLBGARH-II | 2013-04-28 08:04 | 2013-04-28 20:12 | 0 | 0 | 0 | 0.50556 | OSPD | S/D by UPPCL for Xing of 400kv MNP-Orai line. | N-2071
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 12:14
NR140057 | 104120 | 400KV KNP-BLBGARH-III | 2013-04-12 07:10 | 2013-04-12 19:10 | 0 | 0 | 0 | 0.5 | LCSD | S/D for stringing work of 765kv Agra-Meerut line. | N-991
NR140057 | 104148 | 400KV KNP-BLBGARH-III | 2013-04-15 14:27 | 2013-04-15 19:01 | 0.19028 | 0 | 0 | 0 | OSPT | S/D for Y-ph Bushing replacement of S/reactor at Blb. | N-1195
NR140057 | 104241 | 400KV KNP-BLBGARH-III | 2013-04-27 08:06 | 2013-04-27 20:07 | 0 | 0 | 0 | 0.50069 | OSPD | S/D by UPPCL for Xing of 400kv MNP-Orai line. | N-1994
NR140057 | 104251 | 400KV KNP-BLBGARH-III | 2013-04-28 08:04 | 2013-04-28 20:13 | 0 | 0 | 0 | 0.50625 | OSPD | S/D by UPPCL for Xing of 400kv MNP-Orai line. | N-2071
|  | SUB TOTAL |  |  | 0.19028 | 0 | 0 | 1899-12-31 12:10
NR140105 | 104068 | 400KV KNP-FATEHPUR-II | 2013-04-07 07:40 | 2013-04-07 18:27 | 0 | 0 | 0 | 0.44931 | LCSD | S/D for stringing work of 765kv Agra-Fthpr line. | N-559
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.44931
NR140060 | 103196 | 400KV KOTA-MERTA-I | 2013-04-01 | 2013-04-01 12:36 | 0 | 0 | 0 | 0.525 | LVRD | Kept open for voltage regulation. Kota-425KV. Out since 1805hrs of 31/03/13. | N-2325
NR140060 | 104012 | 400KV KOTA-MERTA-I | 2013-04-02 20:01 | 2013-04-02 20:06 | 0 | 0 | 0.0034722 | 0 | GOVC | Trip on O/V protn at Merta>432kv. D/T recd at Kota.
NR140060 | 104013 | 400KV KOTA-MERTA-I | 2013-04-02 20:06 | 2013-04-03 15:45 | 0 | 0 | 0 | 0.81875 | LVRD | Kept open for voltage regulation. Kota-425KV | N/149
NR140060 | 104059 | 400KV KOTA-MERTA-I | 2013-04-06 04:02 | 2013-04-06 04:05 | 0 | 0 | 0.0020833 | 0 | GOVC | Tripped on Over Voltage protection. DT received at Kota.
NR140060 | 104060 | 400KV KOTA-MERTA-I | 2013-04-06 04:05 | 2013-04-06 06:30 | 0 | 0 | 0 | 0.10069 | LVRD | Kept open for voltage regulation. | N-465
NR140060 | 104117 | 400KV KOTA-MERTA-I | 2013-04-12 04:00 | 2013-04-12 04:02 | 0 | 0 | 0.0013889 | 0 | GOVC | Tripped on Over voltage protn at Merta. D/T recvd at Kota
NR140060 | 104118 | 400KV KOTA-MERTA-I | 2013-04-12 04:02 | 2013-04-12 07:43 | 0 | 0 | 0 | 0.15347 | LVRD | Kept open for VOL/Regulation. Kota-426kv. | N/982
NR140060 | 104127 | 400KV KOTA-MERTA-I | 2013-04-13 03:08 | 2013-04-13 06:25 | 0 | 0 | 0 | 0.13681 | LVRD | H/Tripped for voltage regulation.Kota=427kv. | N-1060
NR140060 | 104136 | 400KV KOTA-MERTA-I | 2013-04-14 04:04 | 2013-04-14 06:27 | 0 | 0 | 0 | 0.099306 | LVRD | H/Triped for voltage regulation. Kota-430kv. | N-1113
NR140060 | 104146 | 400KV KOTA-MERTA-I | 2013-04-15 04:03 | 2013-04-15 04:07 | 0 | 0 | 0.0027778 | 0 | GOVC | Tripped on O/V protn at Merta>434kv. D/T recd at Kota.
NR140060 | 104147 | 400KV KOTA-MERTA-I | 2013-04-15 04:07 | 2013-04-15 09:29 | 0 | 0 | 0 | 0.22361 | LVRD | Kept open for voltage regulation. Kota-428kv. | N-1168
NR140060 | 104156 | 400KV KOTA-MERTA-I | 2013-04-16 18:09 | 2013-04-17 09:43 | 0 | 0 | 0 | 0.64861 | LVRD | H/Tripped for voltage regulation. Kota=430kv. | N-1295
NR140060 | 104189 | 400KV KOTA-MERTA-I | 2013-04-20 03:25 | 2013-04-20 10:32 | 0 | 0 | 0 | 0.29653 | LVRD | H/Tripped for voltage regulation. Kota=430kv. | N-1535
NR140060 | 104195 | 400KV KOTA-MERTA-I | 2013-04-20 17:04 | 2013-04-20 17:09 | 0 | 0 | 0.0034722 | 0 | GOVC | Tripped on O/V protn at Merta>434kv. D/T recd at Kota.
NR140060 | 104196 | 400KV KOTA-MERTA-I | 2013-04-20 17:09 | 2013-04-22 12:16 | 0 | 0 | 0 | 1899-12-31 19:07 | LVRD | Kept open for voltage regulation. Kota-428kv. | N-1583
NR140060 | 104212 | 400KV KOTA-MERTA-I | 2013-04-23 03:16 | 2013-04-24 11:01 | 0 | 0 | 0 | 1899-12-31 07:45 | LVRD | H/Tripped for voltage regulation. Kota-424kv. | N-1743
NR140060 | 104221 | 400KV KOTA-MERTA-I | 2013-04-24 11:01 | 2013-04-24 17:35 | 0 | 0 | 0 | 0.27361 | OSPD | S/D by RRVPNL for maintenance work at Merta S/yard. | N-1814
NR140060 | 104235 | 400KV KOTA-MERTA-I | 2013-04-26 04:21 | 2013-04-26 09:39 | 0 | 0 | 0 | 0.22083 | LVRD | H/Tripped for voltage regulation. Kota-424kv. | N-1921
NR140060 | 104248 | 400KV KOTA-MERTA-I | 2013-04-28 02:11 | 2013-04-28 07:00 | 0 | 0 | 0 | 0.20069 | LVRD | H/Tripped for voltage regulation. Kota-424kv. | N-2064
NR140060 | 104257 | 400KV KOTA-MERTA-I | 2013-04-29 03:27 | 2013-04-29 06:31 | 0 | 0 | 0 | 0.12778 | LVRD | H/Tripped for voltage regulation. Kota-430 KV. | N-2124
|  | SUB TOTAL |  |  | 0 | 0 | 0.013194 | 1900-01-05 22:41
NR140063 | 104115 | 400KV KOTESHWR-KHEP-I | 2013-04-11 16:37 | 2013-04-11 16:57 | 0 | 0 | 0 | 0.013889 | OSPD | S/D by KHEP for charging of their Bus-Coupler. | N/945
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.013889
NR140070 | 104076 | 400KV LUCKNOW-GORAKH-III | 2013-04-07 18:08 | 2013-04-08 14:41 | 0 | 0 | 0 | 0.85625 | LVRD | Hand tripped for voltage regulation. Gkp-430kv. | N-594
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.85625
NR140071 | 103174 | 400KV LUCKNOW-GORAKH-IV | 2013-04-01 | 2013-04-06 10:47 | 0 | 0 | 0 | 1900-01-04 10:47 | LVRD | H/Triped for VOL/Regulation.LKO=433kv. Out since 1718hrs of 27/03/13. | N-1976
NR140071 | 104133 | 400KV LUCKNOW-GORAKH-IV | 2013-04-13 21:52 | 2013-04-16 09:09 | 0 | 0 | 0 | 1900-01-01 11:17 | LVRD | H/Triped for voltage regulation. GKP-429 KV | N-1104
NR140071 | 104203 | 400KV LUCKNOW-GORAKH-IV | 2013-04-21 04:03 | 2013-04-30 12:58 | 0 | 0 | 0 | 1900-01-08 08:55 | LVRD | H/Tripped for voltage regulation. Gkp-432kv. | N-1617
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-16 06:59
NR140072 | 104017 | 400KV LUCKNOW-LKO(UP) | 2013-04-02 22:41 | 2013-04-02 23:59 | 0 | 0.054167 | 0 | 0 | SBBU | Tripped on Bus bar protn at Lko-UP S/S due to blasting of their transfer Bus CT.
|  | SUB TOTAL |  |  | 0 | 0.054167 | 0 | 0
NR140114 | 104023 | 400KV LUCKNOW-ROSA-I | 2013-04-03 03:05 | 2013-04-03 03:07 | 0 | 0 | 0.0013889 | 0 | GOVC | Tripped on Over Voltage protection at Rosa.
NR140114 | 104026 | 400KV LUCKNOW-ROSA-I | 2013-04-03 03:07 | 2013-04-03 05:39 | 0 | 0 | 0 | 0.10556 | LVRD | Kept open for voltage regulation. Luck-432 KV | N/178
NR140114 | 104072 | 400KV LUCKNOW-ROSA-I | 2013-04-07 12:58 | 2013-04-07 13:05 | 0 | 0.0048611 | 0 | 0 | OMSU | Tripped on Y-N fault due to tree encroachment at Rosa.
NR140114 | 104073 | 400KV LUCKNOW-ROSA-I | 2013-04-07 13:05 | 2013-04-07 16:14 | 0 | 0 | 0 | 0.13125 | OSFD | Charged after tree lopping by Rosa-P near gantry tower.
|  | SUB TOTAL |  |  | 0 | 0.0048611 | 0.0013889 | 0.23681
NR140141 | 104035 | 400KV LUCKNOW-SOHAWAL-I | 2013-04-04 09:48 | 2013-04-04 18:04 | 0 | 0 | 0 | 0.34444 | LCSD | S/D for remote commissioning of isolators at Sohawal. | N-305
NR140141 | 104044 | 400KV LUCKNOW-SOHAWAL-I | 2013-04-05 09:08 | 2013-04-05 13:50 | 0 | 0 | 0 | 0.19583 | LCSD | S/D for remote commissioning of isolators at Sohawal. | N-396
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.54028
NR140121 | 104049 | 400KV LUCKNOW-SOHAWAL-II | 2013-04-05 13:32 | 2013-04-05 13:35 | 0 | 0 | 0.0020833 | 0 | GOVC | Tripped on Over Voltage protection. DT received at LKO.
NR140121 | 104052 | 400KV LUCKNOW-SOHAWAL-II | 2013-04-05 13:35 | 2013-04-05 19:00 | 0 | 0 | 0 | 0.22569 | LVRD | Kept open for voltage regulation. Balia-432kv. | N-417
NR140121 | 104062 | 400KV LUCKNOW-SOHAWAL-II | 2013-04-06 08:42 | 2013-04-06 17:41 | 0 | 0 | 0 | 0.37431 | LCSD | S/D for remote commissioning of isolators at Sohawal. | N-489
|  | SUB TOTAL |  |  | 0 | 0 | 0.0020833 | 0.6
NR140076 | 104181 | 400KV MBAD-MURADNGR | 2013-04-19 13:02 | 2013-04-19 13:37 | 0 | 0.024306 | 0 | 0 | OMSU | Tripped on B/Bar protn at Mngr-UP due to system fault.
NR140076 | 104209 | 400KV MBAD-MURADNGR | 2013-04-22 10:20 | 2013-04-22 18:39 | 0 | 0 | 0 | 0.34653 | OSPD | S/D by UPPCL for LA replacement at Moradabad. | N-1687
|  | SUB TOTAL |  |  | 0 | 0.024306 | 0 | 0.34653
NR140142 | 104106 | 400KV MEERUT-BAREILLY-I | 2013-04-10 17:26 | 2013-04-10 17:44 | 0 | 0.0125 | 0 | 0 | OMSU | A/R and trip on B-N fault in PLINK portion, FLR:Bly-129km
|  | SUB TOTAL |  |  | 0 | 0.0125 | 0 | 0
NR140130 | 104266 | 400KV MEERUT-BAREILLY-II | 2013-04-30 16:24 | 2013-04-30 16:31 | 0 | 0.0048611 | 0 | 0 | OMSU | Line tripped on R-B fault in PLINK portion. Bly-140.2km, Mrt-143.5km.
|  | SUB TOTAL |  |  | 0 | 0.0048611 | 0 | 0
NR140103 | 104102 | 400KV MERTA-BEAWAR | 2013-04-10 11:10 | 2013-04-10 16:54 | 0 | 0 | 0 | 0.23889 | OSPD | S/D by Merta-RRVPNL to attend isolator hot spot | N-840
NR140103 | 104192 | 400KV MERTA-BEAWAR | 2013-04-20 11:00 | 2013-04-20 20:02 | 0 | 0 | 0 | 0.37639 | OSPD | S/D by RRVPNL for bay eqpt maint work at Merta. | N-1557
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.61528
NR140139 | 104105 | 400KV NAVADA-GR.NOIDA | 2013-04-10 16:05 | 2013-04-10 18:52 | 0 | 0 | 0 | 0.11597 | OSPD | S/D by UPPCL for Attending hot spot at Gr. Noida | N/855
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.11597
NR140108 | 104010 | 400KV NIMRANA-SIKAR-I | 2013-04-02 17:22 | 2013-04-03 08:38 | 0 | 0 | 0 | 0.63611 | LVRD | Hand tripped for voltage regulation. Sikar=438kv. | N/138
NR140108 | 104041 | 400KV NIMRANA-SIKAR-I | 2013-04-05 00:27 | 2013-04-05 06:11 | 0 | 0 | 0 | 0.23889 | LVRD | Hand tripped for voltage regulation. Sikar=438kv. | N-362
NR140108 | 104077 | 400KV NIMRANA-SIKAR-I | 2013-04-07 21:51 | 2013-04-08 06:21 | 0 | 0 | 0 | 0.35417 | LVRD | Hand tripped for voltage regulation. Nimrana-431kv. | N-610
NR140108 | 104094 | 400KV NIMRANA-SIKAR-I | 2013-04-09 23:36 | 2013-04-10 10:22 | 0 | 0 | 0 | 0.44861 | LVRD | H/Triped for voltage regulation. Nimr-433kv | N-800
NR140108 | 104125 | 400KV NIMRANA-SIKAR-I | 2013-04-13 00:12 | 2013-04-13 10:52 | 0 | 0 | 0 | 0.44444 | LVRD | H/Tripped for voltage regulation. BHI-432 KV | N-1053
NR140108 | 104131 | 400KV NIMRANA-SIKAR-I | 2013-04-13 21:17 | 2013-04-16 09:08 | 0 | 0 | 0 | 1900-01-01 11:51 | LVRD | H/Triped for voltage regulation. Nimr-434 KV | N-1100
NR140108 | 104184 | 400KV NIMRANA-SIKAR-I | 2013-04-19 16:45 | 2013-04-20 08:37 | 0 | 0 | 0 | 0.66111 | LVRD | H/Tripped for voltage regulation. Sikar-432kv | N-1508
NR140108 | 104201 | 400KV NIMRANA-SIKAR-I | 2013-04-21 03:27 | 2013-04-22 10:34 | 0 | 0 | 0 | 1899-12-31 07:07 | LVRD | H/Tripped for voltage regulation. Nim-434kv. | N-1615
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-05 13:46
NR140109 | 104057 | 400KV NIMRANA-SIKAR-II | 2013-04-05 23:03 | 2013-04-06 05:57 | 0 | 0 | 0 | 0.2875 | LVRD | Hand tripped for voltage regulation. Sikar=438kv. | N-454
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.2875
NR140084 | 104220 | 400KV RIHAND-ALLD-I | 2013-04-24 09:49 | 2013-04-24 18:54 | 0 | 0 | 0 | 0.37847 | OSPD | S/D by Rh/NTPC for protection testing work. | N-1809
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.37847
NR140085 | 104163 | 400KV RIHAND-ALLD-II | 2013-04-17 14:13 | 2013-04-17 19:10 | 0.20625 | 0 | 0 | 0 | OSPT | S/D for Restoration of open sub-Jumper at loc-205. | N-1356
|  | SUB TOTAL |  |  | 0.20625 | 0 | 0 | 0
NR140086 | 104045 | 400KV ROORKI-MUZFRNGR | 2013-04-05 09:52 | 2013-04-05 10:48 | 0 | 0.038889 | 0 | 0 | OMSU | Tripped on R-N fault in UPPCL portion. FLR:Roorki-58km.
NR140086 | 104064 | 400KV ROORKI-MUZFRNGR | 2013-04-06 11:15 | 2013-04-06 19:49 | 0 | 0 | 0 | 0.35694 | OSPD | S/D by UPPCL for maintenance work of their line. | N-500
|  | SUB TOTAL |  |  | 0 | 0.038889 | 0 | 0.35694
NR140088 | 404131 | 400KV SASARAM-BIHARSHRF-I | 2013-04-13 09:35 | 2013-04-13 23:01 | 0 | 0 | 0 | 0.55972 | LCSD | S/D FOR RELAY RETROFITTING WORK AT BSF S/S
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.55972
NR140089 | 404154 | 400KV SASARAM-BIHARSHRF-II | 2013-04-14 09:20 | 2013-04-14 19:53 | 0 | 0 | 0 | 0.43958 | LCSD | S/D FOR RELAY RETROFITTING WORK AT BSF S/S
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.43958
NR140111 | 104116 | 400KV SING-FATEHPUR | 2013-04-11 18:16 | 2013-04-11 22:45 | 0 | 0 | 0 | 0.18681 | OSPD | S/D by NTPC for relay rectofitment work at Sing. | N/956
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.18681
NR140095 | 104018 | 400KV SING-LKO(UP) | 2013-04-02 22:41 | 2013-04-03 00:21 | 0 | 0.069444 | 0 | 0 | SBBU | Tripped on Bus bar protn at Lko-UP S/S due to blasting of their transfer Bus CT.
|  | SUB TOTAL |  |  | 0 | 0.069444 | 0 | 0
NR140096 | 104141 | 400KV SING-RIHAND-I | 2013-04-14 15:41 | 2013-04-14 16:48 | 0 | 0.046528 | 0 | 0 | OMSU | A/R at Singrauli but tripped from Rh-NTPC with Unit#V due to relay malfunction on B-N fault. FLR:Rh-7.5km.
|  | SUB TOTAL |  |  | 0 | 0.046528 | 0 | 0
N-W40001 | 104086 | 400KV SING-VINDH-I | 2013-04-09 12:31 | 2013-04-09 17:25 | 0 | 0 | 0 | 0.20417 | LCSD | S/D for M-I relay Retro-fitment work at Vindhyachal. | N-755
N-W40001 | 104223 | 400KV SING-VINDH-I | 2013-04-24 11:24 | 2013-04-24 14:32 | 0 | 0 | 0 | 0.13056 | LCSD | S/D for installation of polymer insulator strings on Gantry tower. | N-1815
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.33472
N-W40002 | 104054 | 400KV SING-VINDH-II | 2013-04-05 15:53 | 2013-04-05 19:47 | 0 | 0 | 0 | 0.1625 | LCSD | S/D for M-II relay Retro-fitment work at Vindhyachal. | N-422
N-W40002 | 104224 | 400KV SING-VINDH-II | 2013-04-24 11:24 | 2013-04-24 14:29 | 0 | 0 | 0 | 0.12847 | LCSD | S/D for installation of polymer insulator strings on Gantry tower. | N-1815
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.29097
BILUP2202 | 104233 | 220KV ALLD-REWA RD-I | 2013-04-25 14:55 | 2013-04-25 15:43 | 0 | 0.033333 | 0 | 0 | OMSU | Trip only from UPPCL end due to system fault at RewaRd.
BILUP2202 | 104252 | 220KV ALLD-REWA RD-I | 2013-04-28 12:29 | 2013-04-28 13:31 | 0 | 0.043056 | 0 | 0 | SBBU | Bus Bar protn oprtd at RwRd due to CT of 160MVA T/F failed. Both Bus became dead.
|  | SUB TOTAL |  |  | 0 | 0.076389 | 0 | 0
BILUP2203 | 104253 | 220KV ALLD-REWA RD-II | 2013-04-28 12:29 | 2013-04-28 13:44 | 0 | 0.052083 | 0 | 0 | SBBU | Bus Bar protn oprtd at RwRd due to CT of 160MVA T/F failed. Both Bus became dead.
|  | SUB TOTAL |  |  | 0 | 0.052083 | 0 | 0
NR122003 | 104199 | 220KV ANTA-DAUSA | 2013-04-21 02:51 | 2013-04-21 03:00 | 0 | 0.00625 | 0 | 0 | OMSU | Trip on D/T recd at Anta due to CT blast & Fire at Dausa-RRVPNL end
NR122003 | 104200 | 220KV ANTA-DAUSA | 2013-04-21 03:00 | 2013-04-21 06:54 | 0 | 0 | 0 | 0.1625 | OSFD | Forced S/d by RRVPNL due to Fire in their s/yard.
NR122003 | 104229 | 220KV ANTA-DAUSA | 2013-04-25 10:13 | 2013-04-25 21:17 | 0 | 0 | 0 | 0.46111 | OSPD | S/D by RRVPNL for maintenance work at Dausa S/yard. | N-1864
|  | SUB TOTAL |  |  | 0 | 0.00625 | 0 | 0.62361
NR122004 | 104122 | 220KV ANTA-RAPPC | 2013-04-12 15:39 | 2013-04-12 19:55 | 0 | 0 | 0 | 0.17778 | LCSD | S/D for Relay reprofitment work at Anta. | N-1027
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.17778
NR122005 | 104230 | 220KV ANTA-S.MDHPR | 2013-04-25 10:54 | 2013-04-25 21:44 | 0 | 0 | 0 | 0.45139 | OSPD | S/D by RRVPNL for maintenance work at Smdhpr S/yard. | N-1863
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.45139
NR122040 | 104111 | 220KV FATEHPUR-KNP SOUTH | 2013-04-11 09:34 | 2013-04-11 19:28 | 0 | 0 | 0 | 0.4125 | LCSD | S/D for stringing work of 765kv Agra-Fthpr-II line. | N/909
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.4125
NR122041 | 104110 | 220KV FATEHPUR-NAUBASTA | 2013-04-11 08:56 | 2013-04-12 19:13 | 0 | 0 | 0 | 1899-12-31 10:17 | OSPD | S/D by UPPCL for control panel replacement at Naubasta. | N/907
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 10:17
BILHY2201 | 104027 | 220KV FGPP-PALLA-I | 2013-04-03 04:05 | 2013-04-03 04:30 | 0 | 0.017361 | 0 | 0 | OMSU | Line A/R at palla but tripped from FGPP due to A/R problem on B-N fault. FLR:FGPP-5.8 kms
BILHY2201 | 104028 | 220KV FGPP-PALLA-I | 2013-04-03 04:30 | 2013-04-03 15:28 | 0 | 0 | 0 | 0.45694 | OSFD | Line hand tripped by palla, on request of FGPP for checking of their protection.
BILHY2201 | 104067 | 220KV FGPP-PALLA-I | 2013-04-07 04:49 | 2013-04-07 05:42 | 0 | 0 | 0 | 0.036806 | OSFD | A/R at FGPP but tripped at Palla on B-N fault due to relay problem. FGPP-6.0km. S/D by HVPNL for testing.
BILHY2201 | 104071 | 220KV FGPP-PALLA-I | 2013-04-07 12:36 | 2013-04-07 16:12 | 0.15 | 0 | 0 | 0 | LEFT | A/R and tripped on R-N fault. FLR:FGPP-10.4km. Charged after patrolling.
BILHY2201 | 104162 | 220KV FGPP-PALLA-I | 2013-04-17 11:55 | 2013-04-17 19:44 | 0 | 0 | 0 | 0.32569 | OSPD | S/D by HVPNL to attend bus jumper Hotspot at Palla end. | N-1341
BILHY2201 | 104187 | 220KV FGPP-PALLA-I | 2013-04-19 23:47 | 2013-04-20 00:49 | 0 | 0.043056 | 0 | 0 | OMSU | Trip from FGPP end on B-N, due to relay problem at FGPP/NTPC end. FGPP=6.39km.
BILHY2201 | 104194 | 220KV FGPP-PALLA-I | 2013-04-20 12:54 | 2013-04-20 19:24 | 0 | 0 | 0 | 0.27083 | OSPD | S/D by Palla/HVPNL to attend Isolator hotspot. | N-1567
|  | SUB TOTAL |  |  | 0.15 | 0.060417 | 0 | 1899-12-31 02:10
BILHY2202 | 104169 | 220KV FGPP-PALLA-II | 2013-04-18 10:55 | 2013-04-18 14:29 | 0 | 0 | 0 | 0.14861 | OSPD | S/D tacken by HVPNL for Bus hot spot attend | N-1423
BILHY2202 | 104216 | 220KV FGPP-PALLA-II | 2013-04-24 05:40 | 2013-04-24 05:50 | 0 | 0.0069444 | 0 | 0 | OMSU | A/R at FGPP but trip from Palla due to HVPNL A/R relay problem on B-N fault. FGPP-2.5km.
BILHY2202 | 104217 | 220KV FGPP-PALLA-II | 2013-04-24 05:50 | 2013-04-24 06:55 | 0 | 0 | 0 | 0.045139 | OSFD | S/D by HVPNL for checking of protn at Palla.
BILHY2202 | 104225 | 220KV FGPP-PALLA-II | 2013-04-25 01:52 | 2013-04-25 02:38 | 0 | 0.031944 | 0 | 0 | SRMU | Trip only from Palla/HVPNL end on relay maloperation.
BILHY2202 | 104242 | 220KV FGPP-PALLA-II | 2013-04-27 08:10 | 2013-04-27 08:30 | 0 | 0.013889 | 0 | 0 | OMSU | A/R at FGPP but tripped from Palla-HVPNL end due to relay problem on B-N fault. FGPP=2.6km, Palla=12km
BILHY2202 | 104264 | 220KV FGPP-PALLA-II | 2013-04-30 10:53 | 2013-04-30 13:50 | 0 | 0 | 0 | 0.12292 | LCSD | S/D for installation of polymer insulator string at loc.10. | N-2208
|  | SUB TOTAL |  |  | 0 | 0.052778 | 0 | 0.31667
BILHY2203 | 104128 | 220KV FGPP-SPUR-I | 2013-04-13 09:48 | 2013-04-13 18:49 | 0 | 0 | 0 | 0.37569 | OSPD | S/D by BBMB for bay eqpt mntc at their end. | N-1071
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.37569
BILHY2204 | 104137 | 220KV FGPP-SPUR-II | 2013-04-14 09:04 | 2013-04-14 16:10 | 0 | 0 | 0 | 0.29583 | OSPD | S/D by BBMB for bay eqpt mntc at samayapur end. | N-1123
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.29583
NR122016 | 104107 | 220KV KNP-MAINPURI | 2013-04-11 01:44 | 2013-04-11 02:58 | 0 | 0.051389 | 0 | 0 | OMSU | Tripped on B-N,Z2 fault in UPPCL portion. KNP-178.7km.
|  | SUB TOTAL |  |  | 0 | 0.051389 | 0 | 0
NR122017 | 104061 | 220KV KNP-NAUBASTA | 2013-04-06 08:32 | 2013-04-07 18:18 | 0 | 0 | 0 | 1899-12-31 09:46 | OSPD | S/D by UPPCL for construction work of their line. | N-488
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 09:46
NR122019 | 104144 | 220KV KNP-PANKI-II | 2013-04-14 18:29 | 2013-04-14 18:40 | 0 | 0.0076389 | 0 | 0 | OMSU | A/R at Knp but tripped from Panki due to B-N fault in UPPCL portion. Knp-20.89km. Remain chargd from Knp.
NR122019 | 104145 | 220KV KNP-PANKI-II | 2013-04-14 18:40 | 2013-04-14 20:22 | 0 | 0 | 0 | 0.070833 | OSFD | Delay in synchronising by UPPCL due to CB problem.
NR122019 | 104210 | 220KV KNP-PANKI-II | 2013-04-22 10:34 | 2013-04-22 19:26 | 0 | 0 | 0 | 0.36944 | OSPD | S/D by UPPCL to attend bus jumper Hotspot at Panki. | N-1692
|  | SUB TOTAL |  |  | 0 | 0.0076389 | 0 | 0.44028
BILUP2204 | 104089 | 220KV MEERUT-MPURAM-I | 2013-04-09 23:06 | 2013-04-09 23:49 | 0 | 0 | 0 | 0.029861 | LPRD | H/Triped for Power regulation. | N-796
BILUP2204 | 104096 | 220KV MEERUT-MPURAM-I | 2013-04-10 01:25 | 2013-04-10 02:48 | 0 | 0 | 0 | 0.057639 | LPRD | H/Triped for Power regulation. | N-809
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.0875
BILUP2205 | 104090 | 220KV MEERUT-MPURAM-II | 2013-04-09 23:06 | 2013-04-09 23:49 | 0 | 0 | 0 | 0.029861 | LPRD | H/Triped for Power regulation. | N-796
BILUP2205 | 104097 | 220KV MEERUT-MPURAM-II | 2013-04-10 01:25 | 2013-04-10 02:48 | 0 | 0 | 0 | 0.057639 | LPRD | H/Triped for Power regulation. | N-809
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.0875
BILUP2206 | 104009 | 220KV MEERUT-NARA | 2013-04-02 11:09 | 2013-04-02 12:29 | 0 | 0.055556 | 0 | 0 | OMSU | Line A/R at MRT but tripped from NARA-UPPCL end on Y-N fault in UPPCL portion. FLR:MRT-13.3 kms
BILUP2206 | 104019 | 220KV MEERUT-NARA | 2013-04-03 00:35 | 2013-04-03 11:09 | 0 | 0 | 0 | 0.44028 | OSFD | Forced S/D by UPPCL due to fault by R-ph jumper broken at Nara S/yard. Line A/R at MRT on R-N fault.
BILUP2206 | 104069 | 220KV MEERUT-NARA | 2013-04-07 09:34 | 2013-04-07 19:29 | 0 | 0 | 0 | 0.41319 | OSPD | S/D by UPPCL for construction work of their line. | N-567
BILUP2206 | 104081 | 220KV MEERUT-NARA | 2013-04-08 10:00 | 2013-04-08 22:14 | 0 | 0 | 0 | 0.50972 | OSPD | S/D by UPPCL for Insulator replacement work. | N-654
BILUP2206 | 104087 | 220KV MEERUT-NARA | 2013-04-09 14:31 | 2013-04-09 15:21 | 0 | 0.034722 | 0 | 0 | OMSU | Triped on B-N Fault in UPPCL portion. MRT=12.1km
BILUP2206 | 104091 | 220KV MEERUT-NARA | 2013-04-09 23:06 | 2013-04-09 23:49 | 0 | 0 | 0 | 0.029861 | LPRD | H/Triped for Power regulation. | N-796
BILUP2206 | 104098 | 220KV MEERUT-NARA | 2013-04-10 01:25 | 2013-04-10 02:48 | 0 | 0 | 0 | 0.057639 | LPRD | H/Triped for Power regulation. | N-809
BILUP2206 | 104113 | 220KV MEERUT-NARA | 2013-04-11 15:23 | 2013-04-11 18:59 | 0 | 0 | 0 | 0.15 | OSPD | S/D by UPPCL to attend bus jumper hot spot. | N/943
|  | SUB TOTAL |  |  | 0 | 0.090278 | 0 | 1899-12-31 14:25
BILUP2207 | 104088 | 220KV MEERUT-SHTBDNGR | 2013-04-09 23:06 | 2013-04-09 23:49 | 0 | 0 | 0 | 0.029861 | LPRD | H/Triped for Power regulation. | N-796
BILUP2207 | 104095 | 220KV MEERUT-SHTBDNGR | 2013-04-10 01:25 | 2013-04-10 02:48 | 0 | 0 | 0 | 0.057639 | LPRD | H/Triped for Power regulation. | N-809
BILUP2207 | 104121 | 220KV MEERUT-SHTBDNGR | 2013-04-12 14:18 | 2013-04-12 18:35 | 0 | 0 | 0 | 0.17847 | OSPD | S/D by UPPCL for Jumper replacement at Shtbdngr. | N-1024
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.26597
BILUP2208 | 104092 | 220KV MEERUT-SIMBHOLI | 2013-04-09 23:06 | 2013-04-09 23:49 | 0 | 0 | 0 | 0.029861 | LPRD | H/Triped for Power regulation. | N-796
BILUP2208 | 104099 | 220KV MEERUT-SIMBHOLI | 2013-04-10 01:25 | 2013-04-10 02:48 | 0 | 0 | 0 | 0.057639 | LPRD | H/Triped for Power regulation. | N-809
BILUP2208 | 104104 | 220KV MEERUT-SIMBHOLI | 2013-04-10 13:10 | 2013-04-10 13:26 | 0 | 0.011111 | 0 | 0 | OMSU | Line A/R and tripped on B-N fault in UPPCL portion, FLR:MRT-15.9 kms
|  | SUB TOTAL |  |  | 0 | 0.011111 | 0 | 0.0875
NR122026 | 104149 | 220KV RAIBRLY-LKO(UP) | 2013-04-15 15:32 | 2013-04-15 16:39 | 0 | 0 | 0 | 0.046528 | OSPD | S/D by UPPCL for line maintenence work. | N-1198
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.046528
NR122042 | 104070 | 220KV SIKAR-RATANGARH-I | 2013-04-07 12:11 | 2013-04-07 12:41 | 0 | 0.020833 | 0 | 0 | OMSU | Tripped on Y-B-N fault in RRVPNL portion. Sikar-2.8km
NR122042 | 104112 | 220KV SIKAR-RATANGARH-I | 2013-04-11 13:10 | 2013-04-11 16:08 | 0.12361 | 0 | 0 | 0 | OSPT | S/D for tree lopping work at Sikar-PG. | N/936
|  | SUB TOTAL |  |  | 0.12361 | 0.020833 | 0 | 0
NR122045 | 104063 | 220KV SIKAR-SIKAR(RJ)-II | 2013-04-06 09:39 | 2013-04-06 10:33 | 0 | 0.0375 | 0 | 0 | OMSU | Tripped on Y-N fault in RRVPNL portion.
|  | SUB TOTAL |  |  | 0 | 0.0375 | 0 | 0
NR122032 | 104179 | 220KV SITARGANJ-BLY(UP) | 2013-04-19 09:48 | 2013-04-19 18:20 | 0 | 0 | 0 | 0.35556 | LCSD | S/D for installation of OPGW bet. loc. 153-162 by m/s BGR. | N-1490
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.35556
NR122033 | 104180 | 220KV TNKPR-BLY(UP) | 2013-04-19 09:48 | 2013-04-19 18:48 | 0 | 0 | 0 | 0.375 | LCSD | S/D for installation of OPGW bet. loc. 153-162 by m/s BGR. | N-1490
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.375
NR1ICT12 | 104263 | 315MVA ICT-III BLBGARH | 2013-04-30 09:15 | 2013-04-30 18:20 | 0 | 0 | 0 | 0.37847 | OSPD | S/D by BBMB for their 220kv bay eqpt maintenance. | N-2204
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.37847
NR1BRT12 |  | 50MVAR B/Reactor MURADNGR | 2013-04-01 | 2013-05-01 | 0 | 0 | 0 | 1900-01-29 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-29
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Classification/ Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(F13:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Classification/ Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM(G13:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Classification/ Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM(H13:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Classification/ Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM(I13:[Deemed Available, row above])
Note on C271: LILO of Mnd-Bly-I at Neerut. DOC-01.04.13

## Verified AVBT_April-13
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.04.2013 to 30.04.2013
SL.NO. | ELEMENT | Element Name | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Total Duration
| NO. |  |  |  | Outage Not To Consider |  | Available for
|  |  | POWERGRID | OTHERS | System Constrnt/ | Deemed | Consideration
[5 empty] | Natural Calamity/ | Available | THM | NSC | Ckt. Kms. | OH x NSC x Cktkm | THM x NSC x Cktkm | Non Availblty Factor/ Month (NAFM) | TAFM
[5 empty] | Militancy |  |  | ( E) | ( F)
|  |  | @ (T) | # (U) | & (C ) | " (D) | E | F | G | H | I | J | K
|  |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs
A |  | 765 KV TRANS LINES | [12 empty] | 0
1 | NR176501 | 765KV LUCKNOW-BALIA |  |  | 0.0041667 | 0.11597 | 719.9 | 4 | 318.919 | 0 | 918359.1524 | 0 | 100 | 0 | 720
2 | NR176502 | 765KV AGRA-FATEHPUR |  |  |  | 0.15069 | 720 | 4 | 334.52 | 0 | 963417.6 | 0 | 100 | 0
3 | NR176503 | 765KV FATEHPUR-GAYA |  |  |  |  | 720 | 4 | 484.6 | 0 | 1395648 | 0 | 100 | 0
B |  | 400 KV TRANS LINES
1 | NR140001 | 400KV AGRA-AGRA(UP)-I |  |  |  |  | 720 | 2 | 29.982 | 0 | 43174.08 | 0 | 100 | 0
2 | NR140002 | 400KV AGRA-AGRA(UP)-II |  |  |  |  | 720 | 2 | 29.982 | 0 | 43174.08 | 0 | 100 | 0
3 | NR140003 | 400KV AGRA-AURAIYA-I |  |  |  | 0.16111 | 720 | 2 | 167.2 | 0 | 240768 | 0 | 100 | 0
4 | NR140004 | 400KV AGRA-AURAIYA-II |  |  |  |  | 720 | 2 | 167.2 | 0 | 240768 | 0 | 100 | 0
5 | NR140005 | 400KV AGRA-BASSI-I |  |  |  | 0.23472 | 720 | 2 | 211.433 | 0 | 304463.52 | 0 | 100 | 0
6 | NR140008 | 400KV AGRA-BHIWADI-I |  |  |  | 0.99444 | 720 | 2 | 208.98 | 0 | 300931.2 | 0 | 100 | 0
7 | NR140009 | 400KV AGRA-BHIWADI-II | 0.053472 |  |  |  | 720 | 2 | 209.51 | 537.7423 | 301694.4 | 0.0017824 | 99.8218 | 1.2833
8 | NR140010 | 400KV AGRA-BLBGRH |  |  |  |  | 720 | 2 | 181.137 | 0 | 260837.28 | 0 | 100 | 0
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I |  |  |  | 0.58889 | 720 | 2 | 253.823 | 0 | 365505.12 | 0 | 100 | 0
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II |  |  |  | 0.21458 | 720 | 2 | 253.823 | 0 | 365505.12 | 0 | 100 | 0
11 | NR140122 | 400KV ALLD-FATEHPUR-I |  |  |  | 1900-01-02 15:52 | 720 | 2 | 139.73 | 0 | 201211.2 | 0 | 100 | 0
12 | NR140123 | 400KV ALLD-FATEHPUR-II |  |  |  | 1899-12-31 11:03 | 720 | 2 | 139.73 | 0 | 201211.2 | 0 | 100 | 0
13 | NR140104 | 400KV ALLD-FATEHPUR-III |  |  |  |  | 720 | 2 | 155.3 | 0 | 223632 | 0 | 100 | 0
14 | NR140012 | 400KV ALLD-KNP-II |  |  |  |  | 720 | 2 | 224 | 0 | 322560 | 0 | 100 | 0
15 | NR140015 | 400KV ALLD-SARNATH |  |  |  | 0.95625 | 720 | 2 | 212 | 0 | 305280 | 0 | 100 | 0
16 | NR140016 | 400KV ALLD-SASARAM |  |  |  | 0.97361 | 720 | 2 | 136 | 0 | 195840 | 0 | 100 | 0
17 | NR140017 | 400KV BALIA-BIHARSHRF-I |  |  |  |  | 720 | 4 | 241.79 | 0 | 696355.2 | 0 | 100 | 0
18 | NR140018 | 400KV BALIA-BIHARSHRF-II | 0.27778 |  |  |  | 720 | 4 | 241.79 | 6447.7333 | 696355.2 | 0.0092593 | 99.0741 | 6.6667
19 | NR140019 | 400KV BALIA-MAU-I |  | 0.029167 |  | 0.16806 | 720 | 2 | 13 | 0 | 18720 | 0 | 100 | 0
20 | NR140020 | 400KV BALIA-MAU-II |  | 0.032639 |  | 0.25069 | 720 | 2 | 13 | 0 | 18720 | 0 | 100 | 0
21 | NR140021 | 400KV BALIA-PATNA-I |  |  | 0.0013889 | 1900-01-05 12:11 | 719.9667 | 4 | 195.32 | 0 | 562495.5573 | 0 | 100 | 0
22 | NR140022 | 400KV BALIA-PATNA-II |  |  |  | 1900-01-05 00:35 | 720 | 4 | 195.32 | 0 | 562521.6 | 0 | 100 | 0
23 | NR140136 | 400KV BALIA-PATNA-III | 0.093056 |  |  | 1900-01-09 05:38 | 720 | 4 | 185 | 1652.6667 | 532800 | 0.0031019 | 99.6898 | 2.2333
24 | NR140137 | 400KV BALIA-PATNA-IV |  |  |  | 1900-01-04 09:23 | 720 | 4 | 185 | 0 | 532800 | 0 | 100 | 0
25 | NR140140 | 400KV BALIA-SOHAWAL-I |  |  | 0.0125 | 0.175 | 719.7 | 2 | 229.163 | 0 | 329857.2222 | 0 | 100 | 0
26 | NR140120 | 400KV BALIA-SOHAWAL-II | 0.086111 |  | 0.0020833 | 1899-12-31 16:08 | 719.95 | 2 | 229.163 | 947.2071 | 329971.8037 | 0.0028706 | 99.7129 | 2.0667
27 | NR140023 | 400KV BAREILLY-BRLY(UP)-I |  |  |  |  | 720 | 2 | 9.2 | 0 | 13248 | 0 | 100 | 0
28 | NR140024 | 400KV BAREILLY-BRLY(UP)-II |  |  |  |  | 720 | 2 | 9.2 | 0 | 13248 | 0 | 100 | 0
29 | NR140025 | 400KV BAREILLY-LKO(UP) |  | 0.056944 |  |  | 720 | 2 | 278.76 | 0 | 401414.4 | 0 | 100 | 0
30 | NR140026 | 400KV BAREILLY-MBAD-I |  | 0.024306 |  |  | 720 | 2 | 92.68 | 0 | 133459.2 | 0 | 100 | 0
31 | NR140027 | 400KV BAREILLY-MBAD-II |  |  |  |  | 720 | 2 | 92.68 | 0 | 133459.2 | 0 | 100 | 0
32 | NR140115 | 400KV BAREILLY-ROSA-I |  | 0.022222 | 0.0013889 | 0.10347 | 719.9667 | 2 | 115.926 | 0 | 166925.7116 | 0 | 100 | 0
33 | NR140028 | 400KV BASSI-BHIWADI-I |  |  |  | 1900-01-02 17:32 | 720 | 2 | 235 | 0 | 338400 | 0 | 100 | 0
34 | NR140029 | 400KV BASSI-BHIWADI-II |  |  |  | 1899-12-31 00:43 | 720 | 2 | 220.261 | 0 | 317175.84 | 0 | 100 | 0
35 | NR140030 | 400KV BASSI-HIRAPURA-I |  |  |  | 1899-12-31 22:27 | 720 | 2 | 47.762 | 0 | 68777.28 | 0 | 100 | 0
36 | NR140031 | 400KV BASSI-HIRAPURA-II |  |  |  | 0.90625 | 720 | 2 | 48.99 | 0 | 70545.6 | 0 | 100 | 0
37 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 0.04375 |  |  | 0.91111 | 720 | 2 | 37.164 | 78.0444 | 53516.16 | 0.0014583 | 99.8542 | 1.05
38 | NR140127 | 400KV BASSI-JAIPUR(S)-II |  |  |  | 0.22222 | 720 | 2 | 37.164 | 0 | 53516.16 | 0 | 100 | 0
39 | NR140032 | 400KV BHIWADI-GURGAON |  |  |  |  | 720 | 2 | 82.8 | 0 | 119232 | 0 | 100 | 0
40 | NR140033 | 400KV BHIWADI-HISAR |  |  |  |  | 720 | 2 | 211.547 | 0 | 304627.68 | 0 | 100 | 0
41 | NR140106 | 400KV BHIWADI-NIMRANA-I |  |  |  | 1900-01-06 23:36 | 720 | 2 | 48.428 | 0 | 69736.32 | 0 | 100 | 0
42 | NR140107 | 400KV BHIWADI-NIMRANA-II |  |  |  | 0.28958 | 720 | 2 | 48.428 | 0 | 69736.32 | 0 | 100 | 0
43 | NR140035 | 400KV BLBGRH-GURGAON |  |  |  |  | 720 | 2 | 42.7 | 0 | 61488 | 0 | 100 | 0
44 | NR140036 | 400KV BLBGRH-MAHRANIBG |  |  |  |  | 720 | 4 | 60.68 | 0 | 174758.4 | 0 | 100 | 0
45 | NR140037 | 400KV BLBGRH-MAINPURI-I |  |  |  | 1899-12-31 17:48 | 720 | 2 | 235.952 | 0 | 339770.88 | 0 | 100 | 0
46 | NR140038 | 400KV BLBGRH-MAINPURI-II |  |  |  | 1899-12-31 02:12 | 720 | 2 | 235.952 | 0 | 339770.88 | 0 | 100 | 0
47 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) |  |  |  |  | 720 | 4 | 12.55 | 0 | 36144 | 0 | 100 | 0
48 | NR140039 | 400KV DAD-GR.NOIDA |  |  |  |  | 720 | 4 | 13.256 | 0 | 38177.28 | 0 | 100 | 0
49 | NR140040 | 400KV DAD-MAHRANIBG |  |  |  |  | 720 | 4 | 54.36 | 0 | 156556.8 | 0 | 100 | 0
50 | NR140041 | 400KV DAD-MANDOLA-I |  |  |  |  | 720 | 4 | 46.3 | 0 | 133344 | 0 | 100 | 0
51 | NR140042 | 400KV DAD-MANDOLA-II |  |  |  |  | 720 | 4 | 46.3 | 0 | 133344 | 0 | 100 | 0
52 | NR140043 | 400KV DAD-MURADNGR | 0.16667 |  |  | 0.065972 | 720 | 2 | 33.098 | 264.784 | 47661.12 | 0.0055556 | 99.4444 | 4
53 | NR140044 | 400KV DAD-PANIPAT-I |  | 0.018056 |  |  | 720 | 2 | 112.322 | 0 | 161743.68 | 0 | 100 | 0
54 | NR140045 | 400KV DAD-PANIPAT-II |  |  | 0.0020833 | 0.12986 | 719.95 | 2 | 117 | 0 | 168468.3 | 0 | 100 | 0
55 | NR140124 | 400KV FATEHPUR-MAINPURI-I |  |  |  | 0.77292 | 720 | 2 | 260.051 | 0 | 374473.44 | 0 | 100 | 0
56 | NR140125 | 400KV FATEHPUR-MAINPURI-II |  |  |  | 0.49514 | 720 | 2 | 260.051 | 0 | 374473.44 | 0 | 100 | 0
57 | NR140046 | 400KV GORKH-GORAKH-I |  |  | 0.0027778 | 0.11806 | 719.9333 | 2 | 45.94 | 0 | 66147.4747 | 0 | 100 | 0
58 | NR140047 | 400KV GORKH-GORAKH-II |  |  |  |  | 720 | 2 | 45.94 | 0 | 66153.6 | 0 | 100 | 0
59 | NR140128 | 400KV GURGAON-MANESAR-I |  |  |  | 1900-01-29 | 720 | 2 | 23.462 | 0 | 33785.28 | 0 | 100 | 0
60 | NR140129 | 400KV GURGAON-MANESAR-II | 0.013889 |  |  |  | 720 | 2 | 23.462 | 15.6413 | 33785.28 | 0.00046296 | 99.9537 | 0.33333
61 | NR140132 | 400KV JHATIKALA-BAMNOLI-I |  | 0.021528 |  |  | 720 | 4 | 6.106 | 0 | 17585.28 | 0 | 100 | 0
62 | NR140133 | 400KV JHATIKALA-BAMNOLI-II |  | 0.021528 |  |  | 720 | 4 | 6.106 | 0 | 17585.28 | 0 | 100 | 0
63 | NR140134 | 400KV JHATIKALA-MUNDKA-I |  |  |  |  | 720 | 4 | 6.782 | 0 | 19532.16 | 0 | 100 | 0
64 | NR140135 | 400KV JHATIKALA-MUNDKA-II |  |  |  |  | 720 | 4 | 6.782 | 0 | 19532.16 | 0 | 100 | 0
65 | NR140048 | 400KV KANKROLI-BHINMAL |  |  |  |  | 720 | 2 | 201.2 | 0 | 289728 | 0 | 100 | 0
66 | NR140049 | 400KV KANKROLI-JODHPUR |  |  | 0.0027778 | 0.44653 | 719.9333 | 2 | 187.965 | 0 | 270644.538 | 0 | 100 | 0
67 | NR140050 | 400KV KANKROLI-RAPPC-I |  |  |  |  | 720 | 2 | 198.54 | 0 | 285897.6 | 0 | 100 | 0
68 | NR140051 | 400KV KANKROLI-RAPPC-II |  |  |  |  | 720 | 2 | 198.54 | 0 | 285897.6 | 0 | 100 | 0
69 | NR140052 | 400KV KNP-AGRA | 0.013889 |  |  | 0.85278 | 720 | 2 | 240 | 160 | 345600 | 0.00046296 | 99.9537 | 0.33333
70 | NR140053 | 400KV KNP-AURAIYA-I |  |  |  |  | 720 | 2 | 72.6 | 0 | 104544 | 0 | 100 | 0
71 | NR140054 | 400KV KNP-AURAIYA-II |  |  |  |  | 720 | 2 | 73.2 | 0 | 105408 | 0 | 100 | 0
72 | NR140055 | 400KV KNP-BLBGARH-I | 0.077083 |  |  | 1899-12-31 14:27 | 720 | 2 | 385.69 | 1427.053 | 555393.6 | 0.0025694 | 99.7431 | 1.85
73 | NR140056 | 400KV KNP-BLBGARH-II |  |  |  | 1899-12-31 12:14 | 720 | 2 | 370.772 | 0 | 533911.68 | 0 | 100 | 0
74 | NR140057 | 400KV KNP-BLBGARH-III | 0.19028 |  |  | 1899-12-31 12:10 | 720 | 2 | 370.772 | 3386.3843 | 533911.68 | 0.0063426 | 99.3657 | 4.5667
75 | NR140110 | 400KV KNP-FATEHPUR-I |  |  |  |  | 720 | 2 | 107.079 | 0 | 154193.76 | 0 | 100 | 0
76 | NR140105 | 400KV KNP-FATEHPUR-II |  |  |  | 0.44931 | 720 | 2 | 107.1 | 0 | 154224 | 0 | 100 | 0
77 | NR140058 | 400KV KNP-PANKI-I |  |  |  |  | 720 | 2 | 5.922 | 0 | 8527.68 | 0 | 100 | 0
78 | NR140059 | 400KV KNP-PANKI-II |  |  |  |  | 720 | 2 | 5.86 | 0 | 8438.4 | 0 | 100 | 0
79 | NR140102 | 400KV KOTA-BEAWAR |  |  |  |  | 720 | 2 | 179.711 | 0 | 258783.84 | 0 | 100 | 0
80 | NR140060 | 400KV KOTA-MERTA-I |  |  | 0.013194 | 1900-01-05 22:41 | 719.6833 | 2 | 255.56 | 0 | 367844.5453 | 0 | 100 | 0
81 | NR140062 | 400KV KOTA-RAPPC |  |  |  |  | 720 | 2 | 50.5 | 0 | 72720 | 0 | 100 | 0
82 | NR140063 | 400KV KOTESHWR-KHEP-I |  |  |  | 0.013889 | 720 | 2 | 2.7 | 0 | 3888 | 0 | 100 | 0
83 | NR140064 | 400KV KOTESHWR-KHEP-II |  |  |  |  | 720 | 2 | 2.7 | 0 | 3888 | 0 | 100 | 0
84 | NR140065 | 400KV KOTESHWR-TEHRI-I |  |  |  |  | 720 | 4 | 14.463 | 0 | 41653.44 | 0 | 100 | 0
85 | NR140098 | 400KV KOTESHWR-TEHRI-II |  |  |  |  | 720 | 4 | 16.49 | 0 | 47491.2 | 0 | 100 | 0
86 | NR140069 | 400KV LUCKNOW-BAREILLY-II |  |  |  |  | 720 | 2 | 255.5 | 0 | 367920 | 0 | 100 | 0
87 | NR140070 | 400KV LUCKNOW-GORAKH-III |  |  |  | 0.85625 | 720 | 2 | 263.933 | 0 | 380063.52 | 0 | 100 | 0
88 | NR140071 | 400KV LUCKNOW-GORAKH-IV |  |  |  | 1900-01-16 06:59 | 720 | 2 | 263.933 | 0 | 380063.52 | 0 | 100 | 0
89 | NR140112 | 400KV LUCKNOW-LKO(765)-I |  |  |  |  | 720 | 4 | 2.86 | 0 | 8236.8 | 0 | 100 | 0
90 | NR140113 | 400KV LUCKNOW-LKO(765)-II |  |  |  |  | 720 | 4 | 2.86 | 0 | 8236.8 | 0 | 100 | 0
91 | NR140072 | 400KV LUCKNOW-LKO(UP) |  | 0.054167 |  |  | 720 | 2 | 41.743 | 0 | 60109.92 | 0 | 100 | 0
92 | NR140114 | 400KV LUCKNOW-ROSA-I |  | 0.0048611 | 0.0013889 | 0.23681 | 719.9667 | 2 | 169.785 | 0 | 244479.081 | 0 | 100 | 0
93 | NR140141 | 400KV LUCKNOW-SOHAWAL-I |  |  |  | 0.54028 | 720 | 2 | 98.281 | 0 | 141524.64 | 0 | 100 | 0
94 | NR140121 | 400KV LUCKNOW-SOHAWAL-II |  |  | 0.0020833 | 0.6 | 719.95 | 2 | 98.281 | 0 | 141514.8119 | 0 | 100 | 0
95 | NR140073 | 400KV LUCKNOW-SULTANPR |  |  |  |  | 720 | 2 | 41.743 | 0 | 60109.92 | 0 | 100 | 0
96 | NR140074 | 400KV LUCKNOW-UNNAO-I |  |  |  |  | 720 | 2 | 73.826 | 0 | 106309.44 | 0 | 100 | 0
97 | NR140075 | 400KV LUCKNOW-UNNAO-II |  |  |  |  | 720 | 2 | 73.826 | 0 | 106309.44 | 0 | 100 | 0
98 | NR140076 | 400KV MBAD-MURADNGR |  | 0.024306 |  | 0.34653 | 720 | 2 | 133.5 | 0 | 192240 | 0 | 100 | 0
99 | NR140142 | 400KV MEERUT-BAREILLY-I |  | 0.0125 |  |  | 720 | 2 | 66.009 | 0 | 95052.96 | 0 | 100 | 0
100 | NR140130 | 400KV MEERUT-BAREILLY-II |  | 0.0048611 |  |  | 720 | 2 | 66.009 | 0 | 95052.96 | 0 | 100 | 0
101 | NR140077 | 400KV MEERUT-KOTESHWR-I |  |  |  |  | 720 | 4 | 178.69 | 0 | 514627.2 | 0 | 100 | 0
102 | NR140099 | 400KV MEERUT-KOTESHWR-II |  |  |  |  | 720 | 4 | 175.63 | 0 | 505814.4 | 0 | 100 | 0
103 | NR140078 | 400KV MEERUT-MND-I |  |  |  |  | 720 | 2 | 59.868 | 0 | 86209.92 | 0 | 100 | 0
104 | NR140079 | 400KV MEERUT-MND-II |  |  |  |  | 720 | 2 | 59.868 | 0 | 86209.92 | 0 | 100 | 0
105 | NR140143 | 400KV MEERUT-MND-III |  |  |  |  | 720 | 2 | 54.298 | 0 | 78189.12 | 0 | 100 | 0
106 | NR140131 | 400KV MEERUT-MND-IV |  |  |  |  | 720 | 2 | 54.298 | 0 | 78189.12 | 0 | 100 | 0
107 | NR140080 | 400KV MEERUT-MUZFRNGR |  |  |  |  | 720 | 2 | 37.38 | 0 | 53827.2 | 0 | 100 | 0
108 | NR140103 | 400KV MERTA-BEAWAR |  |  |  | 0.61528 | 720 | 2 | 76.018 | 0 | 109465.92 | 0 | 100 | 0
109 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA |  |  |  | 0.11597 | 720 | 4 | 30.15 | 0 | 86832 | 0 | 100 | 0
110 | NR140118 | 400KV NIMRANA-MANESAR-I |  |  |  |  | 720 | 2 | 67.041 | 0 | 96539.04 | 0 | 100 | 0
111 | NR140119 | 400KV NIMRANA-MANESAR-II |  |  |  |  | 720 | 2 | 67.041 | 0 | 96539.04 | 0 | 100 | 0
112 | NR140108 | 400KV NIMRANA-SIKAR-I |  |  |  | 1900-01-05 13:46 | 720 | 2 | 175.859 | 0 | 253236.96 | 0 | 100 | 0
113 | NR140109 | 400KV NIMRANA-SIKAR-II |  |  |  | 0.2875 | 720 | 2 | 175.859 | 0 | 253236.96 | 0 | 100 | 0
114 | NR140084 | 400KV RIHAND-ALLD-I |  |  |  | 0.37847 | 720 | 2 | 279.245 | 0 | 402112.8 | 0 | 100 | 0
115 | NR140085 | 400KV RIHAND-ALLD-II | 0.20625 |  |  |  | 720 | 2 | 279.245 | 2764.5255 | 402112.8 | 0.006875 | 99.3125 | 4.95
116 | NR140086 | 400KV ROORKI-MUZFRNGR |  | 0.038889 |  | 0.35694 | 720 | 2 | 2.1 | 0 | 3024 | 0 | 100 | 0
117 | NR140087 | 400KV ROORKI-RISHIKESH |  |  |  |  | 720 | 2 | 2.1 | 0 | 3024 | 0 | 100 | 0
118 | NR140088 | 400KV SASARAM-BIHARSHRF-I |  |  |  | 0.55972 | 720 | 2 | 210 | 0 | 302400 | 0 | 100 | 0
119 | NR140089 | 400KV SASARAM-BIHARSHRF-II |  |  |  | 0.43958 | 720 | 2 | 210 | 0 | 302400 | 0 | 100 | 0
120 | NR140090 | 400KV SASARAM-SARNATH |  |  |  |  | 720 | 2 | 76 | 0 | 109440 | 0 | 100 | 0
121 | NR140091 | 400KV SING-ALLD-I |  |  |  |  | 720 | 2 | 224 | 0 | 322560 | 0 | 100 | 0
122 | NR140092 | 400KV SING-ALLD-II |  |  |  |  | 720 | 2 | 202 | 0 | 290880 | 0 | 100 | 0
123 | NR140093 | 400KV SING-ANPARA |  |  |  |  | 720 | 2 | 25.057 | 0 | 36082.08 | 0 | 100 | 0
124 | NR140111 | 400KV SING-FATEHPUR |  |  |  | 0.18681 | 720 | 2 | 330.953 | 0 | 476572.32 | 0 | 100 | 0
125 | NR140095 | 400KV SING-LKO(UP) |  | 0.069444 |  |  | 720 | 2 | 408.6 | 0 | 588384 | 0 | 100 | 0
126 | NR140096 | 400KV SING-RIHAND-I |  | 0.046528 |  |  | 720 | 2 | 42.026 | 0 | 60517.44 | 0 | 100 | 0
127 | NR140097 | 400KV SING-RIHAND-II |  |  |  |  | 720 | 2 | 43.952 | 0 | 63290.88 | 0 | 100 | 0
128 | N-W40001 | 400KV SING-VINDH-I |  |  |  | 0.33472 | 720 | 2 | 3.341 | 0 | 4811.04 | 0 | 100 | 0
129 | N-W40002 | 400KV SING-VINDH-II |  |  |  | 0.29097 | 720 | 2 | 3.317 | 0 | 4776.48 | 0 | 100 | 0
130 | N-W40003 | 400KV KANKROLI-ZERDA-I |  |  |  |  | 720 | 2 | 233.707 | 0 | 336538.08 | 0 | 100 | 0
131 | N-W40004 | 400KV BHINMAL-ZERDA |  |  |  |  | 720 | 2 | 142.8 | 0 | 205632 | 0 | 100 | 0
17527.453
C |  | 220 KV TRANS LINES
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) |  |  |  |  | 720 | 1 | 21.879 | 0 | 15752.88 | 0 | 100 | 0
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) |  |  |  |  | 720 | 1 | 16.894 | 0 | 12163.68 | 0 | 100 | 0
3 | BILUP2202 | 220KV ALLD-REWA RD-I |  | 0.076389 |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
4 | BILUP2203 | 220KV ALLD-REWA RD-II |  | 0.052083 |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
5 | NR122001 | 220KV ANTA-BHIL-I |  |  |  |  | 720 | 1 | 186.667 | 0 | 134400.24 | 0 | 100 | 0
6 | NR122002 | 220KV ANTA-BHIL-II |  |  |  |  | 720 | 1 | 186.667 | 0 | 134400.24 | 0 | 100 | 0
7 | NR122003 | 220KV ANTA-DAUSA |  | 0.00625 |  | 0.62361 | 720 | 1 | 208.307 | 0 | 149981.04 | 0 | 100 | 0
8 | NR122004 | 220KV ANTA-RAPPC |  |  |  | 0.17778 | 720 | 1 | 87.544 | 0 | 63031.68 | 0 | 100 | 0
9 | NR122005 | 220KV ANTA-S.MDHPR |  |  |  | 0.45139 | 720 | 1 | 102.164 | 0 | 73558.08 | 0 | 100 | 0
10 | NR122006 | 220KV AUR-SIKANDARA-I |  |  |  |  | 720 | 1 | 182.176 | 0 | 131166.72 | 0 | 100 | 0
11 | NR122007 | 220KV AUR-SIKANDARA-II |  |  |  |  | 720 | 1 | 182.176 | 0 | 131166.72 | 0 | 100 | 0
12 | NR122008 | 220KV BASSI-BAGRU |  |  |  |  | 720 | 1 | 35.353 | 0 | 25454.16 | 0 | 100 | 0
13 | NR122009 | 220KV BASSI-DAUSA-I |  |  |  |  | 720 | 1 | 20.109 | 0 | 14478.48 | 0 | 100 | 0
14 | NR122010 | 220KV BASSI-DAUSA-II |  |  |  |  | 720 | 1 | 20.109 | 0 | 14478.48 | 0 | 100 | 0
15 | NR122011 | 220KV BASSI-IG NAGAR |  |  |  |  | 720 | 1 | 22.478 | 0 | 16184.16 | 0 | 100 | 0
16 | NR122012 | 220KV DGANGA-BLY(UP)-II |  |  |  |  | 720 | 2 | 234.59 | 0 | 337809.6 | 0 | 100 | 0
17 | NR122013 | 220KV DGANGA-PITHORAGRH |  |  |  |  | 720 | 2 | 59.01 | 0 | 84974.4 | 0 | 100 | 0
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I |  |  |  |  | 720 | 1 | 5.5 | 0 | 3960 | 0 | 100 | 0
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II |  |  |  |  | 720 | 1 | 5.5 | 0 | 3960 | 0 | 100 | 0
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH |  |  |  | 0.4125 | 720 | 1 | 6 | 0 | 4320 | 0 | 100 | 0
21 | NR122041 | 220KV FATEHPUR-NAUBASTA |  |  |  | 1899-12-31 10:17 | 720 | 1 | 6 | 0 | 4320 | 0 | 100 | 0
22 | BILHY2201 | 220KV FGPP-PALLA-I | 0.15 | 0.060417 |  | 1899-12-31 02:10 | 720 | 1 | 15.69 | 56.484 | 11296.8 | 0.005 | 99.5 | 3.6
23 | BILHY2202 | 220KV FGPP-PALLA-II |  | 0.052778 |  | 0.31667 | 720 | 1 | 15.69 | 0 | 11296.8 | 0 | 100 | 0
24 | BILHY2203 | 220KV FGPP-SPUR-I |  |  |  | 0.37569 | 720 | 1 | 17.691 | 0 | 12737.52 | 0 | 100 | 0
25 | BILHY2204 | 220KV FGPP-SPUR-II |  |  |  | 0.29583 | 720 | 1 | 17.691 | 0 | 12737.52 | 0 | 100 | 0
26 | NR122014 | 220KV HIRAPURA-IG NAGAR |  |  |  |  | 720 | 2 | 24.875 | 0 | 35820 | 0 | 100 | 0
27 | NR122015 | 220KV HIRAPURA-SANGANER |  |  |  |  | 720 | 1 | 12 | 0 | 8640 | 0 | 100 | 0
28 | NR122016 | 220KV KNP-MAINPURI |  | 0.051389 |  |  | 720 | 1 | 10.4 | 0 | 7488 | 0 | 100 | 0
29 | NR122017 | 220KV KNP-NAUBASTA |  |  |  | 1899-12-31 09:46 | 720 | 1 | 14.86 | 0 | 10699.2 | 0 | 100 | 0
30 | NR122018 | 220KV KNP-PANKI-I |  |  |  |  | 720 | 1 | 10.4 | 0 | 7488 | 0 | 100 | 0
31 | NR122019 | 220KV KNP-PANKI-II |  | 0.0076389 |  | 0.44028 | 720 | 1 | 14.86 | 0 | 10699.2 | 0 | 100 | 0
32 | NR122020 | 220KV KNP-UNCHR-I |  |  |  |  | 720 | 1 | 143.553 | 0 | 103358.16 | 0 | 100 | 0
33 | NR122021 | 220KV KNP-UNCHR-II |  |  |  |  | 720 | 1 | 143.553 | 0 | 103358.16 | 0 | 100 | 0
34 | NR122022 | 220KV KNP-UNCHR-III |  |  |  |  | 720 | 1 | 144.63 | 0 | 104133.6 | 0 | 100 | 0
35 | NR122023 | 220KV KNP-UNCHR-IV |  |  |  |  | 720 | 1 | 144.63 | 0 | 104133.6 | 0 | 100 | 0
36 | BILUP2204 | 220KV MEERUT-MPURAM-I |  |  |  | 0.0875 | 720 | 1 | 2.316 | 0 | 1667.52 | 0 | 100 | 0
37 | BILUP2205 | 220KV MEERUT-MPURAM-II |  |  |  | 0.0875 | 720 | 1 | 9.254 | 0 | 6662.88 | 0 | 100 | 0
38 | BILUP2206 | 220KV MEERUT-NARA |  | 0.090278 |  | 1899-12-31 14:25 | 720 | 1 | 2.316 | 0 | 1667.52 | 0 | 100 | 0
39 | BILUP2207 | 220KV MEERUT-SHTBDNGR |  |  |  | 0.26597 | 720 | 1 | 8.234 | 0 | 5928.48 | 0 | 100 | 0
40 | BILUP2208 | 220KV MEERUT-SIMBHOLI |  | 0.011111 |  | 0.0875 | 720 | 1 | 9.254 | 0 | 6662.88 | 0 | 100 | 0
41 | NR122024 | 220KV PITHORAGRH-BRLY(UP) |  |  |  |  | 720 | 1 | 177.88 | 0 | 128073.6 | 0 | 100 | 0
42 | NR122025 | 220KV RAIBRLY-CHINHAT |  |  |  |  | 720 | 1 | 1.19 | 0 | 856.8 | 0 | 100 | 0
43 | NR122026 | 220KV RAIBRLY-LKO(UP) |  |  |  | 0.046528 | 720 | 1 | 1.19 | 0 | 856.8 | 0 | 100 | 0
44 | NR122027 | 220KV RAPPB-CHITT-I |  |  |  |  | 720 | 1 | 128.833 | 0 | 92759.76 | 0 | 100 | 0
45 | NR122028 | 220KV RAPPB-CHITT-II |  |  |  |  | 720 | 1 | 128.833 | 0 | 92759.76 | 0 | 100 | 0
46 | NR122029 | 220KV RAPPB-RAPPC |  |  |  |  | 720 | 1 | 0.175 | 0 | 126 | 0 | 100 | 0
47 | NR122030 | 220KV RAPPB-UDAIPUR |  |  |  |  | 720 | 1 | 230.297 | 0 | 165813.84 | 0 | 100 | 0
48 | NR122031 | 220KV S.MDHPR-DAUSA-I |  |  |  |  | 720 | 1 | 106.243 | 0 | 76494.96 | 0 | 100 | 0
49 | NR122042 | 220KV SIKAR-RATANGARH-I | 0.12361 | 0.020833 |  |  | 720 | 1 | 2.83 | 8.3957 | 2037.6 | 0.0041204 | 99.588 | 2.9667
50 | NR122044 | 220KV SIKAR-RATANGARH-II |  |  |  |  | 720 | 1 | 2.83 | 0 | 2037.6 | 0 | 100 | 0
51 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I |  |  |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
52 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II |  | 0.0375 |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
53 | NR122032 | 220KV SITARGANJ-BLY(UP) |  |  |  | 0.35556 | 720 | 1 | 105.72 | 0 | 76118.4 | 0 | 100 | 0
54 | NR122033 | 220KV TNKPR-BLY(UP) |  |  |  | 0.375 | 720 | 1 | 106 | 0 | 76320 | 0 | 100 | 0
55 | NR122034 | 220KV TNKPR-SITARGANJ |  |  |  |  | 720 | 1 | 42.55 | 0 | 30636 | 0 | 100 | 0
56 | NR122035 | 220KV UNCHR-RAIBRLY-I |  |  |  |  | 720 | 1 | 0.92 | 0 | 662.4 | 0 | 100 | 0
57 | NR122036 | 220KV UNCHR-RAIBRLY-II |  |  |  |  | 720 | 1 | 0.92 | 0 | 662.4 | 0 | 100 | 0
58 | NR122037 | 220KV UNCHR-RAIBRLY-III |  |  |  |  | 720 | 1 | 42.5 | 0 | 30600 | 0 | 100 | 0
3441.931
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA |  |  |  |  | 720 | 1 | 58 | 0 | 41760 | 0 | 100 | 0
|  | TOTAL FOR T/LS | 1899-12-31 11:54 | 0.94861 | 0.045833 | 1900-05-23 17:24 |  |  | 21027.384 | 17746.6616 | 32398415.5581 | 0.00054776 | 99.9452
|  | OVERALL SYSTEM AVAILABILITY= |  | 99.9864 | % (AC) | 99.9577 | (AC& HVDC)
E |  | 765/400 KV ICT'S | [5 empty] | M.F. | MVA | OHxMVAxMF | THMxMVAxMF
1 | NR1ICT707 | 400/765KV ICT-I AGRA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
2 | NR1ICT708 | 400/765KV ICT-II AGRA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
3 | NR1ICT701 | 765/400kv ICT-I BALIA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
4 | NR1ICT702 | 765/400kv ICT-II BALIA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
13 | NR1ICT713 | 765/400kv ICT-I MEERUT |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
14 | NR1ICT714 | 765/400kv ICT-II MEERUT |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
F |  | 400/220 KV ICT'S
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
3 | NR1ICT03 | 315MVA ICT-I BASSI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
4 | NR1ICT04 | 315MVA ICT-II BASSI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
5 | NR1ICT05 | 315MVA ICT-III BAWANA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
6 | NR1ICT06 | 315MVA ICT-I BHINMAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
7 | NR1ICT07 | 315MVA ICT-II BHINMAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
8 | NR1ICT08 | 315MVA ICT-I BHIWADI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
9 | NR1ICT09 | 315MVA ICT-II BHIWADI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
10 | NR1ICT54 | 315MVA ICT-III BHIWADI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
11 | NR1ICT10 | 315MVA ICT-I BLBGARH |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
12 | NR1ICT11 | 315MVA ICT-II BLBGARH |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
13 | NR1ICT12 | 315MVA ICT-III BLBGARH |  |  |  | 0.37847 | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
14 | NR1ICT13 | 315MVA ICT-IV BLBGARH |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
15 | NR1ICT48 | 315MVA ICT-I FATEHPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
16 | NR1ICT49 | 315MVA ICT-II FATEHPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
17 | NR1ICT14 | 315MVA ICT-I GORAKHPR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
18 | NR1ICT15 | 315MVA ICT-II GORAKHPR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
19 | NR1ICT42 | 315MVA ICT-I GURGAON |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
20 | NR1ICT51 | 315MVA ICT-II GURGAON |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
21 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
22 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
23 | NR1ICT16 | 315MVA ICT-I KANKROLI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
24 | NR1ICT17 | 315MVA ICT-II KANKROLI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
25 | NR1ICT18 | 315MVA ICT-III KANKROLI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
26 | NR1ICT19 | 315MVA ICT-I KANPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
27 | NR1ICT20 | 315MVA ICT-II KANPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
28 | NR1ICT21 | 315MVA ICT-I KOTA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
29 | NR1ICT22 | 315MVA ICT-II KOTA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
30 | NR1ICT23 | 315MVA ICT-I LUCKNOW |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
31 | NR1ICT53 | 500MVA ICT-II LUCKNOW |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
32 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
33 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
34 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
35 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
36 | NR1ICT26 | 315MVA ICT-I MAINPURI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
37 | NR1ICT27 | 315MVA ICT-II MAINPURI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
38 | NR1ICT28 | 315MVA ICT-I MANDOLA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
39 | NR1ICT29 | 315MVA ICT-II MANDOLA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
40 | NR1ICT30 | 315MVA ICT-III MANDOLA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
41 | NR1ICT31 | 315MVA ICT-IV MANDOLA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
42 | NR1ICT58 | 500MVA ICT-I MANESAR |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
43 | NR1ICT61 | 500MVA ICT-II MANESAR |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
44 | NR1ICT32 | 315MVA ICT-I MEERUT |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
45 | NR1ICT33 | 315MVA ICT-II MEERUT |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
46 | NR1ICT34 | 315MVA ICT-III MEERUT |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
47 | NR1ICT35 | 315MVA ICT-I MUZFRNGR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
48 | NR1ICT55 | 500MVA ICT-I NIMRANA |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
49 | NR1ICT50 | 315MVA ICT-II NIMRANA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
50 | NR1ICT36 | 315MVA ICT-I ROORKI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
51 | NR1ICT37 | 315MVA ICT-II ROORKI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
52 | NR1ICT59 | 315MVA ICT-I SOHAWAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
53 | NR1ICT60 | 315MVA ICT-II SOHAWAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
54 | NR1ICT56 | 315MVA ICT-I SIKAR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
55 | NR1ICT52 | 315MVA ICT-II SIKAR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
|  | TOTAL FOR ICTs | 0 | 0 | 0 | 0.37847 |  | 190 |  | 0 | 72909000 | 0 | 100
H |  | HVDC RIHAND-DADRI | [5 empty] | TCR | RC | TCR x OH | THM x RC
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 1899-12-31 17:21 |  |  | 1899-12-31 00:37 | 720 | 750 | 750 | 31012.5 | 540000 | 0.057431 | 94.2569 | 41.35
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 0.22986 |  |  |  | 720 | 750 | 750 | 4137.5 | 540000 | 0.007662 | 99.2338 | 5.5167
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I |  |  |  |  | 720 | 1250 | 1250 | 0 | 900000 | 0 | 100 | 0
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II |  | 0.0125 |  |  | 720 | 1250 | 1250 | 0 | 900000 | 0 | 100 | 0
|  | TOTAL FOR HVDC line | 1899-12-31 22:52 | 0.0125 | 0 | 1899-12-31 00:37 |  |  |  | 35150 | 2880000 | 0.012205 | 98.7795
J |  | HVDC BTB VINDH | [5 empty] | TCR | RC | TCR x OH | THM x RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I | 1900-01-02 18:29 |  |  | 0.086111 | 720 | 250 | 250 | 22620.8333 | 180000 | 0.12567 | 4071750000.0002 | 90.4833
2 | NR1DCB02 | +/-250MW HVDC B/B BLOCK-II | 1900-01-01 13:51 |  |  | 0.13125 | 720 | 250 | 250 | 15462.5 | 180000 | 0.085903 | 2783249999.9963 | 61.85
|  | TOTAL FOR HVDC VINDHYACHAL | 1900-01-05 08:20 | 0 | 0 | 0.21736 |  |  |  | 38083.3333 | 360000 | 0.10579 | 89.4213
K |  | HVDC BTB SASARAM
1 | NEDCB01 | +/-500MW HVDC B/B SASARAM | 0.42153 | 0.10625 |  |  | 720 | 500 | 500 | 5058.3333 | 360000 | 0.014051 | 98.5949 | 10.1167
|  | TOTAL FOR HVDC SASARAM | 0.42153 | 0.10625 | 0 | 0 |  |  |  | 5058.3333 | 360000 | 0.014051 | 98.5949
L |  | SVC, KANPUR | [5 empty] | M.F. | MVA | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  |  |  |  | 720 | 4 | 280 | 0 | 806400 | 0 | 100 | 0
2 | NR1SVC02 | +/-140MVAR SVC-II |  |  |  |  | 720 | 4 | 280 | 0 | 806400 | 0 | 100 | 0
|  | TOTAL FOR SVC | 0 | 0 | 0 | 0 |  |  |  | 0 | 1612800 | 0 | 100
M |  | Bus & Switch Line Reactor | [5 empty] | M.F. | MVA | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-II AGRA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
2 | NR1BRT26 | 125MVAR B/Reactor-III AGRA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
14 | NR1BRT04 | 50MVAR B/Reactor BASSI |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
15 | NR1BRT05 | 80MVAR B/Reactor BHINMAL |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
16 | NR1BRT15 | 80MVAR B/Reactor BHIWADI |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
18 | NR1BRT07 | 80MVAR B/Reactor BLBGARH |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
19 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
20 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
21 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 |  |  |  |  | 720 | 4 | 330 | 0 | 950400 | 0 | 100 | 0
22 | NR1BRT39 | 125MVAR B/Reactor GORAKHPUR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
23 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
24 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
25 | NR1BRT08 | 50MVAR B/Reactor KANKROLI |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
26 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
27 | NR1BRT09 | 80MVAR B/Reactor KOTA |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
28 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
29 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
30 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
31 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
32 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
33 | NR1BRT11 | 50MVAR B/Reactor MANDOLA |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
34 | NR1BRT30 | 125MVAR B/Reactor MANESAR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
35 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
36 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  |  |  | 1900-01-29 | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
37 | NR1BRT24 | 80MVAR B/Reactor NIMRANA |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
38 | NR1BRT40 | 125MVAR B/Reactor ROORKI |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
39 | NR1BRT29 | 80MVAR B/Reactor SIKAR |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
40 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | 720 | 4 | 93.2 | 0 | 268416 | 0 | 100 | 0
41 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | 720 | 4 | 93.2 | 0 | 268416 | 0 | 100 | 0
42 | NR1BRT42 | 125MVAR B/Reactor-I VINDH |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
43 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
44 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
45 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
46 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
47 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
48 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
49 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
50 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
51 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
52 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line |  |  |  |  | 720 | 4 | 330 | 0 | 950400 | 0 | 100 | 0
53 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
54 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
55 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
56 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
57 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
58 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
59 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
60 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
61 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
62 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
63 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
|  | TOTAL FOR BUS REACTORS | 0 | 0 | 0 | 1900-01-29 |  |  |  | 0 | 22819392 | 0 | 100
|  | TOTAL | 1900-01-09 05:13 | 1899-12-31 01:37 | 0.045833 | 1900-06-24 08:19
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(D18:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM([DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = SUM(E18:[OTHERS, row above])
OTHERS = SUM([OTHERS, row above])
Outage Not To Consider = SUM(F18:[Outage Not To Consider, row above])
Outage Not To Consider = SUM([Outage Not To Consider, row above])
Deemed = SUM(G18:[Deemed, row above])
Deemed = SUM([Deemed, row above])
Note on C155: cpcc: LILO of Alld-Phulpur at Jhusi .DOC-01-08-12
Note on C156: cpcc: LILO of Alld-Phulpur at Jhusi .DOC-01-08-12
Note on C166: Line reconfigured/ connected by RRVPNL at their Bagru S/S on 12/5/10. PG portion unchanged.