## OUTAGE_Jun_13
POWER GRID CORPORATION OF INDIA LTD.
NORTHERN REGION - 1
CPCC, N. DELHI
DOC No: NR-I/CPCC/II
MONTH – June'2013 LINE/ ICT OUTAGE DETAILS
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Classification/ Category Code | REASON OF OUTAGE | NRLDC CODE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Code
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12
NEDCB01 | 406001 | +/-500MW HVDC B/B SASARAM | 2013-06-01 00:27 | 2013-06-04 23:47 | 0 | 0 | 0 | 1900-01-02 23:20 | LPRD | TAKEN INTO AC BYPASS MODE AS PER ERLDC INSTRUCTION FOR POWER REGULATION.
NEDCB01 | 406056 | +/-500MW HVDC B/B SASARAM | 2013-06-05 20:15 | 2013-06-05 20:34 | 0 | 0.013194 | 0 | 0 | OMSU | TRIPPED ON AUX SUPPLY FAILURE AT BSEB
NEDCB01 | 406093 | +/-500MW HVDC B/B SASARAM | 2013-06-08 11:24 | 2013-06-08 11:50 | 0.018056 | 0 | 0 | 0 | SBBT | TRIPPED DUE TO OPERATION OF BUS BAR PROTECTION AT SSRM
NEDCB01 | 406139 | +/-500MW HVDC B/B SASARAM | 2013-06-12 07:44 | 2013-06-12 08:46 | 0 | 0.043056 | 0 | 0 | OMSU | HVDC/PSL TRIPPED DUE TO DIP IN AUXILIARY SUPPLY VOLTAGE
NEDCB01 | 406158 | +/-500MW HVDC B/B SASARAM | 2013-06-13 11:52 | 2013-06-13 12:46 | 0.0375 | 0 | 0 | 0 | OMST | TRIPPED DUE TO VBE (VALVE BASE ELECTRON- ICS) FAILURE AT SSRM END.
NEDCB01 | 406164 | +/-500MW HVDC B/B SASARAM | 2013-06-14 11:09 | 2013-06-26 16:32 | 0 | 0 | 0 | 1900-01-11 05:23 | LPRD | H/T AS PER ERLDC INSTRUCTION.FOR POWER REGULATION
NEDCB01 | 406279 | +/-500MW HVDC B/B SASARAM | 2013-06-27 17:24 | 2013-07-01 | 0 | 0 | 0 | 1900-01-02 06:36 | LPRD | LINE H/T AS PER ERLDC INSTRUCTION FOR POWER REGULATION.
|  | SUB TOTAL |  |  | 0.055556 | 0.05625 | 0 | 1900-01-18 11:19
NWDCB01 | 106005 | VINDH HVDC B/B BLOCK-I | 2013-06-01 10:21 | 2013-06-02 03:03 | 0 | 0 | 0 | 0.69583 | LCSD | S/D for rejumpering after bus extension. PTW returned at 2200hrs. Remain out due to NTPC AC feeder problem. | N-28
NWDCB01 | 106029 | VINDH HVDC B/B BLOCK-I | 2013-06-04 07:48 | 2013-06-04 10:31 | 0 | 0 | 0 | 0.11319 | OSPD | S/D by NTPC for restoration of VSTPP AC Feeder-I. | N-157
NWDCB01 | 106242 | VINDH HVDC B/B BLOCK-I | 2013-06-21 13:07 | 2013-06-21 22:02 | 0.37153 | 0 | 0 | 0 | OSPT | S/D to attend main bay R-ph isolator sparking at Vindh. | N-1546
|  | SUB TOTAL |  |  | 0.37153 | 0 | 0 | 0.80903
NWDCB02 | 106013 | VINDH HVDC B/B BLOCK-II | 2013-06-02 00:45 | 2013-06-02 03:03 | 0 | 0 | 0 | 0.095833 | GOMD | To facilitate S/D of west AC Feeder-I by NTPC due to CVT problem and delay in charging of Feeder-II from VSTPP. | N-57
NWDCB02 | 106030 | VINDH HVDC B/B BLOCK-II | 2013-06-04 07:48 | 2013-06-04 08:38 | 0 | 0 | 0 | 0.034722 | OSPD | S/D by NTPC for restoration of VSTPP AC Feeder-I. | N-157
NWDCB02 | 106217 | VINDH HVDC B/B BLOCK-II | 2013-06-19 01:00 | 2013-06-19 06:45 | 0.23958 | 0 | 0 | 0 | OMST | Tripped on DC O/Current & ground fault protn. Charged after detailed testing.
|  | SUB TOTAL |  |  | 0.23958 | 0 | 0 | 0.13056
NR1DCP02 | 106219 | HVDC R-D POLE-II | 2013-06-19 04:00 | 2013-06-19 06:05 | 0 | 0.086806 | 0 | 0 | OMSU | Tripped due to aux. Supply disturbance from Rh-NTPC.
|  | SUB TOTAL |  |  | 0 | 0.086806 | 0 | 0
NR1DCP03 | 106262 | HVDC BALIA-BHWD POLE-I | 2013-06-24 10:36 | 2013-06-24 10:55 | 0.013194 | 0 | 0 | 0 | OMST | Tripped due to Control System Malfunction at Ballia.
|  | SUB TOTAL |  |  | 0.013194 | 0 | 0 | 0
NR1DCP04 | 106143 | HVDC BALIA-BHWD POLE-II | 2013-06-14 15:26 | 2013-06-14 15:39 | 0.0090278 | 0 | 0 | 0 | OMST | Tripped on DC earth fault, during heavy rainstorm at Bhwd
NR1DCP04 | 106263 | HVDC BALIA-BHWD POLE-II | 2013-06-24 10:36 | 2013-06-24 10:55 | 0.013194 | 0 | 0 | 0 | OMST | Tripped due to Control System Malfunction at Ballia.
|  | SUB TOTAL |  |  | 0.022222 | 0 | 0 | 0
NR176504 | 106043 | 765KV AGRA-JHATIKALA | 2013-06-05 16:11 | 2013-06-05 16:23 | 0.0083333 | 0 | 0 | 0 | OMST | Line tripped due Bay control unit (BCU) hang at Agra.
NR176504 | 106116 | 765KV AGRA-JHATIKALA | 2013-06-11 07:26 | 2013-06-11 23:46 | 0 | 0 | 0 | 0.68056 | LCSD | S/D for resagging of cundocter due to heavy induction. | N-742
NR176504 | 106132 | 765KV AGRA-JHATIKALA | 2013-06-12 07:07 | 2013-06-12 20:24 | 0 | 0 | 0 | 0.55347 | LCSD | S/D for resagging of cundocter due to heavy induction. | N-819
|  | SUB TOTAL |  |  | 0.0083333 | 0 | 0 | 1899-12-31 05:37
NR176505 | 106002 | 765KV AGRA-MEERUT | 2013-06-01 12:17 | 2013-06-01 12:42 | 0.017361 | 0 | 0 | 0 | OSFT | S/D for attending Y-ph WT sparking at Meerut. | N/1725
NR176505 | 106006 | 765KV AGRA-MEERUT | 2013-06-01 12:17 | 2013-06-01 12:42 | 0 | 0 | 0.017361 | 0 | GOVC | Tripped on O/V protn at Agra>800kv.
NR176505 | 106028 | 765KV AGRA-MEERUT | 2013-06-04 07:05 | 2013-06-04 20:02 | 0 | 0 | 0 | 0.53958 | LCSD | S/D for bay/line construction work at Meerut. | N-155
NR176505 | 106039 | 765KV AGRA-MEERUT | 2013-06-05 07:08 | 2013-06-05 19:26 | 0 | 0 | 0 | 0.5125 | LCSD | S/D for bay/line construction work at Meerut. | N/222
NR176505 | 106049 | 765KV AGRA-MEERUT | 2013-06-06 07:00 | 2013-06-06 19:58 | 0 | 0 | 0 | 0.54028 | LCSD | S/D for bay/line construction work at Meerut. | N/290
NR176505 | 106078 | 765KV AGRA-MEERUT | 2013-06-07 07:00 | 2013-06-07 19:29 | 0 | 0 | 0 | 0.52014 | LCSD | S/D for bay/line construction work at Meerut. | N/431
NR176505 | 106193 | 765KV AGRA-MEERUT | 2013-06-17 04:04 | 2013-06-17 06:38 | 0 | 0 | 0 | 0.10694 | LVRD | Line hand tripped for Voltage regulation. Agra-430kv | N-1206
NR176505 | 106323 | 765KV AGRA-MEERUT | 2013-06-30 03:59 | 2013-06-30 04:02 | 0 | 0 | 0.0020833 | 0 | GOVC | Tripped on Over Voltage protection at Agra.
NR176505 | 106325 | 765KV AGRA-MEERUT | 2013-06-30 04:02 | 2013-06-30 06:55 | 0 | 0 | 0 | 0.12014 | LVRD | Line hand tripped for Voltage regulationAgra-812 KV | N/2144
|  | SUB TOTAL |  |  | 0.017361 | 0 | 0.019444 | 1900-01-01 08:09
NR176503 | 106053 | 765KV FATEHPUR-GAYA | 2013-06-06 10:40 | 2013-06-06 12:24 | 0 | 0 | 0.072222 | 0 | GOVC | O/V protn oprtd at Gaya-810kv. D/T received at fatehpur.
NR176503 | 106171 | 765KV FATEHPUR-GAYA | 2013-06-16 09:51 | 2013-06-16 20:46 | 0 | 0 | 0 | 0.45486 | LCSD | S/D taken by ER for erection of Auxiliary Bus at Gaya. | N-1128
NR176503 | 106250 | 765KV FATEHPUR-GAYA | 2013-06-22 10:21 | 2013-06-22 13:22 | 0.12569 | 0 | 0 | 0 | OMST | Tripped on Reactor protn due to moisture in PRV at Fthpr.
NR176503 | 106256 | 765KV FATEHPUR-GAYA | 2013-06-23 09:35 | 2013-06-23 18:04 | 0 | 0 | 0 | 0.35347 | LCSD | S/D By ER for balance Bus Isolator erection work at Gaya. | N-1646
NR176503 | 106265 | 765KV FATEHPUR-GAYA | 2013-06-24 19:12 | 2013-06-24 19:57 | 0.03125 | 0 | 0 | 0 | OMST | Tripped due to Maloperation of REF protection of Line Reactor at Fatehpur.
|  | SUB TOTAL |  |  | 0.15694 | 0 | 0.072222 | 0.80833
NR176506 | 106001 | 765KV FATEHPUR-SASARAM | 2013-06-01 | 2013-06-01 13:19 | 0 | 0 | 0.55486 | 0 | GOVC | Tripped on O/V protn at Sasaram. D/T recd at Fatehpur.
NR176506 | 106008 | 765KV FATEHPUR-SASARAM | 2013-06-01 18:38 | 2013-06-01 18:45 | 0 | 0 | 0.0048611 | 0 | GOVC | Tripped on O/V protn at Sasaram. D/T recd at Fatehpur.
NR176506 | 106009 | 765KV FATEHPUR-SASARAM | 2013-06-01 18:45 | 2013-06-02 23:17 | 0 | 0 | 0 | 1899-12-31 04:32 | LVRD | Kept open for voltage regulation due to high grid voltage
NR176506 | 106014 | 765KV FATEHPUR-SASARAM | 2013-06-02 04:06 | 2013-06-02 04:10 | 0 | 0 | 0.0027778 | 0 | GOVC | Tripped on O/V protn at Sasaram. D/T recd at Fatehpur.
NR176506 | 106015 | 765KV FATEHPUR-SASARAM | 2013-06-02 04:10 | 2013-06-02 11:02 | 0 | 0 | 0 | 0.28611 | LVRD | Kept open for voltage regulation due to high grid voltage
NR176506 | 106020 | 765KV FATEHPUR-SASARAM | 2013-06-02 15:46 | 2013-06-03 13:22 | 0 | 0 | 0 | 0.9 | LVRD | Kept open for voltage regulation due to high grid voltage after O/V protn oprtd at Sasaram >810 KV.
NR176506 | 106027 | 765KV FATEHPUR-SASARAM | 2013-06-03 18:18 | 2013-06-03 21:37 | 0 | 0 | 0.13819 | 0 | GOVC | Tripped on O/V protn at Sasaram. D/T recd at Fatehpur.
NR176506 | 106035 | 765KV FATEHPUR-SASARAM | 2013-06-04 13:42 | 2013-06-04 14:04 | 0 | 0 | 0.015278 | 0 | GOVC | Tripped on O/V protn at Sasaram. D/T recd at Fatehpur.
NR176506 | 106047 | 765KV FATEHPUR-SASARAM | 2013-06-05 20:00 | 2013-06-06 00:01 | 0 | 0 | 0 | 0.16736 | LVRD | D/T received at fatehpur , over voltage at SSRM
NR176506 | 106057 | 765KV FATEHPUR-SASARAM | 2013-06-06 14:06 | 2013-06-06 20:56 | 0.28472 | 0 | 0 | 0 | OMST | S/D for attending carona at loc. No. 68/2, 68/3 | N/318
NR176506 | 106084 | 765KV FATEHPUR-SASARAM | 2013-06-08 08:24 | 2013-06-08 22:27 | 0 | 0 | 0 | 0.58542 | LCSD | S/D by ER for spare L/Reactor CB erection at Sasaram. | N-518
NR176506 | 106154 | 765KV FATEHPUR-SASARAM | 2013-06-15 13:05 | 2013-06-15 13:09 | 0 | 0 | 0.0027778 | 0 | GOVC | O/Voltage protn trip at S/Ram-815kv., D/T recd at F/Pur.
NR176506 | 106155 | 765KV FATEHPUR-SASARAM | 2013-06-15 13:09 | 2013-06-15 19:52 | 0 | 0 | 0 | 0.27986 | LVRD | Kept open for v/regulation due to high grid voltage. | N-1075
NR176506 | 106227 | 765KV FATEHPUR-SASARAM | 2013-06-19 10:23 | 2013-06-19 11:26 | 0 | 0 | 0.04375 | 0 | GOVC | O/V protn oprtd at Sasaram. D/T recd at Fatehpur.
NR176506 | 106315 | 765KV FATEHPUR-SASARAM | 2013-06-29 18:11 | 2013-06-29 19:59 | 0 | 0 | 0 | 0.075 | LVRD | Line hand tripped for Voltage regulation. Fatehpur-788 KV | N/2109
|  | SUB TOTAL |  |  | 0.28472 | 0 | 0.7625 | 1900-01-02 11:35
NR176501 | 106007 | 765KV LUCKNOW-BALIA | 2013-06-01 17:42 | 2013-06-01 17:52 | 0.0069444 | 0 | 0 | 0 | OMST | Tripped only at Balia end on D/T signal recd.
NR176501 | 106208 | 765KV LUCKNOW-BALIA | 2013-06-18 10:56 | 2013-06-18 18:11 | 0.30208 | 0 | 0 | 0 | OMST | S/D for installation of Bird guard & CC rings. | N-1330
|  | SUB TOTAL |  |  | 0.30903 | 0 | 0 | 0
NR140001 | 106172 | 400KV AGRA-AGRA(UP)-I | 2013-06-16 13:24 | 2013-06-16 15:27 | 0 | 0 | 0 | 0.085417 | LVRD | Line hand tripped for Voltage regulation. Agra-430kv | N-1140
NR140001 | 106189 | 400KV AGRA-AGRA(UP)-I | 2013-06-17 03:08 | 2013-06-17 03:12 | 0 | 0 | 0.0027778 | 0 | GOVC | Trip on O/VOL protn at Agra=436kv.
NR140001 | 106191 | 400KV AGRA-AGRA(UP)-I | 2013-06-17 03:12 | 2013-06-17 05:56 | 0 | 0 | 0 | 0.11389 | LVRD | Kept open for VOL/Regulation due to high grid voltage. | N-1207
NR140001 | 106320 | 400KV AGRA-AGRA(UP)-I | 2013-06-30 03:31 | 2013-06-30 03:35 | 0 | 0 | 0.0027778 | 0 | GOVC | Tripped on O/voltage protn at UP end. D/T recd at Agra.
NR140001 | 106321 | 400KV AGRA-AGRA(UP)-I | 2013-06-30 03:35 | 2013-06-30 06:35 | 0 | 0 | 0 | 0.125 | LVRD | Line hand tripped for Voltage regulationAgra-433 KV | N/2140
|  | SUB TOTAL |  |  | 0 | 0 | 0.0055556 | 0.32431
NR140003 | 106114 | 400KV AGRA-AURAIYA-I | 2013-06-11 02:34 | 2013-06-11 07:59 | 0 | 0 | 0 | 0.22569 | LVRD | Line hand tripped for Voltage regulation. Agra-428kv | N/718
NR140003 | 106192 | 400KV AGRA-AURAIYA-I | 2013-06-17 03:26 | 2013-06-17 06:55 | 0 | 0 | 0 | 0.14514 | LVRD | Line hand tripped for Voltage regulation. Agra-430kv | N-1204
NR140003 | 106269 | 400KV AGRA-AURAIYA-I | 2013-06-25 08:20 | 2013-06-25 20:58 | 0 | 0 | 0 | 0.52639 | LCSD | S/D for stringing work of 765KV Agra-Fatehpur - II line. | N-1783
NR140003 | 106279 | 400KV AGRA-AURAIYA-I | 2013-06-26 12:21 | 2013-06-26 12:29 | 0.0055556 | 0 | 0 | 0 | OSPT | S/D to isolate S/R at Agra to attend Oil leakage in Bushing. | N-1860
|  | SUB TOTAL |  |  | 0.0055556 | 0 | 0 | 0.89722
NR140004 | 106270 | 400KV AGRA-AURAIYA-II | 2013-06-25 08:22 | 2013-06-25 21:01 | 0 | 0 | 0 | 0.52708 | LCSD | S/D for stringing work of 765KV Agra-Fatehpur - II line. | N-1783
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.52708
NR140005 | 106108 | 400KV AGRA-BASSI-I | 2013-06-11 02:13 | 2013-06-11 09:10 | 0 | 0 | 0 | 0.28958 | LVRD | Line hand tripped for Voltage regulation. Bassi-433kv. | N/713
NR140005 | 106319 | 400KV AGRA-BASSI-I | 2013-06-30 02:58 | 2013-06-30 23:58 | 0 | 0 | 0 | 0.875 | LVRD | Line hand tripped for Voltage regulationAgra-431 KV | N/2139
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 03:57
NR140008 | 106062 | 400KV AGRA-BHIWADI-I | 2013-06-06 17:08 | 2013-06-07 11:23 | 0 | 0 | 0 | 0.76042 | LVRD | Line hand tripped for Voltage regulation. Bhw-432kv | N/349
NR140008 | 106093 | 400KV AGRA-BHIWADI-I | 2013-06-09 17:45 | 2013-06-10 10:35 | 0 | 0 | 0 | 0.70139 | LVRD | Line hand tripped for Voltage regulation. Bhw-433kv. | N-589
NR140008 | 106102 | 400KV AGRA-BHIWADI-I | 2013-06-11 02:03 | 2013-06-11 08:58 | 0 | 0 | 0 | 0.28819 | LVRD | Line hand tripped for Voltage regulation. Bhw-433kv. | N/708
NR140008 | 106131 | 400KV AGRA-BHIWADI-I | 2013-06-12 04:18 | 2013-06-12 09:42 | 0 | 0 | 0 | 0.225 | LVRD | Line hand tripped for Voltage regulation. Bhw-436kv. | N-816
NR140008 | 106149 | 400KV AGRA-BHIWADI-I | 2013-06-15 04:03 | 2013-06-15 07:51 | 0 | 0 | 0 | 0.15833 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N/1048
NR140008 | 106310 | 400KV AGRA-BHIWADI-I | 2013-06-29 17:34 | 2013-06-29 23:56 | 0 | 0 | 0 | 0.26528 | LVRD | Line hand tripped for Voltage regulation. Ag=428 kv | N/2103
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-01 09:34
NR140009 | 106021 | 400KV AGRA-BHIWADI-II | 2013-06-02 18:08 | 2013-06-02 22:41 | 0 | 0 | 0 | 0.18958 | LVRD | Hand tripped for voltage regulation. Bhwd>430kv. | N-74
NR140009 | 106134 | 400KV AGRA-BHIWADI-II | 2013-06-13 07:31 | 2013-06-13 12:51 | 0 | 0 | 0 | 0.22222 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N/882
NR140009 | 106156 | 400KV AGRA-BHIWADI-II | 2013-06-15 13:30 | 2013-06-16 20:11 | 0 | 0 | 0 | 1899-12-31 06:41 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N-1070
NR140009 | 106179 | 400KV AGRA-BHIWADI-II | 2013-06-16 21:46 | 2013-06-17 09:10 | 0 | 0 | 0 | 0.475 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N-1175
NR140009 | 106201 | 400KV AGRA-BHIWADI-II | 2013-06-18 02:20 | 2013-06-18 08:40 | 0 | 0 | 0 | 0.26389 | LVRD | Line hand tripped for Voltage regulation. Bhw-430kv. | N-1299
NR140009 | 106213 | 400KV AGRA-BHIWADI-II | 2013-06-18 21:59 | 2013-06-19 11:40 | 0 | 0 | 0 | 0.57014 | LVRD | Line hand tripped for Voltage regulation. Bhw-431kv. | N-1376
NR140009 | 106232 | 400KV AGRA-BHIWADI-II | 2013-06-20 04:10 | 2013-06-20 12:10 | 0 | 0 | 0 | 0.33333 | LVRD | Line hand tripped for Voltage regulation. Bhw-431kv. | N-1455
NR140009 | 106259 | 400KV AGRA-BHIWADI-II | 2013-06-23 18:19 | 2013-06-24 09:32 | 0 | 0 | 0 | 0.63403 | LVRD | Line hand tripped for Voltage regulation. Bhw-431kv. | N-1664
NR140009 | 106286 | 400KV AGRA-BHIWADI-II | 2013-06-28 02:18 | 2013-06-28 09:36 | 0 | 0 | 0 | 0.30417 | LVRD | Line hand tripped for Voltage regulation. Ag=429kv | N-1965
NR140009 | 106302 | 400KV AGRA-BHIWADI-II | 2013-06-29 04:18 | 2013-06-29 09:17 | 0 | 0 | 0 | 0.20764 | LVRD | Line hand tripped for Voltage regulation. Ag=429kv | N-2043
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-03 11:29
NR140010 | 105193 | 400KV AGRA-BLBGRH | 2013-05-26 12:06 | 2013-05-26 22:03 | 0.41458 | 0 | 0 | 0 | OSFT | Forecd S/D to replace faulty Y-ph CVT at Agra. | N-1381
|  | SUB TOTAL |  |  | 0.41458 | 0 | 0 | 0
NR140116 | 106036 | 400KV AGRA-JAIPUR(S)-I | 2013-06-04 17:33 | 2013-06-04 18:05 | 0.022222 | 0 | 0 | 0 | OMST | Tripped on B-N fault caused during heavy wind strom. FLR:Agra=269km, Jaipur(S)=0.13km.
NR140116 | 106066 | 400KV AGRA-JAIPUR(S)-I | 2013-06-06 17:14 | 2013-06-06 18:51 | 0 | 0 | 0 | 0.067361 | LVRD | Line hand tripped for Voltage regulation. Agra-428kv | N/355
NR140116 | 106099 | 400KV AGRA-JAIPUR(S)-I | 2013-06-10 15:32 | 2013-06-10 18:57 | 0.14236 | 0 | 0 | 0 | OSPT | S/D for attend hot spot at Jaipur-S on line reactor
NR140116 | 106161 | 400KV AGRA-JAIPUR(S)-I | 2013-06-15 16:20 | 2013-06-15 21:32 | 0 | 0 | 0 | 0.21667 | LVRD | Line hand tripped for Voltage regulation. Jpr(S)-434kv. | N-1086
NR140116 | 106288 | 400KV AGRA-JAIPUR(S)-I | 2013-06-28 03:04 | 2013-06-28 10:10 | 0 | 0 | 0 | 0.29583 | LVRD | Line hand tripped for Voltage regulation. Ag=429kv | N-1970
NR140116 | 106313 | 400KV AGRA-JAIPUR(S)-I | 2013-06-29 17:43 | 2013-06-29 23:53 | 0 | 0 | 0 | 0.25694 | LVRD | Line hand tripped for Voltage regulation agra-427 KV | N/2106
|  | SUB TOTAL |  |  | 0.16458 | 0 | 0 | 0.83681
NR140126 | 106120 | 400KV AGRA-JAIPUR(S)-II | 2013-06-11 13:20 | 2013-06-11 19:52 | 0 | 0 | 0 | 0.27222 | LVRD | Line hand tripped for Voltage regulation. Jpr(S)-434kv. | N-778
NR140126 | 106162 | 400KV AGRA-JAIPUR(S)-II | 2013-06-15 16:20 | 2013-06-16 20:04 | 0 | 0 | 0 | 1899-12-31 03:44 | LVRD | Line hand tripped for Voltage regulation. Jpr(S)-434kv. | N-1086
NR140126 | 106180 | 400KV AGRA-JAIPUR(S)-II | 2013-06-16 21:49 | 2013-06-17 09:04 | 0 | 0 | 0 | 0.46875 | LVRD | Line hand tripped for Voltage regulation. Jpr(S)-434kv. | N-1175
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 21:31
NR140018 | 105240 | 400KV BALIA-BIHARSHRF-II | 2013-06-01 | 2013-06-01 19:28 | 0.81111 | 0 | 0 | 0 | OMST | Trip on B-N fault during heavy rain and Wind storm. Balia=30km, B/Sarif=185km. Out since 1800hrs of 31/05/13.
NR140018 | 106012 | 400KV BALIA-BIHARSHRF-II | 2013-06-01 19:28 | 2013-06-02 14:18 | 0.78472 | 0 | 0 | 0 | OSPT | S/D by ER for anuual line maintenance work. | N-45
NR140018 | 106061 | 400KV BALIA-BIHARSHRF-II | 2013-06-06 17:08 | 2013-06-06 19:12 | 0.086111 | 0 | 0 | 0 | OMST | Line tripped on Y-N fault during heavy storm. Ballia-196km.
|  | SUB TOTAL |  |  | 1899-12-31 16:22 | 0 | 0 | 0
NR140021 | 106069 | 400KV BALIA-PATNA-I | 2013-06-06 17:16 | 2013-06-07 01:14 | 0 | 0 | 0 | 0.33194 | LVRD | Line hand tripped for Voltage regulation. Balia-430kv | N/356
NR140021 | 106086 | 400KV BALIA-PATNA-I | 2013-06-08 18:05 | 2013-06-09 15:36 | 0 | 0 | 0 | 0.89653 | LVRD | Line hand tripped for Voltage regulation. Balia-430kv. | N-545
NR140021 | 106157 | 400KV BALIA-PATNA-I | 2013-06-15 13:50 | 2013-06-17 09:38 | 0 | 0 | 0 | 1899-12-31 19:48 | LVRD | Line hand tripped for Voltage regulation. Balia-430kv. | N-1072
NR140021 | 106317 | 400KV BALIA-PATNA-I | 2013-06-30 02:14 | 2013-06-30 09:44 | 0 | 0 | 0 | 0.3125 | LVRD | Line hand tripped for Voltage regulation.ballia-430 KV | N/2136
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-02 08:47
NR140022 | 105243 | 400KV BALIA-PATNA-II | 2013-06-01 | 2013-06-01 09:15 | 0 | 0 | 0 | 0.38542 | LVRD | Kept open for v/ regulation. Out since 1849hrs of 31/05/13. | N-1709
NR140022 | 106004 | 400KV BALIA-PATNA-II | 2013-06-01 09:15 | 2013-06-01 18:29 | 0.38472 | 0 | 0 | 0 | OSPT | S/D by ER for anuual line maintenance work. | N-08
NR140022 | 106082 | 400KV BALIA-PATNA-II | 2013-06-08 06:11 | 2013-06-08 14:20 | 0 | 0 | 0 | 0.33958 | LVRD | Line hand tripped for Voltage regulation. Balia-430kv | N-512
NR140022 | 106092 | 400KV BALIA-PATNA-II | 2013-06-09 17:18 | 2013-06-10 05:06 | 0 | 0 | 0 | 0.49167 | LVRD | Line hand tripped for Voltage regulation. Balia-430kv. | N-586
|  | SUB TOTAL |  |  | 0.38472 | 0 | 0 | 1899-12-31 05:12
NR140137 | 106282 | 400KV BALIA-PATNA-IV | 2013-06-27 06:52 | 2013-06-27 08:51 | 0 | 0 | 0 | 0.082639 | LVRD | Line hand tripped for Voltage regulation. Balia-429kv.
NR140137 | 106293 | 400KV BALIA-PATNA-IV | 2013-06-28 06:45 | 2013-06-28 06:50 | 0 | 0 | 0.0034722 | 0 | GOVC | Trip on O/VOL protn at Patna>441kv. D/T recd at Balia.
NR140137 | 106294 | 400KV BALIA-PATNA-IV | 2013-06-28 06:50 | 2013-06-28 12:42 | 0 | 0 | 0 | 0.24444 | LVRD | Kept open for VOL/Regulation. Balia-428kv. | N-1977
NR140137 | 106316 | 400KV BALIA-PATNA-IV | 2013-06-30 02:13 | 2013-06-30 19:56 | 0 | 0 | 0 | 0.73819 | LVRD | Line hand tripped for Voltage regulation.ballia-430 KV | N/2137
|  | SUB TOTAL |  |  | 0 | 0 | 0.0034722 | 1899-12-31 01:34
NR140140 | 106220 | 400KV BALIA-SOHAWAL-I | 2013-07-19 07:00 | 2013-07-19 07:05 | 0 | 0 | 0.0034722 | 0 | GOVC | O/V protn oprtd at Sohawal>438kv. D/T rec d at Balia.
NR140140 | 106222 | 400KV BALIA-SOHAWAL-I | 2013-06-19 07:05 | 2013-06-19 09:40 | 0 | 0 | 0 | 0.10764 | LVRD | Kept open for Voltage regulation. Balia-427kv. | N-1398
NR140140 | 106229 | 400KV BALIA-SOHAWAL-I | 2013-06-19 13:37 | 2013-06-19 14:08 | 0.021528 | 0 | 0 | 0 | OMST | Tripped on L/Reactor NGR-PRD maloperation at Sohwal.
|  | SUB TOTAL |  |  | 0.021528 | 0 | 0.0034722 | 0.10764
NR140120 | 106124 | 400KV BALIA-SOHAWAL-II | 2013-06-12 01:43 | 2013-06-12 01:54 | 0 | 0 | 0.0076389 | 0 | GOVC | Trip on O/VOL protn at Showal=437kv.
NR140120 | 106221 | 400KV BALIA-SOHAWAL-II | 2013-07-19 07:00 | 2013-07-19 07:05 | 0 | 0 | 0.0034722 | 0 | GOVC | O/V protn oprtd at Sohawal>438kv. D/T rec d at Balia.
NR140120 | 106223 | 400KV BALIA-SOHAWAL-II | 2013-06-19 07:05 | 2013-06-19 08:55 | 0 | 0 | 0 | 0.076389 | LVRD | Kept open for Voltage regulation. Balia-427kv. | N-1398
|  | SUB TOTAL |  |  | 0 | 0 | 0.011111 | 0.076389
NR140024 | 106165 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-15 17:54 | 2013-06-15 20:16 | 0 | 0 | 0 | 0.098611 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-1093
NR140024 | 106170 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-16 10:00 | 2013-06-16 17:09 | 0 | 0 | 0 | 0.29792 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-1127
NR140024 | 106234 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-20 10:09 | 2013-06-20 21:03 | 0 | 0 | 0 | 0.45417 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-1472
NR140024 | 106239 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-21 09:35 | 2013-06-21 20:38 | 0 | 0 | 0 | 0.46042 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-1534
NR140024 | 106245 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-22 09:15 | 2013-06-22 20:04 | 0 | 0 | 0 | 0.45069 | LCSD | S/D for OPGW instalation work in highly inductive area. | N/1593
NR140024 | 106255 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-23 09:05 | 2013-06-23 20:16 | 0 | 0 | 0 | 0.46597 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-1643
NR140024 | 106275 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-26 09:59 | 2013-06-26 20:26 | 0 | 0 | 0 | 0.43542 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-1843
NR140024 | 106305 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-29 09:05 | 2013-06-29 20:47 | 0 | 0 | 0 | 0.4875 | LCSD | S/D for OPGW instalation work in highly inductive area. | N/2055
NR140024 | 106331 | 400KV BAREILLY-BRLY(UP)-II | 2013-06-30 11:03 | 2013-06-30 18:56 | 0 | 0 | 0 | 0.32847 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-2158
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-02 11:30
NR140025 | 106159 | 400KV BAREILLY-LKO(UP) | 2013-06-15 15:58 | 2013-06-15 16:20 | 0 | 0.015278 | 0 | 0 | OMSU | A/R and trip on Y-N fault due to kite thread. FLR:Bly-227.7km.
|  | SUB TOTAL |  |  | 0 | 0.015278 | 0 | 0
NR140028 | 106063 | 400KV BASSI-BHIWADI-I | 2013-06-06 17:10 | 2013-06-06 19:05 | 0 | 0 | 0 | 0.079861 | LVRD | Line hand tripped for Voltage regulation. Bhw-432kv | N/350
NR140028 | 106103 | 400KV BASSI-BHIWADI-I | 2013-06-11 02:03 | 2013-06-11 04:25 | 0 | 0 | 0 | 0.098611 | LVRD | Line hand tripped for Voltage regulation. Bhw-433kv. | N/708
NR140028 | 106122 | 400KV BASSI-BHIWADI-I | 2013-06-11 13:24 | 2013-06-11 19:58 | 0 | 0 | 0 | 0.27361 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N-779
NR140028 | 106148 | 400KV BASSI-BHIWADI-I | 2013-06-15 03:17 | 2013-06-15 07:42 | 0 | 0 | 0 | 0.18403 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N/1047
NR140028 | 106182 | 400KV BASSI-BHIWADI-I | 2013-06-16 21:54 | 2013-06-17 11:05 | 0 | 0 | 0 | 0.54931 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N-1176
NR140028 | 106202 | 400KV BASSI-BHIWADI-I | 2013-06-18 02:21 | 2013-06-18 08:42 | 0 | 0 | 0 | 0.26458 | LVRD | Line hand tripped for Voltage regulation. Bhw-430kv. | N-1299
NR140028 | 106214 | 400KV BASSI-BHIWADI-I | 2013-06-18 22:00 | 2013-06-19 12:51 | 0 | 0 | 0 | 0.61875 | LVRD | Line hand tripped for Voltage regulation. Bhw-431kv. | N-1376
NR140028 | 106309 | 400KV BASSI-BHIWADI-I | 2013-06-29 17:31 | 2013-06-29 23:43 | 0 | 0 | 0 | 0.25833 | LVRD | Line hand tripped for Voltage regulation. Bassi-431 KV | N/2103
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-01 07:51
NR140029 | 106168 | 400KV BASSI-BHIWADI-II | 2013-06-16 01:11 | 2013-06-16 20:12 | 0 | 0 | 0 | 0.79236 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N-1112
NR140029 | 106236 | 400KV BASSI-BHIWADI-II | 2013-06-20 13:10 | 2013-06-20 14:43 | 0.064583 | 0 | 0 | 0 | OSPT | S/D for tree lopping work by Bassi. | N-1489
NR140029 | 106327 | 400KV BASSI-BHIWADI-II | 2013-06-30 04:17 | 2013-06-30 23:45 | 0 | 0 | 0 | 0.81111 | LVRD | Line hand tripped for Voltage regulation BHI-428 KV | N/2145
|  | SUB TOTAL |  |  | 0.064583 | 0 | 0 | 1899-12-31 14:29
NR140030 | 106023 | 400KV BASSI-HIRAPURA-I | 2013-06-03 10:35 | 2013-06-03 16:25 | 0 | 0 | 0 | 0.24306 | OSPD | S/D by RRVPNL for bay maintenance work. | N-102
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.24306
NR140031 | 106034 | 400KV BASSI-HIRAPURA-II | 2013-06-04 11:15 | 2013-06-04 17:02 | 0 | 0 | 0 | 0.24097 | OSPD | S/D by RRVPNL for bay maintenance work. | N-173
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.24097
NR140117 | 106067 | 400KV BASSI-JAIPUR(S)-I | 2013-06-06 17:14 | 2013-06-06 18:53 | 0 | 0 | 0 | 0.06875 | LVRD | Line hand tripped for Voltage regulation. Agra-428kv | N/355
NR140117 | 106139 | 400KV BASSI-JAIPUR(S)-I | 2013-06-14 07:03 | 2013-06-14 21:12 | 0 | 0 | 0 | 0.58958 | LCSD | S/D for stringing of 400kv Bassi-Phagi line. | N/962
NR140117 | 106152 | 400KV BASSI-JAIPUR(S)-I | 2013-06-15 08:21 | 2013-06-15 21:14 | 0 | 0 | 0 | 0.53681 | LCSD | S/D for stringing of 400kv Bassi-Phagi line. | N-1060
NR140117 | 106181 | 400KV BASSI-JAIPUR(S)-I | 2013-06-16 21:52 | 2013-06-17 09:09 | 0 | 0 | 0 | 0.47014 | LVRD | Line hand tripped for Voltage regulation. Jpr(S)-434kv. | N-1175
NR140117 | 106237 | 400KV BASSI-JAIPUR(S)-I | 2013-06-20 14:57 | 2013-06-20 19:00 | 0.16875 | 0 | 0 | 0 | OSFT | S/D to attend hotspot on B-ph Line Isolator at Jaipur(S). | N-1495
NR140117 | 106289 | 400KV BASSI-JAIPUR(S)-I | 2013-06-28 03:08 | 2013-06-28 10:02 | 0 | 0 | 0 | 0.2875 | LVRD | Line hand tripped for Voltage regulation. Ag=429kv | N-1970
NR140117 | 106314 | 400KV BASSI-JAIPUR(S)-I | 2013-06-29 17:46 | 2013-06-29 23:46 | 0 | 0 | 0 | 0.25 | LVRD | Line hand tripped for Voltage regulation. agra-427 KV | N/2106
|  | SUB TOTAL |  |  | 0.16875 | 0 | 0 | 1900-01-01 04:52
NR140127 | 106121 | 400KV BASSI-JAIPUR(S)-II | 2013-06-11 13:27 | 2013-06-11 19:50 | 0 | 0 | 0 | 0.26597 | LVRD | Line hand tripped for Voltage regulation. Jpr(S)-434kv. | N-778
NR140127 | 106140 | 400KV BASSI-JAIPUR(S)-II | 2013-06-14 07:03 | 2013-06-14 21:13 | 0 | 0 | 0 | 0.59028 | LCSD | S/D for stringing of 400kv Bassi-Phagi line. | N/962
NR140127 | 106153 | 400KV BASSI-JAIPUR(S)-II | 2013-06-15 08:21 | 2013-06-15 21:16 | 0 | 0 | 0 | 0.53819 | LCSD | S/D for stringing of 400kv Bassi-Phagi line. | N-1060
NR140127 | 106166 | 400KV BASSI-JAIPUR(S)-II | 2013-06-15 23:20 | 2013-06-15 23:53 | 0.022917 | 0 | 0 | 0 | OSFT | Forced S/D to attend R-ph L/Isolator sparking at Jaipur(S). | N-1109
NR140127 | 106167 | 400KV BASSI-JAIPUR(S)-II | 2013-06-16 00:36 | 2013-06-16 20:12 | 0 | 0 | 0 | 0.81667 | LVRD | Line hand tripped for Voltage regulation. Jpr(S)-434kv. | N-1111
|  | SUB TOTAL |  |  | 0.022917 | 0 | 0 | 1900-01-01 05:04
NR140032 | 106088 | 400KV BHIWADI-GURGAON | 2013-06-09 10:16 | 2013-06-09 19:37 | 0 | 0 | 0 | 0.38958 | LCSD | S/D for replacement of BUS-I isolator at Gurgaon. | N-573
NR140032 | 106110 | 400KV BHIWADI-GURGAON | 2013-06-11 02:19 | 2013-06-11 02:25 | 0 | 0 | 0.0041667 | 0 | GOVC | Tripped on Over Voltage protection.
NR140032 | 106112 | 400KV BHIWADI-GURGAON | 2013-06-11 02:25 | 2013-06-11 04:19 | 0 | 0 | 0 | 0.079167 | LVRD | Kept open for voltage regulation due to high grid voltage | N/726
|  | SUB TOTAL |  |  | 0 | 0 | 0.0041667 | 0.46875
NR140106 | 106064 | 400KV BHIWADI-NIMRANA-I | 2013-06-06 17:12 | 2013-06-06 19:05 | 0 | 0 | 0 | 0.078472 | LVRD | Line hand tripped for Voltage regulation. Bhw-432kv | N/353
NR140106 | 106109 | 400KV BHIWADI-NIMRANA-I | 2013-06-11 02:17 | 2013-06-11 03:03 | 0 | 0 | 0 | 0.031944 | LVRD | Line hand tripped for Voltage regulation. Bhw-436kv. | N/714
NR140106 | 106175 | 400KV BHIWADI-NIMRANA-I | 2013-06-16 17:11 | 2013-06-16 20:35 | 0 | 0 | 0 | 0.14167 | LVRD | Line hand tripped for Voltage regulation. Bhw-434kv. | N-1146
NR140106 | 106186 | 400KV BHIWADI-NIMRANA-I | 2013-06-17 01:29 | 2013-06-17 11:52 | 0 | 0 | 0 | 0.43264 | LVRD | Line hand tripped for Voltage regulation. Nim-434kv | N-1188
NR140106 | 106297 | 400KV BHIWADI-NIMRANA-I | 2013-06-28 09:49 | 2013-06-28 19:26 | 0 | 0 | 0 | 0.40069 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-1985
NR140106 | 106328 | 400KV BHIWADI-NIMRANA-I | 2013-06-30 04:21 | 2013-06-30 22:38 | 0 | 0 | 0 | 0.76181 | LVRD | Line hand tripped for Voltage regulation BHI-428 KV | N/2146
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 20:20
NR140035 | 106033 | 400KV BLBGRH-GURGAON | 2013-06-04 10:50 | 2013-06-04 20:04 | 0 | 0 | 0 | 0.38472 | LCSD | S/D for Bus extension work at GIS Gurgaon. | N-170
NR140035 | 106059 | 400KV BLBGRH-GURGAON | 2013-06-06 15:32 | 2013-06-06 15:42 | 0.0069444 | 0 | 0 | 0 | OMST | Tripped on R-N fault during heavy storm, FLR:Ggn-1.9km.
NR140035 | 106085 | 400KV BLBGRH-GURGAON | 2013-06-08 09:58 | 2013-06-10 11:38 | 0 | 0 | 0 | 1900-01-01 01:40 | LCSD | S/D for Bus extension work at GIS Gurgaon. | N-521
|  | SUB TOTAL |  |  | 0.0069444 | 0 | 0 | 1900-01-01 10:54
NR140037 | 106199 | 400KV BLBGRH-MAINPURI-I | 2013-06-18 01:23 | 2013-06-18 05:37 | 0 | 0 | 0 | 0.17639 | LVRD | Line hand tripped for Voltage regulation. Mnp-432kv. | N-1296
NR140037 | 106003 | 400KV BLBGRH-MAINPURI-I | 2013-06-01 08:12 | 2013-06-01 10:31 | 0 | 0 | 0 | 0.096528 | LVRD | Hand tripped for voltage regulation. Mnpr>430kv. | N-05
NR140037 | 106068 | 400KV BLBGRH-MAINPURI-I | 2013-06-06 17:15 | 2013-06-06 19:22 | 0 | 0 | 0 | 0.088194 | LVRD | Line hand tripped for Voltage regulation. Mnp-433kv | N/352
NR140037 | 106113 | 400KV BLBGRH-MAINPURI-I | 2013-06-11 02:33 | 2013-06-11 09:07 | 0 | 0 | 0 | 0.27361 | LVRD | Line hand tripped for Voltage regulation. Mnp-432kv. | N/718
NR140037 | 106135 | 400KV BLBGRH-MAINPURI-I | 2013-06-13 07:49 | 2013-06-13 15:33 | 0 | 0 | 0 | 0.32222 | LVRD | Line hand tripped for Voltage regulation. Mnp-433kv | N/884
NR140037 | 106146 | 400KV BLBGRH-MAINPURI-I | 2013-06-14 19:12 | 2013-06-15 00:04 | 0 | 0 | 0 | 0.20278 | LVRD | Line hand tripped for Voltage regulation. Mnp-433kv | N/1027
NR140037 | 106216 | 400KV BLBGRH-MAINPURI-I | 2013-06-19 00:44 | 2013-06-19 06:06 | 0 | 0 | 0 | 0.22361 | LVRD | Line hand tripped for Voltage regulation. Mnp-432kv. | N-1388
NR140037 | 106231 | 400KV BLBGRH-MAINPURI-I | 2013-06-20 04:05 | 2013-06-20 08:48 | 0 | 0 | 0 | 0.19653 | LVRD | Line hand tripped for Voltage regulation. MNP=435kv. | N-1453
NR140037 | 106267 | 400KV BLBGRH-MAINPURI-I | 2013-06-24 21:08 | 2013-06-24 21:10 | 0 | 0.0013889 | 0 | 0 | OMSU | CB A/trip at Blb during failure of Fthpr-I line FSC at Mnpr.
NR140037 | 106287 | 400KV BLBGRH-MAINPURI-I | 2013-06-28 02:22 | 2013-06-28 09:32 | 0 | 0 | 0 | 0.29861 | LVRD | Line hand tripped for Voltage regulation. MNP=438kv | N-1966
NR140037 | 106311 | 400KV BLBGRH-MAINPURI-I | 2013-06-29 17:35 | 2013-06-30 13:58 | 0 | 0 | 0 | 0.84931 | LVRD | Line hand tripped for Voltage regulation. mainpuri-432 KV | N/2104
|  | SUB TOTAL |  |  | 0 | 0.0013889 | 0 | 1900-01-01 17:28
NR140038 | 106147 | 400KV BLBGRH-MAINPURI-II | 2013-06-15 02:49 | 2013-06-17 11:22 | 0 | 0 | 0 | 1900-01-01 08:33 | LVRD | Line hand tripped for Voltage regulation. Mnp-433kv | N/1045
NR140038 | 106268 | 400KV BLBGRH-MAINPURI-II | 2013-06-24 21:08 | 2013-06-24 21:10 | 0 | 0.0013889 | 0 | 0 | OMSU | CB A/trip at Blb during failure of Fthpr-I line FSC at Mnpr.
|  | SUB TOTAL |  |  | 0 | 0.0013889 | 0 | 1900-01-01 08:33
NR140138 | 106252 | 400KV BLBGRH-NAVADA | 2013-06-22 12:25 | 2013-06-22 13:10 | 0 | 0 | 0 | 0.03125 | OSPD | S/D by Nawada-HVPNL for bay isolation work. | N-1601
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.03125
NR140040 | 106054 | 400KV DAD-MAHRANIBG | 2013-06-06 12:52 | 2013-06-06 13:02 | 0 | 0.0069444 | 0 | 0 | OMSU | D/T received at Mahranibag during some testing by NTPC at Dadri.
NR140040 | 106097 | 400KV DAD-MAHRANIBG | 2013-06-10 11:13 | 2013-06-11 20:10 | 0 | 0 | 0 | 1899-12-31 08:57 | OSFD | Forced S/D by NTPC to attend B-ph CT oil leackage. | N-647
NR140040 | 106261 | 400KV DAD-MAHRANIBG | 2013-06-24 10:20 | 2013-06-24 18:52 | 0 | 0 | 0 | 0.35556 | OSPD | S/D by DADRI/NTPC for CB re-jumpering work. | N-1718
|  | SUB TOTAL |  |  | 0 | 0.0069444 | 0 | 1899-12-31 17:29
NR140041 | 106071 | 400KV DAD-MANDOLA-I | 2013-06-06 17:39 | 2013-06-06 17:53 | 0.0097222 | 0 | 0 | 0 | OMST | Line A/R and tripped in reclaim time on B-N fault during online OPGW stringing, FLR:MND-22.66km,
NR140041 | 106079 | 400KV DAD-MANDOLA-I | 2013-06-07 10:34 | 2013-06-07 18:32 | 0 | 0 | 0 | 0.33194 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-444
|  | SUB TOTAL |  |  | 0.0097222 | 0 | 0 | 0.33194
NR140043 | 106283 | 400KV DAD-MURADNGR | 2013-06-27 08:29 | 2013-06-27 21:30 | 0 | 0 | 0 | 0.54236 | LCSD | S/D for installation of Polymer insulator strings. | N-1911
NR140043 | 106296 | 400KV DAD-MURADNGR | 2013-06-28 09:11 | 2013-06-28 22:07 | 0 | 0 | 0 | 0.53889 | LCSD | S/D for installation of Polymer insulator strings. | N-1982
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 01:57
NR140044 | 106072 | 400KV DAD-PANIPAT-I | 2013-06-06 17:45 | 2013-06-06 18:45 | 0.041667 | 0 | 0 | 0 | OMST | Line tripped on Y-B-N fault during heavy storm. Dad-16km.
NR140044 | 106123 | 400KV DAD-PANIPAT-I | 2013-06-12 00:19 | 2013-06-12 00:45 | 0 | 0.018056 | 0 | 0 | OMSU | A/R at Dadri but trip from PPT/BBMB on B-N fault due to relay problem at PPT. FLR:DDR=37.46km PPT=54km
NR140044 | 106215 | 400KV DAD-PANIPAT-I | 2013-06-18 23:43 | 2013-06-18 23:59 | 0 | 0.011111 | 0 | 0 | OMSU | A/R at Dadri but trip from Panipat-BBMB due to A/R relay problem on B-N fault. FLR:Dad-78km, Ppt-21.7km.
NR140044 | 106224 | 400KV DAD-PANIPAT-I | 2013-06-19 07:46 | 2013-06-20 19:44 | 0 | 0 | 0 | 1899-12-31 11:58 | LCSD | S/D by NR-II for stringing work. S/D extend by NTPC for Isolator retrofitment work at DDR(Th). | N-1400
NR140044 | 106290 | 400KV DAD-PANIPAT-I | 2013-06-28 04:17 | 2013-06-28 04:42 | 0 | 0.017361 | 0 | 0 | OMSU | A/R at Dadri but trip from Panipat on Y-N fault due to BBMB A/R relay problem. FLR:Dad-31km, PPT-68km.
|  | SUB TOTAL |  |  | 0.041667 | 0.046528 | 0 | 1899-12-31 11:58
NR140045 | 106308 | 400KV DAD-PANIPAT-II | 2013-06-29 17:01 | 2013-06-29 17:38 | 0 | 0.025694 | 0 | 0 | OMSU | A/R at Dadri but tripped at Panipat on R-N fault due to A/R relay problem. FLR:Dadri-46.9kms, Pnpt-50.27 kms
|  | SUB TOTAL |  |  | 0 | 0.025694 | 0 | 0
NR140124 | 106203 | 400KV FATEHPUR-MAINPURI-I | 2013-06-18 03:43 | 2013-06-18 05:40 | 0 | 0 | 0 | 0.08125 | LVRD | Line hand tripped for Voltage regulation. Mnp-432kv. | N-1304
NR140124 | 106070 | 400KV FATEHPUR-MAINPURI-I | 2013-06-06 17:46 | 2013-06-06 19:18 | 0 | 0 | 0 | 0.063889 | LVRD | Line hand tripped for Voltage regulation. Mnp-433kv | N/366
NR140124 | 106218 | 400KV FATEHPUR-MAINPURI-I | 2013-06-19 01:09 | 2013-06-19 09:04 | 0 | 0 | 0 | 0.32986 | LVRD | Line hand tripped for Voltage regulation. Mnp-432kv. | N-1390
NR140124 | 106264 | 400KV FATEHPUR-MAINPURI-I | 2013-06-24 15:33 | 2013-06-24 19:14 | 0.15347 | 0 | 0 | 0 | OSPT | S/D for attending hot spot in Y-ph WT at Mainpuri. | N-1737
NR140124 | 106266 | 400KV FATEHPUR-MAINPURI-I | 2013-06-24 21:08 | 2013-06-24 21:36 | 0.019444 | 0 | 0 | 0 | OMST | Tripped due to FSC Damping Resistor failure at Mainpuri.
NR140124 | 106291 | 400KV FATEHPUR-MAINPURI-I | 2013-06-28 04:30 | 2013-06-28 09:29 | 0 | 0 | 0 | 0.20764 | LVRD | Line hand tripped for Voltage regulation. MNP=438kv | N-1972
NR140124 | 106312 | 400KV FATEHPUR-MAINPURI-I | 2013-06-29 17:40 | 2013-06-29 20:08 | 0 | 0 | 0 | 0.10278 | LVRD | Line hand tripped for Voltage regulation. mainpuri-432 KV | N/2105
NR140124 | 106318 | 400KV FATEHPUR-MAINPURI-I | 2013-06-30 02:51 | 2013-06-30 14:03 | 0 | 0 | 0 | 0.46667 | LVRD | Line hand tripped for Voltage regulation Fatehpur-436 KV | N/2138
|  | SUB TOTAL |  |  | 0.17292 | 0 | 0 | 1899-12-31 06:03
NR140125 | 106160 | 400KV FATEHPUR-MAINPURI-II | 2013-06-15 16:05 | 2013-06-16 20:11 | 0 | 0 | 0 | 1899-12-31 04:06 | LVRD | Line hand tripped for Voltage regulation. Mnpr-432kv. | N-1083
NR140125 | 106184 | 400KV FATEHPUR-MAINPURI-II | 2013-06-16 23:56 | 2013-06-17 10:38 | 0 | 0 | 0 | 0.44583 | LVRD | Line hand tripped for Voltage regulation. Mnp-432kv. | N-1180
NR140125 | 106280 | 400KV FATEHPUR-MAINPURI-II | 2013-06-27 01:40 | 2013-06-27 01:55 | 0 | 0 | 0.010417 | 0 | GOVC | Tripped on O/V protn at Fatehpur. D/T recd at Mainpuri.
NR140125 | 106281 | 400KV FATEHPUR-MAINPURI-II | 2013-06-27 01:55 | 2013-06-27 03:24 | 0 | 0 | 0 | 0.061806 | LVRD | Kept open for Voltage regulation. Fthpr-428kv.
|  | SUB TOTAL |  |  | 0 | 0 | 0.010417 | 1899-12-31 16:17
NR140047 | 106209 | 400KV GORAKH-GORAKH-II | 2013-06-18 16:54 | 2013-06-18 18:00 | 0 | 0.045833 | 0 | 0 | SBBU | Tripped on Bus Bar protn oprtn at UPPCL S/S Gkhpr.
|  | SUB TOTAL |  |  | 0 | 0.045833 | 0 | 0
NR140128 | 103056 | 400KV GURGAON-MANESAR-I | 2013-06-01 | 2013-06-04 10:15 | 0 | 0 | 0 | 1900-01-02 10:15 | LCSD | S/D for Gurgaon GIS Bus-I extention work. Out since 1242hrs of 06/03/13. | N-520
NR140128 | 106056 | 400KV GURGAON-MANESAR-I | 2013-06-06 13:01 | 2013-06-06 22:58 | 0 | 0 | 0 | 0.41458 | LCSD | S/D for Bus extension work at GIS Gurgaon. | N/311
NR140128 | 106089 | 400KV GURGAON-MANESAR-I | 2013-06-09 10:17 | 2013-06-09 19:51 | 0 | 0 | 0 | 0.39861 | LCSD | S/D for BUS-I isolator erection work at GIS Gurgaon. | N-573
NR140128 | 106141 | 400KV GURGAON-MANESAR-I | 2013-06-14 10:45 | 2013-06-15 19:06 | 0 | 0 | 0 | 1899-12-31 08:21 | LCSD | S/D for Bus extension work at GIS Gurgaon. | N-976
NR140128 | 106196 | 400KV GURGAON-MANESAR-I | 2013-06-17 12:10 | 2013-06-17 17:43 | 0 | 0 | 0 | 0.23125 | LCSD | S/D for Bus-II extention work at GIS Gurgaon. | N-1255
NR140128 | 106235 | 400KV GURGAON-MANESAR-I | 2013-06-20 11:02 | 2013-06-20 18:53 | 0 | 0 | 0 | 0.32708 | LCSD | S/D for Bus-II High voltage Testing at GIS Gurgaon. | N-1477
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-05 03:31
NR140129 | 106019 | 400KV GURGAON-MANESAR-II | 2013-06-02 13:19 | 2013-06-02 21:10 | 0 | 0 | 0 | 0.32708 | LCSD | S/D for HV Testing of 400kv Bus-I at Gurgaon GIS. | N-64
NR140129 | 106024 | 400KV GURGAON-MANESAR-II | 2013-06-03 12:10 | 2013-06-03 18:55 | 0 | 0 | 0 | 0.28125 | LCSD | S/D for HV Testing of 400kv Bus-I at Gurgaon GIS. | N-115
NR140129 | 106055 | 400KV GURGAON-MANESAR-II | 2013-06-06 13:00 | 2013-06-06 22:56 | 0 | 0 | 0 | 0.41389 | LCSD | S/D for Bus extension work at GIS Gurgaon. | N/311
NR140129 | 106090 | 400KV GURGAON-MANESAR-II | 2013-06-09 10:17 | 2013-06-09 19:51 | 0 | 0 | 0 | 0.39861 | LCSD | S/D for BUS-I isolator erection work at GIS Gurgaon. | N-573
NR140129 | 106206 | 400KV GURGAON-MANESAR-II | 2013-06-18 09:49 | 2013-06-18 19:30 | 0 | 0 | 0 | 0.40347 | LCSD | S/D for Bus-II extention work at GIS Gurgaon. | N-1323
NR140129 | 106230 | 400KV GURGAON-MANESAR-II | 2013-06-19 14:56 | 2013-06-24 16:50 | 0 | 0 | 0 | 1900-01-04 01:54 | LCSD | S/D for Bus-II extention work at GIS Gurgaon. | N-1432
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-05 21:41
NR140132 | 106051 | 400KV JHATIKALA-BAMNOLI-I | 2013-06-06 09:15 | 2013-06-06 15:29 | 0 | 0 | 0 | 0.25972 | OSPD | S/D by DTL for their line maintenance work. | N/297
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.25972
NR140134 | 106060 | 400KV JHATIKALA-MUNDKA-I | 2013-06-06 16:41 | 2013-06-11 20:33 | 0 | 0 | 0 | 1900-01-04 03:52 | OSFD | Forced S/D by DTL to attend broken comductor as line tripped on R-N fault in their portion. FLR:Jhatikla-10.27km, | N-321
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-04 03:52
NR140050 | 106044 | 400KV KANKROLI-RAPPC-I | 2013-06-05 16:38 | 2013-06-05 17:00 | 0.015278 | 0 | 0 | 0 | OMST | Tripped during on line OPGW installation work on Y-B-N fault. FLR:KNK-154 kms.
NR140050 | 106045 | 400KV KANKROLI-RAPPC-I | 2013-06-05 17:18 | 2013-06-05 17:59 | 0.028472 | 0 | 0 | 0 | OMST | Tripped during on line OPGW installation work on R-B-N fault. FLR:KNK-119kms.
|  | SUB TOTAL |  |  | 0.04375 | 0 | 0 | 0
NR140052 | 106144 | 400KV KNP-AGRA | 2013-06-14 16:53 | 2013-06-14 18:26 | 0 | 0 | 0 | 0.064583 | LCSD | S/D for M-2 relay retrofitment work at Kanpur. | N-1006
NR140052 | 106322 | 400KV KNP-AGRA | 2013-06-30 03:58 | 2013-06-30 04:00 | 0 | 0 | 0.0013889 | 0 | GOVC | Tripped on Over Voltage protection at Agra.
NR140052 | 106324 | 400KV KNP-AGRA | 2013-06-30 04:00 | 2013-06-30 08:30 | 0 | 0 | 0 | 0.1875 | LVRD | Line hand tripped for Voltage regulationAgra-433 KV | N/2142
|  | SUB TOTAL |  |  | 0 | 0 | 0.0013889 | 0.25208
NR140055 | 106173 | 400KV KNP-BLBGARH-I | 2013-06-16 13:27 | 2013-06-16 19:50 | 0 | 0 | 0 | 0.26597 | LVRD | Line hand tripped for Voltage regulation. Blb-428kv. | N-1138
NR140055 | 106185 | 400KV KNP-BLBGARH-I | 2013-06-17 00:41 | 2013-06-17 11:16 | 0 | 0 | 0 | 0.44097 | LVRD | Line hand tripped for Voltage regulation. Blb-428kv. | N-1184
NR140055 | 106204 | 400KV KNP-BLBGARH-I | 2013-06-18 03:44 | 2013-06-18 05:42 | 0 | 0 | 0 | 0.081944 | LVRD | Line hand tripped for Voltage regulation. Mnp-432kv. | N-1305
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.78889
NR140056 | 106031 | 400KV KNP-BLBGARH-II | 2013-06-04 08:04 | 2013-06-04 19:53 | 0 | 0 | 0 | 0.49236 | LCSD | S/D for installation of polymer insulator strings. | N-158
NR140056 | 106050 | 400KV KNP-BLBGARH-II | 2013-06-06 07:45 | 2013-06-06 20:50 | 0 | 0 | 0 | 0.54514 | LCSD | S/D for installation of polymer insulator strings. | N/294
NR140056 | 106083 | 400KV KNP-BLBGARH-II | 2013-06-08 07:46 | 2013-06-08 20:13 | 0 | 0 | 0 | 0.51875 | LCSD | S/D for installation of polymer insulator strings. | N-517
NR140056 | 106117 | 400KV KNP-BLBGARH-II | 2013-06-11 08:01 | 2013-06-11 20:07 | 0 | 0 | 0 | 0.50417 | LCSD | S/D for installation of polymer insulator strings. | N-746
NR140056 | 106169 | 400KV KNP-BLBGARH-II | 2013-06-16 08:19 | 2013-06-16 19:54 | 0 | 0 | 0 | 0.48264 | LCSD | S/D for installation of polymer insulator strings. | N-1123
NR140056 | 106205 | 400KV KNP-BLBGARH-II | 2013-06-18 07:49 | 2013-06-18 20:20 | 0 | 0 | 0 | 0.52153 | LCSD | S/D for installation of Polymer insulator strings. | N-1314
NR140056 | 106233 | 400KV KNP-BLBGARH-II | 2013-06-20 07:21 | 2013-06-20 19:53 | 0 | 0 | 0 | 0.52222 | LCSD | S/D for installation of Polymer insulator strings. | N-1462
NR140056 | 106244 | 400KV KNP-BLBGARH-II | 2013-06-22 07:40 | 2013-06-22 19:22 | 0 | 0 | 0 | 0.4875 | LCSD | S/D for installation of Polymer insulator strings. | N-1584
NR140056 | 106274 | 400KV KNP-BLBGARH-II | 2013-06-26 09:32 | 2013-06-26 19:36 | 0 | 0 | 0 | 0.41944 | LCSD | S/D for polymer insulator replacement work. | N-1844
NR140056 | 106285 | 400KV KNP-BLBGARH-II | 2013-06-27 10:29 | 2013-06-27 20:17 | 0 | 0 | 0 | 0.40833 | LCSD | S/D for installation of Polymer insulator strings. | N-1929
NR140056 | 106303 | 400KV KNP-BLBGARH-II | 2013-06-29 04:30 | 2013-06-29 07:13 | 0 | 0 | 0 | 0.11319 | LVRD | Line hand tripped for Voltage regulation. BLB=427kv | N-2044
NR140056 | 106304 | 400KV KNP-BLBGARH-II | 2013-06-29 07:13 | 2013-06-29 19:49 | 0 | 0 | 0 | 0.525 | LCSD | S/D for installation of Polymer insulator strings. | N-2047
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-04 12:58
NR140057 | 106040 | 400KV KNP-BLBGARH-III | 2013-06-05 08:12 | 2013-06-05 19:11 | 0 | 0 | 0 | 0.45764 | LCSD | S/D for installation of polymer insulator strings. | N/226
NR140057 | 106080 | 400KV KNP-BLBGARH-III | 2013-06-07 11:40 | 2013-06-07 21:10 | 0 | 0 | 0 | 0.39583 | LCSD | S/D for installation of polymer insulator strings. | N-458
NR140057 | 106087 | 400KV KNP-BLBGARH-III | 2013-06-09 07:52 | 2013-06-09 20:12 | 0 | 0 | 0 | 0.51389 | LCSD | S/D for installation of polymer insulator strings. | N-571
NR140057 | 106133 | 400KV KNP-BLBGARH-III | 2013-06-12 08:18 | 2013-06-12 09:50 | 0 | 0 | 0 | 0.063889 | LCSD | S/D for installation of polymer insulator strings. | N-821
NR140057 | 106151 | 400KV KNP-BLBGARH-III | 2013-06-15 08:07 | 2013-06-15 20:22 | 0 | 0 | 0 | 0.51042 | LCSD | S/D for installation of polymer insulator strings. | N-1059
NR140057 | 106195 | 400KV KNP-BLBGARH-III | 2013-06-17 11:43 | 2013-06-17 20:06 | 0 | 0 | 0 | 0.34931 | LCSD | S/D for installation of Polymer insulator strings. | N-1250
NR140057 | 106225 | 400KV KNP-BLBGARH-III | 2013-06-19 08:24 | 2013-06-19 19:29 | 0 | 0 | 0 | 0.46181 | LCSD | S/D for installation of Polymer insulator strings. | N-1404
NR140057 | 106238 | 400KV KNP-BLBGARH-III | 2013-06-21 07:30 | 2013-06-21 19:00 | 0 | 0 | 0 | 0.47917 | LCSD | S/D for installation of Polymer insulator strings. | N-1527
NR140057 | 106254 | 400KV KNP-BLBGARH-III | 2013-06-23 07:58 | 2013-06-23 19:43 | 0 | 0 | 0 | 0.48958 | LCSD | S/D for installation of Polymer insulator strings. | N-1640
NR140057 | 106292 | 400KV KNP-BLBGARH-III | 2013-06-28 04:52 | 2013-06-28 07:45 | 0 | 0 | 0 | 0.12014 | LVRD | Line hand tripped for Voltage regulation. BLB=427kv | N-1974
NR140057 | 106295 | 400KV KNP-BLBGARH-III | 2013-06-28 07:45 | 2013-06-28 19:52 | 0 | 0 | 0 | 0.50486 | LCSD | S/D for installation of Polymer insulator strings. | N-1979
NR140057 | 106326 | 400KV KNP-BLBGARH-III | 2013-06-30 04:06 | 2013-06-30 09:35 | 0 | 0 | 0 | 0.22847 | LVRD | Line hand tripped for Voltage regulation BLB-428 KV | N/2143
NR140057 | 106330 | 400KV KNP-BLBGARH-III | 2013-06-30 09:35 | 2013-06-30 19:28 | 0 | 0 | 0 | 0.41181 | LCSD | S/D for installation of Polymer insulator strings. | N-2154
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-03 23:41
NR140102 | 106046 | 400KV KOTA-BEAWAR | 2013-06-05 19:58 | 2013-06-05 20:17 | 0.013194 | 0 | 0 | 0 | LEFT | Line tripped on B-N fault in reclaim time. FLR:Kota 90.9km.
NR140102 | 106137 | 400KV KOTA-BEAWAR | 2013-06-14 05:40 | 2013-06-14 09:27 | 0 | 0 | 0 | 0.15764 | LPRD | Line hand tripped for Power regulation . | N/959
|  | SUB TOTAL |  |  | 0.013194 | 0 | 0 | 0.15764
NR140060 | 106010 | 400KV KOTA-MERTA-I | 2013-06-01 19:01 | 2013-06-01 19:05 | 0 | 0 | 0.0027778 | 0 | GOVC | Tripped on O/V protn at Merta>436kv. D/T recd at Kota.
NR140060 | 106011 | 400KV KOTA-MERTA-I | 2013-06-01 19:05 | 2013-06-03 09:47 | 0 | 0 | 0 | 1899-12-31 14:42 | LVRD | Kept open for Voltage regulation. Kota-428kv. | N-44
NR140060 | 106094 | 400KV KOTA-MERTA-I | 2013-06-09 18:06 | 2013-06-09 18:09 | 0 | 0 | 0.0020833 | 0 | GOVC | O/Voltage protection trip at Merta. DT received at Kota.
NR140060 | 106095 | 400KV KOTA-MERTA-I | 2013-06-09 18:09 | 2013-06-10 22:38 | 0 | 0 | 0 | 1899-12-31 04:29 | LVRD | Kept open for Voltage regulation. | N-592
NR140060 | 106136 | 400KV KOTA-MERTA-I | 2013-06-13 18:43 | 2013-06-13 19:58 | 0 | 0 | 0 | 0.052083 | LVRD | Line hand tripped for Voltage regulation. Kota-428kv. | N/939
NR140060 | 106150 | 400KV KOTA-MERTA-I | 2013-06-15 04:26 | 2013-06-17 13:58 | 0 | 0 | 0 | 1900-01-01 09:32 | LVRD | Line hand tripped for Voltage regulation. Kota-428kv. | N/1051
NR140060 | 106200 | 400KV KOTA-MERTA-I | 2013-06-18 01:38 | 2013-06-18 10:47 | 0 | 0 | 0 | 0.38125 | LVRD | Line hand tripped for Voltage regulation. Kota-428kv. | N-1297
NR140060 | 106211 | 400KV KOTA-MERTA-I | 2013-06-18 21:53 | 2013-06-18 21:58 | 0 | 0 | 0.0034722 | 0 | GOVC | O/V protn oprtd at Merta>436kv. D/T recvd at Kota.
NR140060 | 106212 | 400KV KOTA-MERTA-I | 2013-06-18 21:58 | 2013-06-20 08:54 | 0 | 0 | 0 | 1899-12-31 10:56 | LVRD | Kept open for Voltage regulation. Kota-428kv. | N-1378
|  | SUB TOTAL |  |  | 0 | 0 | 0.0083333 | 1900-01-06 02:03
NR140062 | 106243 | 400KV KOTA-RAPPC | 2013-06-21 19:47 | 2013-06-21 20:07 | 0 | 0.013889 | 0 | 0 | OMSU | Line A/R but tripped from RAPPC due to A/R relay out on Y-N fault, FLR:KOTA-44.29kms,
|  | SUB TOTAL |  |  | 0 | 0.013889 | 0 | 0
NR140069 | 106145 | 400KV LUCKNOW-BAREILLY-II | 2013-06-14 18:17 | 2013-06-14 18:28 | 0 | 0.0076389 | 0 | 0 | OMSU | Tripped R-B-N fault caused by kite thread. FLR:Lko-220km, Brly-40km.
|  | SUB TOTAL |  |  | 0 | 0.0076389 | 0 | 0
NR140070 | 106127 | 400KV LUCKNOW-GORAKH-III | 2013-06-12 01:43 | 2013-06-12 02:31 | 0.033333 | 0 | 0 | 0 | OMST | Tripped on 3-ph Fault during heavy rainstrom and lightening in the area. FLR:GKP=160km LKO-70km
NR140070 | 106174 | 400KV LUCKNOW-GORAKH-III | 2013-06-16 14:17 | 2013-06-17 12:02 | 0 | 0 | 0 | 0.90625 | LVRD | Line hand tripped for Voltage regulation. Gkp-429kv. | N-1141
|  | SUB TOTAL |  |  | 0.033333 | 0 | 0 | 0.90625
NR140071 | 106128 | 400KV LUCKNOW-GORAKH-IV | 2013-06-12 01:43 | 2013-06-12 02:14 | 0.021528 | 0 | 0 | 0 | OMST | Tripped on 3-ph Fault during heavy rainstrom and lightening in the area. FLR:GKP=160km LKO-73km
NR140071 | 106163 | 400KV LUCKNOW-GORAKH-IV | 2013-06-15 16:51 | 2013-06-17 14:31 | 0 | 0 | 0 | 1899-12-31 21:40 | LVRD | Line hand tripped for Voltage regulation. Gkp-429kv. | N-1089
|  | SUB TOTAL |  |  | 0.021528 | 0 | 0 | 1899-12-31 21:40
NR140112 | 106129 | 400KV LUCKNOW-LKO(765)-I | 2013-06-12 01:43 | 2013-06-12 03:09 | 0.059722 | 0 | 0 | 0 | OMST | Tripped on Y-B, Z-I, fault during heavy rainstrom and lightening in the area.
|  | SUB TOTAL |  |  | 0.059722 | 0 | 0 | 0
NR140113 | 106130 | 400KV LUCKNOW-LKO(765)-II | 2013-06-12 01:43 | 2013-06-12 03:20 | 0.067361 | 0 | 0 | 0 | OMST | Tripped on Y-B, Z-I, fault during heavy rainstrom and lightening in the area.
|  | SUB TOTAL |  |  | 0.067361 | 0 | 0 | 0
NR140114 | 106228 | 400KV LUCKNOW-ROSA-I | 2013-06-19 10:28 | 2013-06-19 11:06 | 0 | 0.026389 | 0 | 0 | SRMU | Trip due to relay problem at Rosa-UPPCL. D/T recd at Lko.
NR140114 | 106240 | 400KV LUCKNOW-ROSA-I | 2013-06-21 10:49 | 2013-06-21 11:17 | 0 | 0.019444 | 0 | 0 | OMSU | Tripped on Y-N fault in UPPCL portion, FLR:Lko-174km.
|  | SUB TOTAL |  |  | 0 | 0.045833 | 0 | 0
NR140074 | 106048 | 400KV LUCKNOW-UNNAO-I | 2013-06-06 02:10 | 2013-06-06 04:44 | 0 | 0 | 0 | 0.10694 | OSFD | Forced s/d by UPPCL due to isolator sparking at Unnao. | N/285
NR140074 | 106125 | 400KV LUCKNOW-UNNAO-I | 2013-06-12 01:43 | 2013-06-12 02:12 | 0 | 0.020139 | 0 | 0 | OMSU | A/R at LKO but Trip from Unnao/UPPCL on B-N fault during heavy rainstrom and lightening in the area.
|  | SUB TOTAL |  |  | 0 | 0.020139 | 0 | 0.10694
NR140075 | 106126 | 400KV LUCKNOW-UNNAO-II | 2013-06-12 01:43 | 2013-06-12 02:25 | 0 | 0.029167 | 0 | 0 | OMSU | A/R at Lko but trip on D/T recd from Unnao-UPPCL on B-N fault during heavy rainstrom/ lightening in the area.
NR140075 | 106284 | 400KV LUCKNOW-UNNAO-II | 2013-06-27 08:30 | 2013-06-27 08:59 | 0 | 0.020139 | 0 | 0 | SBBU | Bus Bar protn trip at Unnau-UPPCL due to local fault. D/T recd at LKO.
|  | SUB TOTAL |  |  | 0 | 0.049306 | 0 | 0
NR140142 | 106187 | 400KV MEERUT-BAREILLY-I | 2013-06-17 02:58 | 2013-06-17 06:36 | 0 | 0 | 0 | 0.15139 | LVRD | Line hand tripped for Voltage regulation. Mrt-432kv. | N-1201
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.15139
NR140130 | 106115 | 400KV MEERUT-BAREILLY-II | 2013-06-11 06:48 | 2013-06-11 07:01 | 0 | 0.0090278 | 0 | 0 | OMSU | Tripped on R-N fault in PLINK portion during reclaim time. FLR:BRLY-47km, MRT-204.9km. Heavy storm reported.
|  | SUB TOTAL |  |  | 0 | 0.0090278 | 0 | 0
NR140080 | 106075 | 400KV MEERUT-MUZFRNGR | 2013-06-06 19:04 | 2013-06-06 20:04 | 0 | 0.041667 | 0 | 0 | OMSU | D/T recvd at Meerut during testing by UPPCL at Mzfrngr.
NR140080 | 106298 | 400KV MEERUT-MUZFRNGR | 2013-06-28 11:10 | 2013-06-28 15:23 | 0.17569 | 0 | 0 | 0 | OSFT | Forced S/D due to heavy sparking in Y-ph line isolator at MRT. Heavy O/L of line>780mw due to UP system fault. | N-1999
|  | SUB TOTAL |  |  | 0.17569 | 0.041667 | 0 | 0
NR140139 | 106251 | 400KV NAVADA-GR.NOIDA | 2013-06-22 11:50 | 2013-06-22 20:02 | 0 | 0 | 0 | 0.34167 | OSPD | S/D by HVPNL for changing of isolater cotact at Nawada. | N-1601
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.34167
NR140108 | 106025 | 400KV NIMRANA-SIKAR-I | 2013-06-03 12:33 | 2013-06-03 12:59 | 0.018056 | 0 | 0 | 0 | OSPT | S/D for tree lopping work by Sikar. | N-119
NR140108 | 106065 | 400KV NIMRANA-SIKAR-I | 2013-06-06 17:13 | 2013-06-06 20:16 | 0 | 0 | 0 | 0.12708 | LVRD | Line hand tripped for Voltage regulation. Nim-434kv | N/353
NR140108 | 106111 | 400KV NIMRANA-SIKAR-I | 2013-06-11 02:23 | 2013-06-11 09:11 | 0 | 0 | 0 | 0.28333 | LVRD | Line hand tripped for Voltage regulation. | N/714
NR140108 | 106176 | 400KV NIMRANA-SIKAR-I | 2013-06-16 17:10 | 2013-06-17 09:51 | 0 | 0 | 0 | 0.69514 | LVRD | Line hand tripped for Voltage regulation. Nim-434kv | N-1146
NR140108 | 106329 | 400KV NIMRANA-SIKAR-I | 2013-06-30 04:29 | 2013-06-30 22:39 | 0 | 0 | 0 | 0.75694 | LVRD | Line hand tripped for Voltage regulation NEEM-427 KV | N/2146
|  | SUB TOTAL |  |  | 0.018056 | 0 | 0 | 1899-12-31 20:42
NR140109 | 106277 | 400KV NIMRANA-SIKAR-II | 2013-06-26 11:47 | 2013-06-26 20:20 | 0 | 0 | 0 | 0.35625 | LCSD | S/D for new BUS-I Jumpering work at Sikar. | N-1854
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.35625
NR140086 | 106074 | 400KV ROORKI-MUZFRNGR | 2013-06-06 18:46 | 2013-06-06 20:49 | 0 | 0.085417 | 0 | 0 | OMSU | Tripped on R-N fault in UPPCL portion, FLR:Rrk-31km.
NR140086 | 106164 | 400KV ROORKI-MUZFRNGR | 2013-06-15 17:36 | 2013-06-15 17:57 | 0 | 0.014583 | 0 | 0 | OMSU | Trip on R-N Fault in PITCUL portion. Roorki=28.3km,
NR140086 | 106307 | 400KV ROORKI-MUZFRNGR | 2013-06-29 16:06 | 2013-06-29 16:15 | 0 | 0.00625 | 0 | 0 | OMSU | Line tripped R-N fault, dist. Roorkee-7kms, UPPCL portion
NR140086 | 106332 | 400KV ROORKI-MUZFRNGR | 2013-06-30 12:49 | 2013-06-30 17:39 | 0 | 0 | 0 | 0.20139 | OSPD | S/D by UPPCL for tree lopping in their area.
|  | SUB TOTAL |  |  | 0 | 0.10625 | 0 | 0.20139
NR140087 | 106076 | 400KV ROORKI-RISHIKESH | 2013-06-06 19:49 | 2013-06-06 20:58 | 0 | 0 | 0.047917 | 0 | GOVC | Tripped on O/V protn at Roorkee due to sudden volt rise..
NR140087 | 106306 | 400KV ROORKI-RISHIKESH | 2013-06-29 11:54 | 2013-06-29 15:35 | 0 | 0 | 0 | 0.15347 | OSPD | S/D by UPPCL to attend hot spot in Y-ph isolator. | N/2068
|  | SUB TOTAL |  |  | 0 | 0 | 0.047917 | 0.15347
NR140088 | 406041 | 400KV SASARAM-BIHARSHRF-I | 2013-06-04 11:37 | 2013-06-04 11:47 | 0.0069444 | 0 | 0 | 0 | OMST | TRIPPEDON TRANSIENT B-N FAULT, F/L- 45.1KM FROM SSRM END DURING HEAVY RAIN/LIGHTNING/THUNDERING IN THE AREA.
NR140088 | 406064 | 400KV SASARAM-BIHARSHRF-I | 2013-06-06 16:10 | 2013-06-06 16:16 | 0.0041667 | 0 | 0 | 0 | OMST | TRIPPED ON B-N FAULT, DUE TO HEAVY CYCLONE & STORM
NR140088 | 406284 | 400KV SASARAM-BIHARSHRF-I | 2013-06-27 08:16 | 2013-06-27 18:43 | 0 | 0 | 0 | 0.43542 | LCSD | S/D TAKEN FOR BAY CONSTRUCTION WORK AT SSRM END.
NR140088 | 406291 | 400KV SASARAM-BIHARSHRF-I | 2013-06-28 08:34 | 2013-06-28 18:09 | 0 | 0 | 0 | 0.39931 | LCSD | S/D TAKEN FOR BAY CONSTRUCTION WORK AT BSF END.
|  | SUB TOTAL |  |  | 0.011111 | 0 | 0 | 0.83472
NR140089 | 406091 | 400KV SASARAM-BIHARSHRF-II | 2013-06-08 11:24 | 2013-06-08 11:57 | 0.022917 | 0 | 0 | 0 | SBBT | TRIPPED DUE TO OPERATION OF BUS BAR PROTECTION AT SSRM
NR140089 | 406133 | 400KV SASARAM-BIHARSHRF-II | 2013-06-11 19:03 | 2013-06-11 19:50 | 0 | 0.032639 | 0 | 0 | OMSU | S/D TAKEN TOWARDS RELAY RETROFITTING WORK AT BSF.
NR140089 | 406208 | 400KV SASARAM-BIHARSHRF-II | 2013-06-19 10:24 | 2013-06-19 10:24 | 0 | 0 | 0 | 0 | LART | A/R OPERATED OPERATED SUCCESSFULLY Y-NFAULT,F/L-139.4 KM FROM BSF END | N/2068
|  | SUB TOTAL |  |  | 0.022917 | 0.032639 | 0 | 0
NR140092 | 106119 | 400KV SING-ALLD-II | 2013-06-11 10:27 | 2013-06-11 12:16 | 0 | 0.075694 | 0 | 0 | SBBU | Tripped on Busbar protn opted at SING/NTPC.
|  | SUB TOTAL |  |  | 0 | 0.075694 | 0 | 0
NR140093 | 106247 | 400KV SING-ANPARA | 2013-06-22 09:26 | 2013-06-23 01:55 | 0 | 0 | 0 | 0.68681 | OSPD | S/D by NTPC for testing of CVT, CT& AMP work at sing. | N/1592
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.68681
NR140111 | 106096 | 400KV SING-FATEHPUR | 2013-06-10 09:45 | 2013-06-10 10:05 | 0 | 0.013889 | 0 | 0 | SRMU | Line tripped only at Sing-NTPC due to relay problem.
|  | SUB TOTAL |  |  | 0 | 0.013889 | 0 | 0
NR140095 | 106118 | 400KV SING-LKO(UP) | 2013-06-11 10:27 | 2013-06-11 11:57 | 0 | 0.0625 | 0 | 0 | SBBU | Tripped on Busbar protn opted at SING/NTPC.
|  | SUB TOTAL |  |  | 0 | 0.0625 | 0 | 0
NR140096 | 106032 | 400KV SING-RIHAND-I | 2013-06-04 11:03 | 2013-06-04 19:21 | 0 | 0 | 0 | 0.34583 | OSPD | S/D by Rh/NTPC for protection testing. | N-171
NR140096 | 106042 | 400KV SING-RIHAND-I | 2013-06-05 10:02 | 2013-06-05 18:54 | 0 | 0 | 0 | 0.36944 | OSPD | S/D by NTPC for protection testing work. | N/231
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.71528
NR140097 | 106241 | 400KV SING-RIHAND-II | 2013-06-21 12:12 | 2013-06-21 23:17 | 0 | 0 | 0 | 0.46181 | OSPD | S/D by NTPC for testing of CVT, CT& AMP work at sing. | N-1540
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.46181
BILUP2209 | 106026 | 220KV ALLD-JHUSI(UP) | 2013-06-03 13:40 | 2013-06-03 17:45 | 0.17014 | 0 | 0 | 0 | OSPT | S/D for R-ph CVT replacement at ALLD end. | N-125
|  | SUB TOTAL |  |  | 0.17014 | 0 | 0 | 0
NR122002 | 106091 | 220KV ANTA-BHIL-II | 2013-06-09 14:40 | 2013-06-09 18:29 | 0 | 0 | 0 | 0.15903 | OSFD | S/D by Anta/NTPC for CB problem rectification work. | N-579
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.15903
NR122004 | 106073 | 220KV ANTA-RAPPC | 2013-06-06 17:54 | 2013-06-07 21:36 | 1899-12-31 03:42 | 0 | 0 | 0 | OMST | Line tripped B-N fault due to E/wire broken during heavy storm at loc-129. FLR:RAPP-43.72km, Anta-43km.
|  | SUB TOTAL |  |  | 1899-12-31 03:42 | 0 | 0 | 0
NR122006 | 106248 | 220KV AUR-SIKANDARA-I | 2013-06-22 10:10 | 2013-06-22 20:02 | 0 | 0 | 0 | 0.41111 | OSPD | S/D buy UPPCL for stringing of their new line. | N/1595
NR122006 | 106257 | 220KV AUR-SIKANDARA-I | 2013-06-23 09:52 | 2013-06-23 19:56 | 0 | 0 | 0 | 0.41944 | OSPD | S/D buy UPPCL for stringing of their new line. | N-1645
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.83056
NR122007 | 106249 | 220KV AUR-SIKANDARA-II | 2013-06-22 10:10 | 2013-06-22 20:03 | 0 | 0 | 0 | 0.41181 | OSPD | S/D buy UPPCL for stringing of their new line. | N/1595
NR122007 | 106258 | 220KV AUR-SIKANDARA-II | 2013-06-23 09:52 | 2013-06-23 19:57 | 0 | 0 | 0 | 0.42014 | OSPD | S/D buy UPPCL for stringing of their new line. | N-1645
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.83194
NR122009 | 106100 | 220KV BASSI-DAUSA-I | 2013-06-11 02:00 | 2013-06-11 04:45 | 0 | 0 | 0 | 0.11458 | LPRD | Line hand tripped for Power regulation | N/708
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.11458
NR122010 | 106101 | 220KV BASSI-DAUSA-II | 2013-06-11 02:00 | 2013-06-11 04:45 | 0 | 0 | 0 | 0.11458 | LPRD | Line hand tripped for Power regulation | N/708
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.11458
NR122012 | 106188 | 220KV DGANGA-BLY(UP)-II | 2013-06-17 03:05 | 2013-07-01 | 0 | 0 | 0 | 1900-01-12 20:55 | OSFD | Forced S/D by NHPC due to D/Ganga C/Room Flooded. | N-1202
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-12 20:55
NR122013 | 106190 | 220KV DGANGA-PITHORAGRH | 2013-06-17 03:09 | 2013-07-01 | 0 | 0 | 0 | 1900-01-12 20:51 | OSFD | Forced S/D by NHPC due to D/Ganga C/Room Flooded. | N-1202
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-12 20:51
BILHY2201 | 106178 | 220KV FGPP-PALLA-I | 2013-06-16 17:14 | 2013-06-16 23:09 | 0 | 0 | 0.24653 | 0 | LNCC | Tripped on B-N fault during heavy wind storm due to E/wire snapping at loc.21-22. FLR:Palla=13.52km.
BILHY2201 | 106183 | 220KV FGPP-PALLA-I | 2013-06-16 23:09 | 2013-06-17 19:35 | 0 | 0 | 0 | 0.85139 | OSFD | Forced S/D by HVPNL to attend CB problem at Palla end. | N-1178
BILHY2201 | 106272 | 220KV FGPP-PALLA-I | 2013-06-25 10:39 | 2013-06-25 11:30 | 0 | 0.035417 | 0 | 0 | OMSU | A/R at FGPP but trip from Palla-HVPN due to relay problem on B-N fault. FGPP-53km. Palla-15.6km
BILHY2201 | 106276 | 220KV FGPP-PALLA-I | 2013-06-26 10:25 | 2013-06-26 19:25 | 0 | 0 | 0 | 0.375 | OSPD | S/D by NTPC to attend Y-ph line isolator hot spot at FGPP. | N-1850
|  | SUB TOTAL |  |  | 0 | 0.035417 | 0.24653 | 1899-12-31 05:26
NR122017 | 106081 | 220KV KNP-NAUBASTA | 2013-06-07 12:23 | 2013-06-07 15:44 | 0 | 0 | 0 | 0.13958 | OSPD | S/D by UPPCL for their line maintenance work. | N-460
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.13958
NR122019 | 106016 | 220KV KNP-PANKI-II | 2013-06-02 12:19 | 2013-06-02 12:30 | 0 | 0.0076389 | 0 | 0 | OMSU | Line tripped on 3-ph fault in UPPCL portion. Knp-17.49km.
NR122019 | 106017 | 220KV KNP-PANKI-II | 2013-06-02 12:30 | 2013-06-02 16:43 | 0 | 0 | 0 | 0.17569 | OSPD | S/D by UPPCL for attending their line fault.
NR122019 | 106197 | 220KV KNP-PANKI-II | 2013-06-17 12:45 | 2013-06-17 13:00 | 0 | 0.010417 | 0 | 0 | OMSU | Tripped on B-N fault in UPPCL portion. FLR:Knp-20.65km.
NR122019 | 106198 | 220KV KNP-PANKI-II | 2013-06-17 13:00 | 2013-06-21 19:26 | 0 | 0 | 0 | 1900-01-03 06:26 | OSFD | Forced S/d by UPPCL to attend broken E/wire problem. | N-1321
|  | SUB TOTAL |  |  | 0 | 0.018056 | 0 | 1900-01-03 10:39
NR122020 | 106207 | 220KV KNP-UNCHR-I | 2013-06-18 10:37 | 2013-06-18 20:14 | 0 | 0 | 0 | 0.40069 | OSPD | S/D by NTPC for Bus-3 isolator o/hauling at Unchahar. | N-1327
NR122020 | 106260 | 220KV KNP-UNCHR-I | 2013-06-24 09:51 | 2013-06-24 18:25 | 0 | 0 | 0 | 0.35694 | OSPD | S/D by NTPC for BUS-IV isolater Overhauling work. | N-1708
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.75764
NR122021 | 106226 | 220KV KNP-UNCHR-II | 2013-06-19 09:50 | 2013-06-20 19:05 | 0 | 0 | 0 | 1899-12-31 09:15 | OSPD | S/D by NTPC for CB O/hauling at Unchahar. | N-1411
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 09:15
NR122022 | 106273 | 220KV KNP-UNCHR-III | 2013-06-26 08:17 | 2013-06-26 19:08 | 0 | 0 | 0 | 0.45208 | OSPD | S/D Taken by NTPC Unchahar for maint. Work | N-1836
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.45208
NR122023 | 106246 | 220KV KNP-UNCHR-IV | 2013-06-22 09:18 | 2013-06-22 22:16 | 0 | 0 | 0 | 0.54028 | OSPD | S/D by NTPC for CB O/hauling at Unchahar. | N/1594
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.54028
BILUP2204 | 106104 | 220KV MEERUT-MPURAM-I | 2013-06-11 02:06 | 2013-06-11 02:36 | 0 | 0 | 0 | 0.020833 | LPRD | Line hand tripped for Power regulation | N/708
BILUP2204 | 106300 | 220KV MEERUT-MPURAM-I | 2013-06-28 11:15 | 2013-06-28 19:42 | 0 | 0 | 0 | 0.35208 | OSFD | Forced S/D by UPPCL due to E/wire broken and fell on Bus at Modipuram-UPPCL stn. Tripped on 3-ph fault.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.37292
BILUP2205 | 106105 | 220KV MEERUT-MPURAM-II | 2013-06-11 02:06 | 2013-06-11 02:36 | 0 | 0 | 0 | 0.020833 | LPRD | Line hand tripped for Power regulation | N/708
BILUP2205 | 106301 | 220KV MEERUT-MPURAM-II | 2013-06-28 11:15 | 2013-06-28 19:38 | 0 | 0 | 0 | 0.34931 | OSFD | Forced S/D by UPPCL due to E/wire broken and fell on Bus at Modipuram-UPPCL stn. Tripped on 3-ph fault.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.37014
BILUP2206 | 106098 | 220KV MEERUT-NARA | 2013-06-10 11:03 | 2013-06-10 13:24 | 0 | 0.097917 | 0 | 0 | OMSU | Line A/R at MRT tripped at NARA end R-N fault, Dist. MRT-29.5 kms
BILUP2206 | 106194 | 220KV MEERUT-NARA | 2013-06-17 07:40 | 2013-06-17 08:35 | 0 | 0.038194 | 0 | 0 | OMSU | A/R at MRT but Trip from Nara on R-N Fault in UPPCL portion. MRT=14.8km.
BILUP2206 | 106299 | 220KV MEERUT-NARA | 2013-06-28 11:10 | 2013-06-30 12:53 | 0 | 0 | 0 | 1900-01-01 01:43 | OSFD | Forced S/D by UPPCL due to conductor broken at loc. 78-82 in UPPCL portion. Trip on Y-B fault. Mrt-3.3km. | N-2006
|  | SUB TOTAL |  |  | 0 | 0.13611 | 0 | 1900-01-01 01:43
BILUP2207 | 106106 | 220KV MEERUT-SHTBDNGR | 2013-06-11 02:06 | 2013-06-11 02:36 | 0 | 0 | 0 | 0.020833 | LPRD | Line hand tripped for Power regulation | N/708
BILUP2207 | 106210 | 220KV MEERUT-SHTBDNGR | 2013-06-18 21:33 | 2013-06-19 01:23 | 0 | 0 | 0 | 0.15972 | LPRD | Line hand tripped for power regulation | N-1369
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.18056
BILUP2208 | 106107 | 220KV MEERUT-SIMBHOLI | 2013-06-11 02:06 | 2013-06-11 02:36 | 0 | 0 | 0 | 0.020833 | LPRD | Line hand tripped for Power regulation | N/708
BILUP2208 | 106177 | 220KV MEERUT-SIMBHOLI | 2013-06-16 17:30 | 2013-06-16 18:10 | 0 | 0.027778 | 0 | 0 | OMSU | A/R at MRT but Trip from Simbholi on R-N Fault in UPPCL portion. MRT=17.2km.
BILUP2208 | 106253 | 220KV MEERUT-SIMBHOLI | 2013-06-23 05:13 | 2013-06-23 05:32 | 0 | 0.013194 | 0 | 0 | OMSU | A/R at MRT but tripped at simbhaul on R-N fault in UPPCL portion. FLR:MRT-17.2km.
|  | SUB TOTAL |  |  | 0 | 0.040972 | 0 | 0.020833
NR122025 | 106077 | 220KV RAIBRLY-CHINHAT | 2013-06-07 04:39 | 2013-06-07 14:13 | 0 | 0 | 0 | 0.39861 | OSFD | Forced S/D by UPPCL to attend broken E/wire as line trip on Y-B-N fault in UPPCL portion. Raibrly-31.9km
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.39861
NR122026 | 106142 | 220KV RAIBRLY-LKO(UP) | 2013-06-14 11:35 | 2013-06-14 17:55 | 0 | 0 | 0 | 0.26389 | LCSD | S/D for OPGW instalation work in highly inductive area. | N-984
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.26389
NR122027 | 106037 | 220KV RAPPB-CHITT-I | 2013-06-04 21:47 | 2013-06-04 22:00 | 0 | 0.0090278 | 0 | 0 | OMSU | Trip due to A/R relay Faulty at both end on R-N fault. FLR:Chittor-155km,whereas Line length=128km.
NR122027 | 106038 | 220KV RAPPB-CHITT-I | 2013-06-04 22:00 | 2013-06-04 22:55 | 0 | 0 | 0 | 0.038194 | OSPD | S/D by RAPP-B for yard inspection at their end.
|  | SUB TOTAL |  |  | 0 | 0.0090278 | 0 | 0.038194
NR122030 | 106271 | 220KV RAPPB-UDAIPUR | 2013-06-25 09:23 | 2013-06-25 17:31 | 0 | 0 | 0 | 0.33889 | OSPD | S/D by RRVPNL for their BUS AMP work. | N-1782
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.33889
NR122032 | 106041 | 220KV SITARGANJ-BLY(UP) | 2013-06-05 09:19 | 2013-06-05 09:53 | 0.023611 | 0 | 0 | 0 | OMST | Tripped during on line OPGW installation work on B-N fault as it was in Non Auto mode. FLR:Strgnj-87.24km.
NR122032 | 106052 | 220KV SITARGANJ-BLY(UP) | 2013-06-06 09:27 | 2013-06-06 15:46 | 0 | 0 | 0 | 0.26319 | LCSD | S/D for OPGW instalation work in highly inductive area. | N/298
|  | SUB TOTAL |  |  | 0.023611 | 0 | 0 | 0.26319
NR122035 | 106022 | 220KV UNCHR-RAIBRLY-I | 2013-06-03 10:21 | 2013-06-04 20:48 | 0 | 0 | 0 | 1899-12-31 10:27 | OSPD | S/D by UCR/NTPC for their bay eqpt maintenance work. | N-105
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 10:27
NR1ICT51 | 106018 | 315MVA ICT-II GURGAON | 2013-06-02 13:17 | 2013-06-02 19:30 | 0 | 0 | 0 | 0.25903 | SCSD | S/D for HV Testing of 400kv Bus-I at Gurgaon GIS. | N-64
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.25903
NR1ICT29 | 106138 | 315MVA ICT-II MANDOLA | 2013-06-14 06:36 | 2013-06-14 09:25 | 0.11736 | 0 | 0 | 0 | OMST | S/D for 33kv LA replacement work. | N-961
|  | SUB TOTAL |  |  | 0.11736 | 0 | 0 | 0
NR1ICT30 | 106058 | 315MVA ICT-II MEERUT | 2013-06-06 15:43 | 2013-06-06 17:07 | 0.058333 | 0 | 0 | 0 | OSPT | S/D to attend oil leakage in R-ph bushing 220KV side. | N/317
|  | SUB TOTAL |  |  | 0.058333 | 0 | 0 | 0
NR1ICT56 | 106158 | 315MVA ICT-I SIKAR | 2013-06-15 14:45 | 2013-06-15 18:08 | 0 | 0 | 0 | 0.14097 | SCSD | S/D for Jumpering of R-ph extended part of Bus-I. | N-1074
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.14097
NR1ICT52 | 106278 | 315MVA ICT-II SIKAR | 2013-06-26 11:48 | 2013-06-26 20:16 | 0 | 0 | 0 | 0.35278 | SCSD | S/D for Jumpering of R-ph extended part of Bus-I. | N-1854
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.35278
NR1BRT12 |  | 50MVAR B/Reactor MURADNGR | 2013-06-01 | 2013-07-01 | 0 | 0 | 0 | 1900-01-29 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-29
NR1BRT32 |  | 240MVAR B/Reactor-I BALIA-765 | 2013-06-10 01:39 | 2013-06-10 12:12 | 0 | 0 | 0 | 0.43958 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
NR1BRT32 |  | 240MVAR B/Reactor-I BALIA-765 | 2013-06-20 13:56 | 2013-06-21 06:25 | 0 | 0 | 0 | 0.68681 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
NR1BRT32 |  | 240MVAR B/Reactor-I BALIA-765 | 2013-06-23 11:30 | 2013-06-23 17:38 | 0 | 0 | 0 | 0.25556 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 09:10
NR1BRT17 |  | 125MVAR B/Reactor-II BALIA | 2013-06-04 12:40 | 2013-06-04 17:12 | 0 | 0 | 0 | 0.18889 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.18889
NR1BRT27 |  | 125MVAR B/Reactor-III BALIA | 2013-06-04 12:37 | 2013-06-04 17:13 | 0 | 0 | 0 | 0.19167 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.19167
NR1BRT07 |  | 80MVAR B/Reactor BLBGARH | 2013-06-27 14:31 | 2013-06-27 19:06 | 0 | 0 | 0 | 0.19097 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.19097
NR1BRT03 |  | 80MVAR B/Reactor BAREILLY | 2013-06-04 10:10 | 2013-06-04 17:53 | 0 | 0 | 0 | 0.32153 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
NR1BRT03 |  | 80MVAR B/Reactor BAREILLY | 2013-06-05 00:04 | 2013-06-05 05:03 | 0 | 0 | 0 | 0.20764 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.52917
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Classification/ Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(F13:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Classification/ Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM(G13:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Classification/ Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM(H13:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Classification/ Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM(I13:[Deemed Available, row above])
Note on C36: : DOC-01.05.13
Note on C37: : DOC-01.05.13
Note on C350: LILO of Mnd-Bly-I at Neerut. DOC-01.04.13

## AVBT_June-13
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.06.2013 to 30.06.2013
SL.NO. | ELEMENT | Element Name | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Total Duration
| NO. |  |  |  | Outage Not To Consider |  | Available for
|  |  | POWERGRID | OTHERS | System Constrnt/ | Deemed | Consideration
[5 empty] | Natural Calamity/ | Available | THM | NSC | Ckt. Kms. | OH x NSC x Cktkm | THM x NSC x Cktkm | Non Availblty Factor/ Month (NAFM) | TAFM
[5 empty] | Militancy |  |  | ( E) | ( F)
|  |  | @ (T) | # (U) | & (C ) | " (D) | E | F | G | H | I | J | K
|  |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs
A |  | 765 KV TRANS LINES | [12 empty] | 0
1 | NR176501 | 765KV LUCKNOW-BALIA | 0.30903 |  |  |  | 720 | 4 | 318.919 | 9461.2637 | 918486.72 | 0.010301 | 98.9699 | 7.4167 | 720
2 | NR176502 | 765KV AGRA-FATEHPUR |  |  |  |  | 720 | 4 | 334.52 | 0 | 963417.6 | 0 | 100 | 0
3 | NR176503 | 765KV FATEHPUR-GAYA | 0.15694 |  | 0.072222 | 0.80833 | 718.2667 | 4 | 484.6 | 7301.3067 | 1392288.1067 | 0.0052441 | 99.4756 | 3.7667
4 | NR176504 | 765KV AGRA-JHATIKALA | 0.0083333 |  |  | 1899-12-31 05:37 | 720 | 4 | 253.076 | 202.4608 | 728858.88 | 0.00027778 | 99.9722 | 0.2
5 | NR176505 | 765 KV AGRA- MEERUT | 0.017361 |  | 0.019444 | 1900-01-01 08:09 | 719.5333 | 4 | 267.628 | 446.0467 | 770269.0677 | 0.00057908 | 99.9421 | 0.41667
6 | NR176506 | 765KV FATEHPUR-SASARAM-II | 0.28472 |  | 0.7625 | 1900-01-02 11:35 | 701.7 | 4 | 355.008 | 9703.552 | 996436.4544 | 0.0097383 | 99.0262 | 6.8333
B |  | 400 KV TRANS LINES
1 | NR140001 | 400KV AGRA-AGRA(UP)-I |  |  | 0.0055556 | 0.32431 | 719.8667 | 2 | 29.982 | 0 | 43166.0848 | 0 | 100 | 0
2 | NR140002 | 400KV AGRA-AGRA(UP)-II |  |  |  |  | 720 | 2 | 29.982 | 0 | 43174.08 | 0 | 100 | 0
3 | NR140003 | 400KV AGRA-AURAIYA-I | 0.0055556 |  |  | 0.89722 | 720 | 2 | 167.2 | 44.5867 | 240768 | 0.00018519 | 99.9815 | 0.13333
4 | NR140004 | 400KV AGRA-AURAIYA-II |  |  |  | 0.52708 | 720 | 2 | 167.2 | 0 | 240768 | 0 | 100 | 0
5 | NR140005 | 400KV AGRA-BASSI-I |  |  |  | 1899-12-31 03:57 | 720 | 2 | 211.433 | 0 | 304463.52 | 0 | 100 | 0
6 | NR140008 | 400KV AGRA-BHIWADI-I |  |  |  | 1900-01-01 09:34 | 720 | 2 | 208.98 | 0 | 300931.2 | 0 | 100 | 0
7 | NR140009 | 400KV AGRA-BHIWADI-II |  |  |  | 1900-01-03 11:29 | 720 | 2 | 209.51 | 0 | 301694.4 | 0 | 100 | 0
8 | NR140010 | 400KV AGRA-BLBGRH | 0.41458 |  |  |  | 720 | 2 | 181.137 | 3604.6263 | 260837.28 | 0.013819 | 98.6181 | 9.95
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 0.16458 |  |  | 0.83681 | 720 | 2 | 253.823 | 2005.2017 | 365505.12 | 0.0054861 | 99.4514 | 3.95
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II |  |  |  | 1899-12-31 21:31 | 720 | 2 | 253.823 | 0 | 365505.12 | 0 | 100 | 0
11 | NR140122 | 400KV ALLD-FATEHPUR-I |  |  |  |  | 720 | 2 | 139.73 | 0 | 201211.2 | 0 | 100 | 0
12 | NR140123 | 400KV ALLD-FATEHPUR-II |  |  |  |  | 720 | 2 | 139.73 | 0 | 201211.2 | 0 | 100 | 0
13 | NR140104 | 400KV ALLD-FATEHPUR-III |  |  |  |  | 720 | 2 | 155.3 | 0 | 223632 | 0 | 100 | 0
14 | NR140012 | 400KV ALLD-KNP-II |  |  |  |  | 720 | 2 | 224 | 0 | 322560 | 0 | 100 | 0
15 | NR140015 | 400KV ALLD-SARNATH |  |  |  |  | 720 | 2 | 212 | 0 | 305280 | 0 | 100 | 0
16 | NR140016 | 400KV ALLD-SASARAM |  |  |  |  | 720 | 2 | 136 | 0 | 195840 | 0 | 100 | 0
17 | NR140017 | 400KV BALIA-BIHARSHRF-I |  |  |  |  | 720 | 4 | 241.79 | 0 | 696355.2 | 0 | 100 | 0
18 | NR140018 | 400KV BALIA-BIHARSHRF-II | 1899-12-31 16:22 |  |  |  | 720 | 4 | 241.79 | 39041.0253 | 696355.2 | 0.056065 | 94.3935 | 40.3667
19 | NR140019 | 400KV BALIA-MAU-I |  |  |  |  | 720 | 2 | 13 | 0 | 18720 | 0 | 100 | 0
20 | NR140020 | 400KV BALIA-MAU-II |  |  |  |  | 720 | 2 | 13 | 0 | 18720 | 0 | 100 | 0
21 | NR140021 | 400KV BALIA-PATNA-I |  |  |  | 1900-01-02 08:47 | 720 | 4 | 195.32 | 0 | 562521.6 | 0 | 100 | 0
22 | NR140022 | 400KV BALIA-PATNA-II | 0.38472 |  |  | 1899-12-31 05:12 | 720 | 4 | 195.32 | 7213.8187 | 562521.6 | 0.012824 | 98.7176 | 9.2333
23 | NR140136 | 400KV BALIA-PATNA-III |  |  |  |  | 720 | 4 | 185 | 0 | 532800 | 0 | 100 | 0
24 | NR140137 | 400KV BALIA-PATNA-IV |  |  | 0.0034722 | 1899-12-31 01:34 | 719.9167 | 4 | 185 | 0 | 532738.3333 | 0 | 100 | 0
25 | NR140140 | 400KV BALIA-SOHAWAL-I | 0.021528 |  | 0.0034722 | 0.10764 | 719.9167 | 2 | 229.163 | 236.8018 | 329956.5262 | 0.00071768 | 99.9282 | 0.51667
26 | NR140120 | 400KV BALIA-SOHAWAL-II |  |  | 0.011111 | 0.076389 | 719.7333 | 2 | 229.163 | 0 | 329872.4997 | 0 | 100 | 0
27 | NR140023 | 400KV BAREILLY-BRLY(UP)-I |  |  |  |  | 720 | 2 | 9.2 | 0 | 13248 | 0 | 100 | 0
28 | NR140024 | 400KV BAREILLY-BRLY(UP)-II |  |  |  | 1900-01-02 11:30 | 720 | 2 | 9.2 | 0 | 13248 | 0 | 100 | 0
29 | NR140025 | 400KV BAREILLY-LKO(UP) |  | 0.015278 |  |  | 720 | 2 | 278.76 | 0 | 401414.4 | 0 | 100 | 0
30 | NR140026 | 400KV BAREILLY-MBAD-I |  |  |  |  | 720 | 2 | 92.68 | 0 | 133459.2 | 0 | 100 | 0
31 | NR140027 | 400KV BAREILLY-MBAD-II |  |  |  |  | 720 | 2 | 92.68 | 0 | 133459.2 | 0 | 100 | 0
32 | NR140115 | 400KV BAREILLY-ROSA-I |  |  |  |  | 720 | 2 | 115.926 | 0 | 166933.44 | 0 | 100 | 0
33 | NR140028 | 400KV BASSI-BHIWADI-I |  |  |  | 1900-01-01 07:51 | 720 | 2 | 235 | 0 | 338400 | 0 | 100 | 0
34 | NR140029 | 400KV BASSI-BHIWADI-II | 0.064583 |  |  | 1899-12-31 14:29 | 720 | 2 | 220.261 | 682.8091 | 317175.84 | 0.0021528 | 99.7847 | 1.55
35 | NR140030 | 400KV BASSI-HIRAPURA-I |  |  |  | 0.24306 | 720 | 2 | 47.762 | 0 | 68777.28 | 0 | 100 | 0
36 | NR140031 | 400KV BASSI-HIRAPURA-II |  |  |  | 0.24097 | 720 | 2 | 48.99 | 0 | 70545.6 | 0 | 100 | 0
37 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 0.16875 |  |  | 1900-01-01 04:52 | 720 | 2 | 37.164 | 301.0284 | 53516.16 | 0.005625 | 99.4375 | 4.05
38 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 0.022917 |  |  | 1900-01-01 05:04 | 720 | 2 | 37.164 | 40.8804 | 53516.16 | 0.00076389 | 99.9236 | 0.55
39 | NR140032 | 400KV BHIWADI-GURGAON |  |  | 0.0041667 | 0.46875 | 719.9 | 2 | 82.8 | 0 | 119215.44 | 0 | 100 | 0
40 | NR140033 | 400KV BHIWADI-HISAR |  |  |  |  | 720 | 2 | 211.547 | 0 | 304627.68 | 0 | 100 | 0
41 | NR140106 | 400KV BHIWADI-NIMRANA-I |  |  |  | 1899-12-31 20:20 | 720 | 2 | 48.428 | 0 | 69736.32 | 0 | 100 | 0
42 | NR140107 | 400KV BHIWADI-NIMRANA-II |  |  |  | 1900-01-01 10:54 | 720 | 2 | 48.428 | 0 | 69736.32 | 0 | 100 | 0
43 | NR140035 | 400KV BLBGRH-GURGAON | 0.0069444 |  |  |  | 720 | 2 | 42.7 | 14.2333 | 61488 | 0.00023148 | 99.9769 | 0.16667
44 | NR140036 | 400KV BLBGRH-MAHRANIBG |  |  |  |  | 720 | 4 | 60.68 | 0 | 174758.4 | 0 | 100 | 0
45 | NR140037 | 400KV BLBGRH-MAINPURI-I |  | 0.0013889 |  | 1900-01-01 17:28 | 720 | 2 | 235.952 | 0 | 339770.88 | 0 | 100 | 0
46 | NR140038 | 400KV BLBGRH-MAINPURI-II |  | 0.0013889 |  | 1900-01-01 08:33 | 720 | 2 | 235.952 | 0 | 339770.88 | 0 | 100 | 0
47 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) |  |  |  | 0.03125 | 720 | 4 | 12.55 | 0 | 36144 | 0 | 100 | 0
48 | NR140039 | 400KV DAD-GR.NOIDA |  |  |  |  | 720 | 4 | 13.256 | 0 | 38177.28 | 0 | 100 | 0
49 | NR140040 | 400KV DAD-MAHRANIBG |  | 0.0069444 |  | 1899-12-31 17:29 | 720 | 4 | 54.36 | 0 | 156556.8 | 0 | 100 | 0
50 | NR140041 | 400KV DAD-MANDOLA-I | 0.0097222 |  |  | 0.33194 | 720 | 4 | 46.3 | 43.2133 | 133344 | 0.00032407 | 99.9676 | 0.23333
51 | NR140042 | 400KV DAD-MANDOLA-II |  |  |  |  | 720 | 4 | 46.3 | 0 | 133344 | 0 | 100 | 0
52 | NR140043 | 400KV DAD-MURADNGR |  |  |  | 1899-12-31 01:57 | 720 | 2 | 33.098 | 0 | 47661.12 | 0 | 100 | 0
53 | NR140044 | 400KV DAD-PANIPAT-I | 0.041667 | 0.046528 |  | 1899-12-31 11:58 | 720 | 2 | 112.322 | 224.644 | 161743.68 | 0.0013889 | 99.8611 | 1
54 | NR140045 | 400KV DAD-PANIPAT-II |  | 0.025694 |  |  | 720 | 2 | 117 | 0 | 168480 | 0 | 100 | 0
55 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 0.17292 |  |  | 1899-12-31 06:03 | 720 | 2 | 260.051 | 2158.4233 | 374473.44 | 0.0057639 | 99.4236 | 4.15
56 | NR140125 | 400KV FATEHPUR-MAINPURI-II |  |  | 0.010417 | 1899-12-31 16:17 | 719.75 | 2 | 260.051 | 0 | 374343.4145 | 0 | 100 | 0
57 | NR140046 | 400KV GORKH-GORAKH-I |  |  |  |  | 720 | 2 | 45.94 | 0 | 66153.6 | 0 | 100 | 0
58 | NR140047 | 400KV GORKH-GORAKH-II |  | 0.045833 |  |  | 720 | 2 | 45.94 | 0 | 66153.6 | 0 | 100 | 0
59 | NR140128 | 400KV GURGAON-MANESAR-I |  |  |  | 1900-01-05 03:31 | 720 | 2 | 23.462 | 0 | 33785.28 | 0 | 100 | 0
60 | NR140129 | 400KV GURGAON-MANESAR-II |  |  |  | 1900-01-05 21:41 | 720 | 2 | 23.462 | 0 | 33785.28 | 0 | 100 | 0
61 | NR140132 | 400KV JHATIKALA-BAMNOLI-I |  |  |  | 0.25972 | 720 | 4 | 6.106 | 0 | 17585.28 | 0 | 100 | 0
62 | NR140133 | 400KV JHATIKALA-BAMNOLI-II |  |  |  |  | 720 | 4 | 6.106 | 0 | 17585.28 | 0 | 100 | 0
63 | NR140134 | 400KV JHATIKALA-MUNDKA-I |  |  |  | 1900-01-04 03:52 | 720 | 4 | 6.782 | 0 | 19532.16 | 0 | 100 | 0
64 | NR140135 | 400KV JHATIKALA-MUNDKA-II |  |  |  |  | 720 | 4 | 6.782 | 0 | 19532.16 | 0 | 100 | 0
65 | NR140048 | 400KV KANKROLI-BHINMAL |  |  |  |  | 720 | 2 | 201.2 | 0 | 289728 | 0 | 100 | 0
66 | NR140049 | 400KV KANKROLI-JODHPUR |  |  |  |  | 720 | 2 | 187.965 | 0 | 270669.6 | 0 | 100 | 0
67 | NR140050 | 400KV KANKROLI-RAPPC-I | 0.04375 |  |  |  | 720 | 2 | 198.54 | 416.934 | 285897.6 | 0.0014583 | 99.8542 | 1.05
68 | NR140051 | 400KV KANKROLI-RAPPC-II |  |  |  |  | 720 | 2 | 198.54 | 0 | 285897.6 | 0 | 100 | 0
69 | NR140052 | 400KV KNP-AGRA |  |  | 0.0013889 | 0.25208 | 719.9667 | 2 | 240 | 0 | 345584 | 0 | 100 | 0
70 | NR140053 | 400KV KNP-AURAIYA-I |  |  |  |  | 720 | 2 | 72.6 | 0 | 104544 | 0 | 100 | 0
71 | NR140054 | 400KV KNP-AURAIYA-II |  |  |  |  | 720 | 2 | 73.2 | 0 | 105408 | 0 | 100 | 0
72 | NR140055 | 400KV KNP-BLBGARH-I |  |  |  | 0.78889 | 720 | 2 | 385.69 | 0 | 555393.6 | 0 | 100 | 0
73 | NR140056 | 400KV KNP-BLBGARH-II |  |  |  | 1900-01-04 12:58 | 720 | 2 | 370.772 | 0 | 533911.68 | 0 | 100 | 0
74 | NR140057 | 400KV KNP-BLBGARH-III |  |  |  | 1900-01-03 23:41 | 720 | 2 | 370.772 | 0 | 533911.68 | 0 | 100 | 0
75 | NR140110 | 400KV KNP-FATEHPUR-I |  |  |  |  | 720 | 2 | 107.079 | 0 | 154193.76 | 0 | 100 | 0
76 | NR140105 | 400KV KNP-FATEHPUR-II |  |  |  |  | 720 | 2 | 107.1 | 0 | 154224 | 0 | 100 | 0
77 | NR140058 | 400KV KNP-PANKI-I |  |  |  |  | 720 | 2 | 5.922 | 0 | 8527.68 | 0 | 100 | 0
78 | NR140059 | 400KV KNP-PANKI-II |  |  |  |  | 720 | 2 | 5.86 | 0 | 8438.4 | 0 | 100 | 0
79 | NR140102 | 400KV KOTA-BEAWAR | 0.013194 |  |  | 0.15764 | 720 | 2 | 179.711 | 113.817 | 258783.84 | 0.00043981 | 99.956 | 0.31667
80 | NR140060 | 400KV KOTA-MERTA-I |  |  | 0.0083333 | 1900-01-06 02:03 | 719.8 | 2 | 255.56 | 0 | 367904.176 | 0 | 100 | 0
81 | NR140062 | 400KV KOTA-RAPPC |  | 0.013889 |  |  | 720 | 2 | 50.5 | 0 | 72720 | 0 | 100 | 0
82 | NR140063 | 400KV KOTESHWR-KHEP-I |  |  |  |  | 720 | 2 | 2.7 | 0 | 3888 | 0 | 100 | 0
83 | NR140064 | 400KV KOTESHWR-KHEP-II |  |  |  |  | 720 | 2 | 2.7 | 0 | 3888 | 0 | 100 | 0
84 | NR140065 | 400KV KOTESHWR-TEHRI-I |  |  |  |  | 720 | 4 | 14.463 | 0 | 41653.44 | 0 | 100 | 0
85 | NR140098 | 400KV KOTESHWR-TEHRI-II |  |  |  |  | 720 | 4 | 16.49 | 0 | 47491.2 | 0 | 100 | 0
86 | NR140069 | 400KV LUCKNOW-BAREILLY-II |  | 0.0076389 |  |  | 720 | 2 | 255.5 | 0 | 367920 | 0 | 100 | 0
87 | NR140070 | 400KV LUCKNOW-GORAKH-III | 0.033333 |  |  | 0.90625 | 720 | 2 | 263.933 | 422.2928 | 380063.52 | 0.0011111 | 99.8889 | 0.8
88 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 0.021528 |  |  | 1899-12-31 21:40 | 720 | 2 | 263.933 | 272.7308 | 380063.52 | 0.00071759 | 99.9282 | 0.51667
89 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 0.059722 |  |  |  | 720 | 4 | 2.86 | 16.3973 | 8236.8 | 0.0019907 | 99.8009 | 1.4333
90 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 0.067361 |  |  |  | 720 | 4 | 2.86 | 18.4947 | 8236.8 | 0.0022454 | 99.7755 | 1.6167
91 | NR140072 | 400KV LUCKNOW-LKO(UP) |  |  |  |  | 720 | 2 | 41.743 | 0 | 60109.92 | 0 | 100 | 0
92 | NR140114 | 400KV LUCKNOW-ROSA-I |  | 0.045833 |  |  | 720 | 2 | 169.785 | 0 | 244490.4 | 0 | 100 | 0
93 | NR140141 | 400KV LUCKNOW-SOHAWAL-I |  |  |  |  | 720 | 2 | 98.281 | 0 | 141524.64 | 0 | 100 | 0
94 | NR140121 | 400KV LUCKNOW-SOHAWAL-II |  |  |  |  | 720 | 2 | 98.281 | 0 | 141524.64 | 0 | 100 | 0
95 | NR140073 | 400KV LUCKNOW-SULTANPR |  |  |  |  | 720 | 2 | 41.743 | 0 | 60109.92 | 0 | 100 | 0
96 | NR140074 | 400KV LUCKNOW-UNNAO-I |  | 0.020139 |  | 0.10694 | 720 | 2 | 73.826 | 0 | 106309.44 | 0 | 100 | 0
97 | NR140075 | 400KV LUCKNOW-UNNAO-II |  | 0.049306 |  |  | 720 | 2 | 73.826 | 0 | 106309.44 | 0 | 100 | 0
98 | NR140076 | 400KV MBAD-MURADNGR |  |  |  |  | 720 | 2 | 133.5 | 0 | 192240 | 0 | 100 | 0
99 | NR140142 | 400KV MEERUT-BAREILLY-I |  |  |  | 0.15139 | 720 | 2 | 66.009 | 0 | 95052.96 | 0 | 100 | 0
100 | NR140130 | 400KV MEERUT-BAREILLY-II |  | 0.0090278 |  |  | 720 | 2 | 66.009 | 0 | 95052.96 | 0 | 100 | 0
101 | NR140077 | 400KV MEERUT-KOTESHWR-I |  |  |  |  | 720 | 4 | 178.69 | 0 | 514627.2 | 0 | 100 | 0
102 | NR140099 | 400KV MEERUT-KOTESHWR-II |  |  |  |  | 720 | 4 | 175.63 | 0 | 505814.4 | 0 | 100 | 0
103 | NR140078 | 400KV MEERUT-MND-I |  |  |  |  | 720 | 2 | 59.868 | 0 | 86209.92 | 0 | 100 | 0
104 | NR140079 | 400KV MEERUT-MND-II |  |  |  |  | 720 | 2 | 59.868 | 0 | 86209.92 | 0 | 100 | 0
105 | NR140143 | 400KV MEERUT-MND-III |  |  |  |  | 720 | 2 | 54.298 | 0 | 78189.12 | 0 | 100 | 0
106 | NR140131 | 400KV MEERUT-MND-IV |  |  |  |  | 720 | 2 | 54.298 | 0 | 78189.12 | 0 | 100 | 0
107 | NR140080 | 400KV MEERUT-MUZFRNGR | 0.17569 | 0.041667 |  |  | 720 | 2 | 37.38 | 315.238 | 53827.2 | 0.0058565 | 99.4144 | 4.2167
108 | NR140103 | 400KV MERTA-BEAWAR |  |  |  |  | 720 | 2 | 76.018 | 0 | 109465.92 | 0 | 100 | 0
109 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA |  |  |  | 0.34167 | 720 | 4 | 30.15 | 0 | 86832 | 0 | 100 | 0
110 | NR140118 | 400KV NIMRANA-MANESAR-I |  |  |  |  | 720 | 2 | 67.041 | 0 | 96539.04 | 0 | 100 | 0
111 | NR140119 | 400KV NIMRANA-MANESAR-II |  |  |  |  | 720 | 2 | 67.041 | 0 | 96539.04 | 0 | 100 | 0
112 | NR140108 | 400KV NIMRANA-SIKAR-I | 0.018056 |  |  | 1899-12-31 20:42 | 720 | 2 | 175.859 | 152.4111 | 253236.96 | 0.00060185 | 99.9398 | 0.43333
113 | NR140109 | 400KV NIMRANA-SIKAR-II |  |  |  | 0.35625 | 720 | 2 | 175.859 | 0 | 253236.96 | 0 | 100 | 0
114 | NR140084 | 400KV RIHAND-ALLD-I |  |  |  |  | 720 | 2 | 279.245 | 0 | 402112.8 | 0 | 100 | 0
115 | NR140085 | 400KV RIHAND-ALLD-II |  |  |  |  | 720 | 2 | 279.245 | 0 | 402112.8 | 0 | 100 | 0
116 | NR140086 | 400KV ROORKI-MUZFRNGR |  | 0.10625 |  | 0.20139 | 720 | 2 | 2.1 | 0 | 3024 | 0 | 100 | 0
117 | NR140087 | 400KV ROORKI-RISHIKESH |  |  | 0.047917 | 0.15347 | 718.85 | 2 | 2.1 | 0 | 3019.17 | 0 | 100 | 0
118 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 0.011111 |  |  | 0.83472 | 720 | 2 | 210 | 112 | 302400 | 0.00037037 | 99.963 | 0.26667
119 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 0.022917 | 0.032639 |  |  | 720 | 2 | 210 | 231 | 302400 | 0.00076389 | 99.9236 | 0.55
120 | NR140090 | 400KV SASARAM-SARNATH |  |  |  |  | 720 | 2 | 76 | 0 | 109440 | 0 | 100 | 0
121 | NR140091 | 400KV SING-ALLD-I |  |  |  |  | 720 | 2 | 224 | 0 | 322560 | 0 | 100 | 0
122 | NR140092 | 400KV SING-ALLD-II |  | 0.075694 |  |  | 720 | 2 | 202 | 0 | 290880 | 0 | 100 | 0
123 | NR140093 | 400KV SING-ANPARA |  |  |  | 0.68681 | 720 | 2 | 25.057 | 0 | 36082.08 | 0 | 100 | 0
124 | NR140111 | 400KV SING-FATEHPUR |  | 0.013889 |  |  | 720 | 2 | 330.953 | 0 | 476572.32 | 0 | 100 | 0
125 | NR140095 | 400KV SING-LKO(UP) |  | 0.0625 |  |  | 720 | 2 | 408.6 | 0 | 588384 | 0 | 100 | 0
126 | NR140096 | 400KV SING-RIHAND-I |  |  |  | 0.71528 | 720 | 2 | 42.026 | 0 | 60517.44 | 0 | 100 | 0
127 | NR140097 | 400KV SING-RIHAND-II |  |  |  | 0.46181 | 720 | 2 | 43.952 | 0 | 63290.88 | 0 | 100 | 0
128 | N-W40001 | 400KV SING-VINDH-I |  |  |  |  | 720 | 2 | 3.341 | 0 | 4811.04 | 0 | 100 | 0
129 | N-W40002 | 400KV SING-VINDH-II |  |  |  |  | 720 | 2 | 3.317 | 0 | 4776.48 | 0 | 100 | 0
130 | N-W40003 | 400KV KANKROLI-ZERDA-I |  |  |  |  | 720 | 2 | 233.707 | 0 | 336538.08 | 0 | 100 | 0
131 | N-W40004 | 400KV BHINMAL-ZERDA |  |  |  |  | 720 | 2 | 142.8 | 0 | 205632 | 0 | 100 | 0
18403.165
C |  | 220 KV TRANS LINES
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 0.17014 |  |  |  | 720 | 1 | 21.879 | 89.3393 | 15752.88 | 0.0056713 | 99.4329 | 4.0833
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) |  |  |  |  | 720 | 1 | 16.894 | 0 | 12163.68 | 0 | 100 | 0
3 | BILUP2202 | 220KV ALLD-REWA RD-I |  |  |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
4 | BILUP2203 | 220KV ALLD-REWA RD-II |  |  |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
5 | NR122001 | 220KV ANTA-BHIL-I |  |  |  |  | 720 | 1 | 186.667 | 0 | 134400.24 | 0 | 100 | 0
6 | NR122002 | 220KV ANTA-BHIL-II |  |  |  | 0.15903 | 720 | 1 | 186.667 | 0 | 134400.24 | 0 | 100 | 0
7 | NR122003 | 220KV ANTA-DAUSA |  |  |  |  | 720 | 1 | 208.307 | 0 | 149981.04 | 0 | 100 | 0
8 | NR122004 | 220KV ANTA-RAPPC | 1899-12-31 03:42 |  |  |  | 720 | 1 | 87.544 | 2424.9688 | 63031.68 | 0.038472 | 96.1528 | 27.7
9 | NR122005 | 220KV ANTA-S.MDHPR |  |  |  |  | 720 | 1 | 102.164 | 0 | 73558.08 | 0 | 100 | 0
10 | NR122006 | 220KV AUR-SIKANDARA-I |  |  |  | 0.83056 | 720 | 1 | 182.176 | 0 | 131166.72 | 0 | 100 | 0
11 | NR122007 | 220KV AUR-SIKANDARA-II |  |  |  | 0.83194 | 720 | 1 | 182.176 | 0 | 131166.72 | 0 | 100 | 0
12 | NR122008 | 220KV BASSI-BAGRU |  |  |  |  | 720 | 1 | 35.353 | 0 | 25454.16 | 0 | 100 | 0
13 | NR122009 | 220KV BASSI-DAUSA-I |  |  |  | 0.11458 | 720 | 1 | 20.109 | 0 | 14478.48 | 0 | 100 | 0
14 | NR122010 | 220KV BASSI-DAUSA-II |  |  |  | 0.11458 | 720 | 1 | 20.109 | 0 | 14478.48 | 0 | 100 | 0
15 | NR122011 | 220KV BASSI-IG NAGAR |  |  |  |  | 720 | 1 | 22.478 | 0 | 16184.16 | 0 | 100 | 0
16 | NR122012 | 220KV DGANGA-BLY(UP)-II |  |  |  | 1900-01-12 20:55 | 720 | 2 | 234.59 | 0 | 337809.6 | 0 | 100 | 0
17 | NR122013 | 220KV DGANGA-PITHORAGRH |  |  |  | 1900-01-12 20:51 | 720 | 2 | 59.01 | 0 | 84974.4 | 0 | 100 | 0
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I |  |  |  |  | 720 | 1 | 5.5 | 0 | 3960 | 0 | 100 | 0
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II |  |  |  |  | 720 | 1 | 5.5 | 0 | 3960 | 0 | 100 | 0
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH |  |  |  |  | 720 | 1 | 6 | 0 | 4320 | 0 | 100 | 0
21 | NR122041 | 220KV FATEHPUR-NAUBASTA |  |  |  |  | 720 | 1 | 6 | 0 | 4320 | 0 | 100 | 0
22 | BILHY2201 | 220KV FGPP-PALLA-I |  | 0.035417 | 0.24653 | 1899-12-31 05:26 | 714.0833 | 1 | 15.69 | 0 | 11203.9675 | 0 | 100 | 0
23 | BILHY2202 | 220KV FGPP-PALLA-II |  |  |  |  | 720 | 1 | 15.69 | 0 | 11296.8 | 0 | 100 | 0
24 | BILHY2203 | 220KV FGPP-SPUR-I |  |  |  |  | 720 | 1 | 17.691 | 0 | 12737.52 | 0 | 100 | 0
25 | BILHY2204 | 220KV FGPP-SPUR-II |  |  |  |  | 720 | 1 | 17.691 | 0 | 12737.52 | 0 | 100 | 0
26 | NR122014 | 220KV HIRAPURA-IG NAGAR |  |  |  |  | 720 | 2 | 24.875 | 0 | 35820 | 0 | 100 | 0
27 | NR122015 | 220KV HIRAPURA-SANGANER |  |  |  |  | 720 | 1 | 12 | 0 | 8640 | 0 | 100 | 0
28 | NR122016 | 220KV KNP-MAINPURI |  |  |  |  | 720 | 1 | 10.4 | 0 | 7488 | 0 | 100 | 0
29 | NR122017 | 220KV KNP-NAUBASTA |  |  |  | 0.13958 | 720 | 1 | 14.86 | 0 | 10699.2 | 0 | 100 | 0
30 | NR122018 | 220KV KNP-PANKI-I |  |  |  |  | 720 | 1 | 10.4 | 0 | 7488 | 0 | 100 | 0
31 | NR122019 | 220KV KNP-PANKI-II |  | 0.018056 |  | 1900-01-03 10:39 | 720 | 1 | 14.86 | 0 | 10699.2 | 0 | 100 | 0
32 | NR122020 | 220KV KNP-UNCHR-I |  |  |  | 0.75764 | 720 | 1 | 143.553 | 0 | 103358.16 | 0 | 100 | 0
33 | NR122021 | 220KV KNP-UNCHR-II |  |  |  | 1899-12-31 09:15 | 720 | 1 | 143.553 | 0 | 103358.16 | 0 | 100 | 0
34 | NR122022 | 220KV KNP-UNCHR-III |  |  |  | 0.45208 | 720 | 1 | 144.63 | 0 | 104133.6 | 0 | 100 | 0
35 | NR122023 | 220KV KNP-UNCHR-IV |  |  |  | 0.54028 | 720 | 1 | 144.63 | 0 | 104133.6 | 0 | 100 | 0
36 | BILUP2204 | 220KV MEERUT-MPURAM-I |  |  |  | 0.37292 | 720 | 1 | 2.316 | 0 | 1667.52 | 0 | 100 | 0
37 | BILUP2205 | 220KV MEERUT-MPURAM-II |  |  |  | 0.37014 | 720 | 1 | 9.254 | 0 | 6662.88 | 0 | 100 | 0
38 | BILUP2206 | 220KV MEERUT-NARA |  | 0.13611 |  | 1900-01-01 01:43 | 720 | 1 | 2.316 | 0 | 1667.52 | 0 | 100 | 0
39 | BILUP2207 | 220KV MEERUT-SHTBDNGR |  |  |  | 0.18056 | 720 | 1 | 8.234 | 0 | 5928.48 | 0 | 100 | 0
40 | BILUP2208 | 220KV MEERUT-SIMBHOLI |  | 0.040972 |  | 0.020833 | 720 | 1 | 9.254 | 0 | 6662.88 | 0 | 100 | 0
41 | NR122024 | 220KV PITHORAGRH-BRLY(UP) |  |  |  |  | 720 | 1 | 177.88 | 0 | 128073.6 | 0 | 100 | 0
42 | NR122025 | 220KV RAIBRLY-CHINHAT |  |  |  | 0.39861 | 720 | 1 | 1.19 | 0 | 856.8 | 0 | 100 | 0
43 | NR122026 | 220KV RAIBRLY-LKO(UP) |  |  |  | 0.26389 | 720 | 1 | 1.19 | 0 | 856.8 | 0 | 100 | 0
44 | NR122027 | 220KV RAPPB-CHITT-I |  | 0.0090278 |  | 0.038194 | 720 | 1 | 128.833 | 0 | 92759.76 | 0 | 100 | 0
45 | NR122028 | 220KV RAPPB-CHITT-II |  |  |  |  | 720 | 1 | 128.833 | 0 | 92759.76 | 0 | 100 | 0
46 | NR122029 | 220KV RAPPB-RAPPC |  |  |  |  | 720 | 1 | 0.175 | 0 | 126 | 0 | 100 | 0
47 | NR122030 | 220KV RAPPB-UDAIPUR |  |  |  | 0.33889 | 720 | 1 | 230.297 | 0 | 165813.84 | 0 | 100 | 0
48 | NR122031 | 220KV S.MDHPR-DAUSA-I |  |  |  |  | 720 | 1 | 106.243 | 0 | 76494.96 | 0 | 100 | 0
49 | NR122042 | 220KV SIKAR-RATANGARH-I |  |  |  |  | 720 | 1 | 2.83 | 0 | 2037.6 | 0 | 100 | 0
50 | NR122044 | 220KV SIKAR-RATANGARH-II |  |  |  |  | 720 | 1 | 2.83 | 0 | 2037.6 | 0 | 100 | 0
51 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I |  |  |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
52 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II |  |  |  |  | 720 | 1 | 3 | 0 | 2160 | 0 | 100 | 0
53 | NR122032 | 220KV SITARGANJ-BLY(UP) | 0.023611 |  |  | 0.26319 | 720 | 1 | 105.72 | 59.908 | 76118.4 | 0.00078704 | 99.9213 | 0.56667
54 | NR122033 | 220KV TNKPR-BLY(UP) |  |  |  |  | 720 | 1 | 106 | 0 | 76320 | 0 | 100 | 0
55 | NR122034 | 220KV TNKPR-SITARGANJ |  |  |  |  | 720 | 1 | 42.55 | 0 | 30636 | 0 | 100 | 0
56 | NR122035 | 220KV UNCHR-RAIBRLY-I |  |  |  | 1899-12-31 10:27 | 720 | 1 | 0.92 | 0 | 662.4 | 0 | 100 | 0
57 | NR122036 | 220KV UNCHR-RAIBRLY-II |  |  |  |  | 720 | 1 | 0.92 | 0 | 662.4 | 0 | 100 | 0
58 | NR122037 | 220KV UNCHR-RAIBRLY-III |  |  |  |  | 720 | 1 | 42.5 | 0 | 30600 | 0 | 100 | 0
3441.931
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA |  |  |  |  | 720 | 1 | 58 | 0 | 41760 | 0 | 100 | 0
|  | TOTAL FOR T/LS | 1900-01-04 18:02 | 0.86111 | 1899-12-31 04:43 | 1900-05-25 10:30 |  |  | 21903.096 | 87371.4538 | 34890575.1608 | 0.0025042 | 99.7496
|  | OVERALL SYSTEM AVAILABILITY= |  | 99.925 | % (AC) | 99.9225 | (AC& HVDC)
E |  | 765/400 KV ICT'S | [5 empty] | M.F. | MVA | OHxMVAxMF | THMxMVAxMF
1 | NR1ICT707 | 400/765KV ICT-I AGRA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
2 | NR1ICT708 | 400/765KV ICT-II AGRA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
3 | NR1ICT701 | 765/400kv ICT-I BALIA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
4 | NR1ICT702 | 765/400kv ICT-II BALIA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
13 | NR1ICT713 | 765/400kv ICT-I MEERUT |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
14 | NR1ICT714 | 765/400kv ICT-II MEERUT |  |  |  |  | 720 | 2.5 | 1500 | 0 | 2700000 | 0 | 100 | 0
F |  | 400/220 KV ICT'S
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
3 | NR1ICT03 | 315MVA ICT-I BASSI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
4 | NR1ICT04 | 315MVA ICT-II BASSI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
5 | NR1ICT05 | 315MVA ICT-III BAWANA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
6 | NR1ICT06 | 315MVA ICT-I BHINMAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
7 | NR1ICT07 | 315MVA ICT-II BHINMAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
8 | NR1ICT08 | 315MVA ICT-I BHIWADI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
9 | NR1ICT09 | 315MVA ICT-II BHIWADI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
10 | NR1ICT54 | 315MVA ICT-III BHIWADI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
11 | NR1ICT10 | 315MVA ICT-I BLBGARH |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
12 | NR1ICT11 | 315MVA ICT-II BLBGARH |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
13 | NR1ICT12 | 315MVA ICT-III BLBGARH |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
14 | NR1ICT13 | 315MVA ICT-IV BLBGARH |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
15 | NR1ICT48 | 315MVA ICT-I FATEHPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
16 | NR1ICT49 | 315MVA ICT-II FATEHPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
17 | NR1ICT14 | 315MVA ICT-I GORAKHPR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
18 | NR1ICT15 | 315MVA ICT-II GORAKHPR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
19 | NR1ICT42 | 315MVA ICT-I GURGAON |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
20 | NR1ICT51 | 315MVA ICT-II GURGAON |  |  |  | 0.25903 | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
21 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
22 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
23 | NR1ICT16 | 315MVA ICT-I KANKROLI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
24 | NR1ICT17 | 315MVA ICT-II KANKROLI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
25 | NR1ICT18 | 315MVA ICT-III KANKROLI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
26 | NR1ICT19 | 315MVA ICT-I KANPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
27 | NR1ICT20 | 315MVA ICT-II KANPUR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
28 | NR1ICT21 | 315MVA ICT-I KOTA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
29 | NR1ICT22 | 315MVA ICT-II KOTA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
30 | NR1ICT23 | 315MVA ICT-I LUCKNOW |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
31 | NR1ICT53 | 500MVA ICT-II LUCKNOW |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
32 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
33 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
34 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
35 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
36 | NR1ICT26 | 315MVA ICT-I MAINPURI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
37 | NR1ICT27 | 315MVA ICT-II MAINPURI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
38 | NR1ICT28 | 315MVA ICT-I MANDOLA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
39 | NR1ICT29 | 315MVA ICT-II MANDOLA | 0.11736 |  |  |  | 720 | 2.5 | 315 | 2218.125 | 567000 | 0.003912 | 99.6088 | 2.8167
40 | NR1ICT30 | 315MVA ICT-III MANDOLA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
41 | NR1ICT31 | 315MVA ICT-IV MANDOLA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
42 | NR1ICT58 | 500MVA ICT-I MANESAR |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
43 | NR1ICT61 | 500MVA ICT-II MANESAR |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
44 | NR1ICT32 | 315MVA ICT-I MEERUT |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
45 | NR1ICT33 | 315MVA ICT-II MEERUT | 0.058333 |  |  |  | 720 | 2.5 | 315 | 1102.5 | 567000 | 0.0019444 | 99.8056 | 1.4
46 | NR1ICT34 | 315MVA ICT-III MEERUT |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
47 | NR1ICT35 | 315MVA ICT-I MUZFRNGR |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
48 | NR1ICT55 | 500MVA ICT-I NIMRANA |  |  |  |  | 720 | 2.5 | 500 | 0 | 900000 | 0 | 100 | 0
49 | NR1ICT50 | 315MVA ICT-II NIMRANA |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
50 | NR1ICT36 | 315MVA ICT-I ROORKI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
51 | NR1ICT37 | 315MVA ICT-II ROORKI |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
52 | NR1ICT59 | 315MVA ICT-I SOHAWAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
53 | NR1ICT60 | 315MVA ICT-II SOHAWAL |  |  |  |  | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
54 | NR1ICT56 | 315MVA ICT-I SIKAR |  |  |  | 0.14097 | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
55 | NR1ICT52 | 315MVA ICT-II SIKAR |  |  |  | 0.35278 | 720 | 2.5 | 315 | 0 | 567000 | 0 | 100 | 0
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ |  |  |  |  | 720 | 2.5 | 100 | 0 | 180000 | 0 | 100 | 0
|  | TOTAL FOR ICTs | 0.17569 | 0 | 0 | 0.75278 |  | 190 |  | 3320.625 | 72909000 | 4.5545e-05 | 99.9954
H |  | HVDC RIHAND-DADRI | [5 empty] | TCR | RC | TCR x OH | THM x RC
1 | NR1DCP01 | 500KV HVDC R-D POLE-I |  |  |  |  | 720 | 750 | 750 | 0 | 540000 | 0 | 100 | 0
2 | NR1DCP02 | 500KV HVDC R-D POLE-II |  | 0.086806 |  |  | 720 | 750 | 750 | 0 | 540000 | 0 | 100 | 0
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 0.013194 |  |  |  | 720 | 1250 | 1250 | 395.8333 | 900000 | 0.00043981 | 99.956 | 0.31667
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 0.022222 |  |  |  | 720 | 1250 | 1250 | 666.6667 | 900000 | 0.00074074 | 99.9259 | 0.53333
|  | TOTAL FOR HVDC line | 0.035417 | 0.086806 | 0 | 0 |  |  |  | 1062.5 | 2880000 | 0.00036892 | 99.9631
J |  | HVDC BTB VINDH | [5 empty] | TCR | RC | TCR x OH | THM x RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I | 0.37153 |  |  | 0.80903 | 720 | 250 | 250 | 2229.1667 | 180000 | 0.012384 | 98.7616 | 8.9167
2 | NR1DCB02 | +/-250MW HVDC B/B BLOCK-II | 0.23958 |  |  | 0.13056 | 720 | 250 | 250 | 1437.5 | 180000 | 0.0079861 | 99.2014 | 5.75
|  | TOTAL FOR HVDC VINDHYACHAL | 0.61111 | 0 | 0 | 0.93958 |  |  |  | 3666.6667 | 360000 | 0.010185 | 98.9815
K |  | HVDC BTB SASARAM
1 | NEDCB01 | +/-500MW HVDC B/B SASARAM | 0.055556 | 0.05625 |  | 1900-01-18 11:19 | 720 | 500 | 500 | 666.6667 | 360000 | 0.0018519 | 99.8148 | 1.3333
|  | TOTAL FOR HVDC SASARAM | 0.055556 | 0.05625 | 0 | 1900-01-18 11:19 |  |  |  | 666.6667 | 360000 | 0.0018519 | 99.8148
L |  | SVC, KANPUR | [5 empty] | M.F. | MVA | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  |  |  |  | 720 | 4 | 280 | 0 | 806400 | 0 | 100 | 0
2 | NR1SVC02 | +/-140MVAR SVC-II |  |  |  |  | 720 | 4 | 280 | 0 | 806400 | 0 | 100 | 0
|  | TOTAL FOR SVC | 0 | 0 | 0 | 0 |  |  |  | 0 | 1612800 | 0 | 100
M |  | Bus & Switch Line Reactor | [5 empty] | M.F. | MVA | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-II AGRA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
2 | NR1BRT26 | 125MVAR B/Reactor-III AGRA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA |  |  |  | 0.18889 | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA |  |  |  | 0.19167 | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 |  |  |  | 1899-12-31 09:10 | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY |  |  |  | 0.52917 | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
14 | NR1BRT04 | 50MVAR B/Reactor BASSI |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
15 | NR1BRT05 | 80MVAR B/Reactor BHINMAL |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
16 | NR1BRT15 | 80MVAR B/Reactor BHIWADI |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
18 | NR1BRT07 | 80MVAR B/Reactor BLBGARH |  |  |  | 0.19097 | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
19 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
20 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
21 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 |  |  |  |  | 720 | 4 | 330 | 0 | 950400 | 0 | 100 | 0
22 | NR1BRT39 | 125MVAR B/Reactor GORAKHPUR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
23 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
24 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
25 | NR1BRT08 | 50MVAR B/Reactor KANKROLI |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
26 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
27 | NR1BRT09 | 80MVAR B/Reactor KOTA |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
28 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
29 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
30 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
31 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
32 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
33 | NR1BRT11 | 50MVAR B/Reactor MANDOLA |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
34 | NR1BRT30 | 125MVAR B/Reactor MANESAR |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
35 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
36 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  |  |  | 1900-01-29 | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
37 | NR1BRT24 | 80MVAR B/Reactor NIMRANA |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
38 | NR1BRT40 | 125MVAR B/Reactor ROORKI |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
39 | NR1BRT29 | 80MVAR B/Reactor SIKAR |  |  |  |  | 720 | 4 | 80 | 0 | 230400 | 0 | 100 | 0
40 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | 720 | 4 | 93.2 | 0 | 268416 | 0 | 100 | 0
41 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | 720 | 4 | 93.2 | 0 | 268416 | 0 | 100 | 0
42 | NR1BRT42 | 125MVAR B/Reactor-I VINDH |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
43 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
44 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
45 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
46 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
47 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
48 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
49 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
50 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
51 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
52 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line |  |  |  |  | 720 | 4 | 330 | 0 | 950400 | 0 | 100 | 0
53 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
54 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
55 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
56 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
57 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
58 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
59 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE |  |  |  |  | 720 | 4 | 63 | 0 | 181440 | 0 | 100 | 0
60 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
61 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
62 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II |  |  |  |  | 720 | 4 | 50 | 0 | 144000 | 0 | 100 | 0
63 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line |  |  |  |  | 720 | 4 | 240 | 0 | 691200 | 0 | 100 | 0
64 | NR1BRT43 | 125MVAR B/Reactor-II VINDH |  |  |  |  | 720 | 4 | 125 | 0 | 360000 | 0 | 100 | 0
|  | TOTAL FOR BUS REACTORS | 0 | 0 | 0 | 1900-01-31 11:35 |  |  |  | 0 | 23179392 | 0 | 100
|  | TOTAL | 1900-01-05 15:06 | 1899-12-31 00:06 | 1899-12-31 04:43 | 1900-07-18 02:01
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(D18:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM([DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = SUM(E18:[OTHERS, row above])
OTHERS = SUM([OTHERS, row above])
Outage Not To Consider = SUM(F18:[Outage Not To Consider, row above])
Outage Not To Consider = SUM([Outage Not To Consider, row above])
Deemed = SUM(G18:[Deemed, row above])
Deemed = SUM([Deemed, row above])
Note on C158: cpcc: LILO of Alld-Phulpur at Jhusi .DOC-01-08-12
Note on C159: cpcc: LILO of Alld-Phulpur at Jhusi .DOC-01-08-12
Note on C169: Line reconfigured/ connected by RRVPNL at their Bagru S/S on 12/5/10. PG portion unchanged.