## OUTAGE_May_13
POWER GRID CORPORATION OF INDIA LTD.
NORTHERN REGION - 1
CPCC, N. DELHI
DOC No: NR-I/CPCC/II
MONTH – MAY'2013 LINE/ ICT OUTAGE DETAILS
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Classification/ Category Code | REASON OF OUTAGE | NRLDC CODE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Code
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12
NEDCB01 | 405147 | +/-500MW HVDC B/B SASARAM | 2013-05-14 12:50 | 2013-05-14 17:12 | 0.18194 | 0 | 0 | 0 | OMST | TRIPPED DUE TO FAILURE OF CAPACITOR OF EASTERN SIDE CAUSED BY BIRDS STRIKE
NEDCB01 | 405161 | +/-500MW HVDC B/B SASARAM | 2013-05-16 08:41 | 2013-05-16 09:17 | 0 | 0.025 | 0 | 0 | OMSU | TRIPPED DUE TO AUX POWER FAILURE PROBLEM IN BSEB SYSTEM
NEDCB01 | 405187 | +/-500MW HVDC B/B SASARAM | 2013-05-20 17:33 | 2013-05-20 17:37 | 0 | 0.0027778 | 0 | 0 | OMSU | TRIPPED DURING CHARGING OF 765KV,1500MVA ICT AT SSRM END.
NEDCB01 | 405245 | +/-500MW HVDC B/B SASARAM | 2013-05-25 19:02 | 2013-05-25 19:32 | 0 | 0.020833 | 0 | 0 | OMSU | TRIPPED DUE TO FAILURE OF AUXILARY SUPPL
NEDCB01 | 405288 | +/-500MW HVDC B/B SASARAM | 2013-05-28 11:52 | 2013-05-28 12:02 | 0 | 0.0069444 | 0 | 0 | OMSU | TRIPPED DUE TO AXILIARY SUPPLY FAILURE FROM BSEB.
NEDCB01 | 405320 | +/-500MW HVDC B/B SASARAM | 2013-05-30 18:12 | 2013-05-30 18:38 | 0 | 0.018056 | 0 | 0 | OMSU | TRIPPED DUE TO DIP IN AXILIARY SUPPLY FROM BSEB.
NEDCB01 | 405325 | +/-500MW HVDC B/B SASARAM | 2013-05-31 06:07 | 2013-05-31 07:06 | 0 | 0.040972 | 0 | 0 | OMSU | TRIPPED DUE TO AUXILIARY POWER SUPPLY FAILURE FROM BSEB.
|  | SUB TOTAL |  |  | 0.18194 | 0.11458 | 0 | 0
NWDCB01 | 105180 | VINDH HVDC B/B BLOCK-I | 2013-05-23 15:02 | 2013-05-28 01:15 | 0 | 0 | 0 | 1900-01-03 10:13 | SCSD | S/D for Bus extention work to accomodate 2nd Reactor. | N-1233
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-03 10:13
NWDCB02 | 105178 | VINDH HVDC B/B BLOCK-II | 2013-05-23 10:21 | 2013-05-23 12:53 | 0 | 0 | 0 | 0.10556 | SCSD | S/D For New Bus errection for accomodating 2nd Reactor. | N-1216
NWDCB02 | 105216 | VINDH HVDC B/B BLOCK-II | 2013-05-29 08:36 | 2013-05-31 22:29 | 0 | 0 | 0 | 1900-01-01 13:53 | SCSD | S/D for Bus extention work to accomodate 2nd Reactor. | N/1514
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-01 16:25
NR1DCP01 | 105239 | 500KV HVDC R-D POLE-I | 2013-05-31 17:18 | 2013-05-31 17:39 | 0.014583 | 0 | 0 | 0 | LEFT | Trip on DC line Earth Fault. Rh=31.1km, DDR=783.9km.
|  | SUB TOTAL |  |  | 0.014583 | 0 | 0 | 0
NR1DCP02 | 105209 | 500KV HVDC R-D POLE-II | 2013-05-28 10:18 | 2013-05-28 18:03 | 0 | 0 | 0 | 0.32292 | LCSD | S/D for installation of polymer insulator strings. | N-1472
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.32292
NR1DCP03 | 105068 | HVDC BALIA-BHWD POLE-I | 2013-05-09 14:19 | 2013-05-09 18:33 | 0.17639 | 0 | 0 | 0 | OSPT | S/D to attend Y-ph isolator hot spot at Balia. | N-453
|  | SUB TOTAL |  |  | 0.17639 | 0 | 0 | 0
NR176502 | 105024 | 765KV AGRA-FATEHPUR | 2013-05-05 08:13 | 2013-05-05 13:10 | 0.20625 | 0 | 0 | 0 | OSFT | S/D to attend Gantry Jumper hotspot at Fatehpur. | N-217
NR176502 | 105174 | 765KV AGRA-FATEHPUR | 2013-05-23 07:35 | 2013-05-23 21:29 | 0 | 0 | 0 | 0.57917 | LCSD | S/D for installation of polymer insulator strings. | N-1201
NR176502 | 105184 | 765KV AGRA-FATEHPUR | 2013-05-24 07:17 | 2013-05-24 20:42 | 0 | 0 | 0 | 0.55903 | LCSD | S/D for installation of polymer insulator strings. | N-1273
NR176502 | 105190 | 765KV AGRA-FATEHPUR | 2013-05-25 07:19 | 2013-05-25 19:39 | 0 | 0 | 0 | 0.51389 | LCSD | S/D for installation of polymer insulator strings. | N-1336
|  | SUB TOTAL |  |  | 0.20625 | 0 | 0 | 1899-12-31 15:39
NR176504 | 105008 | 765KV AGRA-JHATIKALA | 2013-05-02 09:53 | 2013-05-02 19:00 | 0 | 0 | 0 | 0.37986 | LCSD | S/D due to heavy induction during Fthpr-II line bay eqpt erection work at Agra. | N-53
NR176504 | 105013 | 765KV AGRA-JHATIKALA | 2013-05-03 09:32 | 2013-05-03 20:08 | 0 | 0 | 0 | 0.44167 | LCSD | S/D due to heavy induction during Fthpr-II line bay eqpt erection work at Agra. | N-101
NR176504 | 105040 | 765KV AGRA-JHATIKALA | 2013-05-05 18:47 | 2013-05-05 20:04 | 0 | 0 | 0.053472 | 0 | GOVC | Tripped on O/VOL protn at Agra>800kv.
NR176504 | 105063 | 765KV AGRA-JHATIKALA | 2013-05-09 04:03 | 2013-05-09 04:33 | 0 | 0 | 0.020833 | 0 | GOVC | O/V protn trip at Agra>800kv, D/T recd at Jhatiklan.
NR176504 | 105094 | 765KV AGRA-JHATIKALA | 2013-05-12 17:03 | 2013-05-12 17:24 | 0.014583 | 0 | 0 | 0 | LEFT | A/R & Trip on Y-N fault in reclaim time. Agra=38.8km.
NR176504 | 105110 | 765KV AGRA-JHATIKALA | 2013-05-14 18:28 | 2013-05-14 19:19 | 0.035417 | 0 | 0 | 0 | LEFT | Tripped on Y-N fault in reclaim time. Jhat-9km,Ag-220.6 km.
NR176504 | 105140 | 765KV AGRA-JHATIKALA | 2013-05-19 13:29 | 2013-05-19 13:29 | 0 | 0 | 0 | 0 | LART | A/reclosed on B-N fault. FLR:Ag-31.1km, Jhat-193km.
NR176504 | 105141 | 765KV AGRA-JHATIKALA | 2013-05-19 13:34 | 2013-05-19 13:41 | 0.0048611 | 0 | 0 | 0 | LEFT | A/R and tripped on B-N fault. FLR:Ag-31.9km, Jhat-191km.
NR176504 | 105144 | 765KV AGRA-JHATIKALA | 2013-05-19 18:50 | 2013-05-19 19:28 | 0.026389 | 0 | 0 | 0 | OSPT | S/D for lopping of suspected trees at loc.20/16-17. | N-1001
NR176504 | 105150 | 765KV AGRA-JHATIKALA | 2013-05-20 11:18 | 2013-05-20 21:02 | 0 | 0 | 0 | 0.40556 | LCSD | S/D for construction of Fatehpur-II line bay at Agra. | N-1039
NR176504 | 105156 | 765KV AGRA-JHATIKALA | 2013-05-21 07:37 | 2013-05-21 20:00 | 0 | 0 | 0 | 0.51597 | LCSD | S/D for construction of Fatehpur-II line bay at Agra. | N-1088
NR176504 | 105160 | 765KV AGRA-JHATIKALA | 2013-05-21 20:00 | 2013-05-23 23:18 | 1900-01-01 03:18 | 0 | 0 | 0 | OSPT | S/D for rectification of bend cross arm of B-ph at loc 131/1.
|  | SUB TOTAL |  |  | 1900-01-01 05:15 | 0 | 0.074306 | 1899-12-31 17:50
NR176503 | 105210 | 765KV FATEHPUR-GAYA | 2013-05-28 12:54 | 2013-05-28 20:57 | 0 | 0 | 0 | 0.33542 | LCSD | S/D for aux. Bus isolators erection work at Gaya. | N-1482
NR176503 | 105223 | 765KV FATEHPUR-GAYA | 2013-05-30 10:29 | 2013-05-30 22:47 | 0 | 0 | 0 | 0.5125 | LCSD | S/D by ER for commissioning of isolators connected to 765KV Auxiliary BUS at Gaya SS. | N-1584
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.84792
NR176501 | 105023 | 765KV LUCKNOW-BALIA | 2013-05-05 07:57 | 2013-05-05 20:14 | 0 | 0 | 0 | 0.51181 | LCSD | S/D for installation of polymer insulator strings. | N-215
NR176501 | 105043 | 765KV LUCKNOW-BALIA | 2013-05-06 07:51 | 2013-05-06 20:55 | 0 | 0 | 0 | 0.54444 | LCSD | S/D for installation of polymer insulator strings. | N-270
NR176501 | 105054 | 765KV LUCKNOW-BALIA | 2013-05-07 07:29 | 2013-05-07 20:45 | 0 | 0 | 0 | 0.55278 | LCSD | S/D for installation of polymer insulator strings. | N-318
NR176501 | 105058 | 765KV LUCKNOW-BALIA | 2013-05-08 07:34 | 2013-05-08 20:43 | 0 | 0 | 0 | 0.54792 | LCSD | S/D for installation of polymer insulator strings. | N-358
NR176501 | 105064 | 765KV LUCKNOW-BALIA | 2013-05-09 07:24 | 2013-05-09 20:50 | 0 | 0 | 0 | 0.55972 | LCSD | S/D for installation of polymer insulator strings. | N-428
NR176501 | 105072 | 765KV LUCKNOW-BALIA | 2013-05-10 07:19 | 2013-05-10 19:52 | 0 | 0 | 0 | 0.52292 | LCSD | S/D for installation of polymer insulator strings. | N-498
NR176501 | 105081 | 765KV LUCKNOW-BALIA | 2013-05-11 07:28 | 2013-05-11 21:58 | 0 | 0 | 0 | 0.60417 | LCSD | S/D for installation of polymer insulator strings. | N-560
NR176501 | 105090 | 765KV LUCKNOW-BALIA | 2013-05-12 07:34 | 2013-05-12 20:36 | 0 | 0 | 0 | 0.54306 | LCSD | S/D for installation of polymer insulator strings. | N-610
NR176501 | 105099 | 765KV LUCKNOW-BALIA | 2013-05-13 07:54 | 2013-05-13 20:25 | 0 | 0 | 0 | 0.52153 | LCSD | S/D for installation of polymer insulator strings. | N-661
NR176501 | 105104 | 765KV LUCKNOW-BALIA | 2013-05-14 07:24 | 2013-05-14 20:11 | 0 | 0 | 0 | 0.53264 | LCSD | S/D for installation of polymer insulator strings. | N-705
NR176501 | 105118 | 765KV LUCKNOW-BALIA | 2013-05-15 07:53 | 2013-05-15 22:44 | 0 | 0 | 0 | 0.61875 | LCSD | S/D for installation of polymer insulator strings. | N-771
NR176501 | 105122 | 765KV LUCKNOW-BALIA | 2013-05-16 08:11 | 2013-05-16 19:15 | 0 | 0 | 0 | 0.46111 | LCSD | S/D for installation of polymer insulator strings. | N-827
NR176501 | 105127 | 765KV LUCKNOW-BALIA | 2013-05-17 07:12 | 2013-05-17 19:05 | 0 | 0 | 0 | 0.49514 | LCSD | S/D for installation of polymer insulator strings. | N-881
NR176501 | 105130 | 765KV LUCKNOW-BALIA | 2013-05-18 06:52 | 2013-05-18 19:35 | 0 | 0 | 0 | 0.52986 | LCSD | S/D for installation of polymer insulator strings. | N-931
NR176501 | 105139 | 765KV LUCKNOW-BALIA | 2013-05-19 07:30 | 2013-05-19 19:43 | 0 | 0 | 0 | 0.50903 | LCSD | S/D for installation of polymer insulator strings. | N-984
NR176501 | 105145 | 765KV LUCKNOW-BALIA | 2013-05-20 07:04 | 2013-05-20 19:01 | 0 | 0 | 0 | 0.49792 | LCSD | S/D for installation of polymer insulator strings. | N-1014
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-07 13:16
NR140003 | 105120 | 400KV AGRA-AURAIYA-I | 2013-05-15 10:57 | 2013-05-15 17:41 | 0 | 0 | 0 | 0.28056 | OSPD | S/D by Auriya/NTPC for protection testing work. | N-782
NR140003 | 105133 | 400KV AGRA-AURAIYA-I | 2013-05-18 09:27 | 2013-05-18 19:22 | 0 | 0 | 0 | 0.41319 | OSPD | S/D by NTPC-Auraiya for CB o/hauling work. | N-937
NR140003 | 105146 | 400KV AGRA-AURAIYA-I | 2013-05-20 09:19 | 2013-05-20 20:26 | 0 | 0 | 0 | 0.46319 | OSPD | S/D by UPPCL for stringing of their Mainpuri-Orai line. | N-1018
NR140003 | 105157 | 400KV AGRA-AURAIYA-I | 2013-05-21 09:42 | 2013-05-21 17:50 | 0 | 0 | 0 | 0.33889 | OSPD | S/D by UPPCL for stringing of their Mainpuri-Orai line. | N-1095
NR140003 | 105222 | 400KV AGRA-AURAIYA-I | 2013-05-30 09:24 | 2013-05-30 19:18 | 0 | 0 | 0 | 0.4125 | OSPD | S/D by Auraiya/NTPC for commissioning of new CB. | N-1580
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 21:48
NR140004 | 105129 | 400KV AGRA-AURAIYA-II | 2013-05-17 18:14 | 2013-05-17 18:29 | 0.010417 | 0 | 0 | 0 | OSPT | S/D to attend L/Reactor problem at Agra. | N-913
NR140004 | 105147 | 400KV AGRA-AURAIYA-II | 2013-05-20 09:28 | 2013-05-20 20:26 | 0 | 0 | 0 | 0.45694 | OSPD | S/D by UPPCL for stringing of their Mainpuri-Orai line. | N-1026
NR140004 | 105158 | 400KV AGRA-AURAIYA-II | 2013-05-21 09:43 | 2013-05-21 17:51 | 0 | 0 | 0 | 0.33889 | OSPD | S/D by UPPCL for stringing of their Mainpuri-Orai line. | N-1095
|  | SUB TOTAL |  |  | 0.010417 | 0 | 0 | 0.79583
NR140005 | 105003 | 400KV AGRA-BASSI-I | 2013-05-01 08:46 | 2013-05-01 19:06 | 0 | 0 | 0 | 0.43056 | LCSD | S/D for installation of polymer insulator strings. | N-07
NR140005 | 105007 | 400KV AGRA-BASSI-I | 2013-05-02 07:52 | 2013-05-02 17:57 | 0 | 0 | 0 | 0.42014 | LCSD | S/D for installation of polymer insulator strings. | N-48
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.85069
NR140008 | 105057 | 400KV AGRA-BHIWADI-I | 2013-05-07 14:45 | 2013-05-07 15:30 | 0.03125 | 0 | 0 | 0 | OSPT | S/D for removal of Tree encroachment at loc.416. | N-339
|  | SUB TOTAL |  |  | 0.03125 | 0 | 0 | 0
NR140009 | 105096 | 400KV AGRA-BHIWADI-II | 2013-05-12 17:36 | 2013-05-13 00:02 | 0 | 0 | 0 | 0.26806 | LVRD | H/Tripped for voltage regulation. Bhwd-438KV | N-634
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.26806
NR140010 | 105193 | 400KV AGRA-BLBGRH | 2013-05-26 12:06 | 2013-05-26 22:03 | 0.41458 | 0 | 0 | 0 | OSFT | Forecd S/D to replace faulty Y-ph CVT at Agra. | N-1381
|  | SUB TOTAL |  |  | 0.41458 | 0 | 0 | 0
NR140116 | 105114 | 400KV AGRA-JAIPUR(S)-I | 2013-05-15 04:04 | 2013-05-15 07:00 | 0 | 0 | 0 | 0.12222 | LVRD | H/Tripped for voltage regulation. Bassi-433 KV | N-762
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.12222
NR140126 | 105092 | 400KV AGRA-JAIPUR(S)-II | 2013-05-12 16:16 | 2013-05-13 00:26 | 0 | 0 | 0 | 0.34028 | LVRD | H/Tripped for voltage regulation. Bassi-433 KV | N-628
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.34028
NR140123 | 105002 | 400KV ALLD-FATEHPUR-II | 2013-05-01 08:08 | 2013-05-01 17:55 | 0 | 0 | 0 | 0.40764 | LCSD | S/D for installation of polymer insulator strings. | N-06
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.40764
NR140016 | 105132 | 400KV ALLD-SASARAM | 2013-05-18 08:16 | 2013-05-18 19:47 | 0 | 0 | 0 | 0.47986 | LCSD | S/D for retrofitment of M-I protn relay at Sasaram end. | N-934
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.47986
NR140017 | 105011 | 400KV BALIA-BIHARSHRF-I | 2013-05-03 08:25 | 2013-05-03 12:55 | 0.1875 | 0 | 0 | 0 | OSPT | S/D by ER for AMP works. | N-97
NR140017 | 105154 | 400KV BALIA-BIHARSHRF-I | 2013-05-20 18:01 | 2013-05-20 18:25 | 0 | 0 | 0.016667 | 0 | GOVC | O/V protn oprtd due to sudden voltage rise>440kv at Balia during charging of 765kv Lko-Balia line.
NR140017 | 105225 | 400KV BALIA-BIHARSHRF-I | 2013-05-31 06:01 | 2013-05-31 06:05 | 0 | 0 | 0.0027778 | 0 | GOVC | Tripped on O/V protn at Balia>435kv.
NR140017 | 105227 | 400KV BALIA-BIHARSHRF-I | 2013-05-31 06:05 | 2013-05-31 08:40 | 0 | 0 | 0 | 0.10764 | LVRD | Kept open for voltage regulation. | N-1645
|  | SUB TOTAL |  |  | 0.1875 | 0 | 0.019444 | 0.10764
NR140018 | 105240 | 400KV BALIA-BIHARSHRF-II | 2013-05-31 18:00 | 2013-06-01 | 0.25 | 0 | 0 | 0 | OMST | Trip on B-N fault during heavy rain and Wind storm. Balia=30km, B/Sarif=185km. Charging attempt fail.
|  | SUB TOTAL |  |  | 0.25 | 0 | 0 | 0
NR140021 | 105082 | 400KV BALIA-PATNA-I | 2013-05-11 07:28 | 2013-05-11 08:16 | 0 | 0 | 0.033333 | 0 | GOVC | Trip on O/VOL protn at Patna>435kv. D/T recd at Balia.
NR140021 | 105126 | 400KV BALIA-PATNA-I | 2013-05-16 19:28 | 2013-05-17 08:25 | 0 | 0 | 0 | 0.53958 | LVRD | H/Tripped for V/ Regulation. Balia-429kv. | N-868
NR140021 | 105152 | 400KV BALIA-PATNA-I | 2013-05-20 18:01 | 2013-05-20 18:27 | 0 | 0 | 0.018056 | 0 | GOVC | O/V protn oprtd due to sudden voltage rise>440kv at Balia during charging of 765kv Lko-Balia line.
NR140021 | 105226 | 400KV BALIA-PATNA-I | 2013-05-31 06:07 | 2013-05-31 06:10 | 0 | 0 | 0.0020833 | 0 | GOVC | Tripped on O/V protn at Patna>435kv.
NR140021 | 105228 | 400KV BALIA-PATNA-I | 2013-05-31 06:10 | 2013-05-31 13:55 | 0 | 0 | 0 | 0.32292 | LVRD | Kept open for voltage regulation. | N-1645
|  | SUB TOTAL |  |  | 0 | 0 | 0.053472 | 0.8625
NR140022 | 105089 | 400KV BALIA-PATNA-II | 2013-05-11 22:07 | 2013-05-14 09:34 | 0 | 0 | 0 | 1900-01-01 11:27 | LVRD | H/Tripped for voltage regulation. Balia-430 KV | N-605
NR140022 | 105109 | 400KV BALIA-PATNA-II | 2013-05-14 18:12 | 2013-05-15 09:06 | 0 | 0 | 0 | 0.62083 | LVRD | H/Tripped for voltage regulation. Balia-430KV | N-738
NR140022 | 105138 | 400KV BALIA-PATNA-II | 2013-05-19 06:29 | 2013-05-19 09:25 | 0 | 0 | 0 | 0.12222 | LVRD | Hand tripped for voltage regulation. Patna>428kv. | N-982
NR140022 | 105153 | 400KV BALIA-PATNA-II | 2013-05-20 18:01 | 2013-05-20 18:28 | 0 | 0 | 0.01875 | 0 | GOVC | O/V protn oprtd due to sudden voltage rise>440kv at Balia during charging of 765kv Lko-Balia line.
NR140022 | 105242 | 400KV BALIA-PATNA-II | 2013-05-31 18:44 | 2013-05-31 18:49 | 0 | 0 | 0.0034722 | 0 | GOVC | Trip on O/VOL protn at Balia>436kv.
NR140022 | 105243 | 400KV BALIA-PATNA-II | 2013-05-31 18:49 | 2013-06-01 | 0 | 0 | 0 | 0.21597 | LVRD | Kept open for voltage regulation. | N-1709
|  | SUB TOTAL |  |  | 0 | 0 | 0.022222 | 1900-01-02 10:28
NR140136 | 105100 | 400KV BALIA-PATNA-III | 2013-05-13 10:27 | 2013-05-13 10:48 | 0 | 0 | 0.014583 | 0 | GOVC | Tripped on O/voltage protn at Patna. DT received at Balia.
NR140136 | 105173 | 400KV BALIA-PATNA-III | 2013-05-23 07:08 | 2013-05-23 10:02 | 0 | 0 | 0 | 0.12083 | LVRD | Hand tripped for voltage regulation. Patna>428kv. | N-1199
NR140136 | 105182 | 400KV BALIA-PATNA-III | 2013-05-24 05:51 | 2013-05-24 19:52 | 0 | 0 | 0 | 0.58403 | LCSD | S/D for construction of new bay at Patna/ER. | N-1270
NR140136 | 105188 | 400KV BALIA-PATNA-III | 2013-05-25 06:12 | 2013-05-25 20:23 | 0 | 0 | 0 | 0.59097 | LCSD | S/D for construction of new bay at Patna/ER. | N-1333
|  | SUB TOTAL |  |  | 0 | 0 | 0.014583 | 1899-12-31 07:06
NR140137 | 105183 | 400KV BALIA-PATNA-IV | 2013-05-24 05:52 | 2013-05-24 20:11 | 0 | 0 | 0 | 0.59653 | LCSD | S/D for construction of new bay at Patna/ER. | N-1270
NR140137 | 105189 | 400KV BALIA-PATNA-IV | 2013-05-25 06:13 | 2013-05-25 20:40 | 0 | 0 | 0 | 0.60208 | LCSD | S/D for construction of new bay at Patna/ER. | N-1333
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 04:46
NR140140 | 105012 | 400KV BALIA-SOHAWAL-I | 2013-05-03 09:20 | 2013-05-03 17:56 | 0 | 0 | 0 | 0.35833 | LCSD | S/D for remote commissioning of isolator at Sohawal. | N-98
NR140140 | 105016 | 400KV BALIA-SOHAWAL-I | 2013-05-04 09:52 | 2013-05-04 18:44 | 0 | 0 | 0 | 0.36944 | LCSD | S/D for remote commissioning of isolator at Sohawal.
NR140140 | 105155 | 400KV BALIA-SOHAWAL-I | 2013-05-20 18:01 | 2013-05-20 18:23 | 0 | 0 | 0.015278 | 0 | GOVC | O/V protn oprtd due to sudden voltage rise>440kv at Balia during charging of 765kv Lko-Balia line.
|  | SUB TOTAL |  |  | 0 | 0 | 0.015278 | 0.72778
NR140120 | 105179 | 400KV BALIA-SOHAWAL-II | 2013-05-23 11:05 | 2013-05-23 13:10 | 0.086806 | 0 | 0 | 0 | OSPT | S/D for attending S/Reactor Bushing hot spot at Balia. | N-1230
NR140120 | 105212 | 400KV BALIA-SOHAWAL-II | 2013-05-28 19:14 | 2013-05-28 19:20 | 0 | 0 | 0 | 0.0041667 | LVRD | Hand tripped for taking S/reactor in service at Ballia. | N/1496
NR140120 | 105217 | 400KV BALIA-SOHAWAL-II | 2013-05-29 08:53 | 2013-05-29 09:07 | 0.0097222 | 0 | 0 | 0 | OSPT | S/D to isolate Sohawal-2 S/R at Ballia due to oil leakage.
|  | SUB TOTAL |  |  | 0.096528 | 0 | 0 | 0.0041667
NR140023 | 105085 | 400KV BAREILLY-BRLY(UP)-I | 2013-05-11 10:52 | 2013-05-11 18:36 | 0 | 0 | 0 | 0.32222 | OSPD | S/D by UPPCL to attend B-ph bus Isolator hotspot. | N-573
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.32222
NR140025 | 105197 | 400KV BAREILLY-LKO(UP) | 2013-05-27 12:53 | 2013-05-27 13:33 | 0 | 0.027778 | 0 | 0 | SBBU | B/Bar protn operated at LKO-UPPCL due to S/S Fault.
|  | SUB TOTAL |  |  | 0 | 0.027778 | 0 | 0
NR140026 | 105042 | 400KV BAREILLY-MBAD-I | 2013-05-06 07:37 | 2013-05-06 07:52 | 0 | 0.010417 | 0 | 0 | SPLU | Tripped only from Mbad-UP due to PLCC mal-function.
|  | SUB TOTAL |  |  | 0 | 0.010417 | 0 | 0
NR140115 | 105009 | 400KV BAREILLY-ROSA-I | 2013-05-02 18:20 | 2013-05-02 20:04 | 0.072222 | 0 | 0 | 0 | OSPT | S/D for refixing of one no sub-jumper at loc-06. | N-71
|  | SUB TOTAL |  |  | 0.072222 | 0 | 0 | 0
NR140028 | 105086 | 400KV BASSI-BHIWADI-I | 2013-05-11 17:34 | 2013-05-13 09:48 | 0 | 0 | 0 | 1899-12-31 16:14 | LVRD | H/Tripped for voltage regulation. BHI-432 KV | N-589
NR140028 | 105213 | 400KV BASSI-BHIWADI-I | 2013-05-29 08:00 | 2013-05-29 18:50 | 0 | 0 | 0 | 0.45139 | LCSD | S/D for stringing of 400kv Agra-Sikar D/C line.
NR140028 | 105233 | 400KV BASSI-BHIWADI-I | 2013-05-31 10:24 | 2013-05-31 11:40 | 0 | 0 | 0 | 0.052778 | OSPD | S/D by RRVPNL to get down a man climbed on tower-303. | N-1656
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-01 04:20
NR140117 | 105113 | 400KV BASSI-JAIPUR(S)-I | 2013-05-15 04:02 | 2013-05-15 07:09 | 0 | 0 | 0 | 0.12986 | LVRD | H/Tripped for voltage regulation. Bassi-433 KV | N-762
NR140117 | 105124 | 400KV BASSI-JAIPUR(S)-I | 2013-05-16 10:56 | 2013-05-16 12:38 | 0.070833 | 0 | 0 | 0 | OSPT | S/D for Replacement of Faulty Trip coil at Bassi end. | N-839
|  | SUB TOTAL |  |  | 0.070833 | 0 | 0 | 0.12986
NR140127 | 105093 | 400KV BASSI-JAIPUR(S)-II | 2013-05-12 16:18 | 2013-05-13 00:01 | 0 | 0 | 0 | 0.32153 | LVRD | H/Tripped for voltage regulation. Bassi-433 KV | N-628
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.32153
N-W40004 | 105101 | 400KV BHINMAL-ZERDA | 2013-05-13 10:30 | 2013-05-13 20:00 | 0 | 0 | 0 | 0.39583 | LCSD | S/D for installation of polymer insulator strings. | N-669
N-W40004 | 105106 | 400KV BHINMAL-ZERDA | 2013-05-14 08:53 | 2013-05-14 20:18 | 0 | 0 | 0 | 0.47569 | LCSD | S/D for installation of polymer insulator strings. | N-707
N-W40004 | 105117 | 400KV BHINMAL-ZERDA | 2013-05-15 08:20 | 2013-05-15 20:08 | 0 | 0 | 0 | 0.49167 | LCSD | S/D for installation of polymer insulator strings. | N-769
N-W40004 | 105123 | 400KV BHINMAL-ZERDA | 2013-05-16 08:51 | 2013-05-16 18:06 | 0 | 0 | 0 | 0.38542 | LCSD | S/D for installation of polymer insulator strings. | N-826
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 17:58
NR140032 | 105027 | 400KV BHIWADI-GURGAON | 2013-05-05 10:55 | 2013-05-05 12:26 | 0.063194 | 0 | 0 | 0 | OSPT | S/D for attending CB oil leakage at Gurgaon. | N-227
NR140032 | 105203 | 400KV BHIWADI-GURGAON | 2013-05-27 16:30 | 2013-05-27 23:28 | 0 | 0 | 0 | 0.29028 | LCSD | S/D of Bus-II at GIS Gurgaon for HV Testing of new bay. | N-1429
|  | SUB TOTAL |  |  | 0.063194 | 0 | 0 | 0.29028
NR140106 | 105047 | 400KV BHIWADI-NIMRANA-I | 2013-05-06 14:20 | 2013-05-06 15:43 | 0.057639 | 0 | 0 | 0 | OMST | Tripped during OPGW installation as it was in non-auto.
NR140106 | 105088 | 400KV BHIWADI-NIMRANA-I | 2013-05-11 18:10 | 2013-05-13 11:13 | 0 | 0 | 0 | 1899-12-31 17:03 | LVRD | H/Tripped for voltage regulation. BHI-432 KV | N-590
NR140106 | 105111 | 400KV BHIWADI-NIMRANA-I | 2013-05-14 18:53 | 2013-05-14 19:10 | 0.011806 | 0 | 0 | 0 | OMST | Tripped during OPGW installation on R-N fault as line was in non-auto mode.
NR140106 | 105112 | 400KV BHIWADI-NIMRANA-I | 2013-05-14 19:10 | 2013-05-15 09:31 | 0 | 0 | 0 | 0.59792 | LCSD | S/D for OPGW stringing work. | N-752
NR140106 | 105142 | 400KV BHIWADI-NIMRANA-I | 2013-05-19 18:08 | 2013-05-20 10:56 | 0 | 0 | 0 | 0.7 | LVRD | Hand tripped for voltage regulation. Bhwd-432kv. | N-998
NR140106 | 105211 | 400KV BHIWADI-NIMRANA-I | 2013-05-28 18:57 | 2013-05-28 20:02 | 0.045139 | 0 | 0 | 0 | OMST | Line tripped during OPGW stringing work by BGR, on R-N fault due to snapping of pilot rope. Neem-29.3kms
NR140106 | 105224 | 400KV BHIWADI-NIMRANA-I | 2013-05-30 10:47 | 2013-05-30 13:37 | 0 | 0 | 0 | 0.11806 | LCSD | S/D for OPGW installation work by M/S BGR. | N-1586
|  | SUB TOTAL |  |  | 0.11458 | 0 | 0 | 1900-01-02 03:02
NR140035 | 105029 | 400KV BLBGRH-GURGAON | 2013-05-05 12:44 | 2013-05-05 14:42 | 0.081944 | 0 | 0 | 0 | OSPT | S/D for attending CB oil leakage at Gurgaon. | N-234
NR140035 | 105095 | 400KV BLBGRH-GURGAON | 2013-05-12 17:24 | 2013-05-12 18:20 | 0 | 0 | 0.038889 | 0 | GOVC | Trip on O/VOL protn at Gurgaon.
NR140035 | 105204 | 400KV BLBGRH-GURGAON | 2013-05-27 16:30 | 2013-05-27 23:37 | 0 | 0 | 0 | 0.29653 | LCSD | S/D of Bus-II at GIS Gurgaon for HV Testing of new bay. | N-1429
|  | SUB TOTAL |  |  | 0.081944 | 0 | 0.038889 | 0.29653
NR140037 | 105097 | 400KV BLBGRH-MAINPURI-I | 2013-05-12 17:45 | 2013-05-12 19:50 | 0 | 0 | 0 | 0.086806 | LVRD | H/Tripped for voltage regulation. Mnp-430KV | N-636
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.086806
NR140044 | 105060 | 400KV DAD-PANIPAT-I | 2013-05-08 09:15 | 2013-05-08 11:23 | 0 | 0 | 0 | 0.088889 | OSPD | S/D by NTPC-Dadri for Islanding scheme connection. | N-366
NR140044 | 105115 | 400KV DAD-PANIPAT-I | 2013-05-15 05:18 | 2013-05-15 05:40 | 0 | 0.015278 | 0 | 0 | SRMU | A/Rat Dadri but tripped from Panipat-BBMB due to faulty A/R relay on B-N fault. Dad-77.24KM.
|  | SUB TOTAL |  |  | 0 | 0.015278 | 0 | 0.088889
NR140124 | 105006 | 400KV FATEHPUR-MAINPURI-I | 2013-05-02 07:16 | 2013-05-02 19:06 | 0 | 0 | 0 | 0.49306 | LCSD | S/D for installation of polymer insulator strings. | N-45
NR140124 | 105010 | 400KV FATEHPUR-MAINPURI-I | 2013-05-03 07:21 | 2013-05-03 19:25 | 0 | 0 | 0 | 0.50278 | LCSD | S/D for installation of polymer insulator strings. | N-92
NR140124 | 105014 | 400KV FATEHPUR-MAINPURI-I | 2013-05-04 07:01 | 2013-05-04 18:07 | 0 | 0 | 0 | 0.4625 | LCSD | S/D for installation of polymer insulator strings. | N-149
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 11:00
NR140125 | 105041 | 400KV FATEHPUR-MAINPURI-II | 2013-05-06 07:24 | 2013-05-06 19:03 | 0 | 0 | 0 | 0.48542 | LCSD | S/D for installation of polymer insulator strings. | N-264
NR140125 | 105059 | 400KV FATEHPUR-MAINPURI-II | 2013-05-08 07:35 | 2013-05-08 18:05 | 0 | 0 | 0 | 0.4375 | LCSD | S/D for installation of polymer insulator strings. | N-360
NR140125 | 105065 | 400KV FATEHPUR-MAINPURI-II | 2013-05-09 07:31 | 2013-05-09 17:40 | 0 | 0 | 0 | 0.42292 | LCSD | S/D for installation of polymer insulator strings. | N-427
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 08:18
NR140128 | 103056 | 400KV GURGAON-MANESAR-I | 2013-05-01 | 2013-06-01 | 0 | 0 | 0 | 1900-01-30 | LCSD | S/D for Gurgaon GIS Bus-I extention work. Out since 1242hrs of 06/03/13. | N-520
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-30
NR140129 | 105205 | 400KV GURGAON-MANESAR-II | 2013-05-27 16:30 | 2013-05-27 23:27 | 0 | 0 | 0 | 0.28958 | LCSD | S/D of Bus-II at GIS Gurgaon for HV Testing of new bay. | N-1429
NR140129 | 105236 | 400KV GURGAON-MANESAR-II | 2013-05-31 11:50 | 2013-05-31 18:40 | 0 | 0 | 0 | 0.28472 | LCSD | S/D for HV Testing of 400kv Bus-I at Gurgaon GIS. | N-1677
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.57431
NR140134 | 105176 | 400KV JHATIKALA-MUNDKA-I | 2013-05-23 08:40 | 2013-05-23 16:58 | 0 | 0 | 0 | 0.34583 | OSPD | S/D by DTL for their line maintenance work. | N-1208
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.34583
NR140135 | 105171 | 400KV JHATIKALA-MUNDKA-II | 2013-05-22 07:23 | 2013-05-22 16:53 | 0 | 0 | 0 | 0.39583 | OSPD | S/D by DTL for their line maintenance work. | N-1141
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.39583
NR140048 | 105066 | 400KV KANKROLI-BHINMAL | 2013-05-09 08:10 | 2013-05-09 21:23 | 0 | 0 | 0 | 0.55069 | LCSD | S/D for installation of polymer insulator strings. | N-430
NR140048 | 105075 | 400KV KANKROLI-BHINMAL | 2013-05-10 08:11 | 2013-05-10 19:55 | 0 | 0 | 0 | 0.48889 | LCSD | S/D for installation of polymer insulator strings. | N-502
NR140048 | 105083 | 400KV KANKROLI-BHINMAL | 2013-05-11 08:33 | 2013-05-11 20:52 | 0 | 0 | 0 | 0.51319 | LCSD | S/D for installation of polymer insulator strings. | N-564
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 13:16
NR140055 | 105098 | 400KV KNP-BLBGARH-I | 2013-05-12 18:27 | 2013-05-12 19:50 | 0 | 0 | 0 | 0.057639 | LVRD | H/Tripped for voltage regulation. Blb-428KV | N-640
NR140055 | 105136 | 400KV KNP-BLBGARH-I | 2013-05-18 12:42 | 2013-05-18 12:52 | 0 | 0 | 0.0069444 | 0 | LNCC | Tripped on Y-N fault due to falling of tree during local windstorm in forest area. FLR:Knp-33.24km,Blb-345.3km.
NR140055 | 105137 | 400KV KNP-BLBGARH-I | 2013-05-18 13:08 | 2013-05-18 15:51 | 0 | 0 | 0.11319 | 0 | LNCC | Tripped on Y-N fault due to falling of tree at loc.97-98 during wind storm. FLR:Knp-33.9km, Blb-359km. Removed.
|  | SUB TOTAL |  |  | 0 | 0 | 0.12014 | 0.057639
NR140056 | 105194 | 400KV KNP-BLBGARH-II | 2013-05-27 08:30 | 2013-05-28 20:20 | 1899-12-31 11:50 | 0 | 0 | 0 | SEFT | Trip due to Fire in KNP-II L/Reactor at BLB S/Yeard.
|  | SUB TOTAL |  |  | 1899-12-31 11:50 | 0 | 0 | 0
NR140057 | 105195 | 400KV KNP-BLBGARH-III | 2013-05-27 08:30 | 2013-05-27 13:36 | 0 | 0 | 0 | 0.2125 | GOMD | System constraint due to Fire in BLB S/Yard.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.2125
NR140058 | 105004 | 400KV KNP-PANKI-I | 2013-05-01 10:33 | 2013-05-01 11:29 | 0 | 0 | 0 | 0.038889 | OSFD | Hand tripped by UPPCL due to local Fire after transfer Bus coupler CT blasted at Panki S/S.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.038889
NR140059 | 105005 | 400KV KNP-PANKI-II | 2013-05-01 10:33 | 2013-05-01 11:32 | 0 | 0 | 0 | 0.040972 | OSFD | Hand tripped by UPPCL due to local Fire after transfer Bus coupler CT blasted at Panki S/S.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.040972
NR140063 | 105052 | 400KV KOTESHWR-KHEP-I | 2013-05-06 16:11 | 2013-05-06 16:41 | 0 | 0 | 0.020833 | 0 | GOVC | Tripped on O/voltage protn during disturbance at Tehri.
|  | SUB TOTAL |  |  | 0 | 0 | 0.020833 | 0
NR140064 | 105053 | 400KV KOTESHWR-KHEP-II | 2013-05-06 16:11 | 2013-05-06 16:37 | 0 | 0 | 0.018056 | 0 | GOVC | Tripped on O/voltage protn during disturbance at Tehri.
|  | SUB TOTAL |  |  | 0 | 0 | 0.018056 | 0
NR140065 | 105048 | 400KV KOTESHWR-TEHRI-I | 2013-05-06 16:11 | 2013-05-06 16:45 | 0 | 0.023611 | 0 | 0 | OMSU | Tripped on R-N, Z-2 fault, due to problem at Tehri/THDC.
|  | SUB TOTAL |  |  | 0 | 0.023611 | 0 | 0
NR140098 | 105051 | 400KV KOTESHWR-TEHRI-II | 2013-05-06 16:11 | 2013-05-06 16:33 | 0 | 0 | 0.015278 | 0 | GOVC | Tripped on O/voltage protn during disturbance at Tehri.
NR140098 | 105128 | 400KV KOTESHWR-TEHRI-II | 2013-05-17 07:13 | 2013-05-17 18:19 | 0 | 0 | 0 | 0.4625 | LCSD | S/D to facilitate dismentiling of old line Towers. | N-880
|  | SUB TOTAL |  |  | 0 | 0 | 0.015278 | 0.4625
NR140070 | 105070 | 400KV LUCKNOW-GORAKH-III | 2013-05-09 19:45 | 2013-05-09 21:40 | 0.079861 | 0 | 0 | 0 | OSPT | S/D for demo of line impedence measurement kit. | N-480
|  | SUB TOTAL |  |  | 0.079861 | 0 | 0 | 0
NR140071 | 105071 | 400KV LUCKNOW-GORAKH-IV | 2013-05-09 19:45 | 2013-05-09 21:40 | 0.079861 | 0 | 0 | 0 | OSPT | S/D for demo of line impedence measurement kit. | N-480
|  | SUB TOTAL |  |  | 0.079861 | 0 | 0 | 0
NR140072 | 105017 | 400KV LUCKNOW-LKO(UP) | 2013-05-04 12:03 | 2013-05-04 12:20 | 0 | 0.011806 | 0 | 0 | OMSU | Line tripped on B-N fault in UPPCL portion, FLR:Lko-48km,
NR140072 | 105018 | 400KV LUCKNOW-LKO(UP) | 2013-05-04 12:20 | 2013-05-04 16:17 | 0 | 0 | 0 | 0.16458 | OSPD | S/D by UPPCL for tree lopping in their portion.
NR140072 | 105198 | 400KV LUCKNOW-LKO(UP) | 2013-05-27 12:53 | 2013-05-27 13:26 | 0 | 0.022917 | 0 | 0 | SBBU | B/Bar protn operated at LKO-UPPCL due to S/S Fault.
|  | SUB TOTAL |  |  | 0 | 0.034722 | 0 | 0.16458
NR140141 | 105091 | 400KV LUCKNOW-SOHAWAL-I | 2013-05-12 10:01 | 2013-05-12 10:14 | 0.0090278 | 0 | 0 | 0 | OSPT | S/D to attend low SF6 gas pressure in CB. | N-616
|  | SUB TOTAL |  |  | 0.0090278 | 0 | 0 | 0
NR140073 | 105026 | 400KV LUCKNOW-SULTANPR | 2013-05-05 09:02 | 2013-05-05 09:30 | 0 | 0.019444 | 0 | 0 | OMSU | Tripped on R-Y Fault by Kite Thread. FLR:LKO-7.06km.
NR140073 | 105172 | 400KV LUCKNOW-SULTANPR | 2013-05-22 08:16 | 2013-05-22 20:11 | 0 | 0 | 0 | 0.49653 | OSPD | S/D by UPPCL for their line maintenance work. | N-1145
NR140073 | 105175 | 400KV LUCKNOW-SULTANPR | 2013-05-23 08:28 | 2013-05-23 18:50 | 0 | 0 | 0 | 0.43194 | OSPD | S/D by UPPCL for their line maintenance work. | N-1202
NR140073 | 105185 | 400KV LUCKNOW-SULTANPR | 2013-05-24 08:23 | 2013-05-24 19:41 | 0 | 0 | 0 | 0.47083 | OSPD | S/D by UPPCL for their line maintenance work. | N-1278
NR140073 | 105191 | 400KV LUCKNOW-SULTANPR | 2013-05-25 14:29 | 2013-05-25 22:28 | 0 | 0 | 0 | 0.33264 | OSPD | S/D by UPPCL for their line maintenance work. | N-1355
|  | SUB TOTAL |  |  | 0 | 0.019444 | 0 | 1899-12-31 17:34
NR140074 | 105241 | 400KV LUCKNOW-UNNAO-I | 2013-05-31 18:27 | 2013-05-31 18:53 | 0 | 0 | 0.018056 | 0 | GOVC | Trip on O/VOL protn at Lko>436kv.
|  | SUB TOTAL |  |  | 0 | 0 | 0.018056 | 0
NR140142 | 105055 | 400KV MEERUT-BAREILLY-I | 2013-05-07 08:21 | 2013-05-07 19:35 | 0 | 0 | 0 | 0.46806 | LCSD | S/D for stringing of new 765KV Agra-Meerut line. | N-324
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.46806
NR140130 | 105056 | 400KV MEERUT-BAREILLY-II | 2013-05-07 08:22 | 2013-05-07 19:36 | 0 | 0 | 0 | 0.46806 | LCSD | S/D for stringing of new 765KV Agra-Meerut line. | N-324
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.46806
NR140077 | 105049 | 400KV MEERUT-KOTESHWR-I | 2013-05-06 16:11 | 2013-05-06 16:28 | 0 | 0.011806 | 0 | 0 | OMSU | Tripped on R-N, Z-2 fault, due to problem at Tehri/THDC.
|  | SUB TOTAL |  |  | 0 | 0.011806 | 0 | 0
NR140099 | 105050 | 400KV MEERUT-KOTESHWR-II | 2013-05-06 16:11 | 2013-05-06 16:31 | 0 | 0.013889 | 0 | 0 | OMSU | Tripped on R-N, Z-2 fault, due to problem at Tehri/THDC.
|  | SUB TOTAL |  |  | 0 | 0.013889 | 0 | 0
NR140143 | 105073 | 400KV MEERUT-MND-III | 2013-05-10 07:53 | 2013-05-10 21:12 | 0 | 0 | 0 | 0.55486 | LCSD | S/D for stringing of new 765KV Agra-Meerut line. | N-501
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.55486
NR140131 | 105074 | 400KV MEERUT-MND-IV | 2013-05-10 07:54 | 2013-05-10 21:10 | 0 | 0 | 0 | 0.55278 | LCSD | S/D for stringing of new 765KV Agra-Meerut line. | N-501
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.55278
NR140108 | 105087 | 400KV NIMRANA-SIKAR-I | 2013-05-11 18:09 | 2013-05-13 11:10 | 0 | 0 | 0 | 1899-12-31 17:01 | LVRD | H/Tripped for voltage regulation. BHI-432 KV | N-590
NR140108 | 105143 | 400KV NIMRANA-SIKAR-I | 2013-05-19 18:11 | 2013-05-20 10:59 | 0 | 0 | 0 | 0.7 | LVRD | Hand tripped for voltage regulation. Bhwd-432kv. | N-998
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-01 09:49
NR140085 | 105105 | 400KV RIHAND-ALLD-II | 2013-05-14 08:35 | 2013-05-14 18:30 | 0 | 0 | 0 | 0.41319 | OSPD | S/D by Rihand/NTPC for protection testing. | N-709
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.41319
NR140087 | 105220 | 400KV ROORKI-RISHIKESH | 2013-05-29 13:30 | 2013-05-29 15:08 | 0 | 0.068056 | 0 | 0 | OMSU | Tripped on B-N fault in UPPCL portion. ROORKI-15.5km.
|  | SUB TOTAL |  |  | 0 | 0.068056 | 0 | 0
NR140088 | 405160 | 400KV SASARAM-BIHARSHRF-I | 2013-05-16 08:05 | 2013-05-16 22:54 | 0 | 0 | 0 | 0.61736 | LCSD | S/D FOR RELAY RETROFITTING WORK AT SSRM
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.61736
NR140089 | 405168 | 400KV SASARAM-BIHARSHRF-II | 2013-05-17 08:06 | 2013-05-17 20:30 | 0 | 0 | 0 | 0.51667 | LCSD | S/D FOR RELAY RETROFITTING WORK AT SSRM
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.51667
NR140090 | 105149 | 400KV SASARAM-SARNATH | 2013-05-20 10:15 | 2013-05-20 20:26 | 0 | 0 | 0 | 0.42431 | LCSD | S/D for retrofitment of M-I protn relay at Sasaram end. | N-1017
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.42431
NR140091 | 105019 | 400KV SING-ALLD-I | 2013-05-04 14:32 | 2013-05-04 15:16 | 0.030556 | 0 | 0 | 0 | LEFT | A/R and tripped on R-N fault, FLR:Alld-106.15kms
NR140091 | 105020 | 400KV SING-ALLD-I | 2013-05-04 16:10 | 2013-05-04 16:35 | 0.017361 | 0 | 0 | 0 | LEFT | A/R and tripped on R-N fault, FLR:Alld-110.38kms
|  | SUB TOTAL |  |  | 0.047917 | 0 | 0 | 0
NR140092 | 105021 | 400KV SING-ALLD-II | 2013-05-04 18:51 | 2013-05-04 19:00 | 0 | 0.00625 | 0 | 0 | SEMU | O/V protn maloperated at Sing-NTPC due to CVT problem.
NR140092 | 105022 | 400KV SING-ALLD-II | 2013-05-05 19:00 | 2013-05-06 16:31 | 0 | 0 | 0 | 0.89653 | OSPD | S/D by NTPC For Y-phase CVT testing and replacement. | N/205
NR140092 | 105148 | 400KV SING-ALLD-II | 2013-05-20 10:06 | 2013-05-20 19:30 | 0 | 0 | 0 | 0.39167 | OSPD | S/D by SING/NTPC for relay reprofitment at their end. | N-1031
|  | SUB TOTAL |  |  | 0 | 0.00625 | 0 | 1899-12-31 06:55
NR140093 | 105062 | 400KV SING-ANPARA | 2013-05-08 15:27 | 2013-05-08 16:09 | 0 | 0.029167 | 0 | 0 | OMSU | A/R at Sing but trip from Anpara-UP due to A/R problem on B-N fault. FLR:Sing-77.58%, Anpr-8.5km.
NR140093 | 105076 | 400KV SING-ANPARA | 2013-05-10 09:23 | 2013-05-10 11:53 | 0.10417 | 0 | 0 | 0 | OSPT | S/D for Restoration of open jumper at loc-44. | N-503
NR140093 | 105077 | 400KV SING-ANPARA | 2013-05-10 11:53 | 2013-05-10 13:03 | 0 | 0.048611 | 0 | 0 | OMSU | Operational Delay in charging by UPPCL.
|  | SUB TOTAL |  |  | 0.10417 | 0.077778 | 0 | 0
NR140111 | 105061 | 400KV SING-FATEHPUR | 2013-05-08 12:07 | 2013-05-08 12:22 | 0.010417 | 0 | 0 | 0 | OSPT | S/D for isolating S/R at Fatehpur to attend oil leakage. | N-382
|  | SUB TOTAL |  |  | 0.010417 | 0 | 0 | 0
NR140095 | 105196 | 400KV SING-LKO(UP) | 2013-05-27 12:53 | 2013-05-27 13:35 | 0 | 0.029167 | 0 | 0 | SBBU | B/Bar protn operated at LKO-UPPCL due to S/S Fault.
|  | SUB TOTAL |  |  | 0 | 0.029167 | 0 | 0
N-W40001 | 105067 | 400KV SING-VINDH-I | 2013-05-09 09:26 | 2013-05-09 23:21 | 0 | 0 | 0 | 0.57986 | OSPD | S/D by NTPC-Sing for bay eqpt maint work. | N-437
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.57986
N-W40002 | 105218 | 400KV SING-VINDH-II | 2013-05-29 10:26 | 2013-05-30 14:07 | 0 | 0 | 0 | 1899-12-31 03:41 | OSPD | S/D by NTPC for CB modification work. | N/1529
N-W40002 | 105232 | 400KV SING-VINDH-II | 2013-05-31 09:41 | 2013-05-31 20:33 | 0 | 0 | 0 | 0.45278 | OSPD | S/D by SING/NTPC for CB testing work. | N-1650
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1899-12-31 14:33
BILUP2209 | 105107 | 220KV ALLD-JHUSI(UP) | 2013-05-14 10:08 | 2013-05-14 16:53 | 0 | 0 | 0 | 0.28125 | OSPD | S/D by UPPCL for their line maintenance work. | N-715
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.28125
BILUP2202 | 105102 | 220KV ALLD-REWA RD-I | 2013-05-13 12:39 | 2013-05-13 15:41 | 0 | 0 | 0 | 0.12639 | OSPD | S/D by UPPCL for their line maintenance work. | N-677
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.12639
BILUP2203 | 105121 | 220KV ALLD-REWA RD-II | 2013-05-15 12:15 | 2013-05-15 14:14 | 0 | 0 | 0 | 0.082639 | OSPD | S/D by UPPCL for bay mntc work. | N-786
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.082639
NR122003 | 105237 | 220KV ANTA-DAUSA | 2013-05-31 11:55 | 2013-05-31 13:00 | 0 | 0.045139 | 0 | 0 | SBBU | B/Bar protn opted at Dausa/RRVPNL. D/T recd at Anta.
|  | SUB TOTAL |  |  | 0 | 0.045139 | 0 | 0
NR122009 | 105177 | 220KV BASSI-DAUSA-I | 2013-05-23 09:45 | 2013-05-23 11:46 | 0 | 0 | 0 | 0.084028 | LCSD | S/D for retrofitment of M-II protn relay at Bassi. | N-1212
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.084028
NR122010 | 105186 | 220KV BASSI-DAUSA-II | 2013-05-24 14:20 | 2013-05-24 16:50 | 0 | 0 | 0 | 0.10417 | LCSD | S/D for new relay retrofitment work at Bassi. | N-1301
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.10417
NR122011 | 105181 | 220KV BASSI-IG NAGAR | 2013-05-23 17:21 | 2013-05-23 18:03 | 0 | 0 | 0 | 0.029167 | LCSD | S/D for retrofitment of M-II protn relay at Bassi. | N-1249
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.029167
NR122012 | 105214 | 220KV DGANGA-BLY(UP)-II | 2013-05-29 08:00 | 2013-05-29 11:43 | 0.15486 | 0 | 0 | 0 | OSPT | S/D for restoration of one B-ph sub jumper at loc. No.22.
|  | SUB TOTAL |  |  | 0.15486 | 0 | 0 | 0
NR122038 | 105033 | 220KV FATEHPUR-FTHPR(UP)-I | 2013-05-05 14:43 | 2013-05-05 17:09 | 0 | 0.10139 | 0 | 0 | OMSU | Tripped during disturbance caused after fault in R/BLY-II line due to snapping of E/Wire in UPPCL portion.
|  | SUB TOTAL |  |  | 0 | 0.10139 | 0 | 0
NR122039 | 105034 | 220KV FATEHPUR-FTHPR(UP)-II | 2013-05-05 14:43 | 2013-05-05 17:06 | 0 | 0.099306 | 0 | 0 | OMSU | Tripped during disturbance caused after fault in R/BLY-II line due to snapping of E/Wire in UPPCL portion.
|  | SUB TOTAL |  |  | 0 | 0.099306 | 0 | 0
BILHY2201 | 105165 | 220KV FGPP-PALLA-I | 2013-05-21 23:55 | 2013-05-22 01:32 | 0 | 0.067361 | 0 | 0 | OMSU | Tripped due to local system disturbance during Bus fault at BBMB-Samaipur after their Badshahpur line CT blast.
BILHY2201 | 105230 | 220KV FGPP-PALLA-I | 2013-05-31 07:51 | 2013-05-31 10:40 | 0 | 0 | 0 | 0.11736 | OSPD | S/D by HVPNL for fitting of Isolator clamp at Palla end. | N-1641
|  | SUB TOTAL |  |  | 0 | 0.067361 | 0 | 0.11736
BILHY2202 | 105028 | 220KV FGPP-PALLA-II | 2013-05-05 11:10 | 2013-05-05 12:15 | 0 | 0 | 0 | 0.045139 | OSPD | S/D by Palla/HVPNL to attend jumper hotspot. | N-228
BILHY2202 | 105166 | 220KV FGPP-PALLA-II | 2013-05-21 23:55 | 2013-05-22 01:32 | 0 | 0.067361 | 0 | 0 | OMSU | Tripped due to local system disturbance during Bus fault at BBMB-Samaipur after their Badshahpur line CT blast.
BILHY2202 | 105234 | 220KV FGPP-PALLA-II | 2013-05-31 11:48 | 2013-05-31 14:19 | 0 | 0 | 0 | 0.10486 | OSPD | S/D by HVPNL to attend hotspot. | N-1673
|  | SUB TOTAL |  |  | 0 | 0.067361 | 0 | 0.15
BILHY2203 | 105167 | 220KV FGPP-SPUR-I | 2013-05-21 23:55 | 2013-05-22 01:50 | 0 | 0.079861 | 0 | 0 | SBBU | Tripped on Bus Bar protn at BBMB-Samaipur due to Bus fault after their Badshahpur line CT blast.
|  | SUB TOTAL |  |  | 0 | 0.079861 | 0 | 0
BILHY2204 | 105168 | 220KV FGPP-SPUR-II | 2013-05-21 23:55 | 2013-05-22 01:50 | 0 | 0.079861 | 0 | 0 | SBBU | Tripped on Bus Bar protn at BBMB-Samaipur due to Bus fault after their Badshahpur line CT blast.
|  | SUB TOTAL |  |  | 0 | 0.079861 | 0 | 0
NR122016 | 105219 | 220KV KNP-MAINPURI | 2013-05-29 10:28 | 2013-05-29 21:32 | 0 | 0 | 0 | 0.46111 | LCSD | S/D for stringing of 800KV Agra-Chiryali HVDC line. | N/1530
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.46111
NR122017 | 105108 | 220KV KNP-NAUBASTA | 2013-05-14 13:17 | 2013-05-14 14:48 | 0 | 0 | 0 | 0.063194 | OSPD | S/D by UPPCL for their line maintenance work. | N-723
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.063194
NR122020 | 105035 | 220KV KNP-UNCHR-I | 2013-05-05 14:43 | 2013-05-05 16:05 | 0 | 0.056944 | 0 | 0 | OMSU | Both bus dead at UCR/NTPC due to fault in R/BLY-II line as E/Wire snapped in UPPCL portion,
|  | SUB TOTAL |  |  | 0 | 0.056944 | 0 | 0
NR122021 | 105036 | 220KV KNP-UNCHR-II | 2013-05-05 14:43 | 2013-05-05 16:11 | 0 | 0.061111 | 0 | 0 | OMSU | Both bus dead at UCR/NTPC due to fault in R/BLY-II line as E/Wire snapped in UPPCL portion,
|  | SUB TOTAL |  |  | 0 | 0.061111 | 0 | 0
NR122022 | 105037 | 220KV KNP-UNCHR-III | 2013-05-05 14:43 | 2013-05-05 16:17 | 0 | 0.065278 | 0 | 0 | OMSU | Both bus dead at UCR/NTPC due to fault in R/BLY-II line as E/Wire snapped in UPPCL portion,
|  | SUB TOTAL |  |  | 0 | 0.065278 | 0 | 0
NR122023 | 105038 | 220KV KNP-UNCHR-IV | 2013-05-05 14:43 | 2013-05-05 16:28 | 0 | 0.072917 | 0 | 0 | OMSU | Both bus dead at UCR/NTPC due to fault in R/BLY-II line as E/Wire snapped in UPPCL portion,
|  | SUB TOTAL |  |  | 0 | 0.072917 | 0 | 0
BILUP2204 | 105119 | 220KV MEERUT-MPURAM-I | 2013-05-15 10:50 | 2013-05-15 11:28 | 0 | 0 | 0 | 0.026389 | SCSD | S/D for M-2 relay retrofitment work at Meerut. | N-781
BILUP2204 | 105200 | 220KV MEERUT-MPURAM-I | 2013-05-27 14:54 | 2013-05-27 16:30 | 0 | 0.066667 | 0 | 0 | OMSU | Tripped on B-N fault in UPPCL portion due to E/wire broken. FLR:MRT=6.1km,
BILUP2204 | 105206 | 220KV MEERUT-MPURAM-I | 2013-05-27 16:30 | 2013-05-28 17:24 | 0 | 0 | 0 | 1899-12-31 00:54 | OSFD | S/D taken by UPPCL for restoration of broken E/wire.
BILUP2204 | 105229 | 220KV MEERUT-MPURAM-I | 2013-05-31 07:03 | 2013-05-31 18:22 | 0 | 0 | 0 | 0.47153 | LCSD | S/D for stringing of MRT-Satabdingr line on ERS. | N-1638
|  | SUB TOTAL |  |  | 0 | 0.066667 | 0 | 1899-12-31 12:51
BILUP2205 | 105135 | 220KV MEERUT-MPURAM-II | 2013-05-18 11:39 | 2013-05-18 12:23 | 0 | 0 | 0 | 0.030556 | LCSD | S/D for retrofitment of M-I protn relay at Meerut end. | N-947
BILUP2205 | 105201 | 220KV MEERUT-MPURAM-II | 2013-05-27 14:54 | 2013-05-27 16:50 | 0 | 0.080556 | 0 | 0 | OMSU | Tripped on B-N fault in UPPCL portion. FLR:MRT=19.6km.
|  | SUB TOTAL |  |  | 0 | 0.080556 | 0 | 0.030556
BILUP2206 | 105001 | 220KV MEERUT-NARA | 2013-05-01 04:16 | 2013-05-01 05:18 | 0 | 0.043056 | 0 | 0 | OMSU | Line tripped on R-N fault in UPPCL portion. Mrt-29.2km.
BILUP2206 | 105078 | 220KV MEERUT-NARA | 2013-05-10 11:58 | 2013-05-10 12:42 | 0 | 0 | 0 | 0.030556 | LCSD | S/D for M-2 relay retrofitment work at Meerut. | N-515
BILUP2206 | 105125 | 220KV MEERUT-NARA | 2013-05-16 13:03 | 2013-05-16 20:22 | 0 | 0 | 0 | 0.30486 | OSPD | S/D by UPPCL for attending hotspot. | N-850
|  | SUB TOTAL |  |  | 0 | 0.043056 | 0 | 0.33542
BILUP2207 | 105079 | 220KV MEERUT-SHTBDNGR | 2013-05-10 18:00 | 2013-05-10 18:50 | 0 | 0 | 0 | 0.034722 | LCSD | S/D for M-2 relay retrofitment work at Meerut. | N-534
BILUP2207 | 105202 | 220KV MEERUT-SHTBDNGR | 2013-05-27 14:54 | 2013-05-28 08:00 | 0 | 0 | 0.7125 | 0 | LNCC | Tripped due to Tower collapse at Loc 21/22 during heavy wind strom in that area. S/D for ERS erection.
BILUP2207 | 105208 | 220KV MEERUT-SHTBDNGR | 2013-05-28 08:00 | 2013-05-31 18:17 | 0 | 0 | 0 | 1900-01-02 10:17 | LCSD | S/D for erection of ERS towers for restoration of line.
|  | SUB TOTAL |  |  | 0 | 0 | 0.7125 | 1900-01-02 11:07
BILUP2208 | 105069 | 220KV MEERUT-SIMBHOLI | 2013-05-09 17:21 | 2013-05-09 18:08 | 0 | 0 | 0 | 0.032639 | LCSD | S/D for M-2 relay retrofitment work at Meerut. | N-465
BILUP2208 | 105231 | 220KV MEERUT-SIMBHOLI | 2013-05-31 07:30 | 2013-05-31 09:09 | 0 | 0 | 0 | 0.06875 | OSPD | S/D by UPPCL to attend hotspot on CT clamp. | N-1642
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.10139
NR122024 | 105215 | 220KV PITHORAGRH-BRLY(UP) | 2013-05-29 08:00 | 2013-05-29 08:35 | 0 | 0.024306 | 0 | 0 | OMSU | Hand tripped by Bly-UPPCL due to local problem. CB did not open at other end.
|  | SUB TOTAL |  |  | 0 | 0.024306 | 0 | 0
NR122025 | 105039 | 220KV RAIBRLY-CHINHAT | 2013-05-05 14:43 | 2013-05-05 17:03 | 0 | 0.097222 | 0 | 0 | OMSU | Tripped during disturbance caused after fault in R/BLY-II line due to snapping of E/Wire in UPPCL portion.
|  | SUB TOTAL |  |  | 0 | 0.097222 | 0 | 0
NR122026 | 105044 | 220KV RAIBRLY-LKO(UP) | 2013-05-06 12:00 | 2013-05-06 22:04 | 0 | 0 | 0 | 0.41944 | OSPD | S/D by UPPCL for their line maintenance work. | N-283
NR122026 | 105199 | 220KV RAIBRLY-LKO(UP) | 2013-05-27 12:53 | 2013-05-27 13:40 | 0 | 0.032639 | 0 | 0 | SBBU | B/Bar protn operated at LKO-UPPCL due to S/S Fault.
|  | SUB TOTAL |  |  | 0 | 0.032639 | 0 | 0.41944
NR122027 | 105151 | 220KV RAPPB-CHITT-I | 2013-05-20 13:18 | 2013-05-20 14:13 | 0 | 0.038194 | 0 | 0 | SRMU | Tripped on B-N fault due to A/R relay problem at RAPP-B, FLR:Chittor=65km.
|  | SUB TOTAL |  |  | 0 | 0.038194 | 0 | 0
NR122030 | 105084 | 220KV RAPPB-UDAIPUR | 2013-05-11 09:32 | 2013-05-11 11:19 | 0 | 0.074306 | 0 | 0 | SBBU | Bus Bar protection oprtd at Debari/RRVPNL stn. S/D taken by RRVPNL to attend Bus Fault.
|  | SUB TOTAL |  |  | 0 | 0.074306 | 0 | 0
NR122031 | 105238 | 220KV S.MDHPR-DAUSA-I | 2013-05-31 11:55 | 2013-05-31 12:31 | 0 | 0.025 | 0 | 0 | SBBU | B/Bar protn opted at Dausa/RRVPNL.
|  | SUB TOTAL |  |  | 0 | 0.025 | 0 | 0
NR122033 | 105025 | 220KV TNKPR-BLY(UP) | 2013-05-05 10:20 | 2013-05-05 20:42 | 0 | 0 | 0 | 0.43194 | OSPD | S/D by NHPC for protection testing at Tanakpur. | N-216
NR122033 | 105134 | 220KV TNKPR-BLY(UP) | 2013-05-18 10:32 | 2013-05-18 13:42 | 0 | 0 | 0 | 0.13194 | OSPD | S/D by UPPCL to attend CT jumper sparking at Cbganj. | N-942
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.56389
NR122034 | 105015 | 220KV TNKPR-SITARGANJ | 2013-05-04 09:39 | 2013-05-04 22:10 | 0 | 0 | 0 | 0.52153 | OSPD | S/D by NHPC for protection testing at Tanakpur.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.52153
NR122035 | 105030 | 220KV UNCHR-RAIBRLY-I | 2013-05-05 14:43 | 2013-05-05 15:25 | 0 | 0.029167 | 0 | 0 | OMSU | Both bus dead at UCR/NTPC due to fault in R/BLY-II line as E/Wire snapped in UPPCL portion.
NR122035 | 105045 | 220KV UNCHR-RAIBRLY-I | 2013-05-06 12:38 | 2013-05-06 20:26 | 0 | 0 | 0 | 0.325 | OSPD | S/D by UPPCL for rectification of broken Earth-wire. | N-281
|  | SUB TOTAL |  |  | 0 | 0.029167 | 0 | 0.325
NR122036 | 105031 | 220KV UNCHR-RAIBRLY-II | 2013-05-05 14:43 | 2013-05-06 12:38 | 0 | 0.91319 | 0 | 0 | OMSU | Both bus dead at UCR/NTPC due to fault in R/BLY-II line as E/Wire snapped in UPPCL portion, R/BLY=8.8km.
NR122036 | 105046 | 220KV UNCHR-RAIBRLY-II | 2013-05-06 12:38 | 2013-05-08 22:53 | 0 | 0 | 0 | 1900-01-01 10:15 | OSPD | S/D by UPPCL for rectification of broken Earth-wire. | N-281
|  | SUB TOTAL |  |  | 0 | 0.91319 | 0 | 1900-01-01 10:15
NR122037 | 105032 | 220KV UNCHR-RAIBRLY-III | 2013-05-05 14:43 | 2013-05-05 16:01 | 0 | 0.054167 | 0 | 0 | OMSU | Both bus dead at UCR/NTPC due to fault in R/BLY-II line as E/Wire snapped in UPPCL portion.
|  | SUB TOTAL |  |  | 0 | 0.054167 | 0 | 0
NR1ICT10 | 105161 | 315MVA ICT-I BLBGARH | 2013-05-21 23:55 | 2013-05-22 01:30 | 0 | 0.065972 | 0 | 0 | SBBU | Tripped only from BBMB-220KV side due to Bus fault at Samaipur after their Badshahpur line CT blast.
|  | SUB TOTAL |  |  | 0 | 0.065972 | 0 | 0
NR1ICT11 | 105162 | 315MVA ICT-II BLBGARH | 2013-05-21 23:55 | 2013-05-22 01:00 | 0 | 0.045139 | 0 | 0 | SBBU | Tripped only from BBMB-220KV side due to Bus fault at Samaipur after their Badshahpur line CT blast.
NR1ICT11 | 105169 | 315MVA ICT-II BLBGARH | 2013-05-22 01:00 | 2013-05-22 07:23 | 0 | 0 | 0 | 0.26597 | OSFD | S/D by BBMB for attending 220kv Bus fault at Samaypr.
|  | SUB TOTAL |  |  | 0 | 0.045139 | 0 | 0.26597
NR1ICT12 | 105159 | 315MVA ICT-III BLBGARH | 2013-05-21 16:28 | 2013-05-21 21:01 | 0 | 0 | 0 | 0.18958 | OSPD | S/D by BBMB for attending 220KV side Jumper hot spot. | N-1108
NR1ICT12 | 105163 | 315MVA ICT-III BLBGARH | 2013-05-21 23:55 | 2013-05-22 01:49 | 0 | 0.079167 | 0 | 0 | SBBU | Tripped only from BBMB-220KV side due to Bus fault at Samaipur after their Badshahpur line CT blast.
|  | SUB TOTAL |  |  | 0 | 0.079167 | 0 | 0.18958
NR1ICT13 | 105164 | 315MVA ICT-IV BLBGARH | 2013-05-21 23:55 | 2013-05-22 01:50 | 0 | 0.079861 | 0 | 0 | SBBU | Tripped only from BBMB-220KV side due to Bus fault at Samaipur after their Badshahpur line CT blast.
|  | SUB TOTAL |  |  | 0 | 0.079861 | 0 | 0
NR1ICT51 | 105235 | 315MVA ICT-II GURGAON | 2013-05-31 11:48 | 2013-05-31 18:26 | 0 | 0 | 0 | 0.27639 | SCSD | S/D for HV Testing of 400kv Bus-I at Gurgaon GIS. | N-1678
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.27639
NR1ICT28 | 105207 | 315MVA ICT-I MANDOLA | 2013-05-28 06:08 | 2013-05-28 09:12 | 0 | 0 | 0 | 0.12778 | SCSD | S/D for retrofitment work of 220kv side isolator. | N-1459
NR1ICT28 | 105221 | 315MVA ICT-I MANDOLA | 2013-05-30 06:17 | 2013-05-30 10:11 | 0 | 0 | 0 | 0.1625 | SCSD | S/D for isolator jumpering with bus #2 after retrofitment. | N-1573
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.29028
NR1ICT29 | 105170 | 315MVA ICT-II MANDOLA | 2013-05-22 06:07 | 2013-05-22 09:23 | 0 | 0 | 0 | 0.13611 | SCSD | S/D for retrofitment work of 220kv side isolator. | N-1140
NR1ICT29 | 105187 | 315MVA ICT-II MANDOLA | 2013-05-25 06:05 | 2013-05-25 10:10 | 0 | 0 | 0 | 0.17014 | SCSD | S/D for retrofitment work of 220kv side isolator. | N-1332
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.30625
NR1ICT30 | 105116 | 315MVA ICT-III MANDOLA | 2013-05-15 06:17 | 2013-05-15 09:08 | 0 | 0 | 0 | 0.11875 | SCSD | S/D for retrofitment work of 220kv side isolator. | N-765
NR1ICT30 | 105131 | 315MVA ICT-III MANDOLA | 2013-05-18 07:07 | 2013-05-18 10:25 | 0 | 0 | 0 | 0.1375 | SCSD | S/D for retrofitment work of 220kv side isolator. | N-932
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.25625
NR1ICT31 | 105080 | 315MVA ICT-IV MANDOLA | 2013-05-11 06:03 | 2013-05-11 09:41 | 0 | 0 | 0 | 0.15139 | SCSD | S/D for retrofitment work of 220kv side isolator. | N-556
NR1ICT31 | 105103 | 315MVA ICT-IV MANDOLA | 2013-05-14 06:13 | 2013-05-14 10:03 | 0 | 0 | 0 | 0.15972 | SCSD | S/D for retrofitment work of 220kv side isolator. | N-703
NR1ICT31 | 105192 | 315MVA ICT-IV MANDOLA | 2013-05-25 15:34 | 2013-05-25 15:39 | 0.0034722 | 0 | 0 | 0 | OMST | Tripped during checking of cooling fan operation.
|  | SUB TOTAL |  |  | 0.0034722 | 0 | 0 | 0.31111
NR1BRT12 |  | 50MVAR B/Reactor MURADNGR | 2013-04-01 | 2013-05-01 | 0 | 0 | 0 | 1900-01-29 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-29
NR1BRT32 |  | 240MVAR B/Reactor-I BALIA-765 | 2013-05-18 08:44 | 2013-05-18 18:39 | 0 | 0 | 0 | 0.41319 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.41319
NR1BRT03 |  | 80MVAR B/Reactor BAREILLY | 2013-05-21 15:28 | 2013-05-21 18:20 | 0 | 0 | 0 | 0.11944 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.11944
NR1BRT11 |  | 50MVAR B/Reactor MANDOLA | 2013-05-21 15:38 | 2013-05-21 18:26 | 0 | 0 | 0 | 0.11667 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.11667
NR1BRT35 |  | 240MVAR B/Reactor-2 AGRA-765 | 2013-05-21 15:42 | 2013-05-21 17:49 | 0 | 0 | 0 | 0.088194 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
NR1BRT35 |  | 240MVAR B/Reactor-2 AGRA-765 | 2013-05-23 10:56 | 2013-05-23 19:11 | 0 | 0 | 0 | 0.34375 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.43194
NR1BRT23 |  | 333MVAR B/Reactor FATEHPUR-765 | 2013-05-23 10:24 | 2013-05-23 21:09 | 0 | 0 | 0 | 0.44792 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.44792
NR1BRT04 |  | 50MVAR B/Reactor BASSI | 2013-05-23 10:47 | 2013-05-23 19:15 | 0 | 0 | 0 | 0.35278 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.35278
NR1SRT01 |  | AGRA 50MVAR S/R BHIWADI-I LINE | 2013-05-21 11:48 | 2013-05-21 17:48 | 0 | 0 | 0 | 0.25 | SVRD | H/ tripped for Voltage regolation on RLDC instrn.
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.25
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Classification/ Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(F13:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Classification/ Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM(G13:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Classification/ Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM(H13:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Classification/ Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM(I13:[Deemed Available, row above])
Note on C37: : DOC-01.05.13
Note on C39: : DOC-01.05.13
Note on C40: : DOC-01.05.13
Note on C41: : DOC-01.05.13
Note on C44: : DOC-01.05.13
Note on C45: : DOC-01.05.13
Note on C46: : DOC-01.05.13
Note on C243: LILO of Mnd-Bly-I at Neerut. DOC-01.04.13

## AVBT_May-13
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.05.2013 to 31.05.2013
SL.NO. | ELEMENT | Element Name | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Total Duration
| NO. |  |  |  | Outage Not To Consider |  | Available for
|  |  | POWERGRID | OTHERS | System Constrnt/ | Deemed | Consideration
[5 empty] | Natural Calamity/ | Available | THM | NSC | Ckt. Kms. | OH x NSC x Cktkm | THM x NSC x Cktkm | Non Availblty Factor/ Month (NAFM) | TAFM
[5 empty] | Militancy |  |  | ( E) | ( F)
|  |  | @ (T) | # (U) | & (C ) | " (D) | E | F | G | H | I | J | K
|  |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs
A |  | 765 KV TRANS LINES | [12 empty] | 0
1 | NR176501 | 765KV LUCKNOW-BALIA |  |  |  | 1900-01-07 13:16 | 744 | 4 | 318.919 | 0 | 949102.944 | 0 | 100 | 0 | 744
2 | NR176502 | 765KV AGRA-FATEHPUR | 0.20625 |  |  | 1899-12-31 15:39 | 744 | 4 | 334.52 | 6623.496 | 995531.52 | 0.0066532 | 99.3347 | 4.95
3 | NR176503 | 765KV FATEHPUR-GAYA |  |  |  | 0.84792 | 744 | 4 | 484.6 | 0 | 1442169.6 | 0 | 100 | 0
4 | NR176504 | 765KV AGRA-JHATIKALA | 1900-01-01 05:15 |  | 0.074306 | 1899-12-31 17:50 | 742.2167 | 4 | 253.076 | 53905.188 | 751348.9005 | 0.071745 | 92.8255 | 53.25
B |  | 400 KV TRANS LINES
1 | NR140001 | 400KV AGRA-AGRA(UP)-I |  |  |  | 1899-12-31 21:48 | 744 | 2 | 29.982 | 0 | 44613.216 | 0 | 100 | 0
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 0.010417 |  |  | 0.79583 | 744 | 2 | 29.982 | 14.991 | 44613.216 | 0.00033602 | 99.9664 | 0.25
3 | NR140003 | 400KV AGRA-AURAIYA-I |  |  |  |  | 744 | 2 | 167.2 | 0 | 248793.6 | 0 | 100 | 0
4 | NR140004 | 400KV AGRA-AURAIYA-II |  |  |  |  | 744 | 2 | 167.2 | 0 | 248793.6 | 0 | 100 | 0
5 | NR140005 | 400KV AGRA-BASSI-I |  |  |  | 0.85069 | 744 | 2 | 211.433 | 0 | 314612.304 | 0 | 100 | 0
6 | NR140008 | 400KV AGRA-BHIWADI-I | 0.03125 |  |  |  | 744 | 2 | 208.98 | 313.47 | 310962.24 | 0.0010081 | 99.8992 | 0.75
7 | NR140009 | 400KV AGRA-BHIWADI-II |  |  |  | 0.26806 | 744 | 2 | 209.51 | 0 | 311750.88 | 0 | 100 | 0
8 | NR140010 | 400KV AGRA-BLBGRH | 0.41458 |  |  |  | 744 | 2 | 181.137 | 3604.6263 | 269531.856 | 0.013374 | 98.6626 | 9.95
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I |  |  |  | 0.12222 | 744 | 2 | 253.823 | 0 | 377688.624 | 0 | 100 | 0
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II |  |  |  | 0.34028 | 744 | 2 | 253.823 | 0 | 377688.624 | 0 | 100 | 0
11 | NR140122 | 400KV ALLD-FATEHPUR-I |  |  |  |  | 744 | 2 | 139.73 | 0 | 207918.24 | 0 | 100 | 0
12 | NR140123 | 400KV ALLD-FATEHPUR-II |  |  |  | 0.40764 | 744 | 2 | 139.73 | 0 | 207918.24 | 0 | 100 | 0
13 | NR140104 | 400KV ALLD-FATEHPUR-III |  |  |  |  | 744 | 2 | 155.3 | 0 | 231086.4 | 0 | 100 | 0
14 | NR140012 | 400KV ALLD-KNP-II |  |  |  |  | 744 | 2 | 224 | 0 | 333312 | 0 | 100 | 0
15 | NR140015 | 400KV ALLD-SARNATH |  |  |  |  | 744 | 2 | 212 | 0 | 315456 | 0 | 100 | 0
16 | NR140016 | 400KV ALLD-SASARAM |  |  |  | 0.47986 | 744 | 2 | 136 | 0 | 202368 | 0 | 100 | 0
17 | NR140017 | 400KV BALIA-BIHARSHRF-I | 0.1875 |  | 0.019444 | 0.10764 | 743.5333 | 4 | 241.79 | 4352.22 | 719115.6987 | 0.0060522 | 99.3948 | 4.5
18 | NR140018 | 400KV BALIA-BIHARSHRF-II | 0.25 |  |  |  | 744 | 4 | 241.79 | 5802.96 | 719567.04 | 0.0080645 | 99.1935 | 6
19 | NR140019 | 400KV BALIA-MAU-I |  |  |  |  | 744 | 2 | 13 | 0 | 19344 | 0 | 100 | 0
20 | NR140020 | 400KV BALIA-MAU-II |  |  |  |  | 744 | 2 | 13 | 0 | 19344 | 0 | 100 | 0
21 | NR140021 | 400KV BALIA-PATNA-I |  |  | 0.053472 | 0.8625 | 742.7167 | 4 | 195.32 | 0 | 580269.6773 | 0 | 100 | 0
22 | NR140022 | 400KV BALIA-PATNA-II |  |  | 0.022222 | 1900-01-02 10:28 | 743.4667 | 4 | 195.32 | 0 | 580855.6373 | 0 | 100 | 0
23 | NR140136 | 400KV BALIA-PATNA-III |  |  | 0.014583 | 1899-12-31 07:06 | 743.65 | 4 | 185 | 0 | 550301 | 0 | 100 | 0
24 | NR140137 | 400KV BALIA-PATNA-IV |  |  |  | 1899-12-31 04:46 | 744 | 4 | 185 | 0 | 550560 | 0 | 100 | 0
25 | NR140140 | 400KV BALIA-SOHAWAL-I |  |  | 0.015278 | 0.72778 | 743.6333 | 2 | 229.163 | 0 | 340826.4911 | 0 | 100 | 0
26 | NR140120 | 400KV BALIA-SOHAWAL-II | 0.096528 |  |  | 0.0041667 | 744 | 2 | 229.163 | 1061.7886 | 340994.544 | 0.0031138 | 99.6886 | 2.3167
27 | NR140023 | 400KV BAREILLY-BRLY(UP)-I |  |  |  | 0.32222 | 744 | 2 | 9.2 | 0 | 13689.6 | 0 | 100 | 0
28 | NR140024 | 400KV BAREILLY-BRLY(UP)-II |  |  |  |  | 744 | 2 | 9.2 | 0 | 13689.6 | 0 | 100 | 0
29 | NR140025 | 400KV BAREILLY-LKO(UP) |  | 0.027778 |  |  | 744 | 2 | 278.76 | 0 | 414794.88 | 0 | 100 | 0
30 | NR140026 | 400KV BAREILLY-MBAD-I |  | 0.010417 |  |  | 744 | 2 | 92.68 | 0 | 137907.84 | 0 | 100 | 0
31 | NR140027 | 400KV BAREILLY-MBAD-II |  |  |  |  | 744 | 2 | 92.68 | 0 | 137907.84 | 0 | 100 | 0
32 | NR140115 | 400KV BAREILLY-ROSA-I | 0.072222 |  |  |  | 744 | 2 | 115.926 | 401.8768 | 172497.888 | 0.0023297 | 99.767 | 1.7333
33 | NR140028 | 400KV BASSI-BHIWADI-I |  |  |  | 1900-01-01 04:20 | 744 | 2 | 235 | 0 | 349680 | 0 | 100 | 0
34 | NR140029 | 400KV BASSI-BHIWADI-II |  |  |  |  | 744 | 2 | 220.261 | 0 | 327748.368 | 0 | 100 | 0
35 | NR140030 | 400KV BASSI-HIRAPURA-I |  |  |  |  | 744 | 2 | 47.762 | 0 | 71069.856 | 0 | 100 | 0
36 | NR140031 | 400KV BASSI-HIRAPURA-II |  |  |  |  | 744 | 2 | 48.99 | 0 | 72897.12 | 0 | 100 | 0
37 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 0.070833 |  |  | 0.12986 | 744 | 2 | 37.164 | 126.3576 | 55300.032 | 0.0022849 | 99.7715 | 1.7
38 | NR140127 | 400KV BASSI-JAIPUR(S)-II |  |  |  | 0.32153 | 744 | 2 | 37.164 | 0 | 55300.032 | 0 | 100 | 0
39 | NR140032 | 400KV BHIWADI-GURGAON | 0.063194 |  |  | 0.29028 | 744 | 2 | 82.8 | 251.16 | 123206.4 | 0.0020385 | 99.7961 | 1.5167
40 | NR140033 | 400KV BHIWADI-HISAR |  |  |  |  | 744 | 2 | 211.547 | 0 | 314781.936 | 0 | 100 | 0
41 | NR140106 | 400KV BHIWADI-NIMRANA-I | 0.11458 |  |  | 1900-01-02 03:02 | 744 | 2 | 48.428 | 266.354 | 72060.864 | 0.0036962 | 99.6304 | 2.75
42 | NR140107 | 400KV BHIWADI-NIMRANA-II |  |  |  |  | 744 | 2 | 48.428 | 0 | 72060.864 | 0 | 100 | 0
43 | NR140035 | 400KV BLBGRH-GURGAON | 0.081944 |  | 0.038889 | 0.29653 | 743.0667 | 2 | 42.7 | 167.9533 | 63457.8933 | 0.0026467 | 99.7353 | 1.9667
44 | NR140036 | 400KV BLBGRH-MAHRANIBG |  |  |  |  | 744 | 4 | 60.68 | 0 | 180583.68 | 0 | 100 | 0
45 | NR140037 | 400KV BLBGRH-MAINPURI-I |  |  |  | 0.086806 | 744 | 2 | 235.952 | 0 | 351096.576 | 0 | 100 | 0
46 | NR140038 | 400KV BLBGRH-MAINPURI-II |  |  |  |  | 744 | 2 | 235.952 | 0 | 351096.576 | 0 | 100 | 0
47 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) |  |  |  |  | 744 | 4 | 12.55 | 0 | 37348.8 | 0 | 100 | 0
48 | NR140039 | 400KV DAD-GR.NOIDA |  |  |  |  | 744 | 4 | 13.256 | 0 | 39449.856 | 0 | 100 | 0
49 | NR140040 | 400KV DAD-MAHRANIBG |  |  |  |  | 744 | 4 | 54.36 | 0 | 161775.36 | 0 | 100 | 0
50 | NR140041 | 400KV DAD-MANDOLA-I |  |  |  |  | 744 | 4 | 46.3 | 0 | 137788.8 | 0 | 100 | 0
51 | NR140042 | 400KV DAD-MANDOLA-II |  |  |  |  | 744 | 4 | 46.3 | 0 | 137788.8 | 0 | 100 | 0
52 | NR140043 | 400KV DAD-MURADNGR |  |  |  |  | 744 | 2 | 33.098 | 0 | 49249.824 | 0 | 100 | 0
53 | NR140044 | 400KV DAD-PANIPAT-I |  | 0.015278 |  | 0.088889 | 744 | 2 | 112.322 | 0 | 167135.136 | 0 | 100 | 0
54 | NR140045 | 400KV DAD-PANIPAT-II |  |  |  |  | 744 | 2 | 117 | 0 | 174096 | 0 | 100 | 0
55 | NR140124 | 400KV FATEHPUR-MAINPURI-I |  |  |  | 1899-12-31 11:00 | 744 | 2 | 260.051 | 0 | 386955.888 | 0 | 100 | 0
56 | NR140125 | 400KV FATEHPUR-MAINPURI-II |  |  |  | 1899-12-31 08:18 | 744 | 2 | 260.051 | 0 | 386955.888 | 0 | 100 | 0
57 | NR140046 | 400KV GORKH-GORAKH-I |  |  |  |  | 744 | 2 | 45.94 | 0 | 68358.72 | 0 | 100 | 0
58 | NR140047 | 400KV GORKH-GORAKH-II |  |  |  |  | 744 | 2 | 45.94 | 0 | 68358.72 | 0 | 100 | 0
59 | NR140128 | 400KV GURGAON-MANESAR-I |  |  |  | 1900-01-30 | 744 | 2 | 23.462 | 0 | 34911.456 | 0 | 100 | 0
60 | NR140129 | 400KV GURGAON-MANESAR-II |  |  |  | 0.57431 | 744 | 2 | 23.462 | 0 | 34911.456 | 0 | 100 | 0
61 | NR140132 | 400KV JHATIKALA-BAMNOLI-I |  |  |  |  | 744 | 4 | 6.106 | 0 | 18171.456 | 0 | 100 | 0
62 | NR140133 | 400KV JHATIKALA-BAMNOLI-II |  |  |  |  | 744 | 4 | 6.106 | 0 | 18171.456 | 0 | 100 | 0
63 | NR140134 | 400KV JHATIKALA-MUNDKA-I |  |  |  | 0.34583 | 744 | 4 | 6.782 | 0 | 20183.232 | 0 | 100 | 0
64 | NR140135 | 400KV JHATIKALA-MUNDKA-II |  |  |  | 0.39583 | 744 | 4 | 6.782 | 0 | 20183.232 | 0 | 100 | 0
65 | NR140048 | 400KV KANKROLI-BHINMAL |  |  |  | 1899-12-31 13:16 | 744 | 2 | 201.2 | 0 | 299385.6 | 0 | 100 | 0
66 | NR140049 | 400KV KANKROLI-JODHPUR |  |  |  |  | 744 | 2 | 187.965 | 0 | 279691.92 | 0 | 100 | 0
67 | NR140050 | 400KV KANKROLI-RAPPC-I |  |  |  |  | 744 | 2 | 198.54 | 0 | 295427.52 | 0 | 100 | 0
68 | NR140051 | 400KV KANKROLI-RAPPC-II |  |  |  |  | 744 | 2 | 198.54 | 0 | 295427.52 | 0 | 100 | 0
69 | NR140052 | 400KV KNP-AGRA |  |  |  |  | 744 | 2 | 240 | 0 | 357120 | 0 | 100 | 0
70 | NR140053 | 400KV KNP-AURAIYA-I |  |  |  |  | 744 | 2 | 72.6 | 0 | 108028.8 | 0 | 100 | 0
71 | NR140054 | 400KV KNP-AURAIYA-II |  |  |  |  | 744 | 2 | 73.2 | 0 | 108921.6 | 0 | 100 | 0
72 | NR140055 | 400KV KNP-BLBGARH-I |  |  | 0.12014 | 0.057639 | 741.1167 | 2 | 385.69 | 0 | 571682.5743 | 0 | 100 | 0
73 | NR140056 | 400KV KNP-BLBGARH-II | 1899-12-31 11:50 |  |  |  | 744 | 2 | 370.772 | 26571.9933 | 551708.736 | 0.048163 | 95.1837 | 35.8333
74 | NR140057 | 400KV KNP-BLBGARH-III |  |  |  | 0.2125 | 744 | 2 | 370.772 | 0 | 551708.736 | 0 | 100 | 0
75 | NR140110 | 400KV KNP-FATEHPUR-I |  |  |  |  | 744 | 2 | 107.079 | 0 | 159333.552 | 0 | 100 | 0
76 | NR140105 | 400KV KNP-FATEHPUR-II |  |  |  |  | 744 | 2 | 107.1 | 0 | 159364.8 | 0 | 100 | 0
77 | NR140058 | 400KV KNP-PANKI-I |  |  |  | 0.038889 | 744 | 2 | 5.922 | 0 | 8811.936 | 0 | 100 | 0
78 | NR140059 | 400KV KNP-PANKI-II |  |  |  | 0.040972 | 744 | 2 | 5.86 | 0 | 8719.68 | 0 | 100 | 0
79 | NR140102 | 400KV KOTA-BEAWAR |  |  |  |  | 744 | 2 | 179.711 | 0 | 267409.968 | 0 | 100 | 0
80 | NR140060 | 400KV KOTA-MERTA-I |  |  |  |  | 744 | 2 | 255.56 | 0 | 380273.28 | 0 | 100 | 0
81 | NR140062 | 400KV KOTA-RAPPC |  |  |  |  | 744 | 2 | 50.5 | 0 | 75144 | 0 | 100 | 0
82 | NR140063 | 400KV KOTESHWR-KHEP-I |  |  | 0.020833 |  | 743.5 | 2 | 2.7 | 0 | 4014.9 | 0 | 100 | 0
83 | NR140064 | 400KV KOTESHWR-KHEP-II |  |  | 0.018056 |  | 743.5667 | 2 | 2.7 | 0 | 4015.26 | 0 | 100 | 0
84 | NR140065 | 400KV KOTESHWR-TEHRI-I |  | 0.023611 |  |  | 744 | 4 | 14.463 | 0 | 43041.888 | 0 | 100 | 0
85 | NR140098 | 400KV KOTESHWR-TEHRI-II |  |  | 0.015278 | 0.4625 | 743.6333 | 4 | 16.49 | 0 | 49050.0547 | 0 | 100 | 0
86 | NR140069 | 400KV LUCKNOW-BAREILLY-II |  |  |  |  | 744 | 2 | 255.5 | 0 | 380184 | 0 | 100 | 0
87 | NR140070 | 400KV LUCKNOW-GORAKH-III | 0.079861 |  |  |  | 744 | 2 | 263.933 | 1011.7432 | 392732.304 | 0.0025762 | 99.7424 | 1.9167
88 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 0.079861 |  |  |  | 744 | 2 | 263.933 | 1011.7432 | 392732.304 | 0.0025762 | 99.7424 | 1.9167
89 | NR140112 | 400KV LUCKNOW-LKO(765)-I |  |  |  |  | 744 | 4 | 2.86 | 0 | 8511.36 | 0 | 100 | 0
90 | NR140113 | 400KV LUCKNOW-LKO(765)-II |  |  |  |  | 744 | 4 | 2.86 | 0 | 8511.36 | 0 | 100 | 0
91 | NR140072 | 400KV LUCKNOW-LKO(UP) |  | 0.034722 |  | 0.16458 | 744 | 2 | 41.743 | 0 | 62113.584 | 0 | 100 | 0
92 | NR140114 | 400KV LUCKNOW-ROSA-I |  |  |  |  | 744 | 2 | 169.785 | 0 | 252640.08 | 0 | 100 | 0
93 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 0.0090278 |  |  |  | 744 | 2 | 98.281 | 42.5884 | 146242.128 | 0.00029122 | 99.9709 | 0.21667
94 | NR140121 | 400KV LUCKNOW-SOHAWAL-II |  |  |  |  | 744 | 2 | 98.281 | 0 | 146242.128 | 0 | 100 | 0
95 | NR140073 | 400KV LUCKNOW-SULTANPR |  | 0.019444 |  | 1899-12-31 17:34 | 744 | 2 | 41.743 | 0 | 62113.584 | 0 | 100 | 0
96 | NR140074 | 400KV LUCKNOW-UNNAO-I |  |  | 0.018056 |  | 743.5667 | 2 | 73.826 | 0 | 109789.1055 | 0 | 100 | 0
97 | NR140075 | 400KV LUCKNOW-UNNAO-II |  |  |  |  | 744 | 2 | 73.826 | 0 | 109853.088 | 0 | 100 | 0
98 | NR140076 | 400KV MBAD-MURADNGR |  |  |  |  | 744 | 2 | 133.5 | 0 | 198648 | 0 | 100 | 0
99 | NR140142 | 400KV MEERUT-BAREILLY-I |  |  |  | 0.46806 | 744 | 2 | 66.009 | 0 | 98221.392 | 0 | 100 | 0
100 | NR140130 | 400KV MEERUT-BAREILLY-II |  |  |  | 0.46806 | 744 | 2 | 66.009 | 0 | 98221.392 | 0 | 100 | 0
101 | NR140077 | 400KV MEERUT-KOTESHWR-I |  | 0.011806 |  |  | 744 | 4 | 178.69 | 0 | 531781.44 | 0 | 100 | 0
102 | NR140099 | 400KV MEERUT-KOTESHWR-II |  | 0.013889 |  |  | 744 | 4 | 175.63 | 0 | 522674.88 | 0 | 100 | 0
103 | NR140078 | 400KV MEERUT-MND-I |  |  |  |  | 744 | 2 | 59.868 | 0 | 89083.584 | 0 | 100 | 0
104 | NR140079 | 400KV MEERUT-MND-II |  |  |  |  | 744 | 2 | 59.868 | 0 | 89083.584 | 0 | 100 | 0
105 | NR140143 | 400KV MEERUT-MND-III |  |  |  | 0.55486 | 744 | 2 | 54.298 | 0 | 80795.424 | 0 | 100 | 0
106 | NR140131 | 400KV MEERUT-MND-IV |  |  |  | 0.55278 | 744 | 2 | 54.298 | 0 | 80795.424 | 0 | 100 | 0
107 | NR140080 | 400KV MEERUT-MUZFRNGR |  |  |  |  | 744 | 2 | 37.38 | 0 | 55621.44 | 0 | 100 | 0
108 | NR140103 | 400KV MERTA-BEAWAR |  |  |  |  | 744 | 2 | 76.018 | 0 | 113114.784 | 0 | 100 | 0
109 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA |  |  |  |  | 744 | 4 | 30.15 | 0 | 89726.4 | 0 | 100 | 0
110 | NR140118 | 400KV NIMRANA-MANESAR-I |  |  |  |  | 744 | 2 | 67.041 | 0 | 99757.008 | 0 | 100 | 0
111 | NR140119 | 400KV NIMRANA-MANESAR-II |  |  |  |  | 744 | 2 | 67.041 | 0 | 99757.008 | 0 | 100 | 0
112 | NR140108 | 400KV NIMRANA-SIKAR-I |  |  |  | 1900-01-01 09:49 | 744 | 2 | 175.859 | 0 | 261678.192 | 0 | 100 | 0
113 | NR140109 | 400KV NIMRANA-SIKAR-II |  |  |  |  | 744 | 2 | 175.859 | 0 | 261678.192 | 0 | 100 | 0
114 | NR140084 | 400KV RIHAND-ALLD-I |  |  |  |  | 744 | 2 | 279.245 | 0 | 415516.56 | 0 | 100 | 0
115 | NR140085 | 400KV RIHAND-ALLD-II |  |  |  | 0.41319 | 744 | 2 | 279.245 | 0 | 415516.56 | 0 | 100 | 0
116 | NR140086 | 400KV ROORKI-MUZFRNGR |  |  |  |  | 744 | 2 | 2.1 | 0 | 3124.8 | 0 | 100 | 0
117 | NR140087 | 400KV ROORKI-RISHIKESH |  | 0.068056 |  |  | 744 | 2 | 2.1 | 0 | 3124.8 | 0 | 100 | 0
118 | NR140088 | 400KV SASARAM-BIHARSHRF-I |  |  |  | 0.61736 | 744 | 2 | 210 | 0 | 312480 | 0 | 100 | 0
119 | NR140089 | 400KV SASARAM-BIHARSHRF-II |  |  |  | 0.51667 | 744 | 2 | 210 | 0 | 312480 | 0 | 100 | 0
120 | NR140090 | 400KV SASARAM-SARNATH |  |  |  | 0.42431 | 744 | 2 | 76 | 0 | 113088 | 0 | 100 | 0
121 | NR140091 | 400KV SING-ALLD-I | 0.047917 |  |  |  | 744 | 2 | 224 | 515.2 | 333312 | 0.0015457 | 99.8454 | 1.15
122 | NR140092 | 400KV SING-ALLD-II |  | 0.00625 |  | 1899-12-31 06:55 | 744 | 2 | 202 | 0 | 300576 | 0 | 100 | 0
123 | NR140093 | 400KV SING-ANPARA | 0.10417 | 0.077778 |  |  | 744 | 2 | 25.057 | 125.285 | 37284.816 | 0.0033602 | 99.664 | 2.5
124 | NR140111 | 400KV SING-FATEHPUR | 0.010417 |  |  |  | 744 | 2 | 330.953 | 165.4765 | 492458.064 | 0.00033602 | 99.9664 | 0.25
125 | NR140095 | 400KV SING-LKO(UP) |  | 0.029167 |  |  | 744 | 2 | 408.6 | 0 | 607996.8 | 0 | 100 | 0
126 | NR140096 | 400KV SING-RIHAND-I |  |  |  |  | 744 | 2 | 42.026 | 0 | 62534.688 | 0 | 100 | 0
127 | NR140097 | 400KV SING-RIHAND-II |  |  |  |  | 744 | 2 | 43.952 | 0 | 65400.576 | 0 | 100 | 0
128 | N-W40001 | 400KV SING-VINDH-I |  |  |  | 0.57986 | 744 | 2 | 3.341 | 0 | 4971.408 | 0 | 100 | 0
129 | N-W40002 | 400KV SING-VINDH-II |  |  |  | 1899-12-31 14:33 | 744 | 2 | 3.317 | 0 | 4935.696 | 0 | 100 | 0
130 | N-W40003 | 400KV KANKROLI-ZERDA-I |  |  |  |  | 744 | 2 | 233.707 | 0 | 347756.016 | 0 | 100 | 0
131 | N-W40004 | 400KV BHINMAL-ZERDA |  |  |  | 1899-12-31 17:58 | 744 | 2 | 142.8 | 0 | 212486.4 | 0 | 100 | 0
17780.529
C |  | 220 KV TRANS LINES
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) |  |  |  | 0.28125 | 744 | 1 | 21.879 | 0 | 16277.976 | 0 | 100 | 0
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) |  |  |  |  | 744 | 1 | 16.894 | 0 | 12569.136 | 0 | 100 | 0
3 | BILUP2202 | 220KV ALLD-REWA RD-I |  |  |  | 0.12639 | 744 | 1 | 3 | 0 | 2232 | 0 | 100 | 0
4 | BILUP2203 | 220KV ALLD-REWA RD-II |  |  |  | 0.082639 | 744 | 1 | 3 | 0 | 2232 | 0 | 100 | 0
5 | NR122001 | 220KV ANTA-BHIL-I |  |  |  |  | 744 | 1 | 186.667 | 0 | 138880.248 | 0 | 100 | 0
6 | NR122002 | 220KV ANTA-BHIL-II |  |  |  |  | 744 | 1 | 186.667 | 0 | 138880.248 | 0 | 100 | 0
7 | NR122003 | 220KV ANTA-DAUSA |  | 0.045139 |  |  | 744 | 1 | 208.307 | 0 | 154980.408 | 0 | 100 | 0
8 | NR122004 | 220KV ANTA-RAPPC |  |  |  |  | 744 | 1 | 87.544 | 0 | 65132.736 | 0 | 100 | 0
9 | NR122005 | 220KV ANTA-S.MDHPR |  |  |  |  | 744 | 1 | 102.164 | 0 | 76010.016 | 0 | 100 | 0
10 | NR122006 | 220KV AUR-SIKANDARA-I |  |  |  |  | 744 | 1 | 182.176 | 0 | 135538.944 | 0 | 100 | 0
11 | NR122007 | 220KV AUR-SIKANDARA-II |  |  |  |  | 744 | 1 | 182.176 | 0 | 135538.944 | 0 | 100 | 0
12 | NR122008 | 220KV BASSI-BAGRU |  |  |  |  | 744 | 1 | 35.353 | 0 | 26302.632 | 0 | 100 | 0
13 | NR122009 | 220KV BASSI-DAUSA-I |  |  |  | 0.084028 | 744 | 1 | 20.109 | 0 | 14961.096 | 0 | 100 | 0
14 | NR122010 | 220KV BASSI-DAUSA-II |  |  |  | 0.10417 | 744 | 1 | 20.109 | 0 | 14961.096 | 0 | 100 | 0
15 | NR122011 | 220KV BASSI-IG NAGAR |  |  |  | 0.029167 | 744 | 1 | 22.478 | 0 | 16723.632 | 0 | 100 | 0
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 0.15486 |  |  |  | 744 | 2 | 234.59 | 1743.7857 | 349069.92 | 0.0049955 | 99.5004 | 3.7167
17 | NR122013 | 220KV DGANGA-PITHORAGRH |  |  |  |  | 744 | 2 | 59.01 | 0 | 87806.88 | 0 | 100 | 0
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I |  | 0.10139 |  |  | 744 | 1 | 5.5 | 0 | 4092 | 0 | 100 | 0
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II |  | 0.099306 |  |  | 744 | 1 | 5.5 | 0 | 4092 | 0 | 100 | 0
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH |  |  |  |  | 744 | 1 | 6 | 0 | 4464 | 0 | 100 | 0
21 | NR122041 | 220KV FATEHPUR-NAUBASTA |  |  |  |  | 744 | 1 | 6 | 0 | 4464 | 0 | 100 | 0
22 | BILHY2201 | 220KV FGPP-PALLA-I |  | 0.067361 |  | 0.11736 | 744 | 1 | 15.69 | 0 | 11673.36 | 0 | 100 | 0
23 | BILHY2202 | 220KV FGPP-PALLA-II |  | 0.067361 |  | 0.15 | 744 | 1 | 15.69 | 0 | 11673.36 | 0 | 100 | 0
24 | BILHY2203 | 220KV FGPP-SPUR-I |  | 0.079861 |  |  | 744 | 1 | 17.691 | 0 | 13162.104 | 0 | 100 | 0
25 | BILHY2204 | 220KV FGPP-SPUR-II |  | 0.079861 |  |  | 744 | 1 | 17.691 | 0 | 13162.104 | 0 | 100 | 0
26 | NR122014 | 220KV HIRAPURA-IG NAGAR |  |  |  |  | 744 | 2 | 24.875 | 0 | 37014 | 0 | 100 | 0
27 | NR122015 | 220KV HIRAPURA-SANGANER |  |  |  |  | 744 | 1 | 12 | 0 | 8928 | 0 | 100 | 0
28 | NR122016 | 220KV KNP-MAINPURI |  |  |  | 0.46111 | 744 | 1 | 10.4 | 0 | 7737.6 | 0 | 100 | 0
29 | NR122017 | 220KV KNP-NAUBASTA |  |  |  | 0.063194 | 744 | 1 | 14.86 | 0 | 11055.84 | 0 | 100 | 0
30 | NR122018 | 220KV KNP-PANKI-I |  |  |  |  | 744 | 1 | 10.4 | 0 | 7737.6 | 0 | 100 | 0
31 | NR122019 | 220KV KNP-PANKI-II |  |  |  |  | 744 | 1 | 14.86 | 0 | 11055.84 | 0 | 100 | 0
32 | NR122020 | 220KV KNP-UNCHR-I |  | 0.056944 |  |  | 744 | 1 | 143.553 | 0 | 106803.432 | 0 | 100 | 0
33 | NR122021 | 220KV KNP-UNCHR-II |  | 0.061111 |  |  | 744 | 1 | 143.553 | 0 | 106803.432 | 0 | 100 | 0
34 | NR122022 | 220KV KNP-UNCHR-III |  | 0.065278 |  |  | 744 | 1 | 144.63 | 0 | 107604.72 | 0 | 100 | 0
35 | NR122023 | 220KV KNP-UNCHR-IV |  | 0.072917 |  |  | 744 | 1 | 144.63 | 0 | 107604.72 | 0 | 100 | 0
36 | BILUP2204 | 220KV MEERUT-MPURAM-I |  | 0.066667 |  | 1899-12-31 12:51 | 744 | 1 | 2.316 | 0 | 1723.104 | 0 | 100 | 0
37 | BILUP2205 | 220KV MEERUT-MPURAM-II |  | 0.080556 |  | 0.030556 | 744 | 1 | 9.254 | 0 | 6884.976 | 0 | 100 | 0
38 | BILUP2206 | 220KV MEERUT-NARA |  | 0.043056 |  | 0.33542 | 744 | 1 | 2.316 | 0 | 1723.104 | 0 | 100 | 0
39 | BILUP2207 | 220KV MEERUT-SHTBDNGR |  |  | 0.7125 | 1900-01-02 11:07 | 726.9 | 1 | 8.234 | 0 | 5985.2946 | 0 | 100 | 0
40 | BILUP2208 | 220KV MEERUT-SIMBHOLI |  |  |  | 0.10139 | 744 | 1 | 9.254 | 0 | 6884.976 | 0 | 100 | 0
41 | NR122024 | 220KV PITHORAGRH-BRLY(UP) |  | 0.024306 |  |  | 744 | 1 | 177.88 | 0 | 132342.72 | 0 | 100 | 0
42 | NR122025 | 220KV RAIBRLY-CHINHAT |  | 0.097222 |  |  | 744 | 1 | 1.19 | 0 | 885.36 | 0 | 100 | 0
43 | NR122026 | 220KV RAIBRLY-LKO(UP) |  | 0.032639 |  | 0.41944 | 744 | 1 | 1.19 | 0 | 885.36 | 0 | 100 | 0
44 | NR122027 | 220KV RAPPB-CHITT-I |  | 0.038194 |  |  | 744 | 1 | 128.833 | 0 | 95851.752 | 0 | 100 | 0
45 | NR122028 | 220KV RAPPB-CHITT-II |  |  |  |  | 744 | 1 | 128.833 | 0 | 95851.752 | 0 | 100 | 0
46 | NR122029 | 220KV RAPPB-RAPPC |  |  |  |  | 744 | 1 | 0.175 | 0 | 130.2 | 0 | 100 | 0
47 | NR122030 | 220KV RAPPB-UDAIPUR |  | 0.074306 |  |  | 744 | 1 | 230.297 | 0 | 171340.968 | 0 | 100 | 0
48 | NR122031 | 220KV S.MDHPR-DAUSA-I |  | 0.025 |  |  | 744 | 1 | 106.243 | 0 | 79044.792 | 0 | 100 | 0
49 | NR122042 | 220KV SIKAR-RATANGARH-I |  |  |  |  | 744 | 1 | 2.83 | 0 | 2105.52 | 0 | 100 | 0
50 | NR122044 | 220KV SIKAR-RATANGARH-II |  |  |  |  | 744 | 1 | 2.83 | 0 | 2105.52 | 0 | 100 | 0
51 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I |  |  |  |  | 744 | 1 | 3 | 0 | 2232 | 0 | 100 | 0
52 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II |  |  |  |  | 744 | 1 | 3 | 0 | 2232 | 0 | 100 | 0
53 | NR122032 | 220KV SITARGANJ-BLY(UP) |  |  |  |  | 744 | 1 | 105.72 | 0 | 78655.68 | 0 | 100 | 0
54 | NR122033 | 220KV TNKPR-BLY(UP) |  |  |  | 0.56389 | 744 | 1 | 106 | 0 | 78864 | 0 | 100 | 0
55 | NR122034 | 220KV TNKPR-SITARGANJ |  |  |  | 0.52153 | 744 | 1 | 42.55 | 0 | 31657.2 | 0 | 100 | 0
56 | NR122035 | 220KV UNCHR-RAIBRLY-I |  | 0.029167 |  | 0.325 | 744 | 1 | 0.92 | 0 | 684.48 | 0 | 100 | 0
57 | NR122036 | 220KV UNCHR-RAIBRLY-II |  | 0.91319 |  | 1900-01-01 10:15 | 744 | 1 | 0.92 | 0 | 684.48 | 0 | 100 | 0
58 | NR122037 | 220KV UNCHR-RAIBRLY-III |  | 0.054167 |  |  | 744 | 1 | 42.5 | 0 | 31620 | 0 | 100 | 0
3441.931
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA |  |  |  |  | 744 | 1 | 58 | 0 | 43152 | 0 | 100 | 0
|  | TOTAL FOR T/LS | 1900-01-04 19:08 | 1900-01-01 14:43 | 1899-12-31 03:26 | 1900-04-03 16:42 |  |  | 21280.46 | 108080.2569 | 34225441.9594 | 0.0031579 | 99.6842
|  | OVERALL SYSTEM AVAILABILITY= |  | 99.9203 | % (AC) | 99.9211 | (AC& HVDC)
E |  | 765/400 KV ICT'S | [5 empty] | M.F. | MVA | OHxMVAxMF | THMxMVAxMF
1 | NR1ICT707 | 400/765KV ICT-I AGRA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
2 | NR1ICT708 | 400/765KV ICT-II AGRA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
3 | NR1ICT701 | 765/400kv ICT-I BALIA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
4 | NR1ICT702 | 765/400kv ICT-II BALIA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
13 | NR1ICT713 | 765/400kv ICT-I MEERUT |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
14 | NR1ICT714 | 765/400kv ICT-II MEERUT |  |  |  |  | 744 | 2.5 | 1500 | 0 | 2790000 | 0 | 100 | 0
F |  | 400/220 KV ICT'S
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
3 | NR1ICT03 | 315MVA ICT-I BASSI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
4 | NR1ICT04 | 315MVA ICT-II BASSI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
5 | NR1ICT05 | 315MVA ICT-III BAWANA |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
6 | NR1ICT06 | 315MVA ICT-I BHINMAL |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
7 | NR1ICT07 | 315MVA ICT-II BHINMAL |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
8 | NR1ICT08 | 315MVA ICT-I BHIWADI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
9 | NR1ICT09 | 315MVA ICT-II BHIWADI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
10 | NR1ICT54 | 315MVA ICT-III BHIWADI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
11 | NR1ICT10 | 315MVA ICT-I BLBGARH |  | 0.065972 |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
12 | NR1ICT11 | 315MVA ICT-II BLBGARH |  | 0.045139 |  | 0.26597 | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
13 | NR1ICT12 | 315MVA ICT-III BLBGARH |  | 0.079167 |  | 0.18958 | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
14 | NR1ICT13 | 315MVA ICT-IV BLBGARH |  | 0.079861 |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
15 | NR1ICT48 | 315MVA ICT-I FATEHPUR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
16 | NR1ICT49 | 315MVA ICT-II FATEHPUR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
17 | NR1ICT14 | 315MVA ICT-I GORAKHPR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
18 | NR1ICT15 | 315MVA ICT-II GORAKHPR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
19 | NR1ICT42 | 315MVA ICT-I GURGAON |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
20 | NR1ICT51 | 315MVA ICT-II GURGAON |  |  |  | 0.27639 | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
21 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
22 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
23 | NR1ICT16 | 315MVA ICT-I KANKROLI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
24 | NR1ICT17 | 315MVA ICT-II KANKROLI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
25 | NR1ICT18 | 315MVA ICT-III KANKROLI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
26 | NR1ICT19 | 315MVA ICT-I KANPUR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
27 | NR1ICT20 | 315MVA ICT-II KANPUR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
28 | NR1ICT21 | 315MVA ICT-I KOTA |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
29 | NR1ICT22 | 315MVA ICT-II KOTA |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
30 | NR1ICT23 | 315MVA ICT-I LUCKNOW |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
31 | NR1ICT53 | 500MVA ICT-II LUCKNOW |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
32 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
33 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
34 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
35 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
36 | NR1ICT26 | 315MVA ICT-I MAINPURI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
37 | NR1ICT27 | 315MVA ICT-II MAINPURI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
38 | NR1ICT28 | 315MVA ICT-I MANDOLA |  |  |  | 0.29028 | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
39 | NR1ICT29 | 315MVA ICT-II MANDOLA |  |  |  | 0.30625 | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
40 | NR1ICT30 | 315MVA ICT-III MANDOLA |  |  |  | 0.25625 | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
41 | NR1ICT31 | 315MVA ICT-IV MANDOLA | 0.0034722 |  |  | 0.31111 | 744 | 2.5 | 315 | 65.625 | 585900 | 0.00011201 | 99.9888 | 0.083333
42 | NR1ICT58 | 500MVA ICT-I MANESAR |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
43 | NR1ICT61 | 500MVA ICT-II MANESAR |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
44 | NR1ICT32 | 315MVA ICT-I MEERUT |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
45 | NR1ICT33 | 315MVA ICT-II MEERUT |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
46 | NR1ICT34 | 315MVA ICT-III MEERUT |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
47 | NR1ICT35 | 315MVA ICT-I MUZFRNGR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
48 | NR1ICT55 | 500MVA ICT-I NIMRANA |  |  |  |  | 744 | 2.5 | 500 | 0 | 930000 | 0 | 100 | 0
49 | NR1ICT50 | 315MVA ICT-II NIMRANA |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
50 | NR1ICT36 | 315MVA ICT-I ROORKI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
51 | NR1ICT37 | 315MVA ICT-II ROORKI |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
52 | NR1ICT59 | 315MVA ICT-I SOHAWAL |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
53 | NR1ICT60 | 315MVA ICT-II SOHAWAL |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
54 | NR1ICT56 | 315MVA ICT-I SIKAR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
55 | NR1ICT52 | 315MVA ICT-II SIKAR |  |  |  |  | 744 | 2.5 | 315 | 0 | 585900 | 0 | 100 | 0
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH |  |  |  |  | 744 | 2.5 | 100 | 0 | 186000 | 0 | 100 | 0
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH |  |  |  |  | 744 | 2.5 | 100 | 0 | 186000 | 0 | 100 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY |  |  |  |  | 744 | 2.5 | 100 | 0 | 186000 | 0 | 100 | 0
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY |  |  |  |  | 744 | 2.5 | 100 | 0 | 186000 | 0 | 100 | 0
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY |  |  |  |  | 744 | 2.5 | 100 | 0 | 186000 | 0 | 100 | 0
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ |  |  |  |  | 744 | 2.5 | 100 | 0 | 186000 | 0 | 100 | 0
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ |  |  |  |  | 744 | 2.5 | 100 | 0 | 186000 | 0 | 100 | 0
|  | TOTAL FOR ICTs | 0.0034722 | 0.27014 | 0 | 1899-12-31 21:30 |  | 190 |  | 65.625 | 75339300 | 8.7106e-07 | 99.9999
H |  | HVDC RIHAND-DADRI | [5 empty] | TCR | RC | TCR x OH | THM x RC
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 0.014583 |  |  |  | 744 | 750 | 750 | 262.5 | 558000 | 0.00047043 | 99.953 | 0.35
2 | NR1DCP02 | 500KV HVDC R-D POLE-II |  |  |  | 0.32292 | 744 | 750 | 750 | 0 | 558000 | 0 | 100 | 0
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 0.17639 |  |  |  | 744 | 1250 | 1250 | 5291.6667 | 930000 | 0.00569 | 99.431 | 4.2333
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II |  |  |  |  | 744 | 1250 | 1250 | 0 | 930000 | 0 | 100 | 0
|  | TOTAL FOR HVDC line | 0.19097 | 0 | 0 | 0.32292 |  |  |  | 5554.1667 | 2976000 | 0.0018663 | 99.8134
J |  | HVDC BTB VINDH | [5 empty] | TCR | RC | TCR x OH | THM x RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I |  |  |  | 1900-01-03 10:13 | 744 | 250 | 250 | 0 | 186000 | 0 | 0 | 0
2 | NR1DCB02 | +/-250MW HVDC B/B BLOCK-II |  |  |  | 1900-01-01 16:25 | 744 | 250 | 250 | 0 | 186000 | 0 | 0 | 0
|  | TOTAL FOR HVDC VINDHYACHAL | 0 | 0 | 0 | 1900-01-06 02:38 |  |  |  | 0 | 372000 | 0 | 100
K |  | HVDC BTB SASARAM
1 | NEDCB01 | +/-500MW HVDC B/B SASARAM | 0.18194 | 0.11458 |  |  | 744 | 500 | 500 | 2183.3333 | 372000 | 0.0058692 | 99.4131 | 4.3667
|  | TOTAL FOR HVDC SASARAM | 0.18194 | 0.11458 | 0 | 0 |  |  |  | 2183.3333 | 372000 | 0.0058692 | 99.4131
L |  | SVC, KANPUR | [5 empty] | M.F. | MVA | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  |  |  |  | 744 | 4 | 280 | 0 | 833280 | 0 | 100 | 0
2 | NR1SVC02 | +/-140MVAR SVC-II |  |  |  |  | 744 | 4 | 280 | 0 | 833280 | 0 | 100 | 0
|  | TOTAL FOR SVC | 0 | 0 | 0 | 0 |  |  |  | 0 | 1666560 | 0 | 100
M |  | Bus & Switch Line Reactor | [5 empty] | M.F. | MVA | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-II AGRA |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
2 | NR1BRT26 | 125MVAR B/Reactor-III AGRA |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 |  |  |  | 0.43194 | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 |  |  |  | 0.41319 | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY |  |  |  | 0.11944 | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
14 | NR1BRT04 | 50MVAR B/Reactor BASSI |  |  |  | 0.35278 | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
15 | NR1BRT05 | 80MVAR B/Reactor BHINMAL |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
16 | NR1BRT15 | 80MVAR B/Reactor BHIWADI |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
18 | NR1BRT07 | 80MVAR B/Reactor BLBGARH |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
19 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
20 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
21 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 |  |  |  | 0.44792 | 744 | 4 | 330 | 0 | 982080 | 0 | 100 | 0
22 | NR1BRT39 | 125MVAR B/Reactor GORAKHPUR |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
23 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
24 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
25 | NR1BRT08 | 50MVAR B/Reactor KANKROLI |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
26 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
27 | NR1BRT09 | 80MVAR B/Reactor KOTA |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
28 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
29 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
30 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
31 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
32 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
33 | NR1BRT11 | 50MVAR B/Reactor MANDOLA |  |  |  | 0.11667 | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
34 | NR1BRT30 | 125MVAR B/Reactor MANESAR |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
35 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
36 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  |  |  | 1900-01-29 | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
37 | NR1BRT24 | 80MVAR B/Reactor NIMRANA |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
38 | NR1BRT40 | 125MVAR B/Reactor ROORKI |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
39 | NR1BRT29 | 80MVAR B/Reactor SIKAR |  |  |  |  | 744 | 4 | 80 | 0 | 238080 | 0 | 100 | 0
40 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | 744 | 4 | 93.2 | 0 | 277363.2 | 0 | 100 | 0
41 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | 744 | 4 | 93.2 | 0 | 277363.2 | 0 | 100 | 0
42 | NR1BRT42 | 125MVAR B/Reactor-I VINDH |  |  |  |  | 744 | 4 | 125 | 0 | 372000 | 0 | 100 | 0
43 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I |  |  |  | 0.25 | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
44 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
45 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
46 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
47 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
48 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
49 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
50 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
51 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
52 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line |  |  |  |  | 744 | 4 | 330 | 0 | 982080 | 0 | 100 | 0
53 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
54 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
55 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE |  |  |  |  | 744 | 4 | 63 | 0 | 187488 | 0 | 100 | 0
56 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE |  |  |  |  | 744 | 4 | 63 | 0 | 187488 | 0 | 100 | 0
57 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
58 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE |  |  |  |  | 744 | 4 | 63 | 0 | 187488 | 0 | 100 | 0
59 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE |  |  |  |  | 744 | 4 | 63 | 0 | 187488 | 0 | 100 | 0
60 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
61 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
62 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II |  |  |  |  | 744 | 4 | 50 | 0 | 148800 | 0 | 100 | 0
63 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line |  |  |  |  | 744 | 4 | 240 | 0 | 714240 | 0 | 100 | 0
|  | TOTAL FOR BUS REACTORS | 0 | 0 | 0 | 1900-01-31 03:10 |  |  |  | 0 | 23580038.4 | 0 | 100
|  | TOTAL | 1900-01-05 04:10 | 1900-01-01 23:57 | 1899-12-31 03:26 | 1900-05-15 03:45
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(D18:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM([DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = SUM(E18:[OTHERS, row above])
OTHERS = SUM([OTHERS, row above])
Outage Not To Consider = SUM(F18:[Outage Not To Consider, row above])
Outage Not To Consider = SUM([Outage Not To Consider, row above])
Deemed = SUM(G18:[Deemed, row above])
Deemed = SUM([Deemed, row above])
Note on C156: cpcc: LILO of Alld-Phulpur at Jhusi .DOC-01-08-12
Note on C157: cpcc: LILO of Alld-Phulpur at Jhusi .DOC-01-08-12
Note on C167: Line reconfigured/ connected by RRVPNL at their Bagru S/S on 12/5/10. PG portion unchanged.