## SOP DATA NR1 May-17
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.05.2017 to 31.05.2017
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [24 empty] | 0
1 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | 2017-05-16 21:57 | 2017-05-16 22:30 |  |  |  | 0 | 0 | 0.022917 | 0 |  |  |  | LNCC | Line tripped on R-N fault during heavy wind storm. FLR-Jhatikara-62.9km, Agra-189.1 km, if-4.10KA. | [7 empty] | 744
[6 empty] | 2017-05-19 17:05 | 2017-05-20 15:44 |  |  |  | 0 | 0 | 0.94375 | 0 |  |  |  | LNCC | Line A/R and tripped on R-N fault during heavy wind storm. FLR-Ag-187.2Km, Jht-64.8Km, If-4.2kA. Forced S/D due to E/W found snapped between loc.506-507.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.96667 | 0 | [6 empty] | 720.8 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
2 | NR176509 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | 2017-05-24 09:30 | 2017-05-24 20:25 |  |  |  | 0.45486 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken by NR-1 for Line bay maintenance.
[6 empty] | 2017-05-29 03:19 | 2017-05-29 03:19 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/R on B-N fault, FLR-Phagi-180.52Km, If-3.305KA.
[6 empty] | 2017-05-31 12:13 | 2017-06-01 |  |  |  | 0 | 0 | 0.49097 | 0 |  |  |  | LNCC | Tripped on Y-N fault due to LA failure during heavy thunder storm and lightening at Phagi end. Phagi-0.28km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.45486 | 0 | 0.49097 | 0 | [6 empty] | 732.2167 | 1155 | 271.571 | 313664.505 | 308988.0602 | 98.5091
3 | NR176515 | 765KV BHIWANI-PHAGI(JPR)-II | 279.583 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1155 | 279.583 | 322918.365 | 322918.365 | 100
4 | NR176511 | 765KV MEERUT-GR.NOIDA | 119.159 | NR1 | -- | 2017-05-22 04:03 | 2017-05-22 05:17 |  |  |  | 0 | 0.051389 | 0 | 0 |  |  |  | OMSU | A/R from Meerut but tripped from GrNoida-UPPTCL end due to A/R problem on R-N fault during wind storm. FLR: Mrt-31.6km, IF-1.53KA, G. noida-93.81km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.051389 | 0 | 0 | [6 empty] | 744 | 1002 | 119.159 | 119397.318 | 119397.318 | 100
5 | NR276502 | 765KV JHATIKALA-BHIWANI | 85.188 | NR1 | -- | 2017-05-05 08:11 | 2017-05-05 20:47 |  |  |  | 0.525 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line mntc & other AMP work.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.525 | 0 | 0 | 0 | [6 empty] | 744 | 2250 | 85.188 | 191673 | 188426.925 | 98.3065
6 | NR276503 | 765KV MEERUT-BHIWANI | 173 | NR1 | -- | 2017-05-10 21:38 | 2017-05-10 22:07 |  |  |  | 0 | 0 | 0.020139 | 0 |  |  |  | LNCC | Tripped on Y-N fault during severe wind storm. FLR-Mrt-91km,IF-5.4KA, Bwn-80.3km, IF-7.7KA
[6 empty] | 2017-05-21 16:18 | 2017-05-21 17:29 |  |  |  | 0 | 0 | 0.049306 | 0 |  |  |  | LNCC | Tripped on Y-N fault during severe wind storm. FLR, Mrt-91.1km, IF-5.8KA
[6 empty] | 2017-05-29 04:54 | 2017-05-29 11:48 |  |  |  | 0 | 0 | 0 | 0.2875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-808kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.069444 | 0.2875 | [6 empty] | 742.3333 | 1466 | 173 | 253618 | 253618 | 100
7 | NR276501 | 765KV MOGA-BHIWANI | 273 | NR1 | -- | 2017-05-10 10:55 | 2017-05-10 17:28 |  |  |  | 0.27292 | 0 | 0 | 0 |  |  |  | LHWT | Tripped on Y-N fault due to polymer string broken at loc-120. FLR-Bhwn-38.64km, IF-10.39KA, Moga-229.76km
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.27292 | 0 | 0 | 0 | [6 empty] | 744 | 1791 | 273 | 488943 | 484638.4615 | 99.1196
B |  | 400 KV TRANS LINES |  |  | --
1 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2017-05-21 17:34 | 2017-05-21 22:55 | -- | -- | -- | 0 | 0 | 0 | 0.22292 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-437 kV
[6 empty] | 2017-05-29 01:57 | 2017-05-29 12:02 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.64306 | -- | -- | -- |  |  |  | 744 | 307 | 253.823 | 77923.661 | 77923.661 | 100
2 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 307 | 253.823 | 77923.661 | 77923.661 | 100
3 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2017-05-01 08:05 | 2017-05-02 16:36 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:31 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2017-05-07 18:01 | 2017-05-07 23:21 |  |  |  | 0 | 0 | 0 | 0.22222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra =433kv.
[6 empty] | 2017-05-09 04:08 | 2017-05-11 12:37 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:29 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra =430kv.
[6 empty] | 2017-05-17 08:28 | 2017-05-17 19:43 |  |  |  | 0.46875 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line Maintenance work by Sikar.
[6 empty] | 2017-05-19 07:56 | 2017-05-19 19:47 |  |  |  | 0.49375 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line Maintenance work by Sikar.
[6 empty] | 2017-05-20 03:38 | 2017-05-20 07:55 |  |  |  | 0 | 0 | 0 | 0.17847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2017-05-20 14:18 | 2017-05-20 20:37 |  |  |  | 0.26319 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line Maintenance work by Sikar.
[6 empty] | 2017-05-21 17:21 | 2017-05-23 15:28 |  |  |  | 0 | 0 | 0 | 1899-12-31 22:07 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2017-05-28 08:24 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 1900-01-02 15:36 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 05:25 | 0 | 0 | 1900-01-08 16:20 | -- | -- | -- |  |  |  | 744 | 568 | 393.9 | 223735.2 | 214889.039 | 96.0461
4 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2017-05-18 07:52 | 2017-05-18 22:38 | -- | -- | -- | 0.61528 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for line Maintenance work by Sikar.
[6 empty] | 2017-05-20 08:34 | 2017-05-20 13:58 |  |  |  | 0.225 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line Maintenance work by Sikar.
[6 empty] | 2017-05-27 18:35 | 2017-05-27 18:35 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/R on R-N fault, FLR-Agr-126Km, Sikar-274Km, If-1.6KA.
[6 empty] | 2017-05-28 03:45 | 2017-05-28 03:50 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | O/V protn operated at Agra>435kv during wide spread storm and load crash in the grid. DT received at Sikar.
[6 empty] | 2017-05-28 03:50 | 2017-05-28 21:46 |  |  |  | 0 | 0 | 0 | 0.74722 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage,
[6 empty] | 2017-05-29 01:17 | 2017-05-29 01:22 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | O/V protn operated at Agra>435kv during wide spread storm and load crash in the grid. DT received at Sikar.
[6 empty] | 2017-05-29 01:22 | 2017-05-29 12:36 |  |  |  | 0 | 0 | 0 | 0.46806 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage,
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.84028 | 0 | 0.0069444 | 1899-12-31 05:10 | -- | -- | -- |  |  |  | 743.8333 | 568 | 393.9 | 223735.2 | 217669.3342 | 97.2888
6 | NR140174 | 400KV BAGHPAT-DEHRADUN | 165 | NR1 | -- | 2017-05-03 08:47 | 2017-05-03 19:06 | -- | -- | -- | 0 | 0 | 0 | 0.42986 | -- | -- | -- | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-04 08:01 | 2017-05-04 19:10 |  |  |  | 0 | 0 | 0 | 0.46458 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-05 08:02 | 2017-05-05 19:00 |  |  |  | 0 | 0 | 0 | 0.45694 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-06 08:01 | 2017-05-06 19:29 |  |  |  | 0 | 0 | 0 | 0.47778 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-23 09:09 | 2017-05-23 19:53 |  |  |  | 0 | 0 | 0 | 0.44722 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-24 08:38 | 2017-05-24 19:55 |  |  |  | 0 | 0 | 0 | 0.47014 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-25 08:07 | 2017-05-25 19:19 |  |  |  | 0 | 0 | 0 | 0.46667 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-26 08:16 | 2017-05-26 19:33 |  |  |  | 0 | 0 | 0 | 0.47014 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-27 08:18 | 2017-05-27 19:31 |  |  |  | 0 | 0 | 0 | 0.46736 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-28 08:00 | 2017-05-28 20:16 |  |  |  | 0 | 0 | 0 | 0.51111 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 15:53 | -- | -- | -- |  |  |  | 744 | 687 | 165 | 113355 | 113355 | 100
5 | NR140173 | 400KV BAGPAT-SAHARANPUR | 121 | NR1 | -- | 2017-05-19 00:27 | 2017-05-19 00:27 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | LART | A/R on Y-N fault in Z-1. FLR:Baghpat-2.5km, IF 15.84KA, Saharanpur-122.4km, IF-0.34KA
[6 empty] | 2017-05-29 08:17 | 2017-05-29 19:45 |  |  |  | 0 | 0 | 0 | 0.47778 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-30 07:56 | 2017-05-30 20:14 |  |  |  | 0 | 0 | 0 | 0.5125 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-31 08:06 | 2017-05-31 19:42 |  |  |  | 0 | 0 | 0 | 0.48333 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:22 | -- | -- | -- |  |  |  | 744 | 687 | 121 | 83127 | 83127 | 100
5 | NR240006 | 400KV BAHADURGRH-BAWANA | 48.981 | NR1 | -- | 2017-05-21 16:47 | 2017-05-21 17:30 | -- | -- | -- | 0 | 0.029861 | 0 | 0 | -- | -- | -- | SBBU | Tripped due to Bus bar protn operation operated at Bawana (DTL) S/S
[6 empty] | 2017-05-21 17:30 | 2017-05-22 18:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:44 |  |  |  | OSFD | Forced S/D by DTL due to sparking observed in isolator during synchronisation at Bawana end.
[6 empty] | 2017-05-22 19:15 | 2017-05-22 19:52 |  |  |  | 0 | 0 | 0 | 0.025694 |  |  |  | OSFD | Forced S/D by DTL due to sparking observed at Bawana end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.029861 | 0 | 1899-12-31 01:21 | -- | -- | -- |  |  |  | 744 | 515 | 48.981 | 25225.215 | 25225.215 | 100
7 | NR240038 | 400KV BAHADURGRH-SONIPAT-I | 53.4 | NR1 | -- | 2017-05-31 11:22 | 2017-05-31 14:33 | -- | -- | -- | 0.13264 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D to attend B-ph isolator sparking at Sonipat.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.13264 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 605 | 53.4 | 32307 | 32168.7689 | 99.5721
8 | NR240039 | 400KV BAHADURGRH-SONIPAT-II | 53.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 605 | 53.4 | 32307 | 32307 | 100
9 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- | 2017-05-01 | 2017-05-07 15:25 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 15:25 | -- | -- | -- | LCSD | S/D for diversion of line due to DFCC rail project. Open since 22-04-2017 09:20:00
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 15:25 | -- | -- | -- |  |  |  | 744 | 416 | 235 | 97760 | 97760 | 100
10 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 47.762 | 24597.43 | 24597.43 | 100
11 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 48.99 | 25229.85 | 25229.85 | 100
12 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 37.164 | 19139.46 | 19139.46 | 100
13 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 37.164 | 19139.46 | 19139.46 | 100
14 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 247 | 106.153 | 26219.791 | 26219.791 | 100
17 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 48.432 | 33272.784 | 33272.784 | 100
18 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- | 2017-05-25 10:07 | 2017-05-25 20:30 | -- | -- | -- | 0 | 0 | 0 | 0.43264 | -- | -- | -- | OSPD | S/D by RRVPNL for Bus maintenance work at Phagi.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.43264 | -- | -- | -- |  |  |  | 744 | 687 | 48.432 | 33272.784 | 33272.784 | 100
15 | NR140171 | 400KV BASSI-SIKAR-I | 169.8 | NR1 | -- | 2017-05-13 11:03 | 2017-05-13 13:04 | -- | -- | -- | 0.084028 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for removing of a big Tarpolin piece at loc-288, flown and struck during wind storm.
[6 empty] | 2017-05-21 16:45 | 2017-05-22 09:56 |  |  |  | 0 | 0 | 0.71597 | 0 |  |  |  | LNCC | Tripped on B-N fault during severe wind storm. FLR:Sikar-108km, IF-3.9KA
[6 empty] | 2017-05-29 04:48 | 2017-05-29 04:53 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | O/V protn operated at Sikar>435kv during wide spread storm and load crash in the grid. DT received at Bassi.
[6 empty] | 2017-05-29 04:53 | 2017-05-29 05:54 |  |  |  | 0 | 0 | 0 | 0.042361 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage,
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.084028 | 0 | 0.71944 | 0.042361 | -- | -- | -- |  |  |  | 726.7333 | 515 | 169.8 | 87447 | 87204.3368 | 99.7225
16 | NR140172 | 400KV BASSI-SIKAR-II | 169.8 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 169.8 | 87447 | 87447 | 100
33 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | 2017-05-06 15:42 | 2017-05-06 18:24 |  |  |  | 0 | 0 | 0 | 0.1125 |  |  |  | OSPD | S/D by GETCO for new B/bar protn integration at Zerda.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.1125 | -- | -- | -- |  |  |  | 744 | 272 | 142.8 | 38841.6 | 38841.6 | 100
19 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | 2017-05-01 | 2017-05-07 15:22 |  |  |  | 0 | 0 | 0 | 1900-01-05 15:22 |  |  |  | LCSD | S/D for diversion of line due to DFCC rail project. Open since 22-04-2017 06:59:00
[6 empty] | 2017-05-21 17:29 | 2017-05-21 20:10 |  |  |  | 0 | 0 | 0.11181 | 0 |  |  |  | LNCC | Tripped on R-N fault during severe wind storm. FLR:Bwd-41.29km, IF-7.9KA
[6 empty] | 2017-05-29 04:27 | 2017-05-29 04:32 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | O/V protn operated at Bhwd>434kv during wide spread storm and heavy load crash in the grid.. DT received at GGN.
[6 empty] | 2017-05-29 04:32 | 2017-05-29 09:55 |  |  |  | 0 | 0 | 0 | 0.22431 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage,
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.11528 | 1900-01-05 20:45 | -- | -- | -- |  |  |  | 741.2333 | 515 | 82.8 | 42642 | 42642 | 100
20 | NR140033 | 400KV BHIWADI-HISAR-I | 211.547 | NR1 | -- | 2017-05-14 12:58 | 2017-05-14 13:13 | -- | -- | -- | 0.010417 | 0 | 0 | 0 | -- | -- | -- | LEFT | A/R at Hisar & trip from Bhw on Y-N fault. BWD=96.08km.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.010417 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 403 | 211.547 | 85253.441 | 85224.794 | 99.9664
21 | NR240087 | 400KV BHIWADI-HISAR-II | 144 | NR1 | -- | 2017-05-09 20:10 | 2017-05-09 20:56 |  |  |  | 0 | 0 | 0.031944 | 0 |  |  |  | LNCC | A/R form Hisar & tripped from Bhiwadi on Y-N fault during heavy wind strom. FLR-Bwd-12.15km, Hisar-103.5km.
[6 empty] | 2017-05-21 17:45 | 2017-05-24 19:41 |  |  |  | 0 | 0 | 0 | 1900-01-02 01:56 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-432 kV
[6 empty] | 2017-05-26 16:06 | 2017-05-26 17:38 |  |  |  | 0.063889 | 0 | 0 | 0 |  |  |  | OSPT | S/D for testing of auto-reclose relay at Bhiwadi end.
[6 empty] | 2017-05-29 04:51 | 2017-05-29 11:55 |  |  |  | 0 | 0 | 0 | 0.29444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.063889 | 0 | 0.031944 | 1900-01-02 09:00 | -- | -- | -- |  |  |  | 743.2333 | 331 | 144 | 47664 | 47565.6664 | 99.7937
22 | NR240088 | 400KV BHIWADI-HISAR-III | 144 | NR1 | -- | 2017-05-29 04:51 | 2017-05-29 10:30 |  |  |  | 0 | 0 | 0 | 0.23542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
[11 empty] | 0 | 0 | 0 | 0 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.23542 | -- | -- | -- |  |  |  | 744 | 331 | 144 | 47664 | 47664 | 100
23 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- | 2017-05-16 07:44 | 2017-05-16 13:05 | -- | -- | -- | 0.22292 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D by Kotputli for attending damaged jumper terminal.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.22292 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 132.428 | 68200.42 | 67710.0003 | 99.2809
24 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2017-05-19 19:11 | 2017-05-21 09:41 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 14:30 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMR-425 kV
[6 empty] | 2017-05-29 04:42 | 2017-05-29 10:12 |  |  |  | 0 | 0 | 0 | 0.22917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
[6 empty] | 2017-05-31 12:38 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 0.47361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 07:22 | -- | -- | -- |  |  |  | 744 | 515 | 48.428 | 24940.42 | 24940.42 | 100
25 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 48.428 | 24940.42 | 24940.42 | 100
26 | NR240061 | 400KV BHIWANI-BAWANA | 97.415 | NR1 | -- | 2017-05-21 16:47 | 2017-05-21 17:30 | -- | -- |  | 0 | 0.029861 | 0 | 0 | -- | -- | -- | SBBU | Tripped due to Bus bar protn operation operated at Bawana (DTL) S/S
[6 empty] | 2017-05-21 17:30 | 2017-05-21 21:21 |  |  |  | 0 | 0 | 0 | 0.16042 |  |  |  | OSFD | Forced S/D by DTL for attending Bus bar fault occured at Bawana.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.029861 | 0 | 0.16042 | -- | -- | -- |  |  |  | 744 | 515 | 97.415 | 50168.725 | 50168.725 | 100
27 | NR240059 | 400KV BHIWANI-BHIWANI(BBMB) | 33.962 | NR1 | -- | 2017-05-11 09:47 | 2017-05-11 17:37 | -- | -- |  | 0.32639 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for annual maintenance work.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.32639 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 33.962 | 17490.43 | 17306.279 | 98.9471
31 | NR240068 | 400KV BHIWANI-JIND-I | 82.23 | NR1 | -- | 2017-05-01 | 2017-06-01 | -- | -- |  | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bwn-432 kV. Open since 07-03-2017 21:43:00
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- |  |  |  | 744 | 515 | 82.23 | 42348.45 | 42348.45 | 100
32 | NR240069 | 400KV BHIWANI-JIND-II | 82.23 | NR1 | -- | 2017-05-01 | 2017-05-17 17:32 | -- | -- |  | 0 | 0 | 0 | 1900-01-15 17:32 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BWN-428 kV. Open since 13-03-2017 17:04:00
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-15 17:32 | -- | -- | -- |  |  |  | 744 | 515 | 82.23 | 42348.45 | 42348.45 | 100
34 | NR240103 | 400KV BHIWANI-KABULPR | 26.64 | NR1 | -- | 2017-05-18 13:32 | 2017-05-18 14:19 |  |  |  | 0 | 0 | 0.032639 | 0 |  |  |  | LNCC | Tripped on B-N fault due to forest fire at Loc.no-190-191. FLR-Bhiwani-18km,IF-12KA, Kabulpur-44.7km,IF-8.1KA
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.032639 | 0 | -- | -- | -- |  |  |  | 743.2167 | 515 | 26.64 | 13719.6 | 13719.6 | 100
34 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 42.7 | 21990.5 | 21990.5 | 100
35 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | 2017-05-21 17:44 | 2017-05-21 19:14 |  |  |  | 0 | 0 | 0.0625 | 0 |  |  |  | LNCC | A/R from Blb & tripped from Mhrnbg on B-N fault during severe wind storm. FLR:Blb-44.7km, Mbag-40.2km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.0625 | 0 | -- | -- | -- |  |  |  | 742.5 | 691 | 60.68 | 41929.88 | 41929.88 | 100
36 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) | 12.55 | NR1 | -- | 2017-05-26 05:31 | 2017-05-26 07:29 | -- | -- |  | 0 | 0 | 0 | 0.081944 | -- | -- | -- | OSFD | Forced S/D by HVPNL due to sparking in R-ph isolator at Navada s/yard
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.081944 | -- | -- | -- |  |  |  | 744 | 691 | 12.55 | 8672.05 | 8672.05 | 100
37 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 13.256 | 9159.896 | 9159.896 | 100
38 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 54.36 | 37562.76 | 37562.76 | 100
39 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 46.3 | 31993.3 | 31993.3 | 100
40 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 691 | 46.3 | 31993.3 | 31993.3 | 100
41 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2017-05-05 18:23 | 2017-05-05 21:40 | -- | -- |  | 0 | 0 | 0 | 0.13681 | -- | -- | -- | OSFD | Forced S/D by UPPCL to attend hotspot in B-ph Bus isolator at Mnagar end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.13681 | -- | -- | -- |  |  |  | 744 | 515 | 33.098 | 17045.47 | 17045.47 | 100
42 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 112.322 | 57845.83 | 57845.83 | 100
43 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- | 2017-05-07 20:00 | 2017-05-07 20:16 | -- | -- |  | 0 | 0.011111 | 0 | 0 | -- | -- | -- | OMSU | CB A/trip only from Dadri NTPC on DT received. Line remain charged from Panipat. No other flag facia reported.
[6 empty] | 2017-05-09 04:15 | 2017-05-09 04:52 |  |  |  | 0 | 0.025694 | 0 | 0 |  |  |  | OMSU | CB A/trip only from Dadri NTPC on DT received. Line remain charged from Panipat. No other flag facia reported.
[6 empty] | 2017-05-12 20:21 | 2017-05-12 20:54 |  |  |  | 0 | 0.022917 | 0 | 0 |  |  |  | OMSU | CB A/trip only from Dadri NTPC on DT received. Line remain charged from Panipat. No other flag facia reported.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.059722 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 117 | 60255 | 60255 | 100
44 | NR240026 | 400KV FATEHABAD-HISAR | 88.558 | NR1 | -- | 2017-05-29 03:56 | 2017-05-29 09:45 | -- | -- |  | 0 | 0 | 0 | 0.24236 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Hsr-432 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.24236 | -- | -- | -- |  |  |  | 744 | 515 | 88.558 | 45607.37 | 45607.37 | 100
45 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- | 2017-05-07 22:29 | 2017-05-07 22:46 | -- | -- | -- | 0.011806 | 0 | 0 | 0 | -- | -- | -- | LEFT | Line tripped on R-N fault. FLR-MND-16.8km, if-6.07kAmp.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.011806 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 23.462 | 16118.394 | 16112.2557 | 99.9619
46 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 23.462 | 16118.394 | 16118.394 | 100
28 | NR240060 | 400KV HISAR-BHIWANI-I | 64.461 | NR1 | -- | 2017-05-10 09:01 | 2017-05-10 17:54 | -- | -- |  | 0.37014 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for carrying out AMP work.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.37014 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 64.461 | 33197.415 | 32801.0391 | 98.806
29 | NR240093 | 400KV HISAR-BHIWANI-II | 56.669 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 56.669 | 29184.535 | 29184.535 | 100
30 | NR240094 | 400KV HISAR-BHIWANI-III | 56.669 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 56.669 | 29184.535 | 29184.535 | 100
47 | NR240015 | 400KV HISAR-BHIWANI(BBMB) | 34.52 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 34.52 | 17777.8 | 17777.8 | 100
48 | NR240016 | 400KV HISAR-KAITHAL-I | 113.12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 605 | 113.12 | 68437.6 | 68437.6 | 100
49 | NR240044 | 400KV HISAR-KAITHAL-II | 113.12 | NR1 | -- | 2017-05-29 03:20 | 2017-05-29 03:52 |  |  |  | 0 | 0 | 0.022222 | 0 |  |  |  | LNCC | Line tripped on Y-N fault during severe wind storm, FLR-Hsr-72.61Km, If-5.03KA.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.022222 | 0 | -- | -- | -- |  |  |  | 743.4667 | 385 | 113.12 | 43551.2 | 43551.2 | 100
50 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | 2017-05-01 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 1900-01-30 |  |  |  | OSFD | S/D by DTL for damaged tower rectification ( 1st Dead end tower from Bamnoli). Open since 2100hrs on 22.05.16
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- |  |  |  | 744 | 687 | 6.106 | 4194.822 | 4194.822 | 100
51 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | 2017-05-27 13:25 | 2017-05-27 14:25 |  |  |  | 0 | 0.041667 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-B fault in DTL portion. FLR:Jhatikr-10Km, If-12.6KA
[6 empty] | 2017-05-27 14:25 | 2017-05-27 21:30 |  |  |  | 0 | 0 | 0 | 0.29514 |  |  |  | OSFD | S/D by DTL to attend jumpher problem on ERS tower.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.041667 | 0 | 0.29514 | -- | -- | -- |  |  |  | 744 | 687 | 6.106 | 4194.822 | 4194.822 | 100
52 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- | 2017-05-17 10:11 | 2017-05-17 13:41 | -- | -- | -- | 0 | 0 | 0 | 0.14583 | -- | -- | -- | OSFD | S/D by DTL to attend isolator hotspot at Mundka end.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.14583 | -- | -- | -- |  |  |  | 744 | 687 | 6.782 | 4659.234 | 4659.234 | 100
53 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | 2017-05-17 14:27 | 2017-05-17 19:37 |  |  |  | 0 | 0 | 0 | 0.21528 |  |  |  | OSFD | S/D by DTL to attend isolator hotspot at Mundka end.
[6 empty] | 2017-05-18 07:04 | 2017-05-18 18:59 |  |  |  | 0 | 0 | 0 | 0.49653 |  |  |  | LCSD | S/D for E/wire insulation for Power tapping arrangement under Telecom project.
[6 empty] | 2017-05-19 07:06 | 2017-05-19 20:15 |  |  |  | 0 | 0 | 0 | 0.54792 |  |  |  | LCSD | S/D for E/wire insulation for Power tapping arrangement under Telecom project.
[6 empty] | 2017-05-20 08:52 | 2017-05-20 18:51 |  |  |  | 0 | 0 | 0 | 0.41597 |  |  |  | LCSD | S/D for E/wire insulation for Power tapping arrangement under Telecom project.
[6 empty] | 2017-05-24 09:24 | 2017-05-24 18:56 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LCSD | S/D of final installation of equipment for power tapping project.
[6 empty] | 2017-05-27 10:36 | 2017-05-27 16:28 |  |  |  | 0 | 0 | 0 | 0.24444 |  |  |  | LCSD | S/D for installation of Power tapping equipement under Telecom project.
[5 empty] | -- | 2017-05-30 15:46 | 2017-05-30 18:23 |  |  |  | 0 | 0 | 0 | 0.10903 |  |  |  | LCSD | S/D for installation of Power tapping equipement under Telecom project.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 10:14 | -- | -- | -- |  |  |  | 744 | 687 | 6.782 | 4659.234 | 4659.234 | 100
54 | NR240102 | 400KV KABULPR-BAHADURGRH | 38.58 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 38.58 | 19868.7 | 19868.7 | 100
56 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 225 | 201.2 | 45270 | 45270 | 100
57 | NR140169 | 400KV KANKROLI-CHITTOR(RJ)-I | 71.03 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 71.03 | 36580.45 | 36580.45 | 100
58 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2017-05-17 12:25 | 2017-05-17 12:36 | -- | -- | -- | 0 | 0.0076389 | 0 | 0 | -- | -- | -- | OMSU | Tripped on D/T Signal at Kankroli during Bus S/D at Jodhpur by RRVPNL.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.0076389 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 187.965 | 96801.975 | 96801.975 | 100
59 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 395 | 198.54 | 78423.3 | 78423.3 | 100
60 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | 2017-05-06 09:00 | 2017-05-06 15:23 |  |  |  | 0 | 0 | 0 | 0.26597 |  |  |  | OSPD | S/D by GETCO for new B/bar protn integration at Zerda.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.26597 | -- | -- | -- |  |  |  | 744 | 236 | 233.707 | 55154.852 | 55154.852 | 100
61 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- | 2017-05-16 09:26 | 2017-05-17 00:08 | -- | -- | -- | 0 | 0 | 0 | 0.6125 | -- | -- | -- | OSFD | S/D taken by Sri Cement for replacement of defective R-Ph CVT at Beawar end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.6125 | [6 empty] | 744 | 515 | 179.711 | 92551.165 | 92551.165 | 100
62 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- | 2017-05-10 18:11 | 2017-05-11 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.475 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Mrta =421kv.
[6 empty] | 2017-05-16 22:25 | 2017-05-17 07:01 |  |  |  | 0 | 0 | 0 | 0.35833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-418 kV
[6 empty] | 2017-05-19 18:26 | 2017-05-20 08:16 |  |  |  | 0 | 0 | 0 | 0.57639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-418 kV
[6 empty] | 2017-05-21 01:44 | 2017-05-21 09:09 |  |  |  | 0 | 0 | 0 | 0.30903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Merta-418 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 17:15 | -- | -- | -- |  |  |  | 744 | 309 | 255.56 | 78968.04 | 78968.04 | 100
63 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | 2017-05-25 10:49 | 2017-05-25 15:55 |  |  |  | 0.2125 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend heavy sparking in Y-ph line isolator at Kota.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.2125 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 50.5 | 26007.5 | 25829.2228 | 99.3145
64 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.7 | 1390.5 | 1390.5 | 100
65 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- | 2017-05-09 10:23 | 2017-05-09 10:39 | -- | -- | -- | 0 | 0 | 0 | 0.011111 | -- | -- | -- | OSPD | S/D by THDC for bus re-configuration at Tehri end
[6 empty] | 2017-05-19 09:18 | 2017-05-19 09:40 |  |  |  | 0 | 0 | 0 | 0.015278 |  |  |  | OSPD | S/D by THDC for bus re-configuration at Tehri end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.026389 | -- | -- | -- |  |  |  | 744 | 515 | 2.7 | 1390.5 | 1390.5 | 100
66 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 633 | 14.463 | 9155.079 | 9155.079 | 100
67 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 633 | 16.49 | 10438.17 | 10438.17 | 100
68 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | 2017-05-13 09:12 | 2017-05-17 16:45 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OSPD | S/D by SW-UPPTCL for LILO at their Hapur S/S.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 133.5 | 68752.5 | 68752.5 | 100
69 | NR140165 | 400KV MEERUT-BAGPAT-I | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 70.976 | 36552.64 | 36552.64 | 100
70 | NR140166 | 400KV MEERUT-BAGPAT-II | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 70.976 | 36552.64 | 36552.64 | 100
71 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
72 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | 2017-05-16 08:23 | 2017-05-16 08:23 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Tine successfully A/R on R-N fault in PowerLink portion. FLR-BRLY-56.7km, If 4.65 kAmp.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
73 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 678 | 178.69 | 121151.82 | 121151.82 | 100
74 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 673 | 175.63 | 118198.99 | 118198.99 | 100
75 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 59.868 | 30832.02 | 30832.02 | 100
76 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 59.868 | 30832.02 | 30832.02 | 100
77 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 54.298 | 27963.47 | 27963.47 | 100
78 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 54.298 | 27963.47 | 27963.47 | 100
79 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 37.38 | 19250.7 | 19250.7 | 100
80 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 76.018 | 39149.27 | 39149.27 | 100
81 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA | 30.15 | NR1 | -- | 2017-05-26 05:31 | 2017-05-26 07:13 | -- | -- | -- | 0 | 0 | 0 | 0.070833 | -- | -- | -- | OSFD | Forced S/D by HVPNL due to sparking in R-ph isolator at Navada s/yard
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.070833 | -- | -- | -- |  |  |  | 744 | 691 | 30.15 | 20833.65 | 20833.65 | 100
82 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- | 2017-05-09 00:49 | 2017-05-09 11:59 | -- | -- | -- | 0.46528 | 0 | 0 | 0 | -- | -- | -- | LEFT | Line tripped on B-N fault. FLR-MNS-19 km, if- 11.77 kAmp.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.46528 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 67.041 | 34526.115 | 34007.9139 | 98.4991
83 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 67.041 | 34526.115 | 34526.115 | 100
84 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- | 2017-05-04 18:43 | 2017-05-07 23:10 | -- | -- |  | 0 | 0 | 0 | 1900-01-02 04:27 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-11 18:00 | 2017-05-12 09:58 |  |  |  | 0 | 0 | 0 | 0.66528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-29 04:48 | 2017-05-29 04:53 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | O/V protn operated at Sikar>435kv during wide spread storm and heavy load crash in the grid. DT received at Bassi.
[6 empty] | 2017-05-29 04:53 | 2017-05-29 10:13 |  |  |  | 0 | 0 | 0 | 0.22222 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage,
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.0034722 | 1900-01-03 01:45 | -- | -- | -- |  |  |  | 743.9167 | 515 | 175.859 | 90567.385 | 90567.385 | 100
85 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- | 2017-05-19 18:35 | 2017-05-21 10:02 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:27 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMR-425 kV
[6 empty] | 2017-05-31 12:36 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMRN-428 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 02:51 | -- | -- | -- |  |  |  | 744 | 515 | 175.859 | 90567.385 | 90567.385 | 100
86 | NR140170 | 400KV RAPPC-CHITTOR(RJ)-I | 155.15 | NR1 | -- | 2017-05-16 05:33 | 2017-05-16 12:34 |  |  |  | 0 | 0.29236 | 0 | 0 |  |  |  | OMSU | Line tripped on DT received at RAPPC due to protn problem at Chittor(RRVPNL) end. Charging delayed due to operational problem at RAPP/ RRVPN end
[6 empty] | 2017-05-24 17:58 | 2017-05-24 19:53 |  |  |  | 0 | 0.079861 | 0 | 0 |  |  |  | OMSU | Line tripped on Bus fault at RAPPC, due to blasting of Y-ph CT of 400 RAPPC-Sujalpur line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.37222 | 0 | 0 | 0 | 0 | 0 |  |  |  | 735.0667 | 515 | 155.15 | 79902.25 | 79902.25 | 100
87 | NR140161 | 400KV ROORKI-KASHIPUR-I | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 150.832 | 103621.584 | 103621.584 | 100
88 | NR140162 | 400KV ROORKI-KASHIPUR-II | 150.832 | NR1 | -- | 2017-05-07 11:45 | 2017-05-07 11:45 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | LART | Line A/R on Y-N fault. FLR-Kashipur-73.6 km, If-1.37kA.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 150.832 | 103621.584 | 103621.584 | 100
89 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | 2017-05-18 17:35 | 2017-05-19 01:00 |  |  |  | 0 | 0 | 0 | 0.30903 |  |  |  | OSPD | S/D by UPPCLfor replacement of M-1 relay at Muzfrngr.
[6 empty] | 2017-05-29 07:37 | 2017-05-29 08:33 |  |  |  | 0 | 0.038889 | 0 | 0 |  |  |  | OMSU | A/R at Roorki but Trip from Mzfrngr on Y-N Fault in UPPCL portion. Roorki=28km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.038889 | 0 | 0.30903 | -- | -- | -- |  |  |  | 744 | 515 | 2.1 | 1081.5 | 1081.5 | 100
90 | NR140175 | 400KV ROORKEE -DEHRADUN | 79.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 79.7 | 54753.9 | 54753.9 | 100
91 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.1 | 1081.5 | 1081.5 | 100
92 | NR140167 | 400KV ROORKI-SAHARANPUR-I | 36.535 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 36.535 | 25099.545 | 25099.545 | 100
94 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 |  | 2017-05-01 | 2017-05-01 07:48 |  |  |  | 0 | 0 | 0 | 0.325 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv. Open since 30-04-2017 18:09:00
[6 empty] | 2017-05-03 15:36 | 2017-05-04 07:26 |  |  |  | 0 | 0 | 0 | 0.65972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-04 14:19 | 2017-05-11 10:34 |  |  |  | 0 | 0 | 0 | 1900-01-05 20:15 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-11 18:10 | 2017-05-11 22:37 |  |  |  | 0 | 0 | 0 | 0.18542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-13 17:36 | 2017-05-13 22:24 |  |  |  | 0 | 0 | 0 | 0.2 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-14 16:36 | 2017-05-15 06:02 |  |  |  | 0 | 0 | 0 | 0.55972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-16 20:38 | 2017-05-17 08:23 |  |  |  | 0 | 0 | 0 | 0.48958 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-420 kV
[6 empty] | 2017-05-19 16:46 | 2017-05-20 08:57 |  |  |  | 0 | 0 | 0 | 0.67431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. R/Garh-425 kV
[6 empty] | 2017-05-21 01:34 | 2017-05-21 08:06 |  |  |  | 0 | 0 | 0 | 0.27222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. R/Garh-425 kV
[6 empty] | 2017-05-21 16:27 | 2017-05-22 21:49 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:22 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-419 kV
[6 empty] | 2017-05-26 18:04 | 2017-05-27 05:43 |  |  |  | 0 | 0 | 0 | 0.48542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Skr-420 kV
[6 empty] | 2017-05-27 18:17 | 2017-05-27 22:34 |  |  |  | 0 | 0 | 0 | 0.17847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Skr-420 kV
[6 empty] | 2017-05-29 02:15 | 2017-05-29 05:45 |  |  |  | 0 | 0.14583 | 0 | 0 |  |  |  | SBBU | Ratangarh S/S blackout during heavy wind storm.
[6 empty] | 2017-05-31 12:15 | 2017-05-31 22:13 |  |  |  | 0 | 0 | 0 | 0.41528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.14583 | 0 | 1900-01-11 12:18 | -- | -- | -- |  |  |  | 744 | 515 | 76.48 | 39387.2 | 39387.2 | 100
95 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 |  | 2017-05-01 18:10 | 2017-05-01 19:16 |  |  |  | 0 | 0 | 0 | 0.045833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=424kv.
[6 empty] | 2017-05-29 02:15 | 2017-05-29 06:37 |  |  |  | 0 | 0.18194 | 0 | 0 |  |  |  | SBBU | Ratangarh S/S blackout during heavy wind storm.
[6 empty] | 2017-05-31 18:38 | 2017-05-31 19:26 |  |  |  | 0 | 0.033333 | 0 | 0 |  |  |  | SRMU | Line tripped during charging of 400 kv BUS-2 at Ratangarh end. DT received at Sikar End.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.21528 | 0 | 0.045833 | -- | -- | -- |  |  |  | 744 | 515 | 76.48 | 39387.2 | 39387.2 | 100
220KV LINES
1 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | 2017-05-21 23:59 | 2017-05-22 22:37 |  |  |  | 0 | 0 | 0 | 0.94306 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Anta-231 kV
[6 empty] | 2017-05-29 05:43 | 2017-05-29 12:20 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Anta>240kv
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 05:15 | -- | -- | -- |  |  |  | 744 | 132 | 186.667 | 24640.044 | 24640.044 | 100
2 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | 2017-05-10 13:47 | 2017-05-10 14:48 |  |  |  | 0 | 0 | 0.042361 | 0 |  |  |  | LNCC | Tripped on B-N fault in Z-1 due to forest fire. FLR-Anta-101km, Bhil-108km.
[6 empty] | 2017-05-10 14:48 | 2017-05-10 18:13 |  |  |  | 0 | 0 | 0 | 0.14236 |  |  |  | OSFD | Forced S/D taken by NTPC for attending CB Problem at Anta end .
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.042361 | 0.14236 | -- | -- | -- |  |  |  | 742.9833 | 132 | 186.667 | 24640.044 | 24640.044 | 100
3 | NR122046 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 180.287 | 23797.884 | 23797.884 | 100
4 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 87.544 | 11468.264 | 11468.264 | 100
5 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 102.164 | 13485.648 | 13485.648 | 100
6 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 35.353 | 4631.243 | 4631.243 | 100
7 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 20.109 | 2634.279 | 2634.279 | 100
8 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 20.109 | 2634.279 | 2634.279 | 100
9 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | 2017-05-14 00:18 | 2017-05-14 01:00 |  |  |  | 0 | 0.029167 | 0 | 0 |  |  |  | OMSU | 3-ph protn trip due to fault in RRVPNL section near IG-Nagar, caused by tower collapse after hit by a dumper.
[6 empty] | 2017-05-14 01:00 | 2017-05-27 12:56 |  |  |  | 0 | 0 | 0 | 1900-01-12 11:56 |  |  |  | OSFD | Forced S/D by RRVPNL due to Tower failure in their section at IG Nagar.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.029167 | 0 | 1900-01-12 11:56 | -- | -- | -- |  |  |  | 744 | 131 | 22.478 | 2944.618 | 2944.618 | 100
10 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 15.69 | 2055.39 | 2055.39 | 100
11 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 15.69 | 2055.39 | 2055.39 | 100
12 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 17.691 | 2317.521 | 2317.521 | 100
13 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 17.691 | 2317.521 | 2317.521 | 100
14 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | 2017-05-14 00:18 | 2017-05-14 01:00 |  |  |  | 0 | 0.029167 | 0 | 0 |  |  |  | OMSU | 3-ph protn trip due to fault in RRVPNL section near IG-Nagar, caused by tower collapse after hit by a dumper.
[6 empty] | 2017-05-14 01:00 | 2017-05-27 12:56 |  |  |  | 0 | 0 | 0 | 1900-01-12 11:56 |  |  |  | OSFD | Forced S/D by RRVPNL due to Tower failure in their section at IG Nagar.
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0.029167 | 0 | 1900-01-12 11:56 | [6 empty] | 744 | 131 | 24.875 | 3258.625 | 3258.625 | 100
15 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 12 | 1572 | 1572 | 100
16 | NR222004 | 220KV HISAR-HISAR I/A-I | 132 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 13.77 | 1817.64 | 1817.64 | 100
17 | NR222005 | 220KV HISAR-HISAR I/A-II | 132 | NR1 | -- | 2017-05-29 11:51 | 2017-05-29 18:23 |  |  |  | 0 | 0 | 0 | 0.27222 |  |  |  | OSFD | Forced S/D by HVPNL to attend B-ph isolator hotspot at their end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0.27222 | [6 empty] | 744 | 132 | 13.77 | 1817.64 | 1817.64 | 100
18 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | 2017-05-14 08:30 | 2017-05-15 19:50 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:20 |  |  |  | LCSD | S/D for shifting of 400kv Agra-Bassi line on ERS, falling in same span, for Diversion work due to new Railway track.
[6 empty] | 2017-05-23 08:10 | 2017-05-23 20:10 |  |  |  | 0 | 0 | 0 | 0.5 |  |  |  | LCSD | S/D for shifting of 400kv Agra-Bassi line from ERS to new tower due to diversion work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 23:20 | -- | -- | -- |  |  |  | 744 | 132 | 28.02 | 3698.64 | 3698.64 | 100
19 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 2.316 | 305.712 | 305.712 | 100
20 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 9.254 | 1221.528 | 1221.528 | 100
21 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- | 2017-05-31 13:17 | 2017-05-31 16:13 | -- | -- | -- | 0 | 0.12222 | 0 | 0 | -- | -- | -- | OMSU | Tripped on R-Y fault in UPPCL section. Mrt-22.4km.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.12222 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 2.316 | 305.712 | 305.712 | 100
22 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 8.234 | 1086.888 | 1086.888 | 100
23 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- | 2017-05-18 11:33 | 2017-05-18 20:00 |  |  |  | 0 | 0 | 0 | 0.35208 |  |  |  | OSPD | S/D by UPPCL for OPGW stringing at Simbholi end.
[6 empty] | 2017-05-19 07:00 | 2017-05-19 19:49 |  |  |  | 0 | 0 | 0 | 0.53403 |  |  |  | OSPD | S/D by UPPCL for OPGW stringing at Simbholi end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.88611 | -- | -- | -- |  |  |  | 744 | 132 | 9.254 | 1221.528 | 1221.528 | 100
24 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | 2017-05-11 05:00 | 2017-05-11 13:33 |  |  |  | 0 | 0 | 0 | 0.35625 |  |  |  | OSFD | S/D by NPCIL for replacement of Y-ph defective CT at RAPP end
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.35625 | -- | -- | -- |  |  |  | 744 | 131 | 128.833 | 16877.123 | 16877.123 | 100
25 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 128.833 | 16877.123 | 16877.123 | 100
26 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | 2017-05-29 19:19 | 2017-05-29 19:57 |  |  |  | 0 | 0.026389 | 0 | 0 |  |  |  | OMSU | Trip due to Directional over current relay oprtd at RAPC end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.026389 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 0.175 | 22.925 | 22.925 | 100
27 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- | 2017-05-19 14:29 | 2017-05-19 15:40 | -- | -- |  | 0 | 0 | 0 | 0.049306 | -- | -- | -- | OSFD | Hand tripped by RRVPNL due to fire in grass below the line at Debari S/yard.
[6 empty] | 2017-05-21 10:30 | 2017-05-21 19:48 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-22 07:53 | 2017-05-22 19:50 |  |  |  | 0 | 0 | 0 | 0.49792 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
[6 empty] | 2017-05-23 07:50 | 2017-05-23 20:35 |  |  |  | 0 | 0 | 0 | 0.53125 |  |  |  | LCSD | S/D for Polymer insulator string installation work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:11 | -- | -- | -- |  |  |  | 744 | 131 | 230.297 | 30168.907 | 30168.907 | 100
28 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | 2017-05-14 08:50 | 2017-05-15 20:52 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:02 |  |  |  | LCSD | S/D for shifting of 400kv Agra-Bassi line on ERS, falling in same span, for Diversion work due to new Railway track.
[5 empty] | -- | 2017-05-23 08:34 | 2017-05-23 20:10 |  |  |  | 0 | 0 | 0 | 0.48333 |  |  |  | LCSD | S/D for shifting of 400kv Agra-Bassi line from ERS to new tower due to diversion work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 23:38 | -- | -- | -- |  |  |  | 744 | 132 | 106.243 | 14024.076 | 14024.076 | 100
29 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- | 2017-05-23 13:10 | 2017-05-23 16:16 | -- | -- | -- | 0 | 0 | 0 | 0.12917 | -- | -- | -- | OSFD | Forced S/D taken by RRVPNL for attending CT oil leakage at Ratangarh.
[5 empty] | -- | 2017-05-29 02:15 | 2017-05-29 03:04 | -- | -- | -- | 0 | 0.034028 | 0 | 0 | -- | -- | -- | SBBU | Ratangarh S/S blackout during heavy wind storm.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.034028 | 0 | 0.12917 | -- | -- | -- |  |  |  | 744 | 132 | 2.83 | 373.56 | 373.56 | 100
30 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | 2017-05-18 15:12 | 2017-05-18 18:24 |  |  |  | 0 | 0 | 0 | 0.13333 |  |  |  | OSFD | S/D by RRVPNL to attend oil leakage in Y-ph CT at Rtngrh
[6 empty] | 2017-05-29 02:15 | 2017-05-29 03:04 |  |  |  | 0 | 0.034028 | 0 | 0 |  |  |  | SBBU | Ratangarh S/S blackout during heavy wind storm.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.034028 | 0 | 0.13333 | -- | -- | -- |  |  |  | 744 | 132 | 2.83 | 373.56 | 373.56 | 100
31 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- | 2017-05-03 16:16 | 2017-05-03 18:51 | -- | -- |  | 0.10764 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D to attend hot spot in Y-Ph L/Isolator at Sikar(PG)end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10764 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 394.625 | 99.6528
32 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
[5 empty] | -- | [17 empty] | 1637.99
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-09 15:40 | 1900-01-01 12:50 | 1900-01-04 03:04 | 1900-12-22 02:48 | [9 empty] | 6781974.837 | 6752552.9386 | 99.5662
%'(HVDC)
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | 2017-05-27 02:38 | 2017-05-27 20:30 |  |  |  | 0.74444 | 0 | 0 | 0 | -- | -- | -- | OSFT | Hand tripped due to TC-I faulty alarm. Charged after replacement of DC control cable.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.74444 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1463.9785 | 97.5986
5 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
7 | NR2ICT46 | 765/400KV ICT-I BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1000 |  | 1000 | 1000 | 100
8 | NR2ICT48 | 765/400KV ICT-II BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1000 |  | 1000 | 1000 | 100
F |  | 400/220 KV ICT'S |  | NR1 | --
1 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
2 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT68 | 500MVA ICT-III BASSI | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
4 | NR1ICT75 | 500MVA ICT-I BAGPAT | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
5 | NR1ICT78 | 500MVA ICT-II BAGPAT | 315 | NR1 |  | 2017-05-19 23:47 | 2017-05-20 02:51 |  |  |  | 0.12778 | 0 | 0 | 0 |  |  |  | OSFT | Hand tripped on observing abnormal chattering sound in the relay panel.
[6 empty] | 2017-05-29 10:32 | 2017-05-29 16:12 |  |  |  | 0.23611 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend sparking in relay panel.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.36389 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 494.1308 | 98.8262
6 | NR2ICT08 | 315MVA ICT-I BAHADURGARH | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
7 | NR2ICT42 | 500MVA ICT-II BAHADURGARH | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 500 |  | 500 | 500 | 100
8 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | 2017-05-21 16:47 | 2017-05-21 17:30 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | SBBU | Tripped due to Bus bar protn operation operated at Bawana (DTL) S/S
[6 empty] | 2017-05-21 17:30 | 2017-05-22 00:36 |  |  |  | 0 | 0 | 0 | 0.29583 |  |  |  | OSFD | Forced S/D by DTL for attending Bus bar fault occured at Bawana.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.029861 | 0 | 0.29583 | 0 | 0 | 0 |  |  |  | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
10 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
13 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
14 | NR2ICT49 | 315MVA ICT-I BHIWANI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
15 | NR2ICT50 | 315MVA ICT-II BHIWANI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
16 | NR1ICT71 | 500MVA ICT-I BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
17 | NR1ICT79 | 500MVA ICT-II BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
18 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | 2017-05-12 09:19 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 1900-01-18 14:41 |  |  |  | SCSD | S/D for retrofitment with new 500MVA ICT under capacity augmentation for DTL.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-18 14:41 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
19 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
19 | NR1ICT81 | 315MVA ICT-I DEHRADUN | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
19 | NR1ICT82 | 315MVA ICT-II DEHRADUN | 315 | NR1 | -- | 2017-05-01 | 2017-05-04 16:50 | -- | -- | -- | 1900-01-02 16:50 | 0 | 0 | 0 | -- | -- | -- | OSFT | Forced s/d due to abnormal DGA report. Open since 24-04-2017 09:20:00
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-02 16:50 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 277.3891 | 88.06
20 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | 2017-05-16 14:37 | 2017-05-16 16:16 |  |  |  | 0 | 0 | 0.06875 | 0 |  |  |  | GOLC | Tripped on over current protection operated due to high over loading.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.06875 | 0 | -- | -- | -- |  |  |  | 742.35 | 315 |  | 315 | 315 | 100
21 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | 2017-05-16 14:37 | 2017-06-01 |  |  |  | 1900-01-14 09:23 | 0 | 0 | 0 |  |  |  | SICT | Differential protn operated due to fault in 220kv cable.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-14 09:23 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 158.6079 | 50.3517
22 | NR2ICT09 | 315MVA ICT-I HISAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
23 | NR2ICT10 | 315MVA ICT-II HISAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
24 | NR2ICT34 | 315MVA ICT-III HISAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
25 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
26 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
27 | NR2ICT53 | 315MVA ICT-I JIND | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
28 | NR2ICT54 | 315MVA ICT-II JIND | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
29 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
30 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
31 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
32 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
33 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
34 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
35 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
36 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
37 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
38 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
39 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
40 | NR1ICT72 | 315MVA ICT-I MANDOLA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
41 | NR1ICT80 | 500MVA ICT-II MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
42 | NR1ICT73 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
43 | NR1ICT74 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
44 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
45 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
46 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 316 |  | 316 | 316 | 100
47 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
48 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
49 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
50 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
51 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
52 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
53 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
54 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
55 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
56 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
57 | NR1ICT76 | 315MVA ICT-I SAHARANPUR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
58 | NR1ICT77 | 315MVA ICT-II SAHARANPUR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
59 | NR2ICT36 | 315MVA ICT-I SONIPAT | 500 | NR1 | -- | 2017-05-15 09:40 | 2017-05-19 12:42 |  |  |  | 1900-01-03 03:02 | 0 | 0 | 0 |  |  |  | OSPT | S/D for replacement of defective Y-Ph bushing.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-03 03:02 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 273.0706 | 86.6891
60 | NR2ICT35 | 315MVA ICT-II SONIPAT | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT57 | 125MVAR B/Reactor-I BAGPAT | 50 | NR1 | -- | 2017-05-23 10:58 | 2017-05-23 16:00 |  |  |  | 0 | 0 | 0 | 0.20972 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-24 14:21 | 2017-05-26 18:29 |  |  |  | 0 | 0 | 0 | 1900-01-01 04:08 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 09:10 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
2 | NR1BRT04 | 50MVAR B/Reactor-I BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
3 | NR1BRT53 | 50MVAR B/Reactor-II BASSI | 50 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
4 | NR1BRT54 | 50MVAR B/Reactor-III BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
5 | NR1BRT60 | 125MVAR B/Reactor-IV BASSI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
6 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
7 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
8 | NR2BRT27 | 240MVAR B/Reactor-I BHIWANI | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
9 | NR2BRT28 | 240MVAR B/Reactor-II BHIWANI | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
10 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- | 2017-05-12 16:17 | 2017-05-21 07:05 | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 14:48 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-25 12:30 | 2017-05-26 07:34 |  |  |  | 0 | 0 | 0 | 0.79444 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-26 16:14 | 2017-05-27 04:07 |  |  |  | 0 | 0 | 0 | 0.49514 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 21:45 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
11 | NR1BRT63 | 80MVAR B/Reactor-I DEHRADUN | 80 | NR1 | -- | 2017-05-22 21:18 | 2017-05-26 19:54 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 22:36 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-29 17:05 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:55 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 05:31 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
12 | NR2BRT22 | 125MVAR B/Reactor-II HISAR | 125 | NR1 | -- | 2017-05-11 15:05 | 2017-05-12 04:02 |  |  |  | 0 | 0 | 0 | 0.53958 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[5 empty] | -- | 2017-05-25 10:14 | 2017-05-28 04:11 |  |  |  | 0 | 0 | 0 | 1900-01-01 17:57 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-02 06:54 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
13 | NR1BRT37 | 125MVAR B/Reactor-I JAIPUR(S) | 125 | NR1 | -- | 2017-05-01 22:18 | 2017-05-02 05:05 |  |  |  | 0 | 0 | 0 | 0.28264 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-13 22:25 | 2017-05-14 09:18 |  |  |  | 0 | 0 | 0 | 0.45347 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-15 22:22 | 2017-05-21 03:08 |  |  |  | 0 | 0 | 0 | 1900-01-04 04:46 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-30 12:08 | 2017-05-30 16:00 |  |  |  | 0 | 0 | 0 | 0.16111 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-05 02:18 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
14 | NR1BRT31 | 240MVAR B/Reactor-I JHATIKALA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 240 |  | 240 | 240 | 100
15 | NR1BRT52 | 240MVAR B/Reactor-II JHATIKALA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
16 | NR2BRT35 | 125MVAR Bus/eactor JIND | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
17 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
18 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
19 | NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 80 |  | 80 | 80 | 100
20 | NR1BRT55 | 50MVAR B/Reactor KOTA | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
21 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | 2017-05-01 22:16 | 2017-05-02 04:05 |  |  |  | 0 | 0 | 0 | 0.24236 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-13 22:16 | 2017-05-14 05:08 |  |  |  | 0 | 0 | 0 | 0.28611 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-15 22:08 | 2017-05-16 18:04 |  |  |  | 0 | 0 | 0 | 0.83056 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-17 23:11 | 2017-05-18 18:03 |  |  |  | 0 | 0 | 0 | 0.78611 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 03:29 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
22 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
23 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | 2016-05-20 07:36
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 2016-05-28 18:19 | 0 | 0 |  |  |  | 744 | 125 |  | 125 | 125 | 100
24 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | 2017-05-13 21:23 | 2017-05-21 19:18 |  |  |  | 0 | 0 | 0 | 1900-01-06 21:55 |  |  |  | SVRD | H/ tripped for voltage regulation<750kv. (Standing Instrn)
[6 empty] | 2017-05-25 09:46 | 2017-05-27 03:18 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:32 |  |  |  | SVRD | H/ tripped for voltage regulation<750kv. (Standing Instrn)
[6 empty] | 2017-05-27 20:54 | 2017-05-28 04:19 |  |  |  | 0 | 0 | 0 | 0.30903 |  |  |  | SVRD | H/ tripped for voltage regulation<750kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-08 22:52 | 2016-05-28 18:19 | 0 | 0 |  |  |  | 744 | 240 |  | 240 | 240 | 100
25 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
26 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
27 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI(JPR)-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 240 |  | 240 | 240 | 100
28 | NR1BRT48 | 125MVAR B/Reactor-I RATANGARH(RJ) | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
29 | NR1BRT40 | 125MVAR B/Reactor ROORKI | 125 | NR1 | -- | 2017-05-01 22:17 | 2017-05-07 18:03 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 19:46 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-08 14:48 | 2017-05-21 20:21 |  |  |  | 0 | 0 | 0 | 1900-01-12 05:33 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-22 21:15 | 2017-05-26 19:08 |  |  |  | 0 | 0 | 0 | 1900-01-02 21:53 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-27 22:04 | 2017-05-28 05:00 |  |  |  | 0 | 0 | 0 | 0.28889 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-22 06:08 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
30 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
31 | NR2BRT13 | 125MVAR B/Reactor SONIPAT | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
32 | NR2BRT29 | BHIWANI 240MVAR S/R MEERUT line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
33 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
34 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
35 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh-I LINE | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 50 |  | 50 | 50 | 100
36 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 50 |  | 50 | 50 | 100
37 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
38 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
39 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
40 | NR1BRT58 | 50MVAR B/Reactor-I SAHARANPUR | 50 | NR1 | -- | 2017-05-01 | 2017-05-01 07:53 |  |  |  | 0 | 0 | 0 | 0.32847 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-09 14:07 | 2017-05-10 07:36 |  |  |  | 0 | 0 | 0 | 0.72847 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-10 15:13 | 2017-05-21 17:37 |  |  |  | 0 | 0 | 0 | 1900-01-10 02:24 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-22 12:30 | 2017-05-26 18:34 |  |  |  | 0 | 0 | 0 | 1900-01-03 06:04 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-27 10:39 | 2017-05-28 04:59 |  |  |  | 0 | 0 | 0 | 0.76389 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-28 13:35 | 2017-05-29 05:50 |  |  |  | 0 | 0 | 0 | 0.67708 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-29 13:33 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:27 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-19 06:52 | 0 | 0 | 0 |  |  |  | 744 | 50 |  | 50 | 50 | 100
41 | NR1BRT59 | 50MVAR B/Reactor-II SAHARANPUR | 50 | NR1 | -- | 2017-05-01 | 2017-05-01 07:53 |  |  |  | 0 | 0 | 0 | 0.32847 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-09 14:07 | 2017-05-10 07:36 |  |  |  | 0 | 0 | 0 | 0.72847 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-10 15:13 | 2017-05-21 17:37 |  |  |  | 0 | 0 | 0 | 1900-01-10 02:24 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-22 12:30 | 2017-05-26 18:34 |  |  |  | 0 | 0 | 0 | 1900-01-03 06:04 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-27 10:39 | 2017-05-28 04:59 |  |  |  | 0 | 0 | 0 | 0.76389 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-28 13:35 | 2017-05-29 05:50 |  |  |  | 0 | 0 | 0 | 0.67708 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2017-05-29 13:33 | 2017-06-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:27 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-19 06:52 | 0 | 0 | 0 |  |  |  | 744 | 50 |  | 50 | 50 | 100
42 | NR1SRT27 | PHAGI(JPR)240MVAR S/R BHIWANI-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
43 | NR1SRT28 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 1900-07-20 21:22 | [9 empty] | 5105 | 5105 |  | %
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L15:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M15:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N15:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O15:[Deemed Available, row above])
Note on C15: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C375: DOC-11-02-15
Note on C435: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14