## SOP DATA NR1 September-17
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.09.2017 to 30.09.2017
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [24 empty] | 0
1 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 720 | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1747 | 253.076 | 442123.772 | 442123.772 | 100 |  | #N/A
2 | NR176509 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1155 | 271.571 | 313664.505 | 313664.505 | 100 |  | #N/A
3 | NR176515 | 765KV BHIWANI-PHAGI(JPR)-II | 279.583 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1155 | 279.583 | 322918.365 | 322918.365 | 100 |  | #N/A
4 | NR176511 | 765KV MEERUT-GR.NOIDA | 119.159 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1002 | 119.159 | 119397.318 | 119397.318 | 100 |  | #N/A
5 | NR276502 | 765KV JHATIKALA-BHIWANI | 85.188 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 2250 | 85.188 | 191673 | 191673 | 100 |  | #N/A
6 | NR276503 | 765KV MEERUT-BHIWANI | 173 | NR1 | -- | 2017-09-01 | 2017-09-01 15:03 |  |  |  | 0 | 0 | 0 | 0.62708 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-799KV. Open since 31-08-2017 17:37. | [8 empty] | 100
[6 empty] | 2017-09-26 06:10 | 2017-09-26 09:54 |  |  |  | 0 | 0 | 0 | 0.15556 |  |  |  | LVRD | Line hand tripped for Voltage regulation.MRT=812KV | [8 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.78264 | [6 empty] | 720 | 1466 | 173 | 253618 | 253618 | 100 |  | #N/A
7 | NR276501 | 765KV MOGA-BHIWANI | 273 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1791 | 273 | 488943 | 488943 | 100 |  | #N/A
B |  | 400 KV TRANS LINES |  |  | -- | [22 empty] | #N/A
1 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2017-09-01 | 2017-09-05 12:17 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 12:17 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-435KV. Open since 31-08-2017 17:14. | [8 empty] | 100
[6 empty] | 2017-09-15 18:14 | 2017-09-21 22:36 |  |  |  | 0 | 0 | 0 | 1900-01-05 04:22 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436KV | [8 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-09 16:39 | -- | -- | -- |  |  |  | 720 | 307 | 253.823 | 77923.661 | 77923.661 | 100 |  | #N/A
2 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2017-09-22 04:09 | 2017-09-25 09:57 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 05:48 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-433KV | [8 empty] | 100
[6 empty] | 2017-09-26 06:11 | 2017-09-30 11:28 |  |  |  | 0 | 0 | 0 | 1900-01-03 05:17 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435KV | [8 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 11:05 | -- | -- | -- |  |  |  | 720 | 307 | 253.823 | 77923.661 | 77923.661 | 100 |  | #N/A
3 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2017-09-01 04:10 | 2017-09-01 19:46 | -- | -- | -- | 0 | 0 | 0 | 0.65 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. AGRA-435KV | [8 empty] | 98.1435
[6 empty] | 2017-09-02 02:53 | 2017-09-03 21:17 |  |  |  | 0 | 0 | 0 | 1899-12-31 18:24 |  |  |  | LVRD | Line hand tripped for Voltage regulation. AGRA-434KV | [8 empty] | #N/A
[6 empty] | 2017-09-05 06:15 | 2017-09-05 21:34 |  |  |  | 0 | 0 | 0 | 0.63819 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432KV | [8 empty] | #N/A
[6 empty] | 2017-09-06 08:02 | 2017-09-07 13:32 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:30 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433KV | [8 empty] | #N/A
[6 empty] | 2017-09-12 03:46 | 2017-09-12 20:31 |  |  |  | 0 | 0 | 0 | 0.69792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra=431kv. | [8 empty] | #N/A
[6 empty] | 2017-09-15 03:04 | 2017-09-15 10:07 |  |  |  | 0 | 0 | 0 | 0.29375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432KV | [8 empty] | #N/A
[6 empty] | 2017-09-15 10:07 | 2017-09-15 22:31 |  |  |  | 0.51667 | 0 | 0 | 0 |  |  |  | OSPT | S/D by NR-3 for tie bay work at Agra-HVDC | [8 empty] | #N/A
[6 empty] | 2017-09-17 17:21 | 2017-09-21 12:04 |  |  |  | 0 | 0 | 0 | 1900-01-02 18:43 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-437KV | [8 empty] | #N/A
[6 empty] | 2017-09-22 08:05 | 2017-09-23 04:08 |  |  |  | 0 | 0 | 0 | 0.83542 |  |  |  | LCSD | S/D for commisioning of new T/bay at Agra. | [8 empty] | #N/A
[6 empty] | 2017-09-23 04:08 | 2017-09-24 20:22 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:14 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434KV | [8 empty] | #N/A
[6 empty] | 2017-09-27 18:11 | 2017-09-27 19:09 |  |  |  | 0.040278 | 0 | 0 | 0 |  |  |  | OSFT | Emergency hand tripped due to PLCC problem at Agra | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.55694 | 0 | 0 | 1900-01-10 13:37 | -- | -- | -- |  |  |  | 720 | 568 | 393.9 | 223735.2 | 219581.5974 | 98.1435 |  | #N/A
4 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2017-09-01 | 2017-09-04 19:47 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 19:47 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-434KV. Open since 29-08-2017 08:08. | [8 empty] | 98.8681
[6 empty] | 2017-09-09 18:47 | 2017-09-09 20:46 |  |  |  | 0.082639 | 0 | 0 | 0 |  |  |  | SPLT | Line tripped due to PLCC Mal-operation at Agra end. | [8 empty] | #N/A
[6 empty] | 2017-09-11 15:39 | 2017-09-11 21:49 |  |  |  | 0.25694 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for rectification of DC Source mixing at Ag/HVDC. | [8 empty] | #N/A
[6 empty] | 2017-09-22 08:05 | 2017-09-23 04:08 |  |  |  | 0 | 0 | 0 | 0.83542 |  |  |  | LCSD | S/D for commisioning of new T/bay at Agra. | [8 empty] | #N/A
[6 empty] | 2017-09-23 04:08 | 2017-09-23 14:45 |  |  |  | 0 | 0 | 0 | 0.44236 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434KV | [8 empty] | #N/A
[6 empty] | 2017-09-24 02:30 | 2017-09-28 11:41 |  |  |  | 0 | 0 | 0 | 1900-01-03 09:11 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-434KV | [8 empty] | #N/A
[6 empty] | 2017-09-30 08:01 | 2017-10-01 |  |  |  | 0 | 0 | 0 | 0.66597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432KV | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.33958 | 0 | 0 | 1900-01-09 03:37 | -- | -- | -- |  |  |  | 720 | 568 | 393.9 | 223735.2 | 221202.6418 | 98.8681 |  | #N/A
6 | NR140174 | 400KV BAGHPAT-DEHRADUN | 165 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 165 | 113355 | 113355 | 100 |  | #N/A
5 | NR140173 | 400KV BAGPAT-SAHARANPUR | 121 | NR1 | -- | 2017-09-09 14:52 | 2017-09-09 15:15 | -- | -- | -- | 0 | 0.015972 | 0 | 0 | -- | -- | -- | OMSU | Line tripped due to Kite thread on R-Y fault, FLR-Bgpt-56.4Km, Spur-55Km, If-8.2KA. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.015972 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 121 | 83127 | 83127 | 100 |  | #N/A
5 | NR240006 | 400KV BAHADURGRH-BAWANA | 48.981 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 48.981 | 25225.215 | 25225.215 | 100 |  | #N/A
7 | NR240038 | 400KV BAHADURGRH-SONIPAT-I | 53.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 605 | 53.4 | 32307 | 32307 | 100 |  | #N/A
8 | NR240039 | 400KV BAHADURGRH-SONIPAT-II | 53.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 605 | 53.4 | 32307 | 32307 | 100 |  | #N/A
9 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 416 | 235 | 97760 | 97760 | 100 |  | #N/A
10 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 47.762 | 24597.43 | 24597.43 | 100 |  | #N/A
11 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | 2017-09-21 12:53 | 2017-09-21 16:44 |  |  |  | 0 | 0.16042 | 0 | 0 |  |  |  | OMSU | Line tripped on DT received at Bassi end due to problem at Heerapura(RRVPNL) end. No flag Facia reported at Bassi end. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.16042 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 48.99 | 25229.85 | 25229.85 | 100 |  | #N/A
12 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- | 2017-09-27 09:03 | 2017-09-27 19:02 |  |  |  | 0.41597 | 0 | 0 | 0 |  |  |  | OSPT | S/D for carrying out AMP work | [8 empty] | 98.6134
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.41597 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 37.164 | 19139.46 | 18874.0772 | 98.6134 |  | #N/A
13 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | 2017-09-28 08:49 | 2017-09-28 17:44 |  |  |  | 0.37153 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line maintenance and AMP work. | [8 empty] | 98.7616
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.37153 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 37.164 | 19139.46 | 18902.432 | 98.7616 |  | #N/A
14 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- | 2017-09-29 09:49 | 2017-09-29 19:52 | -- | -- | -- | 0.41875 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for carrying out Amp work. | [8 empty] | 98.6042
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.41875 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 247 | 106.153 | 26219.791 | 25853.8064 | 98.6042 |  | #N/A
17 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.432 | 33272.784 | 33272.784 | 100 |  | #N/A
18 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.432 | 33272.784 | 33272.784 | 100 |  | #N/A
15 | NR140171 | 400KV BASSI-SIKAR-I | 169.8 | NR1 | -- | 2017-09-24 08:00 | 2017-09-24 19:25 | -- | -- | -- | 0.47569 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for line maintenance & AMP work. | [8 empty] | 98.4144
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.47569 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 169.8 | 87447 | 86060.3983 | 98.4144 |  | #N/A
16 | NR140172 | 400KV BASSI-SIKAR-II | 169.8 | NR1 | -- | 2017-09-06 14:29 | 2017-09-06 14:29 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | LART | A/R on B-N fault, FLR, Bassi-75.3KM, IF-3.9KA | [8 empty] | 98.5669
[6 empty] | 2017-09-07 09:38 | 2017-09-07 11:10 |  |  |  | 0 | 0.063889 | 0 | 0 |  |  |  | OMSU | S/D for removal of kite thread from tower | [8 empty] | #N/A
[6 empty] | 2017-09-08 11:59 | 2017-09-08 15:12 |  |  |  | 0 | 0.13403 | 0 | 0 |  |  |  | OMSU | S/D for removal of kite thread from tower no. 179. | [8 empty] | #N/A
[6 empty] | 2017-09-25 08:34 | 2017-09-25 18:49 |  |  |  | 0.42708 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line maintenance & AMP work. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.42708 | 0.19792 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 169.8 | 87447 | 86202.0948 | 98.5764 |  | #N/A
33 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 272 | 142.8 | 38841.6 | 38841.6 | 100 |  | #N/A
19 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 82.8 | 42642 | 42642 | 100 |  | #N/A
20 | NR140033 | 400KV BHIWADI-HISAR-I | 211.547 | NR1 | -- | 2017-09-11 08:05 | 2017-09-11 19:14 | -- | -- | -- | 0.46458 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for line mntc & other AMP work. | [8 empty] | 96.8588
[6 empty] | 2017-09-12 08:18 | 2017-09-12 19:46 |  |  |  | 0.47778 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work by HSR. | [8 empty] | #N/A
[6 empty] | 2017-09-23 02:39 | 2017-09-26 13:11 |  |  |  | 0 | 0 | 0 | 1900-01-02 10:32 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD=422kv. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.94236 | 0 | 0 | 1900-01-02 10:32 | -- | -- | -- |  |  |  | 720 | 403 | 211.547 | 85253.441 | 82575.4568 | 96.8588 |  | #N/A
21 | NR240087 | 400KV BHIWADI-HISAR-II | 144 | NR1 | -- | 2017-09-01 07:41 | 2017-09-05 12:33 |  |  |  | 0 | 0 | 0 | 1900-01-03 04:52 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-426KV | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 04:52 | -- | -- | -- |  |  |  | 720 | 331 | 144 | 47664 | 47664 | 100 |  | #N/A
22 | NR240088 | 400KV BHIWADI-HISAR-III | 144 | NR1 | -- | 2017-09-01 07:42 | 2017-09-01 12:26 |  |  |  | 0 | 0 | 0 | 0.19722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-426KV | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.19722 | -- | -- | -- |  |  |  | 720 | 331 | 144 | 47664 | 47664 | 100 |  | #N/A
23 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 132.428 | 68200.42 | 68200.42 | 100 |  | #N/A
24 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2017-09-01 04:05 | 2017-09-02 20:14 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 16:09 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMR-426KV | [8 empty] | 100
[6 empty] | 2017-09-23 02:11 | 2017-09-25 11:09 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:58 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-425KV | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 01:07 | -- | -- | -- |  |  |  | 720 | 515 | 48.428 | 24940.42 | 24940.42 | 100 |  | #N/A
25 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 48.428 | 24940.42 | 24940.42 | 100 |  | #N/A
26 | NR240061 | 400KV BHIWANI-BAWANA | 97.415 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 97.415 | 50168.725 | 50168.725 | 100 |  | #N/A
27 | NR240059 | 400KV BHIWANI-BHIWANI(BBMB) | 33.962 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 33.962 | 17490.43 | 17490.43 | 100 |  | #N/A
31 | NR240068 | 400KV BHIWANI-JIND-I | 82.23 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 82.23 | 42348.45 | 42348.45 | 100 |  | #N/A
32 | NR240069 | 400KV BHIWANI-JIND-II | 82.23 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 82.23 | 42348.45 | 42348.45 | 100 |  | #N/A
34 | NR240103 | 400KV BHIWANI-KABULPR | 26.64 | NR1 | -- | 2017-09-22 11:21 | 2017-09-22 15:35 |  |  |  | 0 | 0 | 0 | 0.17639 |  |  |  | OSPD | S/D by HVPNL to attend hotspot in R ph W/Trap at Kabulpr. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.17639 | -- | -- | -- |  |  |  | 720 | 515 | 26.64 | 13719.6 | 13719.6 | 100 |  | #N/A
34 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | 2017-09-04 15:15 | 2017-09-04 18:15 |  |  |  | 0.125 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D to attend the hot spot in B-ph terminal connector at BLB end. | [8 empty] | 99.5833
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.125 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 42.7 | 21990.5 | 21898.8729 | 99.5833 |  | #N/A
35 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | 2017-09-01 16:18 | 2017-09-01 18:55 |  |  |  | 0.10903 | 0 | 0 | 0 |  |  |  | SBBT | Tripped due to 400KV Busbar-I protection operated at M.bagh | [8 empty] | 99.6357
[6 empty] | 2017-09-17 12:18 | 2017-09-17 13:56 |  |  |  | 0 | 0.068056 | 0 | 0 |  |  |  | OMSU | Line tripped due to kite thread on R-Y fault FLR-BLB-60Km, M/Bagh-1.1Km, If-8.8KA. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.10903 | 0.068056 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 60.68 | 41929.88 | 41777.4959 | 99.6366 |  | #N/A
36 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) | 12.55 | NR1 | -- | 2017-09-19 10:29 | 2017-09-19 16:02 | -- | -- |  | 0 | 0 | 0 | 0.23125 | -- | -- | -- | OSFD | S/D by HVPNL for attending hot spot on line isolator at Navada end | [8 empty] | 100
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.23125 | -- | -- | -- |  |  |  | 720 | 691 | 12.55 | 8672.05 | 8672.05 | 100 |  | #N/A
37 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 13.256 | 9159.896 | 9159.896 | 100 |  | #N/A
38 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 54.36 | 37562.76 | 37562.76 | 100 |  | #N/A
39 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 46.3 | 31993.3 | 31993.3 | 100 |  | #N/A
40 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 691 | 46.3 | 31993.3 | 31993.3 | 100 |  | #N/A
41 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2017-09-26 09:54 | 2017-09-26 12:10 | -- | -- |  | 0 | 0.094444 | 0 | 0 | -- | -- | -- | SRMU | Tripped due to relay mal-function at Mrdngr(UPPCL) end. DT received at Dadri | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.094444 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 33.098 | 17045.47 | 17045.47 | 100 |  | #N/A
42 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 112.322 | 57845.83 | 57845.83 | 100 |  | #N/A
43 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 117 | 60255 | 60255 | 100 |  | #N/A
44 | NR240026 | 400KV FATEHABAD-HISAR | 88.558 | NR1 | -- | 2017-09-01 16:35 | 2017-09-04 08:32 | -- | -- |  | 0 | 0 | 0 | 1900-01-01 15:57 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. HISAR 418 KV | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 15:57 | -- | -- | -- |  |  |  | 720 | 515 | 88.558 | 45607.37 | 45607.37 | 100 |  | #N/A
45 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- | 2017-09-09 09:54 | 2017-09-09 19:23 | -- | -- | -- | 0.39514 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for carrying out AMP work. | [8 empty] | 98.6829
[6 empty] | 2017-09-23 09:44 | 2017-09-23 20:11 |  |  |  | 0 | 0 | 0 | 0.43542 |  |  |  | LCSD | S/D for extension work & energisation of B/R-II at Manesar. | [8 empty] | #N/A
[6 empty] | 2017-09-26 11:00 | 2017-09-26 19:20 |  |  |  | 0 | 0 | 0 | 0.34722 |  |  |  | LCSD | S/D for 400KV BUS-II interfacing work at Manesar under GIS extn work | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.39514 | 0 | 0 | 0.78264 | -- | -- | -- |  |  |  | 720 | 687 | 23.462 | 16118.394 | 15906.0939 | 98.6829 |  | #N/A
46 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | 2017-09-12 10:00 | 2017-09-12 18:41 |  |  |  | 0.36181 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP work of line & S/S equipment. | [8 empty] | 98.794
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.36181 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 23.462 | 16118.394 | 15924.0032 | 98.794 |  | #N/A
28 | NR240060 | 400KV HISAR-BHIWANI-I | 64.461 | NR1 | -- | 2017-09-18 15:29 | 2017-09-18 16:51 | -- | -- |  | 0 | 0.056944 | 0 | 0 | -- | -- | -- | OMSU | Trip on R-N fault, due to kite thread. HSR=63.5km, BWN=7.5km. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.056944 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 64.461 | 33197.415 | 33197.415 | 100 |  | #N/A
29 | NR240093 | 400KV HISAR-BHIWANI-II | 56.669 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 56.669 | 29184.535 | 29184.535 | 100 |  | #N/A
30 | NR240094 | 400KV HISAR-BHIWANI-III | 56.669 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 56.669 | 29184.535 | 29184.535 | 100 |  | #N/A
47 | NR240015 | 400KV HISAR-BHIWANI(BBMB) | 34.52 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 34.52 | 17777.8 | 17777.8 | 100 |  | #N/A
48 | NR240016 | 400KV HISAR-KAITHAL-I | 113.12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 605 | 113.12 | 68437.6 | 68437.6 | 100 |  | #N/A
49 | NR240044 | 400KV HISAR-KAITHAL-II | 113.12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 385 | 113.12 | 43551.2 | 43551.2 | 100 |  | #N/A
50 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | 2017-09-01 | 2017-10-01 |  |  |  | 0 | 0 | 0 | 1900-01-29 |  |  |  | OSFD | S/D by DTL for damaged tower rectification ( 1st Dead end tower from Bamnoli). Open since 2100hrs on 22.05.16 | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-29 | -- | -- | -- |  |  |  | 720 | 687 | 6.106 | 4194.822 | 4194.822 | 100 |  | #N/A
51 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.106 | 4194.822 | 4194.822 | 100 |  | #N/A
52 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.782 | 4659.234 | 4659.234 | 100 |  | #N/A
53 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | 2017-09-08 08:01 | 2017-09-08 20:36 |  |  |  | 0 | 0 | 0 | 0.52431 |  |  |  | OSFD | S/D by DTL for attending isolator problem at their end. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.52431 | -- | -- | -- |  |  |  | 720 | 687 | 6.782 | 4659.234 | 4659.234 | 100 |  | #N/A
54 | NR240102 | 400KV KABULPR-BAHADURGRH | 38.58 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 38.58 | 19868.7 | 19868.7 | 100 |  | #N/A
56 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 225 | 201.2 | 45270 | 45270 | 100 |  | #N/A
57 | NR140169 | 400KV KANKROLI-CHITTOR(RJ)-I | 71.03 | NR1 | -- | 2017-09-12 14:20 | 2017-09-12 19:56 |  |  |  | 0 | 0 | 0 | 0.23333 |  |  |  | OSFD | Line hand tripped due to heavy sparking observed in line isolator at Chittorgarh end. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.23333 | -- | -- | -- |  |  |  | 720 | 515 | 71.03 | 36580.45 | 36580.45 | 100 |  | #N/A
58 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 187.965 | 96801.975 | 96801.975 | 100 |  | #N/A
59 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- | 2017-09-13 16:24 | 2017-09-13 16:24 | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | LART | Line A/R on B-N fault. FLR-KNK-73.1 km, If-4.8 Kamp, RAPP-83.91 Km. NOT IN SAP. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 395 | 198.54 | 78423.3 | 78423.3 | 100 |  | #N/A
60 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | 2017-09-08 11:34 | 2017-09-08 17:08 |  |  |  | 0.23194 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend snapped B-Ph conductor jumpher at loc. No. 362 by Kank. | [8 empty] | 99.2269
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.23194 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 236 | 233.707 | 55154.852 | 54728.4233 | 99.2269 |  | #N/A
61 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 179.711 | 92551.165 | 92551.165 | 100 |  | #N/A
62 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 309 | 255.56 | 78968.04 | 78968.04 | 100 |  | #N/A
63 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 50.5 | 26007.5 | 26007.5 | 100 |  | #N/A
63 | NR140178 | 400KV KOTA-RAPPD | 55.103 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 55.103 | 28378.045 | 28378.045 | 100 |  | #N/A
64 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.7 | 1390.5 | 1390.5 | 100 |  | #N/A
65 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.7 | 1390.5 | 1390.5 | 100 |  | #N/A
66 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 633 | 14.463 | 9155.079 | 9155.079 | 100 |  | #N/A
67 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 633 | 16.49 | 10438.17 | 10438.17 | 100 |  | #N/A
68 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 133.5 | 68752.5 | 68752.5 | 100 |  | #N/A
69 | NR140165 | 400KV MEERUT-BAGPAT-I | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 70.976 | 36552.64 | 36552.64 | 100 |  | #N/A
70 | NR140166 | 400KV MEERUT-BAGPAT-II | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 70.976 | 36552.64 | 36552.64 | 100 |  | #N/A
71 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100 |  | #N/A
72 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100 |  | #N/A
73 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 678 | 178.69 | 121151.82 | 121151.82 | 100 |  | #N/A
74 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 673 | 175.63 | 118198.99 | 118198.99 | 100 |  | #N/A
75 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | 2017-09-11 12:16 | 2017-09-11 18:00 |  |  |  | 0.23889 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for replacement of Rph CT at MND due to oil leakage. | [8 empty] | 99.2037
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.23889 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 59.868 | 30832.02 | 30586.5058 | 99.2037 |  | #N/A
76 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | 2017-09-02 02:56 | 2017-09-04 08:23 |  |  |  | 0 | 0 | 0 | 1900-01-01 05:27 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MND-425KV | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 05:27 | 0 | 0 | 0 |  |  |  | 720 | 515 | 59.868 | 30832.02 | 30832.02 | 100 |  | #N/A
77 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | 2017-09-02 02:57 | 2017-09-04 08:25 |  |  |  | 0 | 0 | 0 | 1900-01-01 05:28 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MND-425KV | [8 empty] | 100
[6 empty] | 2017-09-14 01:19 | 2017-09-14 01:28 |  |  |  | 0 | 0.00625 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-N fault. FLR-MRT-69.92 km, If-6.5 Kamp. Fault is in Power Link portion, | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.00625 | 0 | 1900-01-01 05:28 | 0 | 0 | 0 |  |  |  | 720 | 515 | 54.298 | 27963.47 | 27963.47 | 100 |  | #N/A
78 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 54.298 | 27963.47 | 27963.47 | 100 |  | #N/A
79 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 37.38 | 19250.7 | 19250.7 | 100 |  | #N/A
80 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 76.018 | 39149.27 | 39149.27 | 100 |  | #N/A
81 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA | 30.15 | NR1 | -- | 2017-09-04 18:20 | 2017-09-05 10:06 | -- | -- | -- | 0 | 0 | 0 | 0.65694 | -- | -- | -- | LPRD | Line hand tripped for Power regulation. Agra-432KV. Line opened without intimating to CPCC so entered today . | [8 empty] | 100
[6 empty] | 2017-09-07 18:56 | 2017-09-08 10:42 |  |  |  | 0 | 0 | 0 | 0.65694 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-08 18:28 | 2017-09-09 10:19 |  |  |  | 0 | 0 | 0 | 0.66042 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-09 18:40 | 2017-09-11 07:21 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:41 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-11 18:40 | 2017-09-12 07:37 |  |  |  | 0 | 0 | 0 | 0.53958 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-12 19:14 | 2017-09-13 07:46 |  |  |  | 0 | 0 | 0 | 0.52222 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-13 19:14 | 2017-09-14 12:58 |  |  |  | 0 | 0 | 0 | 0.73889 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-14 18:50 | 2017-09-15 10:10 |  |  |  | 0 | 0 | 0 | 0.63889 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-15 18:32 | 2017-09-16 09:08 |  |  |  | 0 | 0 | 0 | 0.60833 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-16 18:37 | 2017-09-17 08:45 |  |  |  | 0 | 0 | 0 | 0.58889 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-18 18:58 | 2017-09-19 08:23 |  |  |  | 0 | 0 | 0 | 0.55903 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-19 18:40 | 2017-09-20 07:55 |  |  |  | 0 | 0 | 0 | 0.55208 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-20 18:27 | 2017-09-21 06:22 |  |  |  | 0 | 0 | 0 | 0.49653 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-21 19:08 | 2017-09-22 06:32 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-22 18:55 | 2017-09-23 18:23 |  |  |  | 0 | 0 | 0 | 0.97778 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-23 21:26 | 2017-09-24 09:34 |  |  |  | 0 | 0 | 0 | 0.50556 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-25 19:17 | 2017-09-27 07:05 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:48 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-27 18:57 | 2017-09-28 06:55 |  |  |  | 0 | 0 | 0 | 0.49861 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-28 19:01 | 2017-09-29 08:32 |  |  |  | 0 | 0 | 0 | 0.56319 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
[6 empty] | 2017-09-29 19:32 | 2017-09-30 08:50 |  |  |  | 0 | 0 | 0 | 0.55417 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-12 19:31 | -- | -- | -- |  |  |  | 720 | 691 | 30.15 | 20833.65 | 20833.65 | 100 |  | #N/A
82 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- | 2017-09-01 04:04 | 2017-09-01 09:53 | -- | -- | -- | 0 | 0 | 0 | 0.24236 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMR-426KV | [8 empty] | #N/A
[6 empty] | 2017-09-23 02:00 | 2017-09-25 11:09 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:09 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433KV | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 14:58 | -- | -- | -- |  |  |  | 720 | 515 | 67.041 | 34526.115 | 34526.115 | 100 |  | #N/A
83 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 67.041 | 34526.115 | 34526.115 | 100 |  | #N/A
84 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 175.859 | 90567.385 | 90567.385 | 100 |  | #N/A
85 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 175.859 | 90567.385 | 90567.385 | 100 |  | #N/A
86 | NR140170 | 400KV RAPPC-CHITTOR(RJ)-I | 155.15 | NR1 | -- | 2017-09-11 18:11 | 2017-09-12 12:34 |  |  |  | 0 | 0.76597 | 0 | 0 |  |  |  | OMSU | Trip on Y-N, RAPPC=127.3km. Line tripped due to LA problem (Damaged) at RAPP end. No fault found during complete tower top patroling of Line.S/D taken by RAPP due to Y-Phase LA found damaged at RAPP end. | [8 empty] | 100
[6 empty] | 2017-09-12 12:34 | 2017-09-12 16:35 |  |  |  | 0 | 0 | 0 | 0.16736 |  |  |  | OSFD | Line was taken in forced S/D by RAPPC due to their isolator problem and closed their isolator at 16:35 hrs. | [8 empty] | #N/A
[6 empty] | 2017-09-12 16:35 | 2017-09-13 20:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:25 |  |  |  | OSFD | S/D taken by RAPP due to Y-Phase LA found damaged at RAPP end. | [8 empty] | #N/A
[6 empty] | 2017-09-20 22:54 | 2017-09-21 06:15 |  |  |  | 0 | 0.30625 | 0 | 0 |  |  |  | OMSU | Line tripped due CT blast in 220 kV Chittorgarh-Debari Line(RRVPNL line) at chittorgarh end. DT received at RAPPC end. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 1899-12-31 01:44 | 0 | 1899-12-31 07:26 | 0 | 0 | 0 |  |  |  | 694.2667 | 515 | 155.15 | 79902.25 | 79902.25 | 100 |  | #N/A
90 | NR140175 | 400KV ROORKEE -DEHRADUN | 79.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 79.7 | 54753.9 | 54753.9 | 100 |  | #N/A
87 | NR140161 | 400KV ROORKI-KASHIPUR-I | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 150.832 | 103621.584 | 103621.584 | 100 |  | #N/A
88 | NR140162 | 400KV ROORKI-KASHIPUR-II | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 150.832 | 103621.584 | 103621.584 | 100 |  | #N/A
89 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | 2017-09-20 14:11 | 2017-09-20 15:39 |  |  |  | 0 | 0.061111 | 0 | 0 |  |  |  | OMSU | Tripped on B-N fault. FLR-RRK-8.799 km, If- 9.628 Kamp. Fault is in PITCUL portion. | [8 empty] | 100
[6 empty] | 2017-09-27 10:41 | 2017-09-27 10:41 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OMSU | A/R on B-N fault, FLR, Rrk-66.4km, fault in UPPCL portion | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.061111 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.1 | 1081.5 | 1081.5 | 100 |  | #N/A
91 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | 2017-09-02 13:27 | 2017-09-02 14:27 |  |  |  | 0 | 0.041667 | 0 | 0 |  |  |  | OMSU | A/R at Roorki & Trip from Rishikesh on R-N, Roorki=19.8km. Fault in PITCUL portion. | [8 empty] | 100
[6 empty] | 2017-09-10 13:25 | 2017-09-10 13:25 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on R-N fault.FLR-RRK-18.1km. Fault in PITCUL portion | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.041667 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.1 | 1081.5 | 1081.5 | 100 |  | #N/A
92 | NR140167 | 400KV ROORKI-SAHARANPUR-I | 36.535 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 36.535 | 25099.545 | 25099.545 | 100 |  | #N/A
94 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 |  | 2017-09-01 | 2017-09-01 09:47 |  |  |  | 0 | 0 | 0 | 0.40764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-424KV. Open since 31-08-2017 03:48. | [8 empty] | 100
[6 empty] | 2017-09-02 17:15 | 2017-09-03 22:28 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:13 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-424KV | [8 empty] | #N/A
[6 empty] | 2017-09-04 03:14 | 2017-09-04 07:36 |  |  |  | 0 | 0 | 0 | 0.18194 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-424KV | [8 empty] | #N/A
[6 empty] | 2017-09-04 16:11 | 2017-09-04 23:24 |  |  |  | 0 | 0 | 0 | 0.30069 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422KV | [8 empty] | #N/A
[6 empty] | 2017-09-05 16:59 | 2017-09-05 22:28 |  |  |  | 0 | 0 | 0 | 0.22847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-424KV | [8 empty] | #N/A
[6 empty] | 2017-09-06 04:06 | 2017-09-06 06:34 |  |  |  | 0 | 0 | 0 | 0.10278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-424KV | [8 empty] | #N/A
[6 empty] | 2017-09-07 04:06 | 2017-09-07 09:30 |  |  |  | 0 | 0 | 0 | 0.225 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-423KV | [8 empty] | #N/A
[6 empty] | 2017-09-07 16:35 | 2017-09-08 09:34 |  |  |  | 0 | 0 | 0 | 0.70764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-423KV | [8 empty] | #N/A
[6 empty] | 2017-09-08 16:16 | 2017-09-08 19:37 |  |  |  | 0 | 0 | 0 | 0.13958 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-423KV | [8 empty] | #N/A
[6 empty] | 2017-09-09 16:09 | 2017-09-13 07:01 |  |  |  | 0 | 0 | 0 | 1900-01-02 14:52 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-423KV | [8 empty] | #N/A
[6 empty] | 2017-09-15 02:46 | 2017-09-15 07:22 |  |  |  | 0 | 0 | 0 | 0.19167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422KV | [8 empty] | #N/A
[6 empty] | 2017-09-17 04:05 | 2017-09-18 09:58 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:53 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422KV | [8 empty] | #N/A
[6 empty] | 2017-09-19 04:10 | 2017-09-19 07:41 |  |  |  | 0 | 0 | 0 | 0.14653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422KV | [8 empty] | #N/A
[6 empty] | 2017-09-22 04:06 | 2017-09-22 06:44 |  |  |  | 0 | 0 | 0 | 0.10972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar--423KV | [8 empty] | #N/A
[6 empty] | 2017-09-23 04:10 | 2017-09-23 07:06 |  |  |  | 0 | 0 | 0 | 0.12222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=427kv. | [8 empty] | #N/A
[6 empty] | 2017-09-23 18:19 | 2017-09-25 11:07 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:48 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=427kv. | [8 empty] | #N/A
[6 empty] | 2017-09-25 16:18 | 2017-09-26 09:49 |  |  |  | 0 | 0 | 0 | 0.72986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=427kv. | [8 empty] | #N/A
[6 empty] | 2017-09-26 16:33 | 2017-09-27 15:17 |  |  |  | 0 | 0 | 0 | 0.94722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar=416kv. | [8 empty] | #N/A
[6 empty] | 2017-09-29 16:10 | 2017-09-30 06:44 |  |  |  | 0 | 0 | 0 | 0.60694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-425KV | [8 empty] | #N/A
[6 empty] | 2017-09-30 16:10 | 2017-09-30 22:38 |  |  |  | 0 | 0 | 0 | 0.26944 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-425KV | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-12 04:47 | -- | -- | -- |  |  |  | 720 | 515 | 76.48 | 39387.2 | 39387.2 | 100 |  | #N/A
95 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 76.48 | 39387.2 | 39387.2 | 100 |  | #N/A
#N/A
|  | 220KV LINES | [25 empty] | #N/A
1 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | 2017-09-27 18:09 | 2017-09-27 22:55 |  |  |  | 0 | 0 | 0 | 0.19861 |  |  |  | OSFD | S/D by NTPC for attending hot spot at Anta end | [8 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.19861 | -- | -- | -- |  |  |  | 720 | 132 | 186.667 | 24640.044 | 24640.044 | 100 |  | #N/A
2 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 186.667 | 24640.044 | 24640.044 | 100 |  | #N/A
3 | NR122046 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- | 2017-09-07 10:20 | 2017-09-07 13:20 | -- | -- | -- | 0 | 0 | 0 | 0.125 | -- | -- | -- | OSPD | S/D by RRVPNL for preventive maintenance work | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.125 | -- | -- | -- |  |  |  | 720 | 132 | 180.287 | 23797.884 | 23797.884 | 100 |  | #N/A
4 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 87.544 | 11468.264 | 11468.264 | 100 |  | #N/A
5 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 102.164 | 13485.648 | 13485.648 | 100 |  | #N/A
6 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | 2017-09-01 | 2017-09-03 08:36 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:36 |  |  |  | OSPD | S/D by RRVPNL for height raising of tower b/w loc- 02 to 05 due to ring road construction. S/D by 08.09.17 | [8 empty] | 100
[6 empty] | 2017-09-26 09:18 | 2017-09-26 12:26 |  |  |  | 0 | 0 | 0 | 0.13056 |  |  |  | OSPD | S/D by RRVPNL for maintenance work | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 11:44 | -- | -- | -- |  |  |  | 720 | 131 | 35.353 | 4631.243 | 4631.243 | 100 |  | #N/A
7 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | 2017-09-24 11:03 | 2017-09-24 14:00 |  |  |  | 0 | 0 | 0 | 0.12292 |  |  |  | OSPD | S/D by RRVPNL for quarterly maintenance work. | [8 empty] | 100
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.12292 | -- | -- | -- |  |  |  | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100 |  | #N/A
8 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | 2017-09-25 09:30 | 2017-09-25 15:22 |  |  |  | 0 | 0 | 0 | 0.24444 |  |  |  | OSPD | S/D by RRVPNL for quarterly maintenance work. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.24444 | -- | -- | -- |  |  |  | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100 |  | #N/A
9 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 22.478 | 2944.618 | 2944.618 | 100 |  | #N/A
10 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 15.69 | 2055.39 | 2055.39 | 100 |  | #N/A
11 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 15.69 | 2055.39 | 2055.39 | 100 |  | #N/A
12 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 17.691 | 2317.521 | 2317.521 | 100 |  | #N/A
13 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 17.691 | 2317.521 | 2317.521 | 100 |  | #N/A
14 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 24.875 | 3258.625 | 3258.625 | 100 |  | #N/A
15 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 12 | 1572 | 1572 | 100 |  | #N/A
16 | NR222004 | 220KV HISAR-HISAR I/A-I | 132 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 13.77 | 1817.64 | 1817.64 | 100 |  | #N/A
17 | NR222005 | 220KV HISAR-HISAR I/A-II | 132 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 13.77 | 1817.64 | 1817.64 | 100 |  | #N/A
18 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 28.02 | 3698.64 | 3698.64 | 100 |  | #N/A
19 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- | 2017-09-19 14:15 | 2017-09-19 17:35 | -- | -- | -- | 0 | 0 | 0 | 0.13889 | -- | -- | -- | OSFD | S/D by UPPCL for attending hot spot on R-ph isolator clamp at Mdprm end | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.13889 | -- | -- | -- |  |  |  | 720 | 132 | 2.316 | 305.712 | 305.712 | 100 |  | #N/A
20 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- | 2017-09-18 10:55 | 2017-09-18 13:54 | -- | -- | -- | 0 | 0 | 0 | 0.12431 | -- | -- | -- | OSPD | S/D by UPPCL to attend R ph CT clamp at M,purm end. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.12431 | -- | -- | -- |  |  |  | 720 | 132 | 9.254 | 1221.528 | 1221.528 | 100 |  | #N/A
21 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- | 2017-09-04 07:27 | 2017-09-04 07:27 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | OMSU | Line A/R successfully on B-N fault. FLR-MRT-26.3 km, Fault is in UPPCL portion. | [8 empty] | 100
[6 empty] | 2017-09-29 11:16 | 2017-09-29 11:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OMSU | Line A/R on B-N fault. FLR- MRT-17.7 km, if-8.4 kAmp. Fault is in UPPCL portion | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 2.316 | 305.712 | 305.712 | 100 |  | #N/A
22 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- | 2017-09-08 07:30 | 2017-09-08 07:30 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | OMSU | Line A/R on B-N faulr, FLR-Mrt-12.03Km, If-10.7KA., Fault in UPPCL portion. | [8 empty] | 100
[6 empty] | 2017-09-22 09:12 | 2017-09-22 11:00 |  |  |  | 0 | 0.075 | 0 | 0 |  |  |  | OMSU | A/R at MRT & Trip only from Stdngr (UPPCL) end on B-N fault, due to A/R relay problem at UPPCL end. FLR, MRT=7.9km. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.075 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 8.234 | 1086.888 | 1086.888 | 100 |  | #N/A
23 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- | 2017-09-05 18:57 | 2017-09-06 09:44 |  |  |  | 0 | 0.61597 | 0 | 0 |  |  |  | OMSU | Trip on Y-B fault due to conductor broken in UPPCL portion b/w loc-12-13,FLR, Mrt- 44.77 km. Iy-6.2 Kamp. Ib-3.55 Kamp | [8 empty] | 100
[6 empty] | 2017-09-06 09:44 | 2017-09-08 18:59 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:15 |  |  |  | OSFD | S/D by UPPCL for rectification of broken conductor b/w loc-12-13 | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.61597 | 0 | 1900-01-01 09:15 | -- | -- | -- |  |  |  | 720 | 132 | 9.254 | 1221.528 | 1221.528 | 100 |  | #N/A
24 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 128.833 | 16877.123 | 16877.123 | 100 |  | #N/A
25 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 128.833 | 16877.123 | 16877.123 | 100 |  | #N/A
26 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | 2017-09-06 11:03 | 2017-09-06 16:33 |  |  |  | 0 | 0 | 0 | 0.22917 |  |  |  | OSFD | S/D by RAPP for replacement of broken R-ph CT conductor at RAPPB end | [8 empty] | 100
[6 empty] | 2017-09-12 13:33 | 2017-09-12 14:25 |  |  |  | 0 | 0.036111 | 0 | 0 |  |  |  | OMSU | Tripped due to tripping of 220 kV Kota-RAPPC line (RRVPNL line). | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.036111 | 0 | 0.22917 | -- | -- | -- |  |  |  | 720 | 131 | 0.175 | 22.925 | 22.925 | 100 |  | #N/A
27 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 230.297 | 30168.907 | 30168.907 | 100 |  | #N/A
28 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | 2017-09-17 11:20 | 2017-09-17 12:57 |  |  |  | 0.067361 | 0 | 0 | 0 |  |  |  | OSFT | S/D by PG to attend demaged pilot string at loc no. 367. | [8 empty] | 99.7755
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.067361 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 106.243 | 14024.076 | 13992.5868 | 99.7755 |  | #N/A
29 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 2.83 | 373.56 | 373.56 | 100 |  | #N/A
30 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | 2017-09-08 11:22 | 2017-09-08 18:56 |  |  |  | 0 | 0 | 0 | 0.31528 |  |  |  | OSPD | S/D by RRVPNL for AMP . | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.31528 | -- | -- | -- |  |  |  | 720 | 132 | 2.83 | 373.56 | 373.56 | 100 |  | #N/A
31 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- | 2017-09-28 09:59 | 2017-09-28 17:05 | -- | -- |  | 0 | 0 | 0 | 0.29583 | -- | -- | -- | OSPD | S/D by RRVPNL for general maintenance work at their end. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.29583 | -- | -- | -- |  |  |  | 720 | 132 | 3 | 396 | 396 | 100 |  | #N/A
32 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 3 | 396 | 396 | 100 |  | #N/A
[5 empty] | -- | [17 empty] | 1637.99 |  |  |  |  | #N/A
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-09 22:54 | 1900-01-04 00:06 | 0 | 1900-09-14 10:44 | [9 empty] | 6810352.882 | 6796134.7004 | 99.7912 |  | #N/A
[21 empty] | %'(HVDC) | [6 empty] | #N/A
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor |  |  |  | #N/A
1 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100 |  | #N/A
2 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100 |  | #N/A
3 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100 |  | #N/A
4 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100 |  | #N/A
5 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100 |  | #N/A
6 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100 |  | #N/A
7 | NR2ICT46 | 765/400KV ICT-I BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1000 |  | 1000 | 1000 | 100 |  | #N/A
8 | NR2ICT48 | 765/400KV ICT-II BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1000 |  | 1000 | 1000 | 100 |  | #N/A
F |  | 400/220 KV ICT'S |  | NR1 | -- | [22 empty] | #N/A
1 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | 2017-09-12 09:42 | 2017-09-12 18:30 |  |  |  | 0.36667 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work . | [8 empty] | 98.7778
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.36667 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 311.15 | 98.7778 |  | #N/A
2 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | 2017-09-13 09:27 | 2017-09-13 16:01 |  |  |  | 0.27361 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work. | [8 empty] | 99.088
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.27361 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 312.1271 | 99.088 |  | #N/A
3 | NR1ICT68 | 500MVA ICT-III BASSI | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
4 | NR1ICT75 | 500MVA ICT-I BAGPAT | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
5 | NR1ICT78 | 500MVA ICT-II BAGPAT | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
6 | NR2ICT08 | 315MVA ICT-I BAHADURGARH | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
7 | NR2ICT42 | 500MVA ICT-II BAHADURGARH | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
8 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
9 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
10 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
11 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
12 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
13 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
14 | NR2ICT49 | 315MVA ICT-I BHIWANI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
15 | NR2ICT50 | 315MVA ICT-II BHIWANI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
16 | NR1ICT71 | 500MVA ICT-I BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
17 | NR1ICT79 | 500MVA ICT-II BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
18 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
18 | NR1ICT83 | 500MVA ICT-III BLBGARH | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
19 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
19 | NR1ICT84 | 500MVA ICT-IV BLBGARH | 500 | NR1 | -- | 2017-09-23 16:20 | 2017-09-23 17:38 | -- | -- | -- | 0.054167 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D to attend hotspot in Y-ph arm of 220kv isolator. | [8 empty] | 99.8194
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.054167 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 499.0972 | 99.8194 |  | #N/A
19 | NR1ICT81 | 315MVA ICT-I DEHRADUN | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
19 | NR1ICT82 | 315MVA ICT-II DEHRADUN | 315 | NR1 | -- | 2017-09-12 12:20 | 2017-09-12 13:22 | -- | -- | -- | 0 | 0.043056 | 0 | 0 | -- | -- | -- | SBBU | Tripped due to busbar operated. Bus bar operated due to tripping of 220KV DEHRADUN-JHAJRA-I& II (PICUL) lines. | [8 empty] | 100
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.043056 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
20 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | 2017-09-01 17:13 | 2017-09-01 17:56 |  |  |  | 0.029861 | 0 | 0 | 0 |  |  |  | OMST | Tripped only from 220KV side due to 220KV Busbar-II protection operated at GIS Gurgaon | [8 empty] | 98.0278
[6 empty] | 2017-09-16 09:30 | 2017-09-16 22:59 |  |  |  | 0.56181 | 0 | 0 | 0 |  |  |  | OSPT | S/D for carrying out AMP work. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.59167 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 308.7875 | 98.0278 |  | #N/A
21 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | 2017-09-01 17:13 | 2017-09-01 17:56 |  |  |  | 0.029861 | 0 | 0 | 0 |  |  |  | OMST | Tripped only from 220KV side due to 220KV Busbar-II protection operated at GIS Gurgaon | [8 empty] | 99.9005
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.029861 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 314.6865 | 99.9005 |  | #N/A
21 | NR1ICT85 | 500MVA ICT-III GURGAON | 315 | NR1 | -- | 2017-09-01 17:13 | 2017-09-03 18:48 |  |  |  | 1900-01-01 01:35 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to earth switch equipment damage at GIS Gurgaon .NOT IN SAP | [8 empty] | 93.1134
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-01 01:35 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 465.5671 | 93.1134 |  | #N/A
22 | NR2ICT09 | 315MVA ICT-I HISAR | 315 | NR1 | -- | 2017-09-29 10:45 | 2017-09-29 19:14 |  |  |  | 0.35347 | 0 | 0 | 0 |  |  |  | OSPT | S/D for carrying out AMP work. | [8 empty] | 98.8218
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.35347 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 311.2885 | 98.8218 |  | #N/A
23 | NR2ICT10 | 315MVA ICT-II HISAR | 315 | NR1 | -- | 2017-09-27 09:27 | 2017-09-27 19:30 |  |  |  | 0.41875 | 0 | 0 | 0 |  |  |  | OSPT | S/D for carrying out AMP work | [8 empty] | 98.6042
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.41875 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 310.6031 | 98.6042 |  | #N/A
24 | NR2ICT34 | 315MVA ICT-III HISAR | 315 | NR1 | -- | 2017-09-28 10:16 | 2017-09-28 17:55 |  |  |  | 0.31875 | 0 | 0 | 0 |  |  |  | OSPT | S/D for carrying out AMP work. | [8 empty] | 98.9375
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.31875 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 311.6531 | 98.9375 |  | #N/A
25 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
26 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
27 | NR2ICT53 | 315MVA ICT-I JIND | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
28 | NR2ICT54 | 315MVA ICT-II JIND | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
29 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
30 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
31 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
32 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
33 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
34 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
35 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
36 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
37 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | 2017-09-01 16:18 | 2017-10-01 |  |  |  | 1900-01-28 07:42 | 0 | 0 | 0 |  |  |  | SBBT | Tripped due to 400KV Busbar-I protection operated at M.bagh & flash over in ICT-II gas chamber. | [8 empty] | 2.2639
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-28 07:42 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 7.1313 | 2.2639 |  | #N/A
38 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | 2017-09-01 16:18 | 2017-09-01 20:50 |  |  |  | 0.18889 | 0 | 0 | 0 |  |  |  | SBBT | Tripped due to 400KV Busbar-I protection operated at M.bagh | [8 empty] | 99.3704
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.18889 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 496.8519 | 99.3704 |  | #N/A
39 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
40 | NR1ICT72 | 315MVA ICT-I MANDOLA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
41 | NR1ICT80 | 500MVA ICT-II MANDOLA | 315 | NR1 | -- | 2017-09-05 05:33 | 2017-09-05 12:58 |  |  |  | 0.30903 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D to attend red hot spot in 220 kv Side B-Ph LA terminal connector damaged strands rectification. | [8 empty] | 98.9699
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.30903 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 311.7552 | 98.9699 |  | #N/A
42 | NR1ICT73 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
43 | NR1ICT74 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
44 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
45 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | 2017-09-22 10:26 | 2017-09-29 19:17 |  |  |  | 0 | 0 | 0 | 1900-01-06 08:51 |  |  |  | SCSD | S/D for extension work & energisation of B/R-II at Manesar. | [8 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 08:51 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
46 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
47 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
48 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
49 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
50 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
51 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100 |  | #N/A
52 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
53 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
54 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
55 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
56 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
57 | NR1ICT76 | 315MVA ICT-I SAHARANPUR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
58 | NR1ICT77 | 315MVA ICT-II SAHARANPUR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
59 | NR2ICT36 | 315MVA ICT-I SONIPAT | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
60 | NR2ICT35 | 315MVA ICT-II SONIPAT | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100 |  | #N/A
| ICT | [22 empty] | 33990 | 33615.6985 | 98.8988 |  | #N/A
|  | SVC | [25 empty] | #N/A
60 | NR1SVC-01 | +400/-300MVAR SVC KANKROLI | 700 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 700 |  | 700 | 700 | 100 | % | #N/A
| SVC | TOTAL FOR SVC | [21 empty] | 700 | 700 | 100 | % | #N/A
#N/A
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF |  |  | #N/A
1 | NR1BRT57 | 125MVAR B/Reactor-I BAGPAT | 50 | NR1 | -- | 2017-09-10 19:17 | 2017-09-12 04:12 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:55 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[6 empty] | 2017-09-12 18:40 | 2017-09-13 04:12 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-20 15:23 | 2017-09-22 14:10 |  |  |  | 0 | 0 | 0 | 1899-12-31 22:47 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-02 17:14 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
2 | NR1BRT04 | 50MVAR B/Reactor-I BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
3 | NR1BRT53 | 50MVAR B/Reactor-II BASSI | 50 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
4 | NR1BRT54 | 50MVAR B/Reactor-III BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
5 | NR1BRT60 | 125MVAR B/Reactor-IV BASSI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
6 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
7 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
8 | NR2BRT27 | 240MVAR B/Reactor-I BHIWANI | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
9 | NR2BRT28 | 240MVAR B/Reactor-II BHIWANI | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
10 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- | 2017-09-15 14:32 | 2017-09-25 03:16 | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 12:44 | -- | -- | -- | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 12:44 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
11 | NR1BRT63 | 80MVAR B/Reactor-I DEHRADUN | 80 | NR1 | -- | 2017-09-11 14:22 | 2017-10-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-18 09:38 | -- | -- | -- | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-18 09:38 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
12 | NR2BRT03 | 50MVAR B/Reactor-I HISAR | 50 | NR1 | -- | 2017-09-01 | 2017-10-01 |  |  |  | 0 | 0 | 0 | 1900-01-29 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-29 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
12 | NR2BRT22 | 125MVAR B/Reactor-II HISAR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
13 | NR1BRT37 | 125MVAR B/Reactor-I JAIPUR(S) | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
14 | NR1BRT31 | 240MVAR B/Reactor-I JHATIKALA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
15 | NR1BRT52 | 240MVAR B/Reactor-II JHATIKALA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
16 | NR2BRT35 | 125MVAR Bus/eactor JIND | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
17 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
18 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
19 | NR1BRT09 | 80MVAR B/Reactor-II KOTA | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
20 | NR1BRT55 | 50MVAR B/Reactor KOTA | 50 | NR1 | -- | [15 empty] | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
21 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
21 | NR1BRT64 | 125MVAR B/Reactor Koteshwr HEP | 125 | NR1 | -- | 2017-09-01 | 2017-09-01 11:39 |  |  |  | 0 | 0 | 0 | 0.48542 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[6 empty] | 2017-09-02 20:00 | 2017-09-04 03:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:00 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-04 19:00 | 2017-09-05 05:11 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | SVRD | Hand tripped for voltage regulation<390kv. | [8 empty] | #N/A
[6 empty] | 2017-09-04 22:00 | 2017-09-05 05:11 |  |  |  | 0 | 0 | 0 | 0.29931 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-05 19:47 | 2017-09-23 02:42 |  |  |  | 0 | 0 | 0 | 1900-01-16 06:55 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-18 18:56 | -- | -- | -- |  |  |  | 216 | 125 |  | 125 | 125 | 100 |  | #N/A
22 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
23 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | 2016-05-20 07:36 | [12 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 2016-05-28 18:19 | 0 | 0 |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
24 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | 2017-09-15 14:56 | 2017-09-17 09:34 |  |  |  | 0 | 0 | 0 | 1899-12-31 18:38 |  |  |  | SVRD | Hand tripped for voltage regulation<720kv. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 18:38 | 2016-05-28 18:19 | 0 | 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
25 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
26 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
27 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI(JPR)-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
28 | NR1BRT48 | 125MVAR B/Reactor-I RATANGARH(RJ) | 125 | NR1 | -- | [15 empty] | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
29 | NR1BRT40 | 125MVAR B/Reactor ROORKI | 125 | NR1 | -- | 2017-09-01 | 2017-09-01 04:08 | -- | -- | -- | 0 | 0 | 0 | 0.17222 | -- | -- | -- | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.17222 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
30 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100 |  | #N/A
31 | NR2BRT13 | 125MVAR B/Reactor-I SONIPAT | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100 |  | #N/A
40 | NR1BRT58 | 50MVAR B/Reactor-I SAHARANPUR | 50 | NR1 | -- | 2017-09-02 19:25 | 2017-09-03 06:14 |  |  |  | 0 | 0 | 0 | 0.45069 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[6 empty] | 2017-09-05 19:42 | 2017-09-07 01:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:32 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-07 18:18 | 2017-09-08 05:33 |  |  |  | 0 | 0 | 0 | 0.46875 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-08 11:59 | 2017-09-12 06:21 |  |  |  | 0 | 0 | 0 | 1900-01-02 18:22 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-12 11:07 | 2017-09-22 13:24 |  |  |  | 0 | 0 | 0 | 1900-01-09 02:17 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-25 12:15 | 2017-09-26 05:59 |  |  |  | 0 | 0 | 0 | 0.73889 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-26 11:19 | 2017-10-01 |  |  |  | 0 | 0 | 0 | 1900-01-03 12:41 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-20 06:40 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
41 | NR1BRT59 | 50MVAR B/Reactor-II SAHARANPUR | 50 | NR1 | -- | 2017-09-02 19:25 | 2017-09-03 06:14 |  |  |  | 0 | 0 | 0 | 0.45069 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | 100
[6 empty] | 2017-09-05 19:42 | 2017-09-07 01:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:32 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-07 18:18 | 2017-09-08 05:33 |  |  |  | 0 | 0 | 0 | 0.46875 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-08 11:59 | 2017-09-12 06:21 |  |  |  | 0 | 0 | 0 | 1900-01-02 18:22 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-12 11:07 | 2017-09-22 13:24 |  |  |  | 0 | 0 | 0 | 1900-01-09 02:17 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-25 12:15 | 2017-09-26 05:59 |  |  |  | 0 | 0 | 0 | 0.73889 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
[6 empty] | 2017-09-26 11:19 | 2017-10-01 |  |  |  | 0 | 0 | 0 | 1900-01-03 12:41 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. | [8 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-20 06:40 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
32 | NR2BRT29 | BHIWANI 240MVAR S/R MEERUT line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
33 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
34 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
35 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh-I LINE | 50 | NR1 | -- | 2017-09-14 14:47 | 2017-09-17 04:24 |  |  |  | 0 | 0 | 0 | 1900-01-01 13:37 |  |  |  | SVRD | Hand tripped for voltage regulation<395kv. Not in SAP | [8 empty] | 100
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 13:37 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
36 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
37 | NR1SRT21 | MEERUT 240MVAR S/R G.NOIDA line | 240 | NR1 | -- | 2017-09-28 09:54 | 2017-09-28 17:42 |  |  |  | 0.325 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP | [8 empty] | 98.9167
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.325 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 240 |  | 240 | 237.4 | 98.9167 |  | #N/A
38 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
39 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100 |  | #N/A
42 | NR1SRT27 | PHAGI(JPR)240MVAR S/R BHIWANI-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
43 | NR1SRT28 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #N/A
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100 |  | #N/A
#N/A
| REACTORS | TOTAL FOR BUS REACTORS | [8 empty] | 0.65 | 0 | 0 | 1900-09-07 14:02 | [9 empty] | 5330 | 5327.4 | 99.9512 | % | #N/A
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L15:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M15:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N15:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O15:[Deemed Available, row above])
Note on C15: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C383: DOC-11-02-15
Note on C439: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14

## AVBT_Septmber-17 (hidden)
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.09.2017 to 30.09.2017
DURATION OF OUTAGE ATTRIBUTABLE TO
SL.NO. | ELEMENT | Element Name |  |  | Outage Not To Consider |  | Total Duration |  |  |  |  | Percentage
| ID |  | POWERGRID | OTHERS | System Constrnt/ | Deemed | Available for |  |  | Weightage |  | Availability
[5 empty] | Natural Calamity/ | Available | Consideration | SIL | Ckt. Kms. | Factor | H=(G*(Z-@))/Z | I=(H/G)*100
[5 empty] | Militancy |  | (Z) | ( E) | ( F) | G=E x F
|  |  | @ (T) | # (U) | & (C ) | " (D) |  | E | F | G | H | I
|  |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs
A |  | 765 KV TRANS LINES | [10 empty] | 0
1 | NR176504 | 765KV AGRA-JHATIKALA | #N/A | #N/A | #N/A | #N/A | #N/A | 1747 | 253.076 | 442123.772 | #N/A | #N/A | 720
2 | NR176509 | 765KV BHIWANI-PHAGI(JPR)-I | #N/A | #N/A | #N/A | #N/A | #N/A | 1155 | 271.571 | 313664.505 | #N/A | #N/A
3 | NR176515 | 765KV BHIWANI-PHAGI(JPR)-II | #N/A | #N/A | #N/A | #N/A | #N/A | 1155 | 279.583 | 322918.365 | #N/A | #N/A
4 | NR276502 | 765KV JHATIKALA-BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 2250 | 85.188 | 191673 | #N/A | #N/A
5 | NR276503 | 765KV MEERUT-BHIWANI | 0 | 0 | 0 | 0.78264 | 720 | 1466 | 173 | 253618 | 253618 | 100
6 | NR176511 | 765KV MEERUT-GR.NOIDA | #N/A | #N/A | #N/A | #N/A | #N/A | 1002 | 119.159 | 119397.318 | #N/A | #N/A
7 | NR276501 | 765KV MOGA-BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 1791 | 273 | 488943 | #N/A | #N/A
B |  | 400 KV TRANS LINES
1 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 0 | 0 | 0 | 1900-01-09 16:39 | 720 | 307 | 253.823 | 77923.661 | 77923.661 | 100
2 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 0 | 0 | 0 | 1900-01-06 11:05 | 720 | 307 | 253.823 | 77923.661 | 77923.661 | 100
3 | NR140144 | 400KV AGRA-SIKAR-I | 0.55694 | 0 | 0 | 1900-01-10 13:37 | 720 | 568 | 393.9 | 223735.2 | 219581.5974 | 98.1435
4 | NR140145 | 400KV AGRA-SIKAR-II | 0.33958 | 0 | 0 | 1900-01-09 03:37 | 720 | 568 | 393.9 | 223735.2 | 221202.6418 | 98.8681
5 | NR140174 | 400KV BAGPAT-DEHRADUN | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 165 | 113355 | #N/A | #N/A
6 | NR140173 | 400KV BAGPAT-SAHARANPUR | 0 | 0.015972 | 0 | 0 | 719.6167 | 687 | 121 | 83127 | 83127 | 100
7 | NR240006 | 400KV BAHADURGRH-BAWANA | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 48.981 | 25225.215 | #N/A | #N/A
8 | NR240102 | 400KV BAHADURGRH-KABULPR | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 38.58 | 19868.7 | #N/A | #N/A
9 | NR240038 | 400KV BAHADURGRH-SONIPAT-I | #N/A | #N/A | #N/A | #N/A | #N/A | 605 | 53.4 | 32307 | #N/A | #N/A
10 | NR240039 | 400KV BAHADURGRH-SONIPAT-II | #N/A | #N/A | #N/A | #N/A | #N/A | 605 | 53.4 | 32307 | #N/A | #N/A
11 | NR140028 | 400KV BASSI-BHIWADI-I | #N/A | #N/A | #N/A | #N/A | #N/A | 416 | 235 | 97760 | #N/A | #N/A
12 | NR140030 | 400KV BASSI-HIRAPURA-I | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 47.762 | 24597.43 | #N/A | #N/A
13 | NR140031 | 400KV BASSI-HIRAPURA-II | 0 | 0.16042 | 0 | 0 | 716.15 | 515 | 48.99 | 25229.85 | 25229.85 | 100
14 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 0.41597 | 0 | 0 | 0 | 720 | 515 | 37.164 | 19139.46 | 18874.0772 | 98.6134
15 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 0.37153 | 0 | 0 | 0 | 720 | 515 | 37.164 | 19139.46 | 18902.432 | 98.7616
16 | NR140148 | 400KV BASSI-KOTPUTLI | 0.41875 | 0 | 0 | 0 | 720 | 247 | 106.153 | 26219.791 | 25853.8064 | 98.6042
17 | NR140146 | 400KV BASSI-PHAGI-I | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 48.432 | 33272.784 | #N/A | #N/A
18 | NR140147 | 400KV BASSI-PHAGI-II | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 48.432 | 33272.784 | #N/A | #N/A
19 | NR140171 | 400KV BASSI-SIKAR-I | 0.47569 | 0 | 0 | 0 | 720 | 515 | 169.8 | 87447 | 86060.3983 | 98.4144
20 | NR140172 | 400KV BASSI-SIKAR-II | 0.42708 | 0.19792 | 0 | 0 | 715.25 | 515 | 169.8 | 87447 | 86193.8273 | 98.5669
21 | N-W40004 | 400KV BHINMAL-ZERDA | #N/A | #N/A | #N/A | #N/A | #N/A | 272 | 142.8 | 38841.6 | #N/A | #N/A
22 | NR140032 | 400KV BHIWADI-GURGAON | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 82.8 | 42642 | #N/A | #N/A
23 | NR140033 | 400KV BHIWADI-HISAR-I | 0.94236 | 0 | 0 | 1900-01-02 10:32 | 720 | 403 | 211.547 | 85253.441 | 82575.4568 | 96.8588
24 | NR240087 | 400KV BHIWADI-HISAR-II | 0 | 0 | 0 | 1900-01-03 04:52 | 720 | 331 | 144 | 47664 | 47664 | 100
25 | NR240088 | 400KV BHIWADI-HISAR-III | 0 | 0 | 0 | 0.19722 | 720 | 331 | 144 | 47664 | 47664 | 100
26 | NR140149 | 400KV BHIWADI-KOTPUTLI | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 132.428 | 68200.42 | #N/A | #N/A
27 | NR140106 | 400KV BHIWADI-NIMRANA-I | 0 | 0 | 0 | 1900-01-03 01:07 | 720 | 515 | 48.428 | 24940.42 | 24940.42 | 100
28 | NR140107 | 400KV BHIWADI-NIMRANA-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 48.428 | 24940.42 | #N/A | #N/A
29 | NR240061 | 400KV BHIWANI-BAWANA | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 97.415 | 50168.725 | #N/A | #N/A
30 | NR240059 | 400KV BHIWANI-BHIWANI(BBMB) | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 33.962 | 17490.43 | #N/A | #N/A
31 | NR240068 | 400KV BHIWANI-JIND-I | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 82.23 | 42348.45 | #N/A | #N/A
32 | NR240069 | 400KV BHIWANI-JIND-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 82.23 | 42348.45 | #N/A | #N/A
33 | NR240103 | 400KV BHIWANI-KABULPR | 0 | 0 | 0 | 0.17639 | 720 | 515 | 26.64 | 13719.6 | 13719.6 | 100
34 | NR140035 | 400KV BLBGRH-GURGAON | 0.125 | 0 | 0 | 0 | 720 | 515 | 42.7 | 21990.5 | 21898.8729 | 99.5833
35 | NR140036 | 400KV BLBGRH-MAHRANIBG | 0.10903 | 0.068056 | 0 | 0 | 718.3667 | 691 | 60.68 | 41929.88 | 41777.1495 | 99.6357
36 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) | 0 | 0 | 0 | 0.23125 | 720 | 691 | 12.55 | 8672.05 | 8672.05 | 100
37 | NR140039 | 400KV DAD-GR.NOIDA | #N/A | #N/A | #N/A | #N/A | #N/A | 691 | 13.256 | 9159.896 | #N/A | #N/A
38 | NR140040 | 400KV DAD-MAHRANIBG | #N/A | #N/A | #N/A | #N/A | #N/A | 691 | 54.36 | 37562.76 | #N/A | #N/A
39 | NR140041 | 400KV DAD-MANDOLA-I | #N/A | #N/A | #N/A | #N/A | #N/A | 691 | 46.3 | 31993.3 | #N/A | #N/A
40 | NR140042 | 400KV DAD-MANDOLA-II | #N/A | #N/A | #N/A | #N/A | #N/A | 691 | 46.3 | 31993.3 | #N/A | #N/A
41 | NR140043 | 400KV DAD-MURADNGR | 0 | 0.094444 | 0 | 0 | 717.7333 | 515 | 33.098 | 17045.47 | 17045.47 | 100
42 | NR140044 | 400KV DAD-PANIPAT-I | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 112.322 | 57845.83 | #N/A | #N/A
43 | NR140045 | 400KV DAD-PANIPAT-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 117 | 60255 | #N/A | #N/A
44 | NR240026 | 400KV FATEHABAD-HISAR | 0 | 0 | 0 | 1900-01-01 15:57 | 720 | 515 | 88.558 | 45607.37 | 45607.37 | 100
45 | NR140128 | 400KV GURGAON-MANESAR-I | 0.39514 | 0 | 0 | 0.78264 | 720 | 687 | 23.462 | 16118.394 | 15906.0939 | 98.6829
46 | NR140129 | 400KV GURGAON-MANESAR-II | 0.36181 | 0 | 0 | 0 | 720 | 687 | 23.462 | 16118.394 | 15924.0032 | 98.794
47 | NR240015 | 400KV HISAR-BHIWANI(BBMB) | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 34.52 | 17777.8 | #N/A | #N/A
48 | NR240060 | 400KV HISAR-BHIWANI-I | 0 | 0.056944 | 0 | 0 | 718.6333 | 515 | 64.461 | 33197.415 | 33197.415 | 100
49 | NR240093 | 400KV HISAR-BHIWANI-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 56.669 | 29184.535 | #N/A | #N/A
50 | NR240094 | 400KV HISAR-BHIWANI-III | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 56.669 | 29184.535 | #N/A | #N/A
51 | NR240016 | 400KV HISAR-KAITHAL-I | #N/A | #N/A | #N/A | #N/A | #N/A | 605 | 113.12 | 68437.6 | #N/A | #N/A
52 | NR240044 | 400KV HISAR-KAITHAL-II | #N/A | #N/A | #N/A | #N/A | #N/A | 385 | 113.12 | 43551.2 | #N/A | #N/A
53 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 0 | 0 | 0 | 1900-01-29 | 720 | 687 | 6.106 | 4194.822 | 4194.822 | 100
54 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 6.106 | 4194.822 | #N/A | #N/A
55 | NR140134 | 400KV JHATIKALA-MUNDKA-I | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 6.782 | 4659.234 | #N/A | #N/A
56 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 0 | 0 | 0 | 0.52431 | 720 | 687 | 6.782 | 4659.234 | 4659.234 | 100
57 | NR140048 | 400KV KANKROLI-BHINMAL | #N/A | #N/A | #N/A | #N/A | #N/A | 225 | 201.2 | 45270 | #N/A | #N/A
58 | NR140169 | 400KV KANKROLI-CHITTOR(RJ)-I | 0 | 0 | 0 | 0.23333 | 720 | 515 | 71.03 | 36580.45 | 36580.45 | 100
59 | NR140049 | 400KV KANKROLI-JODHPUR | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 187.965 | 96801.975 | #N/A | #N/A
60 | NR140051 | 400KV KANKROLI-RAPPC-II | 0 | 0 | 0 | 0 | 720 | 395 | 198.54 | 78423.3 | 78423.3 | 100
61 | N-W40003 | 400KV KANKROLI-ZERDA-I | 0.23194 | 0 | 0 | 0 | 720 | 236 | 233.707 | 55154.852 | 54728.4233 | 99.2269
62 | NR140102 | 400KV KOTA-BEAWAR | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 179.711 | 92551.165 | #N/A | #N/A
63 | NR140060 | 400KV KOTA-MERTA-I | #N/A | #N/A | #N/A | #N/A | #N/A | 309 | 255.56 | 78968.04 | #N/A | #N/A
64 | NR140062 | 400KV KOTA-RAPPC | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 50.5 | 26007.5 | #N/A | #N/A
65 | NR140178 | 400KV KOTA-RAPPD | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 55.103 | 28378.045 | #N/A | #N/A
66 | NR140063 | 400KV KOTESHWR-KHEP-I | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 2.7 | 1390.5 | #N/A | #N/A
67 | NR140064 | 400KV KOTESHWR-KHEP-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 2.7 | 1390.5 | #N/A | #N/A
68 | NR140065 | 400KV KOTESHWR-TEHRI-I | #N/A | #N/A | #N/A | #N/A | #N/A | 633 | 14.463 | 9155.079 | #N/A | #N/A
69 | NR140098 | 400KV KOTESHWR-TEHRI-II | #N/A | #N/A | #N/A | #N/A | #N/A | 633 | 16.49 | 10438.17 | #N/A | #N/A
70 | NR140076 | 400KV MBAD-MURADNGR
71 | NR140165 | 400KV MEERUT-BAGPAT-I | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 70.976 | 36552.64 | #N/A | #N/A
72 | NR140166 | 400KV MEERUT-BAGPAT-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 70.976 | 36552.64 | #N/A | #N/A
73 | NR140142 | 400KV MEERUT-BAREILLY-I | #N/A | #N/A | #N/A | #N/A | #N/A | 616 | 66.009 | 40661.544 | #N/A | #N/A
74 | NR140130 | 400KV MEERUT-BAREILLY-II | #N/A | #N/A | #N/A | #N/A | #N/A | 616 | 66.009 | 40661.544 | #N/A | #N/A
75 | NR140077 | 400KV MEERUT-KOTESHWR-I | #N/A | #N/A | #N/A | #N/A | #N/A | 678 | 178.69 | 121151.82 | #N/A | #N/A
76 | NR140099 | 400KV MEERUT-KOTESHWR-II | #N/A | #N/A | #N/A | #N/A | #N/A | 673 | 175.63 | 118198.99 | #N/A | #N/A
77 | NR140078 | 400KV MEERUT-MND-I | 0.23889 | 0 | 0 | 0 | 720 | 515 | 59.868 | 30832.02 | 30586.5058 | 99.2037
78 | NR140079 | 400KV MEERUT-MND-II | 0 | 0 | 0 | 1900-01-01 05:27 | 720 | 515 | 59.868 | 30832.02 | 30832.02 | 100
79 | NR140143 | 400KV MEERUT-MND-III | 0 | 0.00625 | 0 | 1900-01-01 05:28 | 719.85 | 515 | 54.298 | 27963.47 | 27963.47 | 100
80 | NR140131 | 400KV MEERUT-MND-IV | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 54.298 | 27963.47 | #N/A | #N/A
81 | NR140080 | 400KV MEERUT-MUZFRNGR | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 37.38 | 19250.7 | #N/A | #N/A
82 | NR140103 | 400KV MERTA-BEAWAR | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 76.018 | 39149.27 | #N/A | #N/A
83 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA | 0 | 0 | 0 | 1900-01-12 19:31 | 720 | 691 | 30.15 | 20833.65 | 20833.65 | 100
84 | NR140118 | 400KV NIMRANA-MANESAR-I | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 67.041 | 34526.115 | #N/A | #N/A
85 | NR140119 | 400KV NIMRANA-MANESAR-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 67.041 | 34526.115 | #N/A | #N/A
86 | NR140108 | 400KV NIMRANA-SIKAR-I | 0 | 0 | 0 | 1900-01-01 14:58 | 720 | 515 | 175.859 | 90567.385 | 90567.385 | 100
87 | NR140109 | 400KV NIMRANA-SIKAR-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 175.859 | 90567.385 | #N/A | #N/A
88 | NR140170 | 400KV RAPPC-CHITTOR(RJ)-I | 0 | 1899-12-31 01:44 | 0 | 1899-12-31 07:26 | 694.2667 | 515 | 155.15 | 79902.25 | 79902.25 | 100
89 | NR140175 | 400KV ROORKI-DEHRADUN | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 79.7 | 54753.9 | #N/A | #N/A
90 | NR140161 | 400KV ROORKI-KASHIPUR-I | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 150.832 | 103621.584 | #N/A | #N/A
91 | NR140162 | 400KV ROORKI-KASHIPUR-II | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 150.832 | 103621.584 | #N/A | #N/A
92 | NR140086 | 400KV ROORKI-MUZFRNGR | 0 | 0.061111 | 0 | 0 | 718.5333 | 515 | 2.1 | 1081.5 | 1081.5 | 100
93 | NR140087 | 400KV ROORKI-RISHIKESH | 0 | 0.041667 | 0 | 0 | 719 | 515 | 2.1 | 1081.5 | 1081.5 | 100
94 | NR140167 | 400KV ROORKI-SAHARANPUR-I | #N/A | #N/A | #N/A | #N/A | #N/A | 687 | 36.535 | 25099.545 | #N/A | #N/A
95 | NR140155 | 400KV SIKAR-RATANGARH-I | 0 | 0 | 0 | 1900-01-12 04:47 | 720 | 515 | 76.48 | 39387.2 | 39387.2 | 100
96 | NR140156 | 400KV SIKAR-RATANGARH-II | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 76.48 | 39387.2 | #N/A | #N/A
70* | NR140176 | 400KV MORADABD-HAPUR(UP) | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 106.85 | 55027.75 | #N/A | #N/A
97 | NR140177 | 400KV MURADNGR-HAPUR(UP) | #N/A | #N/A | #N/A | #N/A | #N/A | 515 | 26.65 | 13724.75 | #N/A | #N/A
10413.72
C |  | 220 KV TRANS LINES
1 | NR122001 | 220KV ANTA-BHIL-I | #N/A | #N/A | #N/A | #N/A | #N/A | 132 | 186.667 | 24640.044 | #N/A | #N/A
2 | NR122002 | 220KV ANTA-BHIL-II | 0 | 0 | 0 | 0.19861 | 720 | 132 | 186.667 | 24640.044 | 24640.044 | 100
3 | NR122046 | 220KV ANTA-LALSOT | 0 | 0 | 0 | 0.125 | 720 | 132 | 180.287 | 23797.884 | 23797.884 | 100
4 | NR122004 | 220KV ANTA-RAPPC | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 87.544 | 11468.264 | #N/A | #N/A
5 | NR122005 | 220KV ANTA-S.MDHPR | #N/A | #N/A | #N/A | #N/A | #N/A | 132 | 102.164 | 13485.648 | #N/A | #N/A
6 | NR122008 | 220KV BASSI-BAGRU | 0 | 0 | 0 | 1900-01-01 11:44 | 720 | 131 | 35.353 | 4631.243 | 4631.243 | 100
7 | NR122009 | 220KV BASSI-DAUSA-I | 0 | 0 | 0 | 0.12292 | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100
8 | NR122010 | 220KV BASSI-DAUSA-II | 0 | 0 | 0 | 0.24444 | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100
9 | NR122011 | 220KV BASSI-IG NAGAR | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 22.478 | 2944.618 | #N/A | #N/A
10 | BILHY2201 | 220KV FGPP-PALLA-I | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 15.69 | 2055.39 | #N/A | #N/A
11 | BILHY2202 | 220KV FGPP-PALLA-II | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 15.69 | 2055.39 | #N/A | #N/A
12 | BILHY2203 | 220KV FGPP-SPUR-I | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 17.691 | 2317.521 | #N/A | #N/A
13 | BILHY2204 | 220KV FGPP-SPUR-II | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 17.691 | 2317.521 | #N/A | #N/A
14 | NR122014 | 220KV HIRAPURA-IG NAGAR | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 24.875 | 3258.625 | #N/A | #N/A
15 | NR122015 | 220KV HIRAPURA-SANGANER | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 12 | 1572 | #N/A | #N/A
16 | NR222004 | 220KV HISAR-HISAR I/A-I | #N/A | #N/A | #N/A | #N/A | #N/A | 132 | 13.77 | 1817.64 | #N/A | #N/A
17 | NR222005 | 220KV HISAR-HISAR I/A-II | #N/A | #N/A | #N/A | #N/A | #N/A | 132 | 13.77 | 1817.64 | #N/A | #N/A
18 | NR122047 | 220KV LALSOT-DAUSA | #N/A | #N/A | #N/A | #N/A | #N/A | 132 | 28.02 | 3698.64 | #N/A | #N/A
19 | BILUP2204 | 220KV MEERUT-MPURAM-I | 0 | 0 | 0 | 0.13889 | 720 | 132 | 2.316 | 305.712 | 305.712 | 100
20 | BILUP2205 | 220KV MEERUT-MPURAM-II | 0 | 0 | 0 | 0.12431 | 720 | 132 | 9.254 | 1221.528 | 1221.528 | 100
21 | BILUP2206 | 220KV MEERUT-NARA | 0 | 0 | 0 | 0 | 720 | 132 | 2.316 | 305.712 | 305.712 | 100
22 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 0 | 0.075 | 0 | 0 | 718.2 | 132 | 8.234 | 1086.888 | 1086.888 | 100
23 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 0 | 0.61597 | 0 | 1900-01-01 09:15 | 705.2167 | 132 | 9.254 | 1221.528 | 1221.528 | 100
24 | NR122027 | 220KV RAPPB-CHITT-I | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 128.833 | 16877.123 | #N/A | #N/A
25 | NR122028 | 220KV RAPPB-CHITT-II | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 128.833 | 16877.123 | #N/A | #N/A
26 | NR122029 | 220KV RAPPB-RAPPC | 0 | 0.036111 | 0 | 0.22917 | 719.1333 | 131 | 0.175 | 22.925 | 22.925 | 100
27 | NR122030 | 220KV RAPPB-UDAIPUR | #N/A | #N/A | #N/A | #N/A | #N/A | 131 | 230.297 | 30168.907 | #N/A | #N/A
28 | NR122031 | 220KV S.MDHPR-DAUSA-I | 0.067361 | 0 | 0 | 0 | 720 | 132 | 106.243 | 14024.076 | 13992.5868 | 99.7755
29 | NR122042 | 220KV SIKAR-RATANGARH-I | #N/A | #N/A | #N/A | #N/A | #N/A | 132 | 2.83 | 373.56 | #N/A | #N/A
30 | NR122044 | 220KV SIKAR-RATANGARH-II | 0 | 0 | 0 | 0.31528 | 720 | 132 | 2.83 | 373.56 | 373.56 | 100
31 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 0 | 0 | 0 | 0.29583 | 720 | 132 | 3 | 396 | 396 | 100
32 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | #N/A | #N/A | #N/A | #N/A | #N/A | 132 | 3 | 396 | #N/A | #N/A
1637.99
136 | Lines | TOTAL FOR T/LS | #N/A | #N/A | #N/A | #N/A |  |  | 12051.71 | 6810352.882 | #N/A | #N/A | %
|  | OVERALL SYSTEM AVAILABILITY= |  | #N/A | % (AC)
D |  | 765/400 KV ICT'S | [5 empty] | MVA |  | Weitage Factor
1 | NR2ICT46 | 765/400KV ICT-I BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 1000 |  | 1000 | #N/A | #N/A
2 | NR2ICT48 | 765/400KV ICT-II BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 1000 |  | 1000 | #N/A | #N/A
3 | NR1ICT709 | 765/400KV ICT-I JHATIKALA | #N/A | #N/A | #N/A | #N/A | #N/A | 1500 |  | 1500 | #N/A | #N/A
4 | NR1ICT710 | 765/400KV ICT-II JHATIKALA | #N/A | #N/A | #N/A | #N/A | #N/A | 1500 |  | 1500 | #N/A | #N/A
5 | NR1ICT711 | 765/400KV ICT-III JHATIKALA | #N/A | #N/A | #N/A | #N/A | #N/A | 1500 |  | 1500 | #N/A | #N/A
6 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | #N/A | #N/A | #N/A | #N/A | #N/A | 1500 |  | 1500 | #N/A | #N/A
7 | NR1ICT713 | 765/400KV ICT-I MEERUT | #N/A | #N/A | #N/A | #N/A | #N/A | 1500 |  | 1500 | #N/A | #N/A
8 | NR1ICT714 | 765/400KV ICT-II MEERUT | #N/A | #N/A | #N/A | #N/A | #N/A | 1500 |  | 1500 | #N/A | #N/A
E |  | 400/220 KV ICT'S
1 | NR1ICT75 | 500MVA ICT-I BAGPAT | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
2 | NR1ICT78 | 500MVA ICT-II BAGPAT | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
3 | NR2ICT08 | 315MVA ICT-I BAHADURGARH | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
4 | NR2ICT42 | 500MVA ICT-II BAHADURGARH | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
5 | NR1ICT03 | 315MVA ICT-I BASSI | 0.36667 | 0 | 0 | 0 | 720 | 315 |  | 315 | 311.15 | 98.7778
6 | NR1ICT04 | 315MVA ICT-II BASSI | 0.27361 | 0 | 0 | 0 | 720 | 315 |  | 315 | 312.1271 | 99.088
7 | NR1ICT68 | 500MVA ICT-III BASSI | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
8 | NR1ICT05 | 315MVA ICT-III BAWANA | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
9 | NR1ICT06 | 315MVA ICT-I BHINMAL | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
10 | NR1ICT07 | 315MVA ICT-II BHINMAL | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
11 | NR1ICT08 | 315MVA ICT-I BHIWADI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
12 | NR1ICT09 | 315MVA ICT-II BHIWADI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
13 | NR1ICT54 | 315MVA ICT-III BHIWADI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
14 | NR2ICT49 | 315MVA ICT-I BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
15 | NR2ICT50 | 315MVA ICT-II BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
16 | NR1ICT71 | 500MVA ICT-I BLBGARH | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
17 | NR1ICT79 | 500MVA ICT-II BLBGARH | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
18 | NR1ICT83 | 500MVA ICT-III BLBGARH | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
19 | NR1ICT84 | 500MVA ICT-IV BLBGARH | 0.054167 | 0 | 0 | 0 | 720 | 500 |  | 500 | 499.0972 | 99.8194
20 | NR1ICT81 | 315MVA ICT-I DEHRADUN | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
21 | NR1ICT82 | 315MVA ICT-II DEHRADUN | 0 | 0.043056 | 0 | 0 | 718.9667 | 315 |  | 315 | 315 | 100
22 | NR1ICT42 | 315MVA ICT-I GURGAON | 0.59167 | 0 | 0 | 0 | 720 | 315 |  | 315 | 308.7875 | 98.0278
23 | NR1ICT51 | 315MVA ICT-II GURGAON | 0.029861 | 0 | 0 | 0 | 720 | 315 |  | 315 | 314.6865 | 99.9005
24 | NR1ICT85 | 500MVA ICT-III GURGAON | 1900-01-01 01:35 | 0 | 0 | 0 | 720 | 500 |  | 500 | 465.5671 | 93.1134
25 | NR2ICT09 | 315MVA ICT-I HISAR | 0.35347 | 0 | 0 | 0 | 720 | 315 |  | 315 | 311.2885 | 98.8218
26 | NR2ICT10 | 315MVA ICT-II HISAR | 0.41875 | 0 | 0 | 0 | 720 | 315 |  | 315 | 310.6031 | 98.6042
27 | NR2ICT34 | 315MVA ICT-III HISAR | 0.31875 | 0 | 0 | 0 | 720 | 315 |  | 315 | 311.6531 | 98.9375
28 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
29 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
30 | NR2ICT53 | 500MVA ICT-I JIND | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
31 | NR2ICT54 | 500MVA ICT-II JIND | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
32 | NR1ICT16 | 315MVA ICT-I KANKROLI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
33 | NR1ICT17 | 315MVA ICT-II KANKROLI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
34 | NR1ICT18 | 315MVA ICT-III KANKROLI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
35 | NR1ICT21 | 315MVA ICT-I KOTA | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
36 | NR1ICT22 | 315MVA ICT-II KOTA | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
37 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
38 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
39 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
40 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 1900-01-28 07:42 | 0 | 0 | 0 | 720 | 315 |  | 315 | 7.1313 | 2.2639
41 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 0.18889 | 0 | 0 | 0 | 720 | 500 |  | 500 | 496.8519 | 99.3704
42 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
43 | NR1ICT72 | 500MVA ICT-I MANDOLA | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
44 | NR1ICT80 | 500MVA ICT-II MANDOLA | 0.30903 | 0 | 0 | 0 | 720 | 500 |  | 500 | 494.8495 | 98.9699
45 | NR1ICT73 | 500MVA ICT-III MANDOLA | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
46 | NR1ICT74 | 500MVA ICT-IV MANDOLA | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
47 | NR1ICT58 | 500MVA ICT-I MANESAR | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
48 | NR1ICT61 | 500MVA ICT-II MANESAR | 0 | 0 | 0 | 1900-01-06 08:51 | 720 | 500 |  | 500 | 500 | 100
49 | NR1ICT32 | 315MVA ICT-I MEERUT | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
50 | NR1ICT33 | 315MVA ICT-II MEERUT | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
51 | NR1ICT34 | 315MVA ICT-III MEERUT | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
52 | NR1ICT69 | 500MVA ICT-IV MEERUT | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
53 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
54 | NR1ICT55 | 500MVA ICT-I NIMRANA | #N/A | #N/A | #N/A | #N/A | #N/A | 500 |  | 500 | #N/A | #N/A
55 | NR1ICT50 | 315MVA ICT-II NIMRANA | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
56 | NR1ICT36 | 315MVA ICT-I ROORKI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
57 | NR1ICT37 | 315MVA ICT-II ROORKI | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
58 | NR1ICT76 | 315MVA ICT-I SAHARANPUR | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
59 | NR1ICT77 | 315MVA ICT-II SAHARANPUR | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
60 | NR1ICT56 | 315MVA ICT-I SIKAR | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
61 | NR1ICT52 | 315MVA ICT-II SIKAR | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
62 | NR2ICT36 | 315MVA ICT-I SONIPAT | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
63 | NR2ICT35 | 315MVA ICT-II SONIPAT | #N/A | #N/A | #N/A | #N/A | #N/A | 315 |  | 315 | #N/A | #N/A
71 | ICT | TOTAL FOR ICTs | #N/A | #N/A | #N/A | #N/A |  | 33100 |  | 33100 | #N/A | #N/A | %
1 | NR1SVC-01 | +400/-300MVAR SVC KANKROLI | #N/A | #N/A | #N/A | #N/A | #N/A | 700 |  | 700 | #N/A | #N/A
|  | TOTAL FOR SVC | #N/A | #N/A | #N/A | #N/A |  |  |  | 700 | #N/A | #N/A | %
F |  | Bus & Switch Line Reactor | [5 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT57 | 125MVAR B/Reactor-I BAGPAT | 0 | 0 | 0 | 1900-01-02 17:14 | 720 | 125 |  | 125 | 125 | 100
2 | NR1BRT04 | 50MVAR B/Reactor-I BASSI | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
3 | NR1BRT53 | 50MVAR B/Reactor-II BASSI | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
4 | NR1BRT54 | 50MVAR B/Reactor-III BASSI | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
5 | NR1BRT60 | 125MVAR B/Reactor-IV BASSI | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
6 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | #N/A | #N/A | #N/A | #N/A | #N/A | 80 |  | 80 | #N/A | #N/A
7 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | #N/A | #N/A | #N/A | #N/A | #N/A | 80 |  | 80 | #N/A | #N/A
8 | NR2BRT27 | 240MVAR B/Reactor-I BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
9 | NR2BRT28 | 240MVAR B/Reactor-II BHIWANI | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
10 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 0 | 0 | 0 | 1900-01-08 12:44 | 720 | 80 |  | 80 | 80 | 100
11 | NR1BRT63 | 80MVAR B/Reactor-I DEHRADUN | 0 | 0 | 0 | 1900-01-18 09:38 | 720 | 80 |  | 80 | 80 | 100
12 | NR2BRT03 | 50MVAR B/Reactor-I HISAR | 0 | 0 | 0 | 1900-01-29 | 720 | 50 |  | 50 | 50 | 100
13 | NR2BRT22 | 125MVAR B/Reactor-II HISAR | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
14 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
15 | NR1BRT62 | 125MVAR B/Reactor-II JAIPUR(S) | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
16 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
17 | NR1BRT52 | 240MVAR B/Reactor-II JHATIKALA-765 | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
18 | NR2BRT35 | 125MVAR B/Reactor JIND | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
19 | NR1BRT08 | 50MVAR B/Reactor-I KANKROLI | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
20 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
21 | NR1BRT09 | 80MVAR B/Reactor-II KOTA | #N/A | #N/A | #N/A | #N/A | #N/A | 80 |  | 80 | #N/A | #N/A
22 | NR1BRT55 | 50MVAR B/Reactor KOTA | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
23 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | #N/A | #N/A | #N/A | #N/A | #N/A | 80 |  | 80 | #N/A | #N/A
24 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
25 | NR1BRT30 | 125MVAR B/Reactor MANESAR | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
26 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 0 | 0 | 0 | 1899-12-31 18:38 | 720 | 240 |  | 240 | 240 | 100
27 | NR1BRT12 | 50MVAR B/Reactor MURADNGR | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
28 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | #N/A | #N/A | #N/A | #N/A | #N/A | 80 |  | 80 | #N/A | #N/A
29 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI(JPR)-765 | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
30 | NR1BRT48 | 125MVAR B/Reactor-I RATANGRH(RJ) | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
31 | NR1BRT40 | 125MVAR B/Reactor ROORKI | 0 | 0 | 0 | 0.17222 | 720 | 125 |  | 125 | 125 | 100
32 | NR1BRT58 | 50MVAR B/Reactor-I SAHARANPUR | 0 | 0 | 0 | 1900-01-20 06:40 | 720 | 50 |  | 50 | 50 | 100
33 | NR1BRT59 | 50MVAR B/Reactor-II SAHARANPUR | 0 | 0 | 0 | 1900-01-20 06:40 | 720 | 50 |  | 50 | 50 | 100
34 | NR1BRT29 | 80MVAR B/Reactor SIKAR | #N/A | #N/A | #N/A | #N/A | #N/A | 80 |  | 80 | #N/A | #N/A
35 | NR2BRT13 | 125MVAR B/Reactor-I SONIPAT | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
36 | NR1BRT61 | 125MVAR B/Reactor-II SONIPAT | #N/A | #N/A | #N/A | #N/A | #N/A | 125 |  | 125 | #N/A | #N/A
37 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
38 | NR2BRT29 | BHIWANI 240MVAR S/R MEERUT line | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
39 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
40 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh-I LINE | 0 | 0 | 0 | 1900-01-01 13:37 | 720 | 50 |  | 50 | 50 | 100
41 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh-II LINE | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
42 | NR1SRT21 | MEERUT 240MVAR S/R G.NOIDA line | 0.325 | 0 | 0 | 0 | 720 | 240 |  | 240 | 237.4 | 98.9167
43 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
44 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | #N/A | #N/A | #N/A | #N/A | #N/A | 50 |  | 50 | #N/A | #N/A
45 | NR1SRT27 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
46 | NR1SRT28 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line | #N/A | #N/A | #N/A | #N/A | #N/A | 240 |  | 240 | #N/A | #N/A
47 | NR1BRT64 | 125MVAR B/Reactor Koteshwr HEP | 0 | 0 | 0 | 1900-01-18 18:56 | 720 | 125 |  | 125 | 125 | 100
%
| REACTORS | TOTAL FOR BUS REACTORS | #N/A | #N/A | #N/A | #N/A |  |  |  | 5655 | #N/A | #N/A
|  | TOTAL | #N/A | #N/A | #N/A | #N/A
Formulas:
POWERGRID = SUMIF('[1]OUTAGE_NR-1_Septmber-17'!$C13:C293,"="&VLOOKUP([Element Name],'[1]OUTAGE_NR-1_Septmber-17'!$C13:I293,1,FALSE()),'[1]OUTAGE_NR-1_Septmber-17'!F$13:F293)
OTHERS = SUMIF('[1]OUTAGE_NR-1_Septmber-17'!$C13:C293,"="&VLOOKUP([Element Name],'[1]OUTAGE_NR-1_Septmber-17'!$C13:I293,1,FALSE()),'[1]OUTAGE_NR-1_Septmber-17'!G$13:G293)
Outage Not To Consider = SUMIF('[1]OUTAGE_NR-1_Septmber-17'!$C13:C293,"="&VLOOKUP([Element Name],'[1]OUTAGE_NR-1_Septmber-17'!$C13:I293,1,FALSE()),'[1]OUTAGE_NR-1_Septmber-17'!H$13:H293)
Deemed = SUMIF('[1]OUTAGE_NR-1_Septmber-17'!$C13:C293,"="&VLOOKUP([Element Name],'[1]OUTAGE_NR-1_Septmber-17'!$C13:I293,1,FALSE()),'[1]OUTAGE_NR-1_Septmber-17'!I$13:I293)
Note on C33: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on C58: Total-45.6km, PG-26.64km, HVPN-19km.
Note on C95: LILO by SWUPPCL at Hapur on 17-05-17
Note on C122: LILO of Moradabad-Muradnagar by UP at HAPUR
Note on C123: LILO of Moradabad-Muradnagar by UP at HAPUR
Note on C128: LILO of Anta-Dausa at LALKOT by RRVPNL. DOC-01-02-14
Note on C143: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14
Note on C195: Charged-01.08.17
Note on C262: DOC-10/09/2014
Note on C269: DOC-03/02/15