## SOP DATA NR1 Feb-17
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.02.2017 to 28.02.2017
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [17 empty] | NRPC | [6 empty] | 0
1 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 672 | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 1747 | 253.076 | 442123.772 | 442123.772 | 100 |  | #REF! | #REF!
2 | NR176509 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 1155 | 271.571 | 313664.505 | 313664.505 | 100 |  | #REF! | #REF!
3 | NR176515 | 765KV BHIWANI-PHAGI(JPR)-II | 279.583 | NR1 | -- | 2017-02-24 15:24 | 2017-02-24 15:48 |  |  |  | 0 | 0.016667 | 0 | 0 |  |  |  | OMSU | CB auto tripped at Phagi (RRVPNL) end. Line remain charged from Bhiwani(PG). No flag/ facia reported. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.016667 | 0 | 0 | [6 empty] | 672 | 1155 | 279.583 | 322918.365 | 322918.365 | 100 |  | #REF! | #REF!
4 | NR176511 | 765KV MEERUT-GR.NOIDA | 119.159 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 1002 | 119.159 | 119397.318 | 119397.318 | 100 |  | #REF! | #REF!
5 | NR276502 | 765KV JHATIKALA-BHIWANI | 85.188 | NR1 | -- | 2017-02-13 00:17 | 2017-02-13 06:20 |  |  |  | 0 | 0 | 0 | 0.25208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-17 01:32 | 2017-02-17 06:43 |  |  |  | 0 | 0 | 0 | 0.21597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-802 kV | [8 empty] | #REF! | #REF!
[5 empty] | -- | 2017-02-19 17:32 | 2017-02-20 10:02 |  |  |  | 0 | 0 | 0 | 0.6875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtkr-806 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 03:44 | [6 empty] | 672 | 2250 | 85.188 | 191673 | 191673 | 100 |  | #REF! | #REF!
6 | NR276503 | 765KV MEERUT-BHIWANI | 173 | NR1 | -- | 2017-02-01 | 2017-02-01 08:16 |  |  |  | 0 | 0 | 0 | 0.34444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV. Open since 31-01-2017 23:53:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-01 17:39 | 2017-02-02 09:28 |  |  |  | 0 | 0 | 0 | 0.65903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-02 23:40 | 2017-02-03 06:39 |  |  |  | 0 | 0 | 0 | 0.29097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-807kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 20:15 | 2017-02-04 09:53 |  |  |  | 0 | 0 | 0 | 0.56806 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 20:47 | 2017-02-05 06:08 |  |  |  | 0 | 0 | 0 | 0.38958 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 21:11 | 2017-02-06 06:08 |  |  |  | 0 | 0 | 0 | 0.37292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 21:01 | 2017-02-07 06:10 |  |  |  | 0 | 0 | 0 | 0.38125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-07 23:45 | 2017-02-08 06:28 |  |  |  | 0 | 0 | 0 | 0.27986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-08 21:41 | 2017-02-09 09:23 |  |  |  | 0 | 0 | 0 | 0.4875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 23:54 | 2017-02-10 08:56 |  |  |  | 0 | 0 | 0 | 0.37639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 03:10 | 2017-02-11 09:16 |  |  |  | 0 | 0 | 0 | 0.25417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 23:19 | 2017-02-12 10:29 |  |  |  | 0 | 0 | 0 | 0.46528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 22:05 | 2017-02-13 08:48 |  |  |  | 0 | 0 | 0 | 0.44653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 21:02 | 2017-02-14 05:45 |  |  |  | 0 | 0 | 0 | 0.36319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 21:08 | 2017-02-15 06:03 |  |  |  | 0 | 0 | 0 | 0.37153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 23:18 | 2017-02-16 06:30 |  |  |  | 0 | 0 | 0 | 0.3 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-804kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-16 21:59 | 2017-02-17 06:05 |  |  |  | 0 | 0 | 0 | 0.3375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-800kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-18 20:07 | 2017-02-20 09:33 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:26 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-20 20:44 | 2017-02-21 09:19 |  |  |  | 0 | 0 | 0 | 0.52431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-21 20:44 | 2017-02-22 05:58 |  |  |  | 0 | 0 | 0 | 0.38472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-806kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-22 20:59 | 2017-02-23 07:41 |  |  |  | 0 | 0 | 0 | 0.44583 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-801kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-23 21:09 | 2017-02-24 06:47 |  |  |  | 0 | 0 | 0 | 0.40139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MRT-807 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 13:25 | 2017-02-25 07:29 |  |  |  | 0 | 0 | 0 | 0.75278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MRT-805 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-26 00:33 | 2017-02-26 08:10 |  |  |  | 0 | 0 | 0 | 0.31736 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MRT-805 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-26 17:08 | 2017-02-27 07:29 |  |  |  | 0 | 0 | 0 | 0.59792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-812kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 16:08 | [6 empty] | 672 | 1466 | 173 | 253618 | 253618 | 100 |  | #REF! | #REF!
7 | NR276501 | 765KV MOGA-BHIWANI | 273 | NR1 | -- | 2017-02-03 02:10 | 2017-02-03 09:48 |  |  |  | 0 | 0 | 0 | 0.31806 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-809kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 00:17 | 2017-02-05 05:52 |  |  |  | 0 | 0 | 0 | 0.23264 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-809kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 00:47 | 2017-02-06 07:30 |  |  |  | 0 | 0 | 0 | 0.27986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-809kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.83056 | [6 empty] | 672 | 1791 | 273 | 488943 | 488943 | 100 |  | #REF! | #REF!
[28 empty] | #REF! | #REF!
B |  | 400 KV TRANS LINES |  |  | -- | [22 empty] | #REF! | #REF!
1 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2017-02-01 | 2017-02-01 07:40 | -- | -- | -- | 0 | 0 | 0 | 0.31944 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV. Open since 31-01-2017 13:07:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-01 21:07 | 2017-02-02 06:29 |  |  |  | 0 | 0 | 0 | 0.39028 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-429 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-02 20:19 | 2017-02-03 06:27 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 20:18 | 2017-02-05 06:04 |  |  |  | 0 | 0 | 0 | 0.40694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 20:54 | 2017-02-06 05:58 |  |  |  | 0 | 0 | 0 | 0.37778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 21:12 | 2017-02-07 07:17 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-07 21:38 | 2017-02-08 07:24 |  |  |  | 0 | 0 | 0 | 0.40694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-08 21:29 | 2017-02-09 06:31 |  |  |  | 0 | 0 | 0 | 0.37639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 21:09 | 2017-02-10 06:20 |  |  |  | 0 | 0 | 0 | 0.38264 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 01:09 | 2017-02-11 06:38 |  |  |  | 0 | 0 | 0 | 0.22847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 23:30 | 2017-02-12 06:00 |  |  |  | 0 | 0 | 0 | 0.27083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 22:20 | 2017-02-13 08:40 |  |  |  | 0 | 0 | 0 | 0.43056 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 20:47 | 2017-02-14 06:17 |  |  |  | 0 | 0 | 0 | 0.39583 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 21:13 | 2017-02-15 07:18 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 21:29 | 2017-02-16 06:30 |  |  |  | 0 | 0 | 0 | 0.37569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-16 22:00 | 2017-02-17 05:45 |  |  |  | 0 | 0 | 0 | 0.32292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-19 18:11 | 2017-02-20 05:58 |  |  |  | 0 | 0 | 0 | 0.49097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-20 17:17 | 2017-02-21 09:15 |  |  |  | 0 | 0 | 0 | 0.66528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-21 20:40 | 2017-02-22 06:00 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-22 20:56 | 2017-02-23 07:01 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-23 21:10 | 2017-02-24 06:54 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-25 00:35 | 2017-02-25 07:32 |  |  |  | 0 | 0 | 0 | 0.28958 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-25 21:13 | 2017-02-26 06:40 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-26 17:20 | 2017-02-27 06:38 |  |  |  | 0 | 0 | 0 | 0.55417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-436 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-27 21:03 | 2017-02-28 06:43 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-08 23:00 | -- | -- | -- |  |  |  | 672 | 307 | 253.823 | 77923.661 | 77923.661 | 100 |  | #REF! | #REF!
2 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 307 | 253.823 | 77923.661 | 77923.661 | 100 |  | #REF! | #REF!
3 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2017-02-01 | 2017-02-01 10:27 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV. Open since 31-01-2017 22:08:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-01 14:16 | 2017-02-02 08:29 |  |  |  | 0 | 0 | 0 | 0.75903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-02 20:27 | 2017-02-03 06:15 |  |  |  | 0 | 0 | 0 | 0.40833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 20:03 | 2017-02-10 10:50 |  |  |  | 0 | 0 | 0 | 1900-01-05 14:47 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 22:19 | 2017-02-11 06:45 |  |  |  | 0 | 0 | 0 | 0.35139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 20:45 | 2017-02-13 08:35 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:50 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 20:47 | 2017-02-14 09:56 |  |  |  | 0 | 0 | 0 | 0.54792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 21:13 | 2017-02-15 07:22 |  |  |  | 0 | 0 | 0 | 0.42292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-17 00:42 | 2017-02-17 06:58 |  |  |  | 0 | 0 | 0 | 0.26111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-18 00:49 | 2017-02-18 08:29 |  |  |  | 0 | 0 | 0 | 0.31944 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-425 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-19 14:09 | 2017-02-20 06:16 |  |  |  | 0 | 0 | 0 | 0.67153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-20 17:17 | 2017-02-22 06:08 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:51 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-22 20:57 | 2017-02-24 07:29 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:32 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 13:27 | 2017-02-25 07:43 |  |  |  | 0 | 0 | 0 | 0.76111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-25 15:12 | 2017-02-26 06:49 |  |  |  | 0 | 0 | 0 | 0.65069 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-26 17:11 | 2017-02-27 06:47 |  |  |  | 0 | 0 | 0 | 0.56667 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-27 21:04 | 2017-02-28 06:49 |  |  |  | 0 | 0 | 0 | 0.40625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-28 21:05 | 2017-03-01 |  |  |  | 0 | 0 | 0 | 0.12153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-16 18:24 | -- | -- | -- |  |  |  | 672 | 568 | 393.9 | 223735.2 | 223735.2 | 100 |  | #REF! | #REF!
4 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2017-02-01 | 2017-02-01 07:45 | -- | -- | -- | 0 | 0 | 0 | 0.32292 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV. Open since 25-01-2017 23:21:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 03:43 | 2017-02-03 07:00 |  |  |  | 0 | 0 | 0 | 0.13681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 01:17 | 2017-02-04 06:42 |  |  |  | 0 | 0 | 0 | 0.22569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 02:32 | 2017-02-05 06:47 |  |  |  | 0 | 0 | 0 | 0.17708 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 23:26 | 2017-02-06 06:54 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 00:18 | 2017-02-09 06:44 |  |  |  | 0 | 0 | 0 | 0.26806 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 00:19 | 2017-02-10 06:29 |  |  |  | 0 | 0 | 0 | 0.25694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-429 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 20:13 | 2017-02-17 09:36 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:23 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-17 21:04 | 2017-02-19 07:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:40 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-19 17:29 | 2017-02-20 10:35 |  |  |  | 0 | 0 | 0 | 0.7125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-22 02:54 | 2017-02-22 06:09 |  |  |  | 0 | 0 | 0 | 0.13542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 01:05 | 2017-02-24 07:30 |  |  |  | 0 | 0 | 0 | 0.26736 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 19:35 | -- | -- | -- |  |  |  | 672 | 568 | 393.9 | 223735.2 | 223735.2 | 100 |  | #REF! | #REF!
5 | NR240006 | 400KV BAHADURGRH-BAWANA | 48.981 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 48.981 | 25225.215 | 25225.215 | 100 |  | #REF! | #REF!
6 | NR140174 | 400KV BAGHPAT-DEHRADUN | 165 | NR1 | -- | 2017-02-23 13:53 | 2017-02-23 19:48 | -- | -- | -- | 0.24653 | 0 | 0 | 0 | -- | -- | -- | LEFT | Line tripped on R-N fault. FLR-Bgpt-96.5km, Ddn-103.7km. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 10:09 | 2017-02-24 20:42 |  |  |  | 0.43958 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped on R-N fault. FLR-DDN- 88km, BGPT-100km. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.68611 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 165 | 113355 | 110577.3527 | 97.5496 |  | #REF! | #REF!
7 | NR240038 | 400KV BAHADURGRH-SONIPAT-I | 53.4 | NR1 | -- | 2017-02-01 | 2017-02-01 11:38 | -- | -- | -- | 0 | 0 | 0 | 0.48472 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Sonipat-425kV. Open since 31-01-2017 22:18:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 01:09 | 2017-02-05 06:45 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:36 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sonpt-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 21:25 | 2017-02-06 10:07 |  |  |  | 0 | 0 | 0 | 0.52917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sonpt-430kV | [9 empty] | #REF!
[6 empty] | 2017-02-07 01:09 | 2017-02-07 08:59 |  |  |  | 0 | 0 | 0 | 0.32639 |  |  |  | LVRD | Line hand tripped for Voltage regulation.snipt-430kV | [9 empty] | #REF!
[6 empty] | 2017-02-08 01:23 | 2017-02-10 10:44 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:21 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sonpt-430 kV | [9 empty] | #REF!
[6 empty] | 2017-02-13 00:06 | 2017-02-13 09:49 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sonpt-430 kV | [9 empty] | #REF!
[6 empty] | 2017-02-21 01:23 | 2017-02-21 11:14 |  |  |  | 0 | 0 | 0 | 0.41042 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sonipat-430kV | [9 empty] | #REF!
[6 empty] | 2017-02-23 01:44 | 2017-02-25 12:08 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:24 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sonipat-430kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 05:05 | -- | -- | -- |  |  |  | 672 | 605 | 53.4 | 32307 | 32307 | 100 |  | #REF! | #REF!
8 | NR240039 | 400KV BAHADURGRH-SONIPAT-II | 53.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 605 | 53.4 | 32307 | 32307 | 100 |  | #REF! | #REF!
9 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 416 | 235 | 97760 | 97760 | 100 |  | #REF! | #REF!
10 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- | 2017-02-01 21:37 | 2017-02-02 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.36319 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bassi-426 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 01:54 | 2017-02-03 05:37 |  |  |  | 0 | 0 | 0 | 0.15486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bassi-427kV | [9 empty] | #REF!
[6 empty] | 2017-02-03 21:58 | 2017-02-04 07:12 |  |  |  | 0 | 0 | 0 | 0.38472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bassi-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-04 21:33 | 2017-02-05 06:45 |  |  |  | 0 | 0 | 0 | 0.38333 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bassi-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-05 20:51 | 2017-02-06 06:41 |  |  |  | 0 | 0 | 0 | 0.40972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bassi-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-07 01:33 | 2017-02-07 06:38 |  |  |  | 0 | 0 | 0 | 0.21181 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Basi-422kV | [9 empty] | #REF!
[6 empty] | 2017-02-12 17:59 | 2017-02-13 09:51 |  |  |  | 0 | 0 | 0 | 0.66111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bassi-422kV | [9 empty] | #REF!
[6 empty] | 2017-02-13 20:45 | 2017-02-14 06:29 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bassi-422kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 23:23 | -- | -- | -- |  |  |  | 672 | 515 | 47.762 | 24597.43 | 24597.43 | 100 |  | #REF! | #REF!
11 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 48.99 | 25229.85 | 25229.85 | 100 |  | #REF! | #REF!
12 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 37.164 | 19139.46 | 19139.46 | 100 |  | #REF! | #REF!
13 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 37.164 | 19139.46 | 19139.46 | 100 |  | #REF! | #REF!
14 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- | 2017-02-21 09:35 | 2017-02-21 20:05 | -- | -- | -- | 0.4375 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for maintenance of line & equipment. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-22 09:22 | 2017-02-22 19:19 |  |  |  | 0.41458 | 0 | 0 | 0 |  |  |  | OSPT | S/D for maintenance of line & equipment. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.85208 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 247 | 106.153 | 26219.791 | 25421.8822 | 96.9568 |  | #REF! | #REF!
15 | NR140171 | 400KV BASSI-SIKAR-I | 169.8 | NR1 | -- | 2017-02-22 12:45 | 2017-02-22 18:19 | -- | -- | -- | 0.23194 | 0 | 0 | 0 | -- | -- | -- | OSFT | To attend critical hotspot at loc no-156. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.23194 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 169.8 | 87447 | 86722.6126 | 99.1716 |  | #REF! | #REF!
16 | NR140172 | 400KV BASSI-SIKAR-II | 169.8 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 169.8 | 87447 | 87447 | 100 |  | #REF! | #REF!
17 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 48.432 | 33272.784 | 33272.784 | 100 |  | #REF! | #REF!
18 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 48.432 | 33272.784 | 33272.784 | 100 |  | #REF! | #REF!
19 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 82.8 | 42642 | 42642 | 100 |  | #REF! | #REF!
20 | NR140033 | 400KV BHIWADI-HISAR-I | 211.547 | NR1 | -- | 2017-02-01 23:32 | 2017-02-02 08:33 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BWD-426 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 21:12 | 2017-02-07 09:13 |  |  |  | 0 | 0 | 0 | 0.50069 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bwd-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-08 00:08 | 2017-02-08 09:04 |  |  |  | 0 | 0 | 0 | 0.37222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Biwadi-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 00:17 | 2017-02-10 13:03 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:46 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Biwadi-428kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 18:44 | -- | -- | -- |  |  |  | 672 | 403 | 211.547 | 85253.441 | 85253.441 | 100 |  | #REF! | #REF!
21 | NR240087 | 400KV BHIWADI-HISAR-II | 144 | NR1 | -- | 2017-02-01 | 2017-02-03 07:03 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:03 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-429kV. 28-01-2017 21:36:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 21:22 | 2017-02-05 07:03 |  |  |  | 0 | 0 | 0 | 0.40347 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 08:46 | 2017-02-06 06:52 |  |  |  | 0 | 0 | 0 | 0.92083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-16 21:56 | 2017-02-17 07:10 |  |  |  | 0 | 0 | 0 | 0.38472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-425kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 00:04 | -- | -- | -- |  |  |  | 672 | 331 | 144 | 47664 | 47664 | 100 |  | #REF! | #REF!
22 | NR240088 | 400KV BHIWADI-HISAR-III | 144 | NR1 | -- | 2017-02-02 23:50 | 2017-02-05 07:03 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:13 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 21:32 | 2017-02-06 06:52 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 20:55 | 2017-02-13 10:25 |  |  |  | 0 | 0 | 0 | 0.5625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-429kV | [9 empty] | #REF!
[6 empty] | 2017-02-13 20:44 | 2017-02-14 06:48 |  |  |  | 0 | 0 | 0 | 0.41944 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-429kV | [9 empty] | #REF!
[6 empty] | 2017-02-19 17:32 | 2017-02-20 10:38 |  |  |  | 0 | 0 | 0 | 0.7125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV | [9 empty] | #REF!
[6 empty] | 2017-02-20 20:38 | 2017-02-21 07:30 |  |  |  | 0 | 0 | 0 | 0.45278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV | [9 empty] | #REF!
[6 empty] | 2017-02-21 20:39 | 2017-02-22 06:24 |  |  |  | 0 | 0 | 0 | 0.40625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-04 05:50 | -- | -- | -- |  |  |  | 672 | 331 | 144 | 47664 | 47664 | 100 |  | #REF! | #REF!
23 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- | 2017-02-06 04:08 | 2017-02-06 09:53 | -- | -- | -- | 0 | 0 | 0 | 0.23958 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bwn-428kV | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.23958 | -- | -- | -- |  |  |  | 672 | 515 | 132.428 | 68200.42 | 68200.42 | 100 |  | #REF! | #REF!
24 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2017-02-01 | 2017-02-01 09:44 | -- | -- |  | 0 | 0 | 0 | 0.40556 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMRN-426 kV. Open since 31-01-2017 16:07:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-01 21:06 | 2017-02-02 06:24 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMRN-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-02 20:16 | 2017-02-03 06:01 |  |  |  | 0 | 0 | 0 | 0.40625 |  |  |  | LVRD | Line hand tripped for Voltage regulation.NMRN-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 20:06 | 2017-02-04 06:08 |  |  |  | 0 | 0 | 0 | 0.41806 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bwd-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 20:20 | 2017-02-05 05:33 |  |  |  | 0 | 0 | 0 | 0.38403 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bwd-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 20:57 | 2017-02-06 05:42 |  |  |  | 0 | 0 | 0 | 0.36458 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bwd-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 21:07 | 2017-02-07 08:49 |  |  |  | 0 | 0 | 0 | 0.4875 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bwd-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-07 21:37 | 2017-02-08 07:09 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bwd-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-08 20:42 | 2017-02-09 06:11 |  |  |  | 0 | 0 | 0 | 0.39514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 21:06 | 2017-02-10 06:14 |  |  |  | 0 | 0 | 0 | 0.38056 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bwd-426kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 21:04 | 2017-02-11 06:12 |  |  |  | 0 | 0 | 0 | 0.38056 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Nmr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 20:46 | 2017-02-13 08:34 |  |  |  | 0 | 0 | 0 | 0.49167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 20:42 | 2017-02-14 05:37 |  |  |  | 0 | 0 | 0 | 0.37153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 21:11 | 2017-02-15 05:52 |  |  |  | 0 | 0 | 0 | 0.36181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 20:10 | 2017-02-16 06:41 |  |  |  | 0 | 0 | 0 | 0.43819 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-18 21:16 | 2017-02-19 07:05 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-432kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-19 14:02 | 2017-02-20 05:52 |  |  |  | 0 | 0 | 0 | 0.65972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-20 20:36 | 2017-02-21 06:29 |  |  |  | 0 | 0 | 0 | 0.41181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-21 20:37 | 2017-02-22 06:02 |  |  |  | 0 | 0 | 0 | 0.39236 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-22 20:53 | 2017-02-23 06:22 |  |  |  | 0 | 0 | 0 | 0.39514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-23 21:04 | 2017-02-24 06:49 |  |  |  | 0 | 0 | 0 | 0.40625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-426 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 18:27 | 2017-02-25 07:24 |  |  |  | 0 | 0 | 0 | 0.53958 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-426 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-25 21:12 | 2017-02-26 06:35 |  |  |  | 0 | 0 | 0 | 0.39097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BWD-426 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-27 00:42 | 2017-02-27 06:33 |  |  |  | 0 | 0 | 0 | 0.24375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-424 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-27 21:05 | 2017-02-28 06:47 |  |  |  | 0 | 0 | 0 | 0.40417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-28 21:00 | 2017-03-01 |  |  |  | 0 | 0 | 0 | 0.125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-431 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-09 10:45 | -- | -- | -- |  |  |  | 672 | 515 | 48.428 | 24940.42 | 24940.42 | 100 |  | #REF! | #REF!
25 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- | 2017-02-16 20:41 | 2017-02-17 06:00 | -- | -- |  | 0 | 0 | 0 | 0.38819 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-17 21:00 | 2017-02-18 05:35 |  |  |  | 0 | 0 | 0 | 0.35764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-432kV | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.74583 | -- | -- | -- |  |  |  | 672 | 515 | 48.428 | 24940.42 | 24940.42 | 100 |  | #REF! | #REF!
26 | NR240061 | 400KV BHIWANI-BAWANA | 97.415 | NR1 | -- | 2017-02-06 00:35 | 2017-02-07 10:23 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:48 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bwn-430kV | [8 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:48 | -- | -- | -- |  |  |  | 672 | 515 | 97.415 | 50168.725 | 50168.725 | 100 |  | #REF! | #REF!
27 | NR240059 | 400KV BHIWANI-BHIWANI(BBMB) | 33.962 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 33.962 | 17490.43 | 17490.43 | 100 |  | #REF! | #REF!
28 | NR240060 | 400KV BHIWANI-HISAR-I | 64.461 | NR1 | -- | 2017-02-04 00:19 | 2017-02-04 07:59 | -- | -- |  | 0 | 0 | 0 | 0.31944 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bwn-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 23:10 | 2017-02-05 06:29 |  |  |  | 0 | 0 | 0 | 0.30486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-05 21:54 | 2017-02-06 09:59 |  |  |  | 0 | 0 | 0 | 0.50347 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwn-428kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 03:04 | -- | -- | -- |  |  |  | 672 | 515 | 64.461 | 33197.415 | 33197.415 | 100 |  | #REF! | #REF!
29 | NR240093 | 400KV BHIWANI-HISAR-II | 56.669 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 56.669 | 29184.535 | 29184.535 | 100 |  | #REF! | #REF!
30 | NR240094 | 400KV BHIWANI-HISAR-III | 56.669 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 56.669 | 29184.535 | 29184.535 | 100 |  | #REF! | #REF!
31 | NR240068 | 400KV BHIWANI-JIND-I | 82.23 | NR1 | -- | 2017-02-01 | 2017-02-08 21:00 | -- | -- |  | 0 | 0 | 0 | 1900-01-06 21:00 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bhiwani-428 kV. Open since 27-01-2017 21:50:00 | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-06 21:00 | -- | -- | -- |  |  |  | 672 | 515 | 82.23 | 42348.45 | 42348.45 | 100 |  | #REF! | #REF!
32 | NR240069 | 400KV BHIWANI-JIND-II | 82.23 | NR1 | -- | 2017-02-04 00:24 | 2017-03-01 | -- | -- |  | 0 | 0 | 0 | 1900-01-23 23:36 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bwn-428kV | [8 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-23 23:36 | -- | -- | -- |  |  |  | 672 | 515 | 82.23 | 42348.45 | 42348.45 | 100 |  | #REF! | #REF!
33 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | 2017-02-08 14:44 | 2017-02-08 20:34 |  |  |  | 0.24306 | 0 | 0 | 0 |  |  |  | OSFT | S/D by WR-2 for B-phase line CVT replacement at Zerda. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.24306 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 272 | 142.8 | 38841.6 | 38504.4333 | 99.1319 |  | #REF! | #REF!
34 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 42.7 | 21990.5 | 21990.5 | 100 |  | #REF! | #REF!
35 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 60.68 | 41929.88 | 41929.88 | 100 |  | #REF! | #REF!
36 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) | 12.55 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 12.55 | 8672.05 | 8672.05 | 100 |  | #REF! | #REF!
37 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 13.256 | 9159.896 | 9159.896 | 100 |  | #REF! | #REF!
38 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 54.36 | 37562.76 | 37562.76 | 100 |  | #REF! | #REF!
39 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | 2017-02-02 01:09 | 2017-02-02 06:20 |  |  |  | 0 | 0 | 0 | 0.21597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. DDR-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 09:42 | 2017-02-13 18:59 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | OSPD | S/D by UPPCL for stringing work of Hapur-Mrdngr line. | [9 empty] | #REF!
[6 empty] | 2017-02-14 09:38 | 2017-02-14 18:44 |  |  |  | 0 | 0 | 0 | 0.37917 |  |  |  | OSPD | S/D by UPPCL for stringing work of Hapur-Mrdngr line. | [9 empty] | #REF!
[5 empty] | -- | 2017-02-15 11:34 | 2017-02-15 18:51 |  |  |  | 0 | 0 | 0 | 0.30347 |  |  |  | OSPD | S/D by UPPCL for stringing work of Hapur-Mrdngr line. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 06:51 | -- | -- | -- |  |  |  | 672 | 691 | 46.3 | 31993.3 | 31993.3 | 100 |  | #REF! | #REF!
40 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | 2017-02-13 09:43 | 2017-02-13 18:59 |  |  |  | 0 | 0 | 0 | 0.38611 |  |  |  | OSPD | S/D by UPPCL for stringing work of Hapur-Mrdngr line. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 09:39 | 2017-02-14 18:45 |  |  |  | 0 | 0 | 0 | 0.37917 |  |  |  | OSPD | S/D by UPPCL for stringing work of Hapur-Mrdngr line. | [9 empty] | #REF!
[6 empty] | 2017-02-15 11:34 | 2017-02-15 19:19 |  |  |  | 0 | 0 | 0 | 0.32292 |  |  |  | OSPD | S/D by UPPCL for stringing work of Hapur-Mrdngr line. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 02:07 | 0 | 0 | 0 |  |  |  | 672 | 691 | 46.3 | 31993.3 | 31993.3 | 100 |  | #REF! | #REF!
41 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2017-02-26 18:47 | 2017-03-01 | -- | -- |  | 0 | 0 | 1900-01-01 05:13 | 0 | -- | -- | -- | LMAC | Tripped on R-Y fault due to collapse of D/C tension tower at loc.52, caused after collision with a dumper truck, by some miscreant, a force majeure event beyond our control. FLR:Dad-Not Reported, Mngr-9.19km. ERS being deployed. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 1900-01-01 05:13 | 0 | -- | -- | -- |  |  |  | 618.7833 | 515 | 33.098 | 17045.47 | 17045.47 | 100 |  | #REF! | #REF!
42 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | 2017-02-02 01:06 | 2017-02-02 06:32 |  |  |  | 0 | 0 | 0 | 0.22639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. DDR-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 00:39 | 2017-02-05 07:15 |  |  |  | 0 | 0 | 0 | 0.275 |  |  |  | LVRD | Line hand tripped for Voltage regulation. DDR-426KV | [9 empty] | #REF!
[6 empty] | 2017-02-14 03:35 | 2017-02-14 07:32 |  |  |  | 0 | 0 | 0 | 0.16458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. DDR-426 kV | [9 empty] | #REF!
[6 empty] | 2017-02-14 13:04 | 2017-02-14 13:47 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | OMSU | Trip on B-N fault in Z-2 from Dadri-NTPC due to problem in BBMB system. No other flag/ facia reported. | [9 empty] | #REF!
[6 empty] | 2017-02-26 18:47 | 2017-03-01 |  |  |  | 0 | 0 | 1900-01-01 05:13 | 0 |  |  |  | LMAC | Tripped on B-N fault due to collapse of D/C tension tower at loc.52, caused after collision with a dumper truck, by some miscreant, a force majeure event beyond our control. FLR:Dad-12.18km, Pnpt-99.97km. ERS being deployed. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.029861 | 1900-01-01 05:13 | 0.66597 | 0 | 0 | 0 |  |  |  | 618.7833 | 515 | 112.322 | 57845.83 | 57845.83 | 100 |  | #REF! | #REF!
43 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- | 2017-02-06 00:52 | 2017-02-06 07:14 | -- | -- |  | 0 | 0 | 0 | 0.26528 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. DDR-426KV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 09:44 | 2017-02-03 17:01 |  |  |  | 0 | 0 | 0 | 0.30347 |  |  |  | OSPD | S/D by UPPCL for construction of LILO of 400kV Mrdngr-Mzfrngr line. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.56875 | -- | -- | -- |  |  |  | 672 | 515 | 117 | 60255 | 60255 | 100 |  | #REF! | #REF!
44 | NR240026 | 400KV FATEHABAD-HISAR | 88.558 | NR1 | -- | 2017-02-01 00:02 | 2017-02-03 10:38 | -- | -- |  | 0 | 0 | 0 | 1900-01-01 10:36 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Hissar-426kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 19:57 | 2017-02-07 09:02 |  |  |  | 0 | 0 | 0 | 1900-01-02 13:05 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Fthbd-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-07 22:00 | 2017-02-08 08:10 |  |  |  | 0 | 0 | 0 | 0.42361 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Fthbd-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-08 22:18 | 2017-02-09 11:25 |  |  |  | 0 | 0 | 0 | 0.54653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Fthbd-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 20:58 | 2017-02-10 21:05 |  |  |  | 0 | 0 | 0.0048611 | 0 |  |  |  | GOVC | Tripped on O/voltage protn operated at Fatehabad >437kv | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 21:05 | 2017-02-11 06:21 |  |  |  | 0 | 0 | 0 | 0.38611 |  |  |  | LVRD | Line kept open for Voltage regulation. Hsr-424kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 20:20 | 2017-02-12 07:01 |  |  |  | 0 | 0 | 0 | 0.44514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Hsr-424kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 20:49 | 2017-02-13 09:57 |  |  |  | 0 | 0 | 0 | 0.54722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Fatebd-431kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 20:36 | 2017-02-14 06:10 |  |  |  | 0 | 0 | 0 | 0.39861 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Hsr-424kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 20:59 | 2017-02-14 21:05 |  |  |  | 0 | 0 | 0.0041667 | 0 |  |  |  | GOVC | Tripped on O/VOL protn operation. Fbad>437kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 21:05 | 2017-02-15 08:16 |  |  |  | 0 | 0 | 0 | 0.46597 |  |  |  | LVRD | Kept open for Voltage regulation. Fbad=435kv | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 21:28 | 2017-02-16 06:24 |  |  |  | 0 | 0 | 0 | 0.37222 |  |  |  | LVRD | Line hand tripped for Voltage regulation.F,bad=429kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-16 20:38 | 2017-02-17 06:59 |  |  |  | 0 | 0 | 0 | 0.43125 |  |  |  | LVRD | Line hand tripped for Voltage regulation.F,bad=431kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-17 20:40 | 2017-02-18 06:12 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LVRD | Line hand tripped for Voltage regulation.F,bad=433kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-18 20:15 | 2017-02-19 06:55 |  |  |  | 0 | 0 | 0 | 0.44444 |  |  |  | LVRD | Line hand tripped for Voltage regulation.F,bad=432kv. | [9 empty] | #REF!
[6 empty] | 2017-02-20 19:55 | 2017-02-21 07:47 |  |  |  | 0 | 0 | 0 | 0.49444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. fatbad-432kV | [9 empty] | #REF!
[6 empty] | 2017-02-21 19:56 | 2017-02-22 07:17 |  |  |  | 0 | 0 | 0 | 0.47292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Fatbad-432kV | [9 empty] | #REF!
[6 empty] | 2017-02-22 20:42 | 2017-02-22 20:45 |  |  |  | 0 | 0 | 0.0020833 | 0 |  |  |  | GOVC | Trip on O/voltage protn at Fbad=439kv. | [9 empty] | #REF!
[6 empty] | 2017-02-22 20:45 | 2017-02-23 09:25 |  |  |  | 0 | 0 | 0 | 0.52778 |  |  |  | LVRD | Kept open for Voltage regulation. fatbad-432kV | [9 empty] | #REF!
[6 empty] | 2017-02-23 20:56 | 2017-02-25 07:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:31 |  |  |  | LVRD | Line hand tripped for Voltage regulation. HSR-426 kV | [9 empty] | #REF!
[6 empty] | 2017-02-25 20:57 | 2017-02-25 21:01 |  |  |  | 0 | 0 | 0.0027778 | 0 |  |  |  | GOVC | Trip on O/VOL protn opted at Fbad=437kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-25 21:01 | 2017-02-26 07:40 |  |  |  | 0 | 0 | 0 | 0.44375 |  |  |  | LVRD | Kept open for Voltage regulation. Fbad=437kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-26 21:24 | 2017-02-28 11:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:50 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Fthbd-434 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-28 20:21 | 2017-03-01 |  |  |  | 0 | 0 | 0 | 0.15208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Hissar-433 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.013889 | 1900-01-14 22:49 | -- | -- | -- |  |  |  | 671.6667 | 515 | 88.558 | 45607.37 | 45607.37 | 100 |  | #REF! | #REF!
45 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- | 2017-02-03 01:54 | 2017-02-03 16:46 | -- | -- | -- | 0 | 0 | 0 | 0.61944 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Grg-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 21:23 | 2017-02-06 06:04 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:41 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Grg-427kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 23:33 | -- | -- | -- |  |  |  | 672 | 687 | 23.462 | 16118.394 | 16118.394 | 100 |  | #REF! | #REF!
46 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 23.462 | 16118.394 | 16118.394 | 100 |  | #REF! | #REF!
47 | NR240015 | 400KV HISAR-BHIWANI(BBMB) | 34.52 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 34.52 | 17777.8 | 17777.8 | 100 |  | #REF! | #REF!
48 | NR240016 | 400KV HISAR-KAITHAL-I | 113.12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 605 | 113.12 | 68437.6 | 68437.6 | 100 |  | #REF! | #REF!
49 | NR240044 | 400KV HISAR-KAITHAL-II | 113.12 | NR1 | -- | 2017-02-10 01:23 | 2017-02-13 17:16 |  |  |  | 0 | 0 | 0 | 1900-01-02 15:53 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Hissar-426kV | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 15:53 | -- | -- | -- |  |  |  | 672 | 385 | 113.12 | 43551.2 | 43551.2 | 100 |  | #REF! | #REF!
50 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | 2017-02-01 | 2017-03-01 |  |  |  | 0 | 0 | 0 | 1900-01-27 |  |  |  | OSFD | S/D by DTL for damaged tower rectification ( 1st Dead end tower from Bamnoli). Open since 2100hrs on 22.05.16 | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-27 | -- | -- | -- |  |  |  | 672 | 687 | 6.106 | 4194.822 | 4194.822 | 100 |  | #REF! | #REF!
51 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 6.106 | 4194.822 | 4194.822 | 100 |  | #REF! | #REF!
52 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 6.782 | 4659.234 | 4659.234 | 100 |  | #REF! | #REF!
53 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 6.782 | 4659.234 | 4659.234 | 100 |  | #REF! | #REF!
54 | NR240102 | 400KV KABULPR-BAHADURGRH | 38.58 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 38.58 | 19868.7 | 19868.7 | 100 |  | #REF! | #REF!
55 | NR240103 | 400KV KABULPR-BHIWANI | 26.64 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 26.64 | 13719.6 | 13719.6 | 100 |  | #REF! | #REF!
56 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 225 | 201.2 | 45270 | 45270 | 100 |  | #REF! | #REF!
57 | NR140169 | 400KV KANKROLI-CHITTOR(RJ)-I | 71.03 | NR1 | -- | 2017-02-27 10:10 | 2017-02-27 22:42 |  |  |  | 0 | 0 | 0 | 0.52222 |  |  |  | LCSD | S/D for Strining of 765KV D/C Ajmer-Chitorgarh line. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-28 09:59 | 2017-02-28 20:56 |  |  |  | 0 | 0 | 0 | 0.45625 |  |  |  | LCSD | S/D for Strining of 765KV D/C Ajmer-Chitorgarh Line | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.97847 | -- | -- | -- |  |  |  | 672 | 515 | 71.03 | 36580.45 | 36580.45 | 100 |  | #REF! | #REF!
58 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2017-02-21 02:04 | 2017-02-21 02:30 | -- | -- | -- | 0 | 0.018056 | 0 | 0 | -- | -- | -- | OMSU | Line A/R at Kank but tripped from Jodhpur-RRVPN end due to A/R problem during Y-N fault, FLR Jodhpur-131Km. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.018056 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 187.965 | 96801.975 | 96801.975 | 100 |  | #REF! | #REF!
59 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- | 2017-02-27 09:09 | 2017-02-27 21:57 | -- | -- |  | 0 | 0 | 0 | 0.53333 | -- | -- | -- | LCSD | S/D for Strining of 765KV D/C Ajmer-Chitorgarh line. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-28 09:02 | 2017-02-28 20:34 |  |  |  | 0 | 0 | 0 | 0.48056 |  |  |  | LCSD | S/D for Strining of 765KV D/C Ajmer-Chitorgarh Line | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 00:20 | -- | -- | -- |  |  |  | 672 | 395 | 198.54 | 78423.3 | 78423.3 | 100 |  | #REF! | #REF!
60 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 236 | 233.707 | 55154.852 | 55154.852 | 100 |  | #REF! | #REF!
61 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 515 | 179.711 | 92551.165 | 92551.165 | 100 |  | #REF! | #REF!
62 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- | 2017-02-03 01:42 | 2017-02-03 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.19583 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Mrta-421kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 04:10 | 2017-02-06 06:24 |  |  |  | 0 | 0 | 0 | 0.093056 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Kota-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-07 04:13 | 2017-02-07 06:32 |  |  |  | 0 | 0 | 0 | 0.096528 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta=423kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 21:37 | 2017-02-11 06:28 |  |  |  | 0 | 0 | 0 | 0.36875 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Mrt-417kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 20:50 | 2017-02-11 22:49 |  |  |  | 0 | 0 | 0 | 0.082639 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Mrt-416kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 17:55 | 2017-02-13 06:12 |  |  |  | 0 | 0 | 0 | 0.51181 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Mrta-416kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 18:15 | 2017-02-14 06:24 |  |  |  | 0 | 0 | 0 | 0.50625 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Mrta-416kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 20:31 | -- | -- | -- |  |  |  | 672 | 309 | 255.56 | 78968.04 | 78968.04 | 100 |  | #REF! | #REF!
63 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 50.5 | 26007.5 | 26007.5 | 100 |  | #REF! | #REF!
64 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- | 2017-02-09 11:26 | 2017-02-09 13:58 | -- | -- | -- | 0 | 0 | 0 | 0.10556 | -- | -- | -- | OSFD | S/D by THDC for Bus protn testing at KHEP end. | [8 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.10556 | -- | -- | -- |  |  |  | 672 | 515 | 2.7 | 1390.5 | 1390.5 | 100 |  | #REF! | #REF!
65 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- | 2017-02-05 13:22 | 2017-02-05 15:00 | -- | -- | -- | 0 | 0.068056 | 0 | 0 | -- | -- | -- | OMSU | A/R on B-N fault but tripped on DT signal received at Koteshwar PG, due to protn problem at THDC. Charged at 1402hrs but Synch delayed by THDC. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 16:09 | 2017-02-06 16:41 |  |  |  | 0 | 0 | 0 | 0.022222 |  |  |  | OSPD | S/D by KHEP for maintenance work at their S/yard. | [9 empty] | #REF!
[6 empty] | 2017-02-09 11:27 | 2017-02-09 13:59 |  |  |  | 0 | 0 | 0 | 0.10556 |  |  |  | OSFD | S/D by THDC for Bus protn testing at KHEP end. | [9 empty] | #REF!
[5 empty] | -- | 2017-02-28 10:19 | 2017-02-28 11:15 | -- | -- | -- | 0 | 0 | 0 | 0.038889 | -- | -- | -- | OSPD | S/D by THDC for switching of bus isolator for taking line-2 from bus-2 to bus-1 at KHEP. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.068056 | 0 | 0.16667 | -- | -- | -- |  |  |  | 672 | 515 | 2.7 | 1390.5 | 1390.5 | 100 |  | #REF! | #REF!
66 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 633 | 14.463 | 9155.079 | 9155.079 | 100 |  | #REF! | #REF!
67 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 672 | 633 | 16.49 | 10438.17 | 10438.17 | 100 |  | #REF! | #REF!
68 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | 2017-02-16 10:18 | 2017-02-18 19:40 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:22 |  |  |  | LCSD | S/D for retrofitment of TBC isolator at Mrdngr end under ADD-CAP. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:22 | -- | -- | -- |  |  |  | 672 | 515 | 133.5 | 68752.5 | 68752.5 | 100 |  | #REF! | #REF!
69 | NR140165 | 400KV MEERUT-BAGPAT-I | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 70.976 | 36552.64 | 36552.64 | 100 |  | #REF! | #REF!
70 | NR140166 | 400KV MEERUT-BAGPAT-II | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 70.976 | 36552.64 | 36552.64 | 100 |  | #REF! | #REF!
71 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- | 2017-02-03 18:12 | 2017-02-03 18:49 | -- | -- | -- | 0 | 0.025694 | 0 | 0 | -- | -- | -- | OMSU | Tripped on Y-B fault caused by kite thread, FLR Mrt-8.6km, Brly-223.1km | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.025694 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 616 | 66.009 | 40661.544 | 40661.544 | 100 |  | #REF! | #REF!
72 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 616 | 66.009 | 40661.544 | 40661.544 | 100 |  | #REF! | #REF!
73 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | 2017-02-04 09:31 | 2017-02-04 15:42 |  |  |  | 0 | 0 | 0 | 0.25764 |  |  |  | LCSD | S/D for erection work of new 765kv bay/Bus for Koteshwar lines. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 09:39 | 2017-02-15 16:16 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | LCSD | S/D for erection of 765kv Bus & bay at MRT. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.53333 | [6 empty] | 672 | 678 | 178.69 | 121151.82 | 121151.82 | 100 |  | #REF! | #REF!
74 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 673 | 175.63 | 118198.99 | 118198.99 | 100 |  | #REF! | #REF!
75 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | 2017-02-05 23:22 | 2017-02-06 09:36 |  |  |  | 0 | 0 | 0 | 0.42639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-01 00:32 | 2017-02-01 10:49 |  |  |  | 0 | 0 | 0 | 0.42847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 23:55 | 2017-02-10 11:57 |  |  |  | 0 | 0 | 0 | 0.50139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-420kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 00:26 | 2017-02-13 09:37 |  |  |  | 0 | 0 | 0 | 0.38264 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-426 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-18 01:42 | 2017-02-18 08:36 |  |  |  | 0 | 0 | 0 | 0.2875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-426kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-23 01:48 | 2017-02-23 06:55 |  |  |  | 0 | 0 | 0 | 0.21319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-424kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 05:45 | 0 | 0 | 0 |  |  |  | 672 | 515 | 59.868 | 30832.02 | 30832.02 | 100 |  | #REF! | #REF!
76 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | 2017-02-05 23:23 | 2017-02-06 10:04 |  |  |  | 0 | 0 | 0 | 0.44514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 00:27 | 2017-02-13 09:41 |  |  |  | 0 | 0 | 0 | 0.38472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-426 kV | [9 empty] | #REF!
[6 empty] | 2017-02-18 01:43 | 2017-02-18 08:36 |  |  |  | 0 | 0 | 0 | 0.28681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-426kV | [9 empty] | #REF!
[6 empty] | 2017-02-23 01:48 | 2017-02-23 06:55 |  |  |  | 0 | 0 | 0 | 0.21319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-424kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:55 | 0 | 0 | 0 |  |  |  | 672 | 515 | 59.868 | 30832.02 | 30832.02 | 100 |  | #REF! | #REF!
77 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | 2017-02-04 00:20 | 2017-02-05 07:09 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:49 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 23:54 | 2017-02-14 07:59 |  |  |  | 0 | 0 | 0 | 0.33681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-426 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 14:54 | [6 empty] | 672 | 515 | 54.298 | 27963.47 | 27963.47 | 100 |  | #REF! | #REF!
78 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | 2017-02-04 00:19 | 2017-02-05 07:08 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:49 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnd-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 23:55 | 2017-02-14 08:02 |  |  |  | 0 | 0 | 0 | 0.33819 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-426 kV | [9 empty] | #REF!
[5 empty] | -- | 2017-02-26 16:22 | 2017-02-26 16:59 |  |  |  | 0 | 0.025694 | 0 | 0 |  |  |  | OMSU | Tripped on R-Y fault due to kite thread. FLR:Mrt-27.7km, Mnd-69km. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.025694 | 0 | 1899-12-31 14:56 | [6 empty] | 672 | 515 | 54.298 | 27963.47 | 27963.47 | 100 |  | #REF! | #REF!
79 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | 2017-02-03 18:12 | 2017-02-03 19:02 |  |  |  | 0 | 0.034722 | 0 | 0 |  |  |  | OMSU | CB auto tripped only from Mzfngr(UPPCL) end. Remain charged from Mrt. No flag/facia reported. | [8 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.034722 | 0 | 0 | [6 empty] | 672 | 515 | 37.38 | 19250.7 | 19250.7 | 100 |  | #REF! | #REF!
80 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 76.018 | 39149.27 | 39149.27 | 100 |  | #REF! | #REF!
81 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA | 30.15 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 691 | 30.15 | 20833.65 | 20833.65 | 100 |  | #REF! | #REF!
82 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- | 2017-02-01 | 2017-02-01 10:25 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMRN-422kV. Open since 31-01-2017 22:06:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 01:54 | 2017-02-06 06:06 |  |  |  | 0 | 0 | 0 | 1900-01-02 04:12 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 08:25 | 2017-03-01 |  |  |  | 0 | 0 | 0 | 1900-01-03 15:35 |  |  |  | LCSD | S/D for diversion of line due to DFCC rail project. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 06:12 | -- | -- | -- |  |  |  | 672 | 515 | 67.041 | 34526.115 | 34526.115 | 100 |  | #REF! | #REF!
83 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- | 2017-02-24 08:25 | 2017-03-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 15:35 | -- | -- | -- | LCSD | S/D for diversion of line due to DFCC rail project. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 15:35 | -- | -- | -- |  |  |  | 672 | 515 | 67.041 | 34526.115 | 34526.115 | 100 |  | #REF! | #REF!
84 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- | 2017-02-01 21:04 | 2017-02-02 06:26 | -- | -- |  | 0 | 0 | 0 | 0.39028 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMRN-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-02 20:12 | 2017-02-03 05:56 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation.NMRN-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-08 20:40 | 2017-02-09 06:10 |  |  |  | 0 | 0 | 0 | 0.39583 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-426kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 21:06 | 2017-02-10 06:12 |  |  |  | 0 | 0 | 0 | 0.37917 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 20:08 | 2017-02-16 06:26 |  |  |  | 0 | 0 | 0 | 0.42917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-23 21:03 | 2017-02-24 06:55 |  |  |  | 0 | 0 | 0 | 0.41111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMRN-428 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 18:30 | 2017-02-25 07:21 |  |  |  | 0 | 0 | 0 | 0.53542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMRN-426 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 22:43 | -- | -- | -- |  |  |  | 672 | 515 | 175.859 | 90567.385 | 90567.385 | 100 |  | #REF! | #REF!
85 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- | 2017-02-01 | 2017-02-01 09:41 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. NMRN-426 kV. Open since 31-01-2017 16:05:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 20:02 | 2017-02-04 06:05 |  |  |  | 0 | 0 | 0 | 0.41875 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 20:15 | 2017-02-05 05:26 |  |  |  | 0 | 0 | 0 | 0.38264 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 20:48 | 2017-02-06 05:40 |  |  |  | 0 | 0 | 0 | 0.36944 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 21:08 | 2017-02-07 08:46 |  |  |  | 0 | 0 | 0 | 0.48472 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-07 21:34 | 2017-02-08 07:26 |  |  |  | 0 | 0 | 0 | 0.41111 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 21:03 | 2017-02-11 06:09 |  |  |  | 0 | 0 | 0 | 0.37917 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Nmr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 00:55 | 2017-02-12 05:29 |  |  |  | 0 | 0 | 0 | 0.19028 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Nmr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 20:43 | 2017-02-13 08:38 |  |  |  | 0 | 0 | 0 | 0.49653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-13 20:40 | 2017-02-14 05:33 |  |  |  | 0 | 0 | 0 | 0.37014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-14 21:11 | 2017-02-15 05:53 |  |  |  | 0 | 0 | 0 | 0.3625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-16 20:41 | 2017-02-17 05:36 |  |  |  | 0 | 0 | 0 | 0.37153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-428kV | [9 empty] | #REF!
[6 empty] | 2017-02-17 21:01 | 2017-02-18 05:34 |  |  |  | 0 | 0 | 0 | 0.35625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-430kV | [9 empty] | #REF!
[6 empty] | 2017-02-18 21:15 | 2017-02-19 08:17 |  |  |  | 0 | 0 | 0 | 0.45972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-430kV | [9 empty] | #REF!
[6 empty] | 2017-02-19 18:06 | 2017-02-20 06:46 |  |  |  | 0 | 0 | 0 | 0.52778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-430kV | [9 empty] | #REF!
[6 empty] | 2017-02-20 20:34 | 2017-02-21 06:28 |  |  |  | 0 | 0 | 0 | 0.4125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-430kV | [9 empty] | #REF!
[6 empty] | 2017-02-21 20:36 | 2017-02-22 05:53 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-22 20:48 | 2017-02-23 06:19 |  |  |  | 0 | 0 | 0 | 0.39653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMR-430kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-25 21:12 | 2017-02-26 06:34 |  |  |  | 0 | 0 | 0 | 0.39028 |  |  |  | LVRD | Line hand tripped for Voltage regulation. NMRN-426 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-27 00:43 | 2017-02-27 06:31 |  |  |  | 0 | 0 | 0 | 0.24167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-424 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-27 21:01 | 2017-02-28 06:46 |  |  |  | 0 | 0 | 0 | 0.40625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-431 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-28 20:54 | 2017-03-01 |  |  |  | 0 | 0 | 0 | 0.12917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Nmrn-431 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 08:20 | -- | -- | -- |  |  |  | 672 | 515 | 175.859 | 90567.385 | 90567.385 | 100 |  | #REF! | #REF!
86 | NR140170 | 400KV RAPPC-CHITTOR(RJ)-I | 155.15 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 672 | 515 | 155.15 | 79902.25 | 79902.25 | 100 |  | #REF! | #REF!
87 | NR140161 | 400KV ROORKI-KASHIPUR-I | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 150.832 | 103621.584 | 103621.584 | 100 |  | #REF! | #REF!
88 | NR140162 | 400KV ROORKI-KASHIPUR-II | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 150.832 | 103621.584 | 103621.584 | 100 |  | #REF! | #REF!
89 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 2.1 | 1081.5 | 1081.5 | 100 |  | #REF! | #REF!
90 | NR140175 | 400KV ROORKEE -DEHRADUN | 79.7 | NR1 | -- | 2017-02-03 09:56 | 2017-02-03 18:50 |  |  |  | 0.37083 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending E/wire sag problem at Loc-24-25. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.37083 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 79.7 | 54753.9 | 54028.7367 | 98.6756 |  | #REF! | #REF!
91 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | 2017-02-05 12:03 | 2017-02-22 15:24 |  |  |  | 0 | 0 | 0 | 1900-01-16 03:21 |  |  |  | OSPD | S/D by PTCUL for tower erection work in their section. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-16 03:21 | -- | -- | -- |  |  |  | 672 | 515 | 2.1 | 1081.5 | 1081.5 | 100 |  | #REF! | #REF!
92 | NR140167 | 400KV ROORKI-SAHARANPUR-I | 36.535 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 36.535 | 25099.545 | 25099.545 | 100 |  | #REF! | #REF!
93 | NR140168 | 400KV ROORKI-SAHARANPUR-II | 36.535 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 687 | 36.535 | 25099.545 | 25099.545 | 100 |  | #REF! | #REF!
94 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 |  | 2017-02-01 | 2017-02-01 06:16 |  |  |  | 0 | 0 | 0 | 0.26111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-424 kV. Open since 31-01-2017 20:46:00 | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-01 20:44 | 2017-02-02 06:58 |  |  |  | 0 | 0 | 0 | 0.42639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-02 18:07 | 2017-02-02 19:01 |  |  |  | 0 | 0 | 0 | 0.0375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-427 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 20:50 | 2017-02-04 06:38 |  |  |  | 0 | 0 | 0 | 0.40833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-04 20:32 | 2017-02-05 06:31 |  |  |  | 0 | 0 | 0 | 0.41597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 20:57 | 2017-02-06 06:44 |  |  |  | 0 | 0 | 0 | 0.40764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-06 20:53 | 2017-02-07 06:35 |  |  |  | 0 | 0 | 0 | 0.40417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422kv. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-07 20:50 | 2017-02-08 06:23 |  |  |  | 0 | 0 | 0 | 0.39792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-422 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-08 20:19 | 2017-02-09 05:57 |  |  |  | 0 | 0 | 0 | 0.40139 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 20:40 | 2017-02-10 06:36 |  |  |  | 0 | 0 | 0 | 0.41389 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-427kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-10 20:48 | 2017-02-11 06:00 |  |  |  | 0 | 0 | 0 | 0.38333 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-11 20:37 | 2017-02-12 06:10 |  |  |  | 0 | 0 | 0 | 0.39792 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 17:57 | 2017-02-13 06:40 |  |  |  | 0 | 0 | 0 | 0.52986 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 17:51 | 2017-02-14 06:31 |  |  |  | 0 | 0 | 0 | 0.52778 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-14 20:44 | 2017-02-15 05:44 |  |  |  | 0 | 0 | 0 | 0.375 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-15 19:38 | 2017-02-16 05:27 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Skr-429kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-16 20:12 | 2017-02-17 06:34 |  |  |  | 0 | 0 | 0 | 0.43194 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Rtngrh-422kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-17 20:30 | 2017-02-18 06:35 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Rtngrh-424kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-18 17:40 | 2017-02-19 05:41 |  |  |  | 0 | 0 | 0 | 0.50069 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Rtngrh-424kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-19 17:18 | 2017-02-20 06:01 |  |  |  | 0 | 0 | 0 | 0.52986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Rtngrh-424kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-24 18:25 | 2017-02-25 06:29 |  |  |  | 0 | 0 | 0 | 0.50278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-424 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-26 17:06 | 2017-02-27 07:07 |  |  |  | 0 | 0 | 0 | 0.58403 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Rtngrh-429 kV | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-27 17:31 | 2017-02-28 06:40 |  |  |  | 0 | 0 | 0 | 0.54792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Rtngrh-429 kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-08 17:09 | -- | -- | -- |  |  |  | 672 | 515 | 76.48 | 39387.2 | 39387.2 | 100 |  | #REF! | #REF!
95 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 515 | 76.48 | 39387.2 | 39387.2 | 100 |  | #REF! | #REF!
[28 empty] | #REF! | #REF!
|  | 220KV LINES | [25 empty] | #REF! | #REF!
1 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | 2017-02-01 10:40 | 2017-02-01 20:12 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | LCSD | S/D for installation of polymer insulator strings. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-02 09:08 | 2017-02-02 18:42 |  |  |  | 0 | 0 | 0 | 0.39861 |  |  |  | LCSD | S/D for installation of polymer insulator strings. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-03 09:40 | 2017-02-03 16:24 |  |  |  | 0 | 0 | 0 | 0.28056 |  |  |  | LCSD | S/D for installation of polymer insulator strings. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-13 23:04 | 2017-02-16 05:57 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:53 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bhilwara-236kV | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-02 08:43 | -- | -- | -- |  |  |  | 672 | 132 | 186.667 | 24640.044 | 24640.044 | 100 |  | #REF! | #REF!
2 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | 2017-02-04 09:26 | 2017-02-04 17:01 |  |  |  | 0 | 0 | 0 | 0.31597 |  |  |  | LCSD | S/D for installation of polymer insulator strings. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-05 09:14 | 2017-02-05 15:45 |  |  |  | 0 | 0 | 0 | 0.27153 |  |  |  | LCSD | S/D for installation of polymer insulator strings. | [9 empty] | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.5875 | -- | -- | -- |  |  |  | 672 | 132 | 186.667 | 24640.044 | 24640.044 | 100 |  | #REF! | #REF!
3 | NR122046 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- | 2017-02-01 | 2017-02-01 10:12 | -- | -- | -- | 0 | 0 | 0 | 0.425 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Open since 27-01-2017 00:55:00 | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.425 | -- | -- | -- |  |  |  | 672 | 132 | 180.287 | 23797.884 | 23797.884 | 100 |  | #REF! | #REF!
4 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- | 2017-02-03 01:06 | 2017-02-03 01:06 | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | LART | A/R on R-N fault, FLR:Anta-52.15km, RAPP-20.95km | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 02:42 | 2017-02-12 02:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/R on Y-N fault. FLR-Anta-41.53km, If-2.83Kamp | [9 empty] | #REF!
[6 empty] | 2017-02-19 02:24 | 2017-02-19 03:10 |  |  |  | 0 | 0.031944 | 0 | 0 |  |  |  | OMSU | A/R from Anta but tripped from RAPP end due to A/R problem during Y-N fault. FLR:Anta-9.64km, RAPP-74.4km | [9 empty] | #REF!
[6 empty] | 2017-02-20 02:21 | 2017-02-20 03:44 |  |  |  | 0 | 0.057639 | 0 | 0 |  |  |  | OMSU | A/R from Anta but tripped from RAPP end due to A/R problem on Y-N fault. FLR:Anta-10.87km, RAPP-73.4km | [9 empty] | #REF!
[5 empty] | -- | 2017-02-22 10:45 | 2017-02-22 13:37 | -- | -- |  | 0.11944 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for Flashover insulator(Y-ph) replacement at loc-210. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.11944 | 0.089583 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 87.544 | 11468.264 | 11419.3418 | 99.5734 |  | #REF! | #REF!
5 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 102.164 | 13485.648 | 13485.648 | 100 |  | #REF! | #REF!
6 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 35.353 | 4631.243 | 4631.243 | 100 |  | #REF! | #REF!
7 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 20.109 | 2634.279 | 2634.279 | 100 |  | #REF! | #REF!
8 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 20.109 | 2634.279 | 2634.279 | 100 |  | #REF! | #REF!
9 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 22.478 | 2944.618 | 2944.618 | 100 |  | #REF! | #REF!
10 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 15.69 | 2055.39 | 2055.39 | 100 |  | #REF! | #REF!
11 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 15.69 | 2055.39 | 2055.39 | 100 |  | #REF! | #REF!
12 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 17.691 | 2317.521 | 2317.521 | 100 |  | #REF! | #REF!
13 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 17.691 | 2317.521 | 2317.521 | 100 |  | #REF! | #REF!
14 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 131 | 24.875 | 3258.625 | 3258.625 | 100 |  | #REF! | #REF!
15 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 131 | 12 | 1572 | 1572 | 100 |  | #REF! | #REF!
16 | NR122015 | 220KV HISAR-HISAR I/A-I | 132 | NR1 | -- | 2017-02-27 10:51 | 2017-02-27 17:32 |  |  |  | 0 | 0 | 0 | 0.27847 |  |  |  | OSPD | S/D by HVPNL to dismantle the old CB at their end. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0.27847 | [6 empty] | 672 | 132 | 13.77 | 1817.64 | 1817.64 | 100 |  | #REF! | #REF!
17 | NR122015 | 220KV HISAR-HISAR I/A-II | 132 | NR1 | -- | 2017-02-27 10:51 | 2017-02-27 17:35 |  |  |  | 0 | 0 | 0 | 0.28056 |  |  |  | OSPD | S/D by HVPNL to dismantle the old CB at their end. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0.28056 | [6 empty] | 672 | 132 | 13.77 | 1817.64 | 1817.64 | 100 |  | #REF! | #REF!
18 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 28.02 | 3698.64 | 3698.64 | 100 |  | #REF! | #REF!
19 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 2.316 | 305.712 | 305.712 | 100 |  | #REF! | #REF!
20 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 9.254 | 1221.528 | 1221.528 | 100 |  | #REF! | #REF!
21 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 2.316 | 305.712 | 305.712 | 100 |  | #REF! | #REF!
22 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 8.234 | 1086.888 | 1086.888 | 100 |  | #REF! | #REF!
23 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 9.254 | 1221.528 | 1221.528 | 100 |  | #REF! | #REF!
24 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | 2017-02-04 12:02 | 2017-02-04 20:04 |  |  |  | 0.33472 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending hot spot in wave trap jumper . | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.33472 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 128.833 | 16877.123 | 16675.3677 | 98.8046 |  | #REF! | #REF!
25 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 128.833 | 16877.123 | 16877.123 | 100 |  | #REF! | #REF!
26 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | 2017-02-13 21:01 | 2017-02-14 22:00 |  |  |  | 0 | 1899-12-31 00:59 | 0 | 0 |  |  |  | OMSU | CB Auto trip only at RAPPC end on O/current protn due to tripping/ fault in 220KV Kota line pof RRVPNL. Remain charged from RAPPB. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 1899-12-31 00:59 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 131 | 0.175 | 22.925 | 22.925 | 100 |  | #REF! | #REF!
27 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- | 2017-02-08 22:03 | 2017-02-08 22:03 | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | LART | Line Auto reclosed on Y-N fault. FLR:Udipr-28.7KM | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-09 10:45 | 2017-02-09 19:48 |  |  |  | 0 | 0 | 0 | 0.37708 |  |  |  | LCSD | S/D for stringging of 765kv D/C Ajmer- Chittorhgarh Line. | [9 empty] | #REF!
[6 empty] | 2017-02-10 10:30 | 2017-02-10 19:38 |  |  |  | 0 | 0 | 0 | 0.38056 |  |  |  | LCSD | S/D for stringging of 765 kv Ajmer- Chittorhgarh Line (PG) | [9 empty] | #REF!
[6 empty] | 2017-02-28 16:17 | 2017-02-28 17:02 |  |  |  | 0 | 0.03125 | 0 | 0 |  |  |  | OMSU | Line tripped on B-N fault due to A/R relay prob at RAPPB end, FLR-RAPPB-21.83Km, Debari-207.4Km. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.03125 | 0 | 0.75764 | -- | -- | -- |  |  |  | 672 | 131 | 230.297 | 30168.907 | 30168.907 | 100 |  | #REF! | #REF!
28 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 106.243 | 14024.076 | 14024.076 | 100 |  | #REF! | #REF!
29 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- | 2017-02-05 03:32 | 2017-02-05 04:08 | -- | -- | -- | 0 | 0.025 | 0 | 0 | -- | -- | -- | OMSU | Line A/R at Sikar but tripped only from RatanGarh end on R-N fault in RRVPNL portion. FLR-Sikar-46.95KM. | [8 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.025 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 2.83 | 373.56 | 373.56 | 100 |  | #REF! | #REF!
30 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 132 | 2.83 | 373.56 | 373.56 | 100 |  | #REF! | #REF!
31 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- | 2017-02-22 12:20 | 2017-02-22 17:51 | -- | -- |  | 0 | 0 | 0 | 0.22986 | -- | -- | -- | OSPD | S/D by RVPNL for AMP work at their end. | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.22986 | -- | -- | -- |  |  |  | 672 | 132 | 3 | 396 | 396 | 100 |  | #REF! | #REF!
32 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- | 2017-02-23 11:57 | 2017-02-23 17:24 | -- | -- | -- | 0 | 0 | 0 | 0.22708 | -- | -- | -- | OSPD | S/D by RRVPNL for Maintenance work at their end. | [8 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.22708 | -- | -- | -- |  |  |  | 672 | 132 | 3 | 396 | 396 | 100 |  | #REF! | #REF!
[5 empty] | -- | [17 empty] | 1637.99 |  |  |  |  | #REF! | #REF!
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-04 16:14 | 1900-01-01 19:28 | 1900-01-07 21:32 | 1901-04-27 00:06 | [9 empty] | 6723947.382 | 6718334.4311 | 99.9165 |  | #REF! | #REF!
[21 empty] | %'(HVDC) | [6 empty] | #REF! | #REF!
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor |  |  |  | #REF! | #REF!
1 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1500 |  | 1500 | 1500 | 100 |  | #REF! | #REF!
2 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1500 |  | 1500 | 1500 | 100 |  | #REF! | #REF!
3 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1500 |  | 1500 | 1500 | 100 |  | #REF! | #REF!
4 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1500 |  | 1500 | 1500 | 100 |  | #REF! | #REF!
5 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1500 |  | 1500 | 1500 | 100 |  | #REF! | #REF!
6 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 672 | 1500 |  | 1500 | 1500 | 100 |  | #REF! | #REF!
7 | NR2ICT46 | 765/400KV ICT-I BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1000 |  | 1000 | 1000 | 100 |  | #REF! | #REF!
8 | NR2ICT48 | 765/400KV ICT-II BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 1000 |  | 1000 | 1000 | 100 |  | #REF! | #REF!
F |  | 400/220 KV ICT'S |  | NR1 | -- | [22 empty] | #REF! | #REF!
1 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
2 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
3 | NR1ICT68 | 500MVA ICT-III BASSI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
4 | NR1ICT75 | 500MVA ICT-I BAGPAT | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
5 | NR1ICT78 | 500MVA ICT-II BAGPAT | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
6 | NR2ICT08 | 315MVA ICT-I BAHADURGARH | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
7 | NR2ICT42 | 500MVA ICT-II BAHADURGARH | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
8 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
9 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
10 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
11 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
12 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
13 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
14 | NR2ICT49 | 315MVA ICT-I BHIWANI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
15 | NR2ICT50 | 315MVA ICT-II BHIWANI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
16 | NR1ICT71 | 500MVA ICT-I BLBGARH | 315 | NR1 | -- | 2017-02-03 11:16 | 2017-02-03 15:06 |  |  |  | 0.15972 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending hot spot in R-ph isolator contact. | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-12 14:27 | 2017-02-12 15:14 |  |  |  | 0 | 0.032639 | 0 | 0 |  |  |  | OMSU | 220KV CB tripped from BBMB side due to LBB protn mal-operated at BBMB s/yard, remain charged from 400kv side. | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.15972 | 0.032639 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 313.2031 | 99.4296 |  | #REF! | #REF!
17 | NR1ICT79 | 500MVA ICT-II BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
18 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
19 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
20 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
21 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
22 | NR2ICT09 | 315MVA ICT-I HISAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
23 | NR2ICT34 | 315MVA ICT-II HISAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
24 | NR2ICT10 | 315MVA ICT-III HISAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
25 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
26 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
27 | NR2ICT53 | 315MVA ICT-I JIND | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
28 | NR2ICT54 | 315MVA ICT-II JIND | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
29 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
30 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
31 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
32 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
33 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
34 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
35 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
36 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
37 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
38 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
39 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
40 | NR1ICT72 | 315MVA ICT-I MANDOLA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
41 | NR1ICT80 | 500MVA ICT-II MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
42 | NR1ICT73 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
43 | NR1ICT74 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
44 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
45 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
46 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 316 |  | 316 | 316 | 100 |  | #REF! | #REF!
47 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
48 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
49 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
50 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
51 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 500 |  | 500 | 500 | 100 |  | #REF! | #REF!
52 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
53 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
54 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
55 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
56 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
57 | NR1ICT76 | 315MVA ICT-I SAHARANPUR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
58 | NR1ICT77 | 315MVA ICT-II SAHARANPUR | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
59 | NR2ICT36 | 315MVA ICT-I SONIPAT | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
60 | NR2ICT35 | 315MVA ICT-II SONIPAT | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 315 |  | 315 | 315 | 100 |  | #REF! | #REF!
[28 empty] | #REF! | #REF!
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF |  |  | #REF! | #REF!
1 | NR1BRT57 | 125MVAR B/Reactor-I BAGPAT | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
2 | NR1BRT04 | 50MVAR B/Reactor-I BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
3 | NR1BRT53 | 50MVAR B/Reactor-II BASSI | 50 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
4 | NR1BRT54 | 50MVAR B/Reactor-III BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
5 | NR1BRT60 | 125MVAR B/Reactor-IV BASSI | 125 | NR1 | -- | 2017-02-10 11:39 | 2017-02-10 14:12 |  |  |  | 0 | 0 | 0 | 0.10625 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn) | [8 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.10625 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
6 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 80 |  | 80 | 80 | 100 |  | #REF! | #REF!
7 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 80 |  | 80 | 80 | 100 |  | #REF! | #REF!
8 | NR2BRT27 | 240MVAR B/Reactor-I BHIWANI | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
9 | NR2BRT28 | 240MVAR B/Reactor-II BHIWANI | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
10 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 80 |  | 80 | 80 | 100 |  | #REF! | #REF!
11 | NR2BRT03 | 50MVAR B/Reactor HISAR | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
12 | NR2BRT22 | 125MVAR B/Reactor HISAR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
13 | NR1BRT37 | 125MVAR B/Reactor-I JAIPUR(S) | 125 | NR1 | -- | 2017-02-23 11:03 | 2017-02-23 15:57 |  |  |  | 0 | 0 | 0 | 0.20417 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn) | [8 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.20417 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
14 | NR1BRT31 | 240MVAR B/Reactor-I JHATIKALA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
15 | NR1BRT52 | 240MVAR B/Reactor-II JHATIKALA-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
16 | NR2BRT35 | 125MVAR Bus/eactor JIND | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
17 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
18 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
19 | NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- | [15 empty] | 672 | 80 |  | 80 | 80 | 100 |  | #REF! | #REF!
20 | NR1BRT55 | 50MVAR B/Reactor KOTA | 50 | NR1 | -- | [15 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
21 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 80 |  | 80 | 80 | 100 |  | #REF! | #REF!
22 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
23 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
24 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
25 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
26 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 80 |  | 80 | 80 | 100 |  | #REF! | #REF!
27 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI(JPR)-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
28 | NR1BRT48 | 125MVAR B/Reactor-I RATANGARH(RJ) | 125 | NR1 | -- | [15 empty] | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
29 | NR1BRT40 | 125MVAR B/Reactor ROORKI | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | [10 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
30 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 80 |  | 80 | 80 | 100 |  | #REF! | #REF!
31 | NR2BRT13 | 125MVAR B/Reactor SONIPAT | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 125 |  | 125 | 125 | 100 |  | #REF! | #REF!
32 | NR2BRT29 | BHIWANI 240MVAR S/R MEERUT line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
33 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
34 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
35 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh-I LINE | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
[11 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
36 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
37 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
38 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
39 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
40 | NR1BRT58 | 50MVAR B/Reactor-I SAHARANPUR | 50 | NR1 | -- | 2017-02-14 14:49 | 2017-02-14 21:26 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn) | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-16 14:12 | 2017-02-16 20:08 |  |  |  | 0 | 0 | 0 | 0.24722 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn) | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.52292 | [6 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
41 | NR1BRT59 | 50MVAR B/Reactor-II SAHARANPUR | 50 | NR1 | -- | 2017-02-14 14:49 | 2017-02-14 21:26 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn) | [8 empty] | #REF! | #REF!
[6 empty] | 2017-02-16 14:12 | 2017-02-16 20:08 |  |  |  | 0 | 0 | 0 | 0.24722 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn) | [8 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.52292 | [6 empty] | 672 | 50 |  | 50 | 50 | 100 |  | #REF! | #REF!
42 | NR1SRT27 | PHAGI(JPR)240MVAR S/R BHIWANI-I | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
43 | NR1SRT28 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF!
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 672 | 240 |  | 240 | 240 | 100 |  | #REF! | #REF!
[28 empty] | #REF! | #REF!
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 1900-01-01 17:06 | [9 empty] | 5075 | 5075 |  | % | #REF! | #REF!
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L12:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M12:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N12:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O12:[Deemed Available, row above])
Note on C12: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C523: DOC-11-02-15
Note on C582: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14