## SOP DATA FOR NOVEMBER 2018 NR1
Standard of Performance data for the month of NOVEMBER - 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - I
Annexure - A
Sr.No. | S.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[7 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[12 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[12 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 3: 765 KV TRANS LINES | [9 empty] | 0
1 | 1 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | 2018-11-13 20:43 | 2018-11-13 20:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on B-N fault. FLR, Jhtkr-102.63KM/6.4KA | [7 empty] | 720
|  | 7: 2018-11-28 10:35; 8: 2018-11-28 19:07; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.35556 | LCSD | S/D for Diamond formation of earth wire at line crossing for maintaining electrical clearance work ..
|  | 7: 2018-11-28 20:14; 8: 2018-11-28 20:14; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | LART | A/R on B-N fault FLR-Jhatkra-162 km,Agra-84.01 IF-7.72KA.
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.35556 |  |  |  | 720 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
4 | 2 | 2: NR176516; 3: 765KV AJMER-CHITTOR-I; 4: 211.01; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 2470 | 211.01 | 521194.7 | 521194.7 | 100
4 | 3 | 2: NR176517; 3: 765KV AJMER-CHITTOR-II; 4: 211.01; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 2470 | 211.01 | 521194.7 | 521194.7 | 100
2 | 4 | NR176509 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | 2018-11-03 20:42 | 2018-11-05 09:43 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:01 |  |  |  | LVRD | Hand tripped for voltage regulation.Bhiwani=806kv.
|  | 7: 2018-11-05 21:20; 8: 2018-11-06 10:33; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.55069 | LVRD | Hand tripped for voltage regulation.Bhiwani=806kv.
|  | 7: 2018-11-07 20:27; 8: 2018-11-10 09:39; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 13:12 | LVRD | Hand tripped for voltage regulation.Bhiwani=801kv.
|  | 7: 2018-11-11 20:53; 8: 2018-11-12 07:04; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42431 | LVRD | Hand tripped for voltage regulation.Bhiwani=801kv.
|  | 7: 2018-11-13 21:04; 8: 2018-11-14 07:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44375 | LVRD | Hand tripped for voltage regulation.Bhwn-806 KV
|  | 7: 2018-11-17 03:48; 8: 2018-11-17 07:44; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.16389 | LVRD | Hand tripped for voltage regulation.Bwn-801KV
|  | 7: 2018-11-17 21:41; 8: 2018-11-18 08:01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43056 | LVRD | Hand tripped for voltage regulation.Bwn-805KV
|  | 7: 2018-11-18 20:26; 8: 2018-11-19 08:25; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49931 | LVRD | Hand tripped for voltage regulation.Bwn-804KV
|  | 7: 2018-11-20 20:38; 8: 2018-11-21 10:21; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.57153 | LVRD | Hand tripped for voltage regulation.Bwn-805KV
|  | 7: 2018-11-21 21:31; 8: 2018-11-22 09:46; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.51042 | LVRD | Hand tripped for voltage regulation.Bwn-805KV
|  | 7: 2018-11-22 21:06; 8: 2018-11-23 08:31; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47569 | LVRD | Hand tripped for voltage regulation.Bwn-805KV
|  | 7: 2018-11-23 20:36; 8: 2018-11-24 07:22; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44861 | LVRD | Hand tripped for voltage regulation.Bwn-805KV
|  | 7: 2018-11-24 21:04; 8: 2018-11-25 10:03; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54097 | LVRD | Hand tripped for voltage regulation.Bwn-805KV
|  | 7: 2018-11-28 02:20; 8: 2018-11-28 08:07; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.24097 | LVRD | Hand tripped for voltage regulation. Bhiwani-802 KV
|  | 7: 2018-11-28 21:05; 8: 2018-11-29 08:30; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47569 | LVRD | Hand tripped for voltage regulation. Bhiwani-802 KV
|  | 7: 2018-11-29 20:16; 8: 2018-11-30 08:06; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49306 | LVRD | Hand tripped for voltage regulation. Bhiwani-801 KV
|  | 7: 2018-11-30 21:14; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.11528 | LVRD | Hand tripped for voltage regulation. Bhiwani-801 KV
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-09 11:27 |  |  |  | 720 | 1155 | 271.571 | 313664.505 | 313664.505 | 100
3 | 5 | NR176515 | 765KV BHIWANI-PHAGI(JPR)-II | 279.583 | NR1 | -- | 2018-11-07 03:16 | 2018-11-07 07:57 |  |  |  | 0 | 0 | 0 | 0.19514 |  |  |  | LVRD | Hand tripped for voltage regulation.Bhiwani=801kv.
|  | 7: 2018-11-19 21:04; 8: 2018-11-20 07:08; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41944 | LVRD | Hand tripped for voltage regulation.Bwni-805KV
|  | 7: 2018-11-25 20:50; 8: 2018-11-26 08:44; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49583 | LVRD | Hand tripped for voltage regulation.Bwn-805KV
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 02:39 |  |  |  | 720 | 1155 | 279.583 | 322918.365 | 322918.365 | 100
5 | 6 | 2: NR276502; 3: 765KV JHATIKALA-BHIWANI; 4: 85.188; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 2250 | 85.188 | 191673 | 191673 | 100
6 | 7 | NR276503 | 765KV MEERUT-BHIWANI | 173 | NR1 | -- | 2018-11-06 02:08 | 2018-11-06 09:20 |  |  |  | 0 | 0 | 0 | 0.3 |  |  |  | LVRD | Hand tripped for voltage regulation.Bhiwani=806kv.
|  | 7: 2018-11-07 16:19; 8: 2018-11-08 07:20; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.62569 | LVRD | Hand tripped for voltage regulation. Bhiwani-806KV
|  | 7: 2018-11-10 20:56; 8: 2018-11-11 10:06; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54861 | LVRD | Hand tripped for voltage regulation.Bhiwani-801 KV
|  | 7: 2018-11-16 01:15; 8: 2018-11-16 06:59; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.23889 | LVRD | Hand tripped for voltage regulation. Mrt-808 KV
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 17:07 |  |  |  | 720 | 1466 | 173 | 253618 | 253618 | 100
4 | 8 | 2: NR176511; 3: 765KV MEERUT-GR.NOIDA; 4: 119.159; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 1002 | 119.159 | 119397.318 | 119397.318 | 100
7 | 9 | NR276501 | 765KV MOGA-BHIWANI | 273 | NR1 | -- | 2018-11-02 09:28 | 2018-11-02 20:03 |  |  |  | 0 | 0 | 0 | 0.44097 |  |  |  | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-03 08:51; 8: 2018-11-03 19:07; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42778 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-04 10:42; 8: 2018-11-04 19:26; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36389 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-05 09:56; 8: 2018-11-05 19:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40278 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-06 09:36; 8: 2018-11-06 19:31; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41319 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-08 09:01; 8: 2018-11-08 19:09; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42222 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-09 09:01; 8: 2018-11-09 19:22; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43125 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-10 09:03; 8: 2018-11-10 19:05; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41806 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-11 15:06; 8: 2018-11-11 19:25; Hrs:Min 12: 0.17986; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | LEFT | Tripped on R-N fault .FLR-Bhiwani-84.07km, IF-7.5KA,Moga-177.66km.
|  | 7: 2018-11-12 10:57; 8: 2018-11-12 19:44; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36597 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-13 09:03; 8: 2018-11-13 19:34; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43819 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-14 10:21; 8: 2018-11-14 19:04; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36319 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-15 10:02; 8: 2018-11-15 19:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.39236 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-16 09:15; 8: 2018-11-16 19:30; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42708 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-17 08:57; 8: 2018-11-17 19:18; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43125 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-18 09:20; 8: 2018-11-18 18:52; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.39722 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-19 08:52; 8: 2018-11-19 19:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42986 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-21 08:55; 8: 2018-11-21 19:08; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42569 | LCSD | S/D for installation of polymer insulator string in place of disc insulator by NR-2.
|  | 7: 2018-11-23 09:42; 8: 2018-11-23 19:03; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.38958 | LCSD | S/D for polymer insulator replacement and tower strenghthening work by NR-II.
|  | 7: 2018-11-24 09:11; 8: 2018-11-24 18:54; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40486 | LCSD | S/D for polymer insulator replacement and tower strenghthening work by NR-II.
|  | 7: 2018-11-14 00:15; 8: 2018-11-14 00:15; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | LART | A/R on Y-N fault. FLR, Bhiwani-18.56KM/14.16KA
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0.17986; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-06 18:51 |  |  |  | 720 | 1791 | 273 | 488943 | 486011.6056 | 99.4005
B |  | 3: 400 KV TRANS LINES; 6: --
1 | 10 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2018-11-03 19:53 | 2018-11-05 09:03 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 13:10 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-05 20:21; 8: 2018-11-06 09:23; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54306 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-09 20:11; 8: 2018-11-11 10:08; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 13:57 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-11 20:14; 8: 2018-11-12 07:56; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.4875 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-12 20:06; 8: 2018-11-13 09:47; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.57014 | LVRD | Hand tripped for voltage regulation.Agra-431 KV
|  | 7: 2018-11-13 20:03; 8: 2018-11-14 09:38; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.56597 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-15 20:08; 8: 2018-11-16 07:16; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46389 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-17 19:55; 8: 2018-11-19 06:45; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 10:50 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-19 20:37; 8: 2018-11-20 06:50; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42569 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-26 08:50; 8: 2018-11-26 18:18; Hrs:Min 12: 0.39444; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSPT | S/D for insulator cleaning work.
|  | 7: 2018-11-27 08:47; 8: 2018-11-27 19:13; Hrs:Min 12: 0.43472; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSPT | S/D for insulator cleaning work.
|  | 7: 2018-11-29 20:04; 8: 2018-11-30 10:40; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.60833 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-30 20:51; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.13125 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.82917 | 0 | 0 | 1900-01-07 09:03 | -- | -- | -- |  |  |  | 720 | 307 | 253.823 | 77923.661 | 75769.9376 | 97.2361
2 | 11 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2018-11-01 | 2018-11-01 10:24 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Agra-432 KV. Out since 31/10/2018 7:25:00 PM
|  | 7: 2018-11-01 20:54; 8: 2018-11-02 09:34; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.52778 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-02 20:49; 8: 2018-11-03 10:50; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.58403 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-06 21:18; 8: 2018-11-08 07:02; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 09:44 | LVRD | Hand tripped for voltage regulation. Agra-428 KV
|  | 7: 2018-11-15 03:08; 8: 2018-11-15 06:39; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.14653 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-16 19:55; 8: 2018-11-17 08:13; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.5125 | LVRD | Hand tripped for voltage regulation. Agra-428 KV
|  | 7: 2018-11-20 19:25; 8: 2018-11-21 09:42; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.59514 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-21 19:44; 8: 2018-11-22 06:57; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46736 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-22 20:47; 8: 2018-11-23 06:45; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41528 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-23 20:09; 8: 2018-11-24 06:41; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43889 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-24 20:45; 8: 2018-11-26 07:59; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 11:14 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-26 20:07; 8: 2018-11-27 07:25; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47083 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-28 10:00; 8: 2018-11-28 20:11; Hrs:Min 12: 0.42431; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSPT | S/D for insulator cleaning work
|  | 7: 2018-11-28 20:11; 8: 2018-11-29 06:48; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44236 | LVRD | Hand tripped for voltage regulation. Agra-430 KV
|  | 7: 2018-11-29 10:04; 8: 2018-11-29 17:04; Hrs:Min 12: 0.29167; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSPT | S/D for insulator cleaning work
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.71597 | 0 | 0 | 1900-01-06 21:47 | -- | -- | -- |  |  |  | 720 | 307 | 253.823 | 77923.661 | 76063.9551 | 97.6134
3 | 12 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2018-11-01 | 2018-11-01 07:56 | -- | -- | -- | 0 | 0 | 0 | 0.33056 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Agra-431 KV. Out since 31/10/2018 1:23:00 PM
|  | 7: 2018-11-01 21:07; 8: 2018-11-04 08:14; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 11:07 | LVRD | Hand tripped for voltage regulation. Agra-435 KV
|  | 7: 2018-11-04 10:08; 8: 2018-11-04 11:18; Hrs:Min 12: 0.048611; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Forced S/D by Agra to attend R ph isolator hotspot.
|  | 7: 2018-11-06 16:09; 8: 2018-11-07 08:42; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.68958 | LVRD | Hand tripped for voltage regulation. Agra-430 KV
|  | 7: 2018-11-07 22:01; 8: 2018-11-11 07:37; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-02 09:36 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-11 21:15; 8: 2018-11-14 09:40; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 12:25 | LVRD | Hand tripped for voltage regulation. Agra-428 KV
|  | 7: 2018-11-17 19:54; 8: 2018-11-21 10:37; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-02 14:43 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-22 19:40; 8: 2018-11-23 07:52; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.50833 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-23 20:17; 8: 2018-11-24 06:40; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43264 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-25 03:13; 8: 2018-11-26 06:49; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 03:36 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-27 04:08; 8: 2018-11-27 06:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.10764 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-28 00:05; 8: 2018-11-28 00:54; Hrs:Min 12: 0.034028; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | LEFT | Tripped on R-N fault. FLR-Agra-295.00 km /1.955 kA
|  | 7: 2018-11-28 03:45; 8: 2018-11-28 05:47; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.084722 | LVRD | Hand tripped for voltage regulation. Agra-430 KV
|  | 7: 2018-11-28 09:51; 8: 2018-11-28 20:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43056 | LCSD | S/D for installation of polymer insulator string.
|  | 7: 2018-11-28 20:11; 8: 2018-11-29 07:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.48056 | LVRD | Hand tripped for voltage regulation. Agra-430 KV
|  | 7: 2018-11-29 08:46; 8: 2018-11-29 19:54; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46389 | LCSD | S/D for installation of polymer insulator string.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.082639 | 0 | 0 | 1900-01-15 16:08 | -- | -- | -- |  |  |  | 720 | 568 | 393.9 | 223735.2 | 223118.8924 | 99.7245
4 | 13 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2018-11-01 13:11 | 2018-11-01 22:42 | -- | -- | -- | 0 | 0 | 0 | 0.39653 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-03 20:34; 8: 2018-11-06 09:09; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 12:35 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-07 03:19; 8: 2018-11-08 06:54; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 03:35 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-11 19:36; 8: 2018-11-12 06:15; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44375 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-14 19:54; 8: 2018-11-16 09:50; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 13:56 | LVRD | Hand tripped for voltage regulation. Agra-428 KV
|  | 7: 2018-11-16 19:54; 8: 2018-11-17 07:19; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47569 | LVRD | Hand tripped for voltage regulation. Agra-428 KV
|  | 7: 2018-11-21 19:43; 8: 2018-11-22 06:55; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46667 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-23 13:13; 8: 2018-11-25 07:48; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 18:35 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-25 20:47; 8: 2018-11-27 09:25; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 12:38 | LVRD | Hand tripped for voltage regulation. Agra-432 KV
|  | 7: 2018-11-27 19:56; 8: 2018-11-28 07:16; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47222 | LVRD | Hand tripped for voltage regulation. Agra-430 KV
|  | 7: 2018-11-29 20:03; 8: 2018-11-30 08:00; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49792 | LVRD | Hand tripped for voltage regulation. Agra-431 KV
|  | 7: 2018-11-30 08:59; 8: 2018-11-30 20:09; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46528 | LCSD | S/D for installation of polymer insulator string.
|  | 7: 2018-11-30 20:09; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.16042 | LVRD | Kept open on VOL/Regulation. Agra=431kv.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 22:24 | -- | -- | -- |  |  |  | 720 | 568 | 393.9 | 223735.2 | 223735.2 | 100
6 | 14 | NR140179 | 400KV AJMER-AJMER(RRVPNL)-I | 65.615 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 65.615 | 45077.505 | 45077.505 | 100
6 | 15 | NR140180 | 400KV AJMER-AJMER(RRVPNL)-II | 65.615 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 65.615 | 45077.505 | 45077.505 | 100
6 | 16 | NR140174 | 400KV BAGHPAT-DEHRADUN | 165 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 165 | 113355 | 113355 | 100
5 | 17 | NR240006 | 400KV BAHADURGRH-BAWANA | 48.981 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 48.981 | 25225.215 | 25225.215 | 100
5 | 18 | NR240102 | 400KV BAHADURGRH-KABULPR | 38.58 | NR1 | -- | 2018-11-24 13:53 | 2018-11-24 13:53 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | LART | Line A/R on B-N fault, FLR-B/Garh-26.3Km, If-7.0KA.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 38.58 | 19868.7 | 19868.7 | 100
7 | 19 | NR240038 | 400KV BAHADURGRH-SONIPAT-I | 53.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 605 | 53.4 | 32307 | 32307 | 100
8 | 20 | NR240039 | 400KV BAHADURGRH-SONIPAT-II | 53.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 27.88 | 20073.6 | 559651.968 | 559651.968 | 100
8 | 21 | NR140187 | 400KV BAMNOLI-TUGHLKBD-I | 53.4 | NR1 | -- | 2018-11-01 | 2018-12-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-29 | -- | -- | -- | OSPD | S/D by DTL for jumper tightening & attending hot spot and further continued by them for replacement of tower at loc-173. Out since 12/10/2018 8:15:00.
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-29 | -- | -- | -- |  |  |  | 720 | 605 | 53.4 | 32307 | 32307 | 100
8 | 22 | NR140188 | 400KV BAMNOLI-TUGHLKBD-II | 53.4 | NR1 | -- | 2018-11-03 03:56 | 2018-11-03 07:40 | -- | -- | -- | 0 | 0 | 0.15556 | 0 | -- | -- | -- | GOVC | Tripped on Over Voltage protection. Tripped only from Bamnoli end.Bamnoli 435KV.
|  | 7: 2018-11-03 20:39; 8: 2018-11-04 17:12; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0.85625; Hrs:Min 15: 0 | GOVC | Tripped on Over Voltage protection. Tripped only from Bamnoli end .Bamnoli 435KV. Over voltage protection relay pronem at Bamnoli.
|  | 7: 2018-11-05 15:33; 8: 2018-11-05 18:41; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.13056 | OSFD | Forced S/D by DTL to attend faulty CVT at Bamnauli.
|  | 7: 2018-11-09 11:36; 8: 2018-11-09 12:25; Hrs:Min 12: 0; Hrs:Min 13: 0.034028; Hrs:Min 14: 0; Hrs:Min 15: 0 | OMSU | Line tripped on R-Y fault, due to VT fuse failure at Bamnoli(DTL) end.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.034028 | 1899-12-31 00:17 | 0.13056 | -- | -- | -- |  |  |  | 695.7167 | 605 | 53.4 | 32307 | 32307 | 100
9 | 23 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 416 | 235 | 97760 | 97760 | 100
10 | 24 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 47.762 | 24597.43 | 24597.43 | 100
11 | 25 | 2: NR140031; 3: 400KV BASSI-HIRAPURA-II; 4: 48.99; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 48.99 | 25229.85 | 25229.85 | 100
12 | 26 | 2: NR140117; 3: 400KV BASSI-JAIPUR(S)-I; 4: 37.164; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 37.164 | 19139.46 | 19139.46 | 100
13 | 27 | 2: NR140127; 3: 400KV BASSI-JAIPUR(S)-II; 4: 37.164; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 37.164 | 19139.46 | 19139.46 | 100
14 | 28 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- | 2018-11-13 08:13 | 2018-11-13 20:00 | -- | -- | -- | 0 | 0 | 0 | 0.49097 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work in S/Y.
|  | 7: 2018-11-14 16:18; 8: 2018-11-14 20:15; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.16458 | LCSD | S/D for polymer insulator replacement work in S/Y.
|  | 7: 2018-11-17 17:42; 8: 2018-11-17 18:05; Hrs:Min 12: 0.015972; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Forced S/D for attending isolator problem at Kotputli.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.015972 | 0 | 0 | 0.65556 | -- | -- | -- |  |  |  | 720 | 247 | 106.153 | 26219.791 | 26205.8314 | 99.9468
17 | 29 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- | 2018-11-30 10:01 | 2018-11-30 20:09 | -- | -- | -- | 0.42222 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for insulator cleaning work
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.42222 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.432 | 33272.784 | 32804.5004 | 98.5926
18 | 30 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.432 | 33272.784 | 33272.784 | 100
15 | 31 | NR140171 | 400KV BASSI-SIKAR-I | 169.8 | NR1 | -- | 2018-11-22 20:34 | 2018-11-23 08:06 | -- | -- | -- | 0 | 0 | 0 | 0.48056 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.48056 | -- | -- | -- |  |  |  | 720 | 515 | 169.8 | 87447 | 87447 | 100
16 | 32 | NR140172 | 400KV BASSI-SIKAR-II | 169.8 | NR1 | -- | 2018-11-01 | 2018-11-01 07:41 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Sikar-426kv. Out since 31/10/2018 7:35:00 PM
|  | 7: 2018-11-06 21:12; 8: 2018-11-07 09:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.51042 | LVRD | Hand tripped for voltage regulation.Bassi-426kv.
|  | 7: 2018-11-07 20:55; 8: 2018-11-08 05:40; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36458 | LVRD | Hand tripped for voltage regulation.Sikar-428kv.
|  | 7: 2018-11-13 21:20; 8: 2018-11-15 07:57; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 10:37 | LVRD | Hand tripped for voltage regulation.Sikar-428KV
|  | 7: 2018-11-21 21:03; 8: 2018-11-22 07:34; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43819 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 01:49 | -- | -- | -- |  |  |  | 720 | 515 | 169.8 | 87447 | 87447 | 100
33 | 33 | 2: N-W40004; 3: 400KV BHINMAL-ZERDA; 4: 142.8; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 272 | 142.8 | 38841.6 | 38841.6 | 100
19 | 34 | 2: NR140032; 3: 400KV BHIWADI-GURGAON; 4: 82.8; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 82.8 | 42642 | 42642 | 100
20 | 35 | NR140033 | 400KV BHIWADI-HISAR-I | 211.547 | NR1 | -- | 2018-11-01 | 2018-11-01 08:46 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. BWD=427kv. Out since 31/10/2018 9:24:00 PM
|  | 7: 2018-11-01 20:57; 8: 2018-11-02 07:19; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43194 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-02 21:13; 8: 2018-11-03 06:46; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.39792 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-03 19:53; 8: 2018-11-05 09:00; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 13:07 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-05 19:52; 8: 2018-11-06 09:00; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54722 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-06 16:33; 8: 2018-11-08 05:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 12:54 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-08 20:53; 8: 2018-11-09 08:59; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.50417 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-13 20:03; 8: 2018-11-14 09:03; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54167 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-19 19:56; 8: 2018-11-20 06:21; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43403 | LVRD | Hand tripped for voltage regulation.Bwd-424KV
|  | 7: 2018-11-20 09:22; 8: 2018-11-20 20:55; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.48125 | LCSD | S/D for polymer insulator replacement in S/Y.
|  | 7: 2018-11-22 20:31; 8: 2018-11-23 06:41; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42361 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-24 20:42; 8: 2018-11-25 07:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45903 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-25 01:41; 8: 2018-11-25 07:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.25139 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-26 21:37; 8: 2018-11-27 09:22; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.48958 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-29 19:14; 8: 2018-11-30 07:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.51528 | LVRD | Hand tripped for voltage regulation. HSR-426 KV
|  | 7: 2018-11-30 20:55; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.12847 | LVRD | Hand tripped for voltage regulation. HSR-426 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 01:19 | -- | -- | -- |  |  |  | 720 | 403 | 211.547 | 85253.441 | 85253.441 | 100
21 | 36 | NR240087 | 400KV BHIWADI-HISAR-II | 144 | NR1 | -- | 2018-11-07 22:05 | 2018-11-09 06:54 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:49 |  |  |  | LVRD | Hand tripped for voltage regulation. Bwd-428 KV
|  | 7: 2018-11-10 20:38; 8: 2018-11-11 10:28; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.57639 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-16 20:44; 8: 2018-11-17 12:32; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.65833 | LVRD | Hand tripped for voltage regulation.Bwd-427KV
|  | 7: 2018-11-20 20:07; 8: 2018-11-21 09:51; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.57222 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-21 19:46; 8: 2018-11-22 10:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.60069 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-24 03:47; 8: 2018-11-24 06:52; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.12847 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  | 7: 2018-11-28 20:52; 8: 2018-11-29 06:52; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41667 | LVRD | Hand tripped for voltage regulation. HSR-426 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 07:41 | -- | -- | -- |  |  |  | 720 | 331 | 144 | 47664 | 47664 | 100
22 | 37 | NR240088 | 400KV BHIWADI-HISAR-III | 144 | NR1 | -- | 2018-11-09 20:09 | 2018-11-10 08:31 |  |  |  | 0 | 0 | 0 | 0.51528 |  |  |  | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-11 20:16; 8: 2018-11-13 09:47; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 13:31 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-17 20:38; 8: 2018-11-19 06:57; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 10:19 | LVRD | Hand tripped for voltage regulation.Bwd-426KV
|  | 7: 2018-11-25 21:00; 8: 2018-11-26 09:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.51875 | LVRD | Hand tripped for voltage regulation. BWD=428kv.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 00:39 | -- | -- | -- |  |  |  | 720 | 331 | 144 | 47664 | 47664 | 100
23 | 38 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- | 2018-11-15 08:30 | 2018-11-15 18:28 | -- | -- | -- | 0 | 0 | 0 | 0.41528 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-16 09:51; 8: 2018-11-16 18:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36458 | LCSD | S/D for polymer insulator replacement work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.77986 | -- | -- | -- |  |  |  | 720 | 515 | 132.428 | 68200.42 | 68200.42 | 100
24 | 39 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2018-11-01 | 2018-11-01 07:47 | -- | -- |  | 0 | 0 | 0 | 0.32431 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Nmrn-430 KV. Out since 31/10/2018 7:13:00 PM
|  | 7: 2018-11-01 20:01; 8: 2018-11-02 07:18; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47014 | LVRD | Hand tripped for voltage regulation. Nmrn-430 KV
|  | 7: 2018-11-02 21:12; 8: 2018-11-03 06:44; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.39722 | LVRD | Hand tripped for voltage regulation. Nmrn-428 KV
|  | 7: 2018-11-03 19:53; 8: 2018-11-04 07:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.48194 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-05 19:51; 8: 2018-11-06 08:59; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54722 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-06 16:06; 8: 2018-11-07 08:28; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.68194 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-08 13:16; 8: 2018-11-09 07:07; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.74375 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-09 13:09; 8: 2018-11-10 06:48; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.73542 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-10 20:16; 8: 2018-11-11 06:26; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42361 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-11 19:34; 8: 2018-11-12 06:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45347 | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-12 20:11; 8: 2018-11-13 09:42; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.56319 | LVRD | Hand tripped for voltage regulation.Nmrn-428 KV
|  | 7: 2018-11-13 19:58; 8: 2018-11-14 09:04; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54583 | LVRD | Hand tripped for voltage regulation.Nmrn-428 KV
|  | 7: 2018-11-14 19:56; 8: 2018-11-15 06:37; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44514 | LVRD | Hand tripped for voltage regulation.Nmrn-428 KV
|  | 7: 2018-11-15 20:03; 8: 2018-11-16 07:05; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45972 | LVRD | Hand tripped for voltage regulation.Nmrn-428 KV
|  | 7: 2018-11-17 20:49; 8: 2018-11-18 07:13; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43333 | LVRD | Hand tripped for voltage regulation.Nmrn-429 KV
|  | 7: 2018-11-18 20:12; 8: 2018-11-19 06:29; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42847 | LVRD | Hand tripped for voltage regulation.Nmrn-431 KV
|  | 7: 2018-11-19 20:30; 8: 2018-11-20 06:20; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40972 | LVRD | Hand tripped for voltage regulation.Bwd-428KV
|  | 7: 2018-11-20 19:21; 8: 2018-11-21 09:41; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.59722 | LVRD | Hand tripped for voltage regulation.Bwd-428KV
|  | 7: 2018-11-21 19:42; 8: 2018-11-22 07:37; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49653 | LVRD | Hand tripped for voltage regulation.Bwd-428KV
|  | 7: 2018-11-22 19:22; 8: 2018-11-23 06:40; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47083 | LVRD | Hand tripped for voltage regulation.Bwd-428KV
|  | 7: 2018-11-23 19:39; 8: 2018-11-24 06:38; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45764 | LVRD | Hand tripped for voltage regulation.Bwd-428KV
|  | 7: 2018-11-24 20:42; 8: 2018-11-25 07:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44792 | LVRD | Hand tripped for voltage regulation.Bwd-428KV
|  | 7: 2018-11-25 14:06; 8: 2018-11-26 06:41; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.69097 | LVRD | Hand tripped for voltage regulation.Bwd-428KV
|  | 7: 2018-11-26 20:02; 8: 2018-11-27 06:58; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45556 | LVRD | Hand tripped for voltage regulation.Bwd-429KV
|  | 7: 2018-11-27 19:49; 8: 2018-11-28 08:01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.50833 | LVRD | Hand tripped for voltage regulation.Bwd-427KV
|  | 7: 2018-11-28 19:44; 8: 2018-11-29 06:35; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45208 | LVRD | Hand tripped for voltage regulation.Bwd-427KV
|  | 7: 2018-11-29 19:13; 8: 2018-11-30 07:31; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.5125 | LVRD | Hand tripped for voltage regulation.Bwd-427KV
|  | 7: 2018-11-30 19:34; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.18472 | LVRD | Hand tripped for voltage regulation.Bwd-427KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-12 19:39 | -- | -- | -- |  |  |  | 720 | 515 | 48.428 | 24940.42 | 24940.42 | 100
25 | 40 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- | 2018-11-04 20:22 | 2018-11-05 08:38 | -- | -- |  | 0 | 0 | 0 | 0.51111 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. BWD=427kv.
|  | 7: 2018-11-07 13:26; 8: 2018-11-08 05:25; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.66597 | LVRD | Hand tripped for voltage regulation. Nmrn=429kv.
|  | 7: 2018-11-16 19:47; 8: 2018-11-17 07:18; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47986 | LVRD | Hand tripped for voltage regulation.Bwd-427 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 15:46 | -- | -- | -- |  |  |  | 720 | 515 | 48.428 | 24940.42 | 24940.42 | 100
26 | 41 | NR240061 | 400KV BHIWANI-BAWANA | 97.415 | NR1 | -- | 2018-11-06 09:58 | 2018-11-06 18:02 | -- | -- |  | 0 | 0 | 0 | 0.33611 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
[12 empty] | 0 | 0 | 0 | 0
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.33611 | -- | -- | -- |  |  |  | 720 | 515 | 97.415 | 50168.725 | 50168.725 | 100
27 | 42 | NR240059 | 400KV BHIWANI-BHIWANI(BBMB) | 33.962 | NR1 | -- | 2018-11-01 10:09 | 2018-11-01 17:20 | -- | -- |  | 0 | 0 | 0 | 0.29931 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-02 10:27; 8: 2018-11-02 18:44; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.34514 | LCSD | S/D for polymer insulator replacement work.
[6 empty] | -- | 2018-11-13 08:03 | 2018-11-13 17:48 | -- | -- |  | 0 | 0 | 0 | 0.40625 | -- | -- | -- | OSPD | S/D by BBMB for AMP work
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 01:13 | -- | -- | -- |  |  |  | 720 | 515 | 33.962 | 17490.43 | 17490.43 | 100
31 | 43 | NR240068 | 400KV BHIWANI-JIND-I | 82.23 | NR1 | -- | 2018-11-03 09:55 | 2018-11-03 17:40 | -- | -- |  | 0 | 0 | 0 | 0.32292 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-10 21:07; 8: 2018-11-11 07:00; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41181 | LVRD | Hand tripped for voltage regulation. Jind-427 KV
|  | 7: 2018-11-15 20:16; 8: 2018-11-16 08:12; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49722 | LVRD | Hand tripped for voltage regulation. Bhiwani=429kv.
|  | 7: 2018-11-27 12:52; 8: 2018-11-27 13:15; Hrs:Min 12: 0.015972; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Line hand tripped due to some chattering noise ovserved in PLCC pannel at Bhiwani end.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.015972 | 0 | 0 | 1899-12-31 05:34 | -- | -- | -- |  |  |  | 720 | 515 | 82.23 | 42348.45 | 42325.9034 | 99.9468
32 | 44 | NR240069 | 400KV BHIWANI-JIND-II | 82.23 | NR1 | -- | 2018-11-11 20:43 | 2018-11-12 07:28 | -- | -- |  | 0 | 0 | 0 | 0.44792 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Jind-427 KV
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.44792 | -- | -- | -- |  |  |  | 720 | 515 | 82.23 | 42348.45 | 42348.45 | 100
32 | 45 | NR240103 | 400KV BHIWANI-KABULPR | 26.64 | NR1 | -- | 2018-11-01 09:34 | 2018-11-01 18:59 | -- | -- |  | 0 | 0 | 0 | 0.39236 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.39236 | -- | -- | -- |  |  |  | 720 | 515 | 26.64 | 13719.6 | 13719.6 | 100
34 | 46 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | 2018-11-03 18:10 | 2018-11-03 18:58 |  |  |  | 0 | 0 | 0 | 0.033333 |  |  |  | LPRD | Hand tripped for power regulation.
|  | 7: 2018-11-19 04:54; 8: 2018-11-19 05:00; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0.0041667; Hrs:Min 15: 0 | GOVC | Tripped on over voltage protection operated at BLBGARH & DT received at Gurgaon. BLB>434KV.
|  | 7: 2018-11-19 05:00; 8: 2018-11-19 06:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.066667 | LVRD | Line kept open for voltage regulation due to high grid voltage.
|  | 7: 2018-11-20 10:22; 8: 2018-11-20 17:29; Hrs:Min 12: 0.29653; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Emergency S/D for replacement of Y-ph CVT at Ballabhgrh.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.29653 | 0 | 0.0041667 | 0.1 | -- | -- | -- |  |  |  | 719.9 | 515 | 42.7 | 21990.5 | 21773.11 | 99.0114
35 | 47 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | 2018-11-21 10:41 | 2018-12-01 |  |  |  | 0 | 0 | 0 | 1900-01-08 13:19 |  |  |  | LCSD | S/D by BLB for Line diversion work. S/D upto 3/12/18.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-08 13:19 | -- | -- | -- |  |  |  | 720 | 691 | 60.68 | 41929.88 | 41929.88 | 100
36 | 48 | NR140138 | 400KV BLBGRH-NAVADA(HVPN) | 12.55 | NR1 | -- | 2018-11-07 04:01 | 2018-11-07 04:05 | -- | -- |  | 0 | 0 | 0.0027778 | 0 | -- | -- | -- | GOVC | Tripped on Over Voltage protection from Blbgrh end only. Blb>432KV
|  | 7: 2018-11-07 04:05; 8: 2018-11-07 05:45; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.069444 | LVRD | Kept open for voltage regulation. Blb-429KV
|  | 7: 2018-11-07 16:01; 8: 2018-11-07 17:25; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0.058333; Hrs:Min 15: 0 | GOVC | Tripped on Over Voltage protection operated at Blbgrh end . Blb>434KV
|  | 7: 2018-11-10 10:55; 8: 2018-11-10 19:52; Hrs:Min 12: 0.37292; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Emergency s/d for replacement of damaged CVT at Ballabhgarh end.
[6 empty] | -- | 2018-11-15 12:51 | 2018-11-15 17:19 | -- | -- |  | 0 | 0 | 0 | 0.18611 | -- | -- | -- | OSFD | S/D by HVPNL to attend R ph Line isolator hotspot at their end.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.37292 | 0 | 0.061111 | 0.25556 | -- | -- | -- |  |  |  | 718.5333 | 691 | 12.55 | 8672.05 | 8564.0316 | 98.7544
38 | 49 | NR140189 | 400KV BLBGRH-TUGHLKBD-I | 27.88 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 27.88 | 19265.08 | 19265.08 | 100
38 | 50 | NR140190 | 400KV BLBGRH-TUGHLKBD-II | 27.88 | NR1 | -- | 2018-11-07 04:01 | 2018-11-07 04:05 | -- | -- |  | 0 | 0 | 0.0027778 | 0 | -- | -- | -- | GOVC | Tripped on Over Voltage protection from Blbgrh end only. Blb>432KV
[6 empty] | -- | 2018-11-07 04:05 | 2018-11-07 07:48 | -- | -- |  | 0 | 0 | 0 | 0.15486 | -- | -- | -- | LVRD | Kept open for voltage regulation. Blb-429KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.0027778 | 0.15486 | -- | -- | -- |  |  |  | 719.9333 | 691 | 27.88 | 19265.08 | 19265.08 | 100
38 | 51 | NR140181 | 400KV CHITTOR-CHITTOR(RVPNL)-I | 48.78 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.78 | 33511.86 | 33511.86 | 100
38 | 52 | NR140182 | 400KV CHITTOR-CHITTOR(RVPNL)-II | 48.78 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 48.78 | 33511.86 | 33511.86 | 100
37 | 53 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- | 2018-11-26 01:57 | 2018-11-26 02:30 | -- | -- |  | 0 | 0.022917 | 0 | 0 | -- | -- | -- | SEFU | Trip due to 400kv Yph CT blast at Noida. S/D taken by UPPCL.
|  | 7: 2018-11-26 02:30; 8: 2018-11-26 08:00; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.22917 | OSFD | S/D by UPPCL for replacement of 400kv Yph CT at G.Noida.
[6 empty] | -- | 2018-11-26 08:00 | 2018-12-01 | -- | -- |  | 0 | 0 | 0 | 1900-01-03 16:00 | -- | -- | -- | OSPD | S/D continued by UPPCL for diversion work for DFCC
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.022917 | 0 | 1900-01-03 21:30 | -- | -- | -- |  |  |  | 720 | 691 | 13.256 | 9159.896 | 9159.896 | 100
38 | 54 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 54.36 | 37562.76 | 37562.76 | 100
39 | 55 | 2: NR140041; 3: 400KV DAD-MANDOLA-I; 4: 46.3; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 691 | 46.3 | 31993.3 | 31993.3 | 100
40 | 56 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | 2018-11-01 | 2018-11-05 17:26 |  |  |  | 0 | 0 | 0 | 1900-01-03 17:26 |  |  |  | LCSD | S/D for installation and commissioning of series reactor at MND. Out since 23/10/2018 9:40:00.
|  | 7: 2018-11-05 17:26; 8: 2018-11-06 12:16; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.78472 | OSPD | S/D extended by NTPC for work in their switch yard, after return of PTW by PGCIL.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-04 12:16 | 0 | 0 | 0 |  |  |  | 720 | 691 | 46.3 | 31993.3 | 31993.3 | 100
41 | 57 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2018-11-19 09:17 | 2018-11-19 15:27 | -- | -- |  | 0 | 0 | 0 | 0.25694 | -- | -- | -- | OSPD | S/D by UPPCL for AMP work.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.25694 | -- | -- | -- |  |  |  | 720 | 515 | 33.098 | 17045.47 | 17045.47 | 100
42 | 58 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | 2018-11-21 09:51 | 2018-11-24 17:11 |  |  |  | 0 | 0 | 0 | 1900-01-02 07:20 |  |  |  | OSPD | S/D by NTPC for pipe dismentling & replacement of CT.
|  | 7: 2018-11-30 20:24; 8: 2018-11-30 22:41; Hrs:Min 12: 0; Hrs:Min 13: 0.095139; Hrs:Min 14: 0; Hrs:Min 15: 0 | OMSU | Trip due to wrong operation during restoration of 400kv Bus-I at DDR/NTPC.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.095139 | 0 | 1900-01-02 07:20 | 0 | 0 | 0 |  |  |  | 720 | 515 | 112.322 | 57845.83 | 57845.83 | 100
43 | 59 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- | 2018-11-01 10:25 | 2018-11-01 13:53 | -- | -- |  | 0 | 0 | 0 | 0.14444 | -- | -- | -- | OSFD | Emergency S/D by BBMB to attend critical hot point of isolator clamp.
|  | 7: 2018-11-11 06:15; 8: 2018-11-11 06:15; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | LART | A/R on R-N fault ,FLR-Dadri-86.65km,IF-2.42KA.
|  | 7: 2018-11-20 09:38; 8: 2018-11-20 17:55; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.34514 | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-26 01:57; 8: 2018-11-26 02:29; Hrs:Min 12: 0; Hrs:Min 13: 0.022222; Hrs:Min 14: 0; Hrs:Min 15: 0 | OMSU | Tripped from DDR-NTPC end only due to local problem during tripping of DDR-G,noida line.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.022222 | 0 | 0.48958 | -- | -- | -- |  |  |  | 720 | 515 | 117 | 60255 | 60255 | 100
39 | 60 | 2: NR140185; 3: 400KV DEHRADUN-ABDULAPUR-I; 4: 89.43; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 89.43 | 61438.41 | 61438.41 | 100
39 | 61 | 2: NR140186; 3: 400KV DEHRADUN-ABDULAPUR-II; 4: 89.43; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 89.43 | 61438.41 | 61438.41 | 100
44 | 62 | NR240026 | 400KV FATEHABAD-HISAR | 88.558 | NR1 | -- | 2018-11-01 | 2018-11-01 10:18 | -- | -- |  | 0 | 0 | 0 | 0.42917 | -- | -- | -- | LVRD | Hand tripped for voltage regulation.Fthbd-422 KV. Out since 31/10/2018 8:11:00 PM
|  | 7: 2018-11-02 22:09; 8: 2018-11-03 07:56; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40764 | LVRD | Hand tripped for voltage regulation.FTBD=426kv.
|  | 7: 2018-11-03 20:09; 8: 2018-11-05 09:20; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 13:11 | LVRD | Hand tripped for voltage regulation.FTBD=426kv.
|  | 7: 2018-11-05 19:49; 8: 2018-11-06 07:44; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49653 | LVRD | Hand tripped for voltage regulation.FTBD=426kv.
|  | 7: 2018-11-06 20:19; 8: 2018-11-09 06:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 10:17 | LVRD | Hand tripped for voltage regulation.FTBD=426kv.
|  | 7: 2018-11-10 20:54; 8: 2018-11-11 05:52; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.37361 | LVRD | Hand tripped for voltage regulation.Hisar-423 KV
|  | 7: 2018-11-11 20:24; 8: 2018-11-12 05:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.37708 | LVRD | Hand tripped for voltage regulation.Hisar-423 KV
|  | 7: 2018-11-12 20:26; 8: 2018-11-13 10:16; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.57639 | LVRD | Hand tripped for voltage regulation.Fthbd-425KV
|  | 7: 2018-11-13 21:15; 8: 2018-11-14 09:42; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.51875 | LVRD | Hand tripped for voltage regulation.Fthbd-430KV
|  | 7: 2018-11-14 21:47; 8: 2018-11-15 08:02; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42708 | LVRD | Hand tripped for voltage regulation.Fthbd-430KV
|  | 7: 2018-11-16 20:52; 8: 2018-11-17 07:21; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43681 | LVRD | Hand tripped for voltage regulation.Fthbd-426KV
|  | 7: 2018-11-18 19:58; 8: 2018-11-19 06:34; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44167 | LVRD | Hand tripped for voltage regulation.Fthbd-426KV
|  | 7: 2018-11-19 20:37; 8: 2018-11-20 06:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41597 | LVRD | Hand tripped for voltage regulation.Fthbd-426KV
|  | 7: 2018-11-20 21:21; 8: 2018-11-21 09:16; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49653 | LVRD | Hand tripped for voltage regulation.Fthbd-424KV
|  | 7: 2018-11-21 21:38; 8: 2018-11-22 08:55; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47014 | LVRD | Hand tripped for voltage regulation.Fthbd-424KV
|  | 7: 2018-11-22 20:25; 8: 2018-11-23 06:45; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43056 | LVRD | Hand tripped for voltage regulation.Fthbd-424KV
|  | 7: 2018-11-23 20:08; 8: 2018-11-24 10:51; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.61319 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-24 20:36; 8: 2018-11-27 07:34; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 10:58 | LVRD | Hand tripped for voltage regulation. Agra-429 KV
|  | 7: 2018-11-27 20:32; 8: 2018-11-28 10:23; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.57708 | LVRD | Hand tripped for voltage regulation. HSR-426 KV
|  | 7: 2018-11-28 20:26; 8: 2018-11-30 08:47; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 12:21 | LVRD | Hand tripped for voltage regulation. FTB-428 KV
|  | 7: 2018-11-30 20:56; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.12778 | LVRD | Hand tripped for voltage regulation. FTB-428 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 13:34 | -- | -- | -- |  |  |  | 720 | 515 | 88.558 | 45607.37 | 45607.37 | 100
45 | 63 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 23.462 | 16118.394 | 16118.394 | 100
46 | 64 | 2: NR140129; 3: 400KV GURGAON-MANESAR-II; 4: 23.462; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 23.462 | 16118.394 | 16118.394 | 100
47 | 65 | NR240015 | 400KV HISAR-BHIWANI(BBMB) | 34.52 | NR1 | -- | 2018-11-12 08:02 | 2018-11-12 18:08 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | OSPD | S/D by BBMB for AMP work
|  | 7: 2018-11-29 10:57; 8: 2018-11-29 18:18; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.30625 | LCSD | S/D for polymer insulator replacement work.
|  | 6: --; 7: 2018-11-30 10:58; 8: 2018-11-30 18:45; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.32431 | LCSD | S/D for polymer insulator replacement work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 01:14 | -- | -- | -- |  |  |  | 720 | 515 | 34.52 | 17777.8 | 17777.8 | 100
28 | 66 | NR240060 | 400KV HISAR-BHIWANI-I | 64.461 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 64.461 | 33197.415 | 33197.415 | 100
29 | 67 | NR240093 | 400KV HISAR-BHIWANI-II | 56.669 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 56.669 | 29184.535 | 29184.535 | 100
30 | 68 | NR240094 | 400KV HISAR-BHIWANI-III | 56.669 | NR1 | -- | 2018-11-05 11:00 | 2018-11-05 17:12 | -- | -- |  | 0 | 0 | 0 | 0.25833 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.25833 | -- | -- | -- |  |  |  | 720 | 515 | 56.669 | 29184.535 | 29184.535 | 100
48 | 69 | NR240016 | 400KV HISAR-KAITHAL-I | 113.12 | NR1 | -- | 2018-11-23 10:40 | 2018-11-23 19:37 |  |  |  | 0 | 0 | 0 | 0.37292 |  |  |  | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-24 10:52; 8: 2018-11-24 17:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.26319 | LCSD | S/D for polymer insulator replacement work.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.63611 | -- | -- | -- |  |  |  | 720 | 605 | 113.12 | 68437.6 | 68437.6 | 100
49 | 70 | NR240044 | 400KV HISAR-KAITHAL-II | 113.12 | NR1 | -- | 2018-11-27 04:58 | 2018-11-27 04:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/R on B-B fault. FLR- Kaithal-58.76 , If- 5.81 KA.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 385 | 113.12 | 43551.2 | 43551.2 | 100
50 | 71 | 2: NR140132; 3: 400KV JHATIKALA-BAMNOLI-I; 4: 6.106; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.106 | 4194.822 | 4194.822 | 100
51 | 72 | 2: NR140133; 3: 400KV JHATIKALA-BAMNOLI-II; 4: 6.106; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.106 | 4194.822 | 4194.822 | 100
52 | 73 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.782 | 4659.234 | 4659.234 | 100
53 | 74 | 2: NR140135; 3: 400KV JHATIKALA-MUNDKA-II; 4: 6.782; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 6.782 | 4659.234 | 4659.234 | 100
56 | 75 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- | 2018-11-01 09:03 | 2018-11-01 20:14 | -- | -- | -- | 0 | 0 | 0 | 0.46597 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-15 08:41; 8: 2018-11-15 19:07; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43472 | LCSD | S/D for polymer insulator replacement work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.90069 | -- | -- | -- |  |  |  | 720 | 225 | 201.2 | 45270 | 45270 | 100
57 | 76 | NR140169 | 400KV KANKROLI-CHITTOR(RJ)-I | 71.03 | NR1 | -- | 2018-11-13 10:19 | 2018-11-13 19:52 |  |  |  | 0 | 0 | 0 | 0.39792 |  |  |  | LCSD | S/D for polymer insulator replacement.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.39792 | -- | -- | -- |  |  |  | 720 | 515 | 71.03 | 36580.45 | 36580.45 | 100
58 | 77 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2018-11-12 09:24 | 2018-11-12 20:58 | -- | -- | -- | 0 | 0 | 0 | 0.48194 | -- | -- | -- | LCSD | S/D for polymer insulator replacement in S/Y.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.48194 | -- | -- | -- |  |  |  | 720 | 515 | 187.965 | 96801.975 | 96801.975 | 100
59 | 78 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- | 2018-11-14 11:16 | 2018-11-14 18:49 | -- | -- |  | 0 | 0 | 0 | 0.31458 | -- | -- | -- | LCSD | S/D for polymer insulator replacement.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.31458 | -- | -- | -- |  |  |  | 720 | 395 | 198.54 | 78423.3 | 78423.3 | 100
60 | 79 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | 2018-11-23 09:19 | 2018-11-23 21:41 |  |  |  | 0 | 0 | 0 | 0.51528 |  |  |  | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-28 12:10; 8: 2018-11-28 12:39; Hrs:Min 12: 0.020139; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSPT | S/D by WR for taking out the L/R for installation of new NIFP system at Zerda
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.020139 | 0 | 0 | 0.51528 | -- | -- | -- |  |  |  | 720 | 236 | 233.707 | 55154.852 | 55117.8268 | 99.9329
61 | 80 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 515 | 179.711 | 92551.165 | 92551.165 | 100
62 | 81 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 309 | 255.56 | 78968.04 | 78968.04 | 100
63 | 82 | 2: NR140062; 3: 400KV KOTA-RAPPC; 4: 50.5; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 50.5 | 26007.5 | 26007.5 | 100
63 | 83 | NR140178 | 400KV KOTA-RAPPD | 55.103 | NR1 | -- | 2018-11-09 07:48 | 2018-11-09 10:21 |  |  |  | 0 | 0 | 0 | 0.10625 |  |  |  | LPRD | Line hand tripped for Power regulation on RLDC instruction.
|  | 7: 2018-11-12 07:28; 8: 2018-11-13 10:18; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 02:50 | LPRD | Line hand tripped for Power regulation on RLDC instruction.
|  | 7: 2018-11-13 17:06; 8: 2018-11-14 09:12; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.67083 | LPRD | Line hand tripped for Power regulation on RLDC instruction.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 21:29 | -- | -- | -- |  |  |  | 720 | 515 | 55.103 | 28378.045 | 28378.045 | 100
64 | 84 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- | 2018-11-17 10:19 | 2018-11-17 10:27 | -- | -- | -- | 0.0055556 | 0 | 0 | 0 | -- | -- | -- | OFST | Hand tripped during S/D of 400KV KOTESHWR-KHEP-II line due to SCADA problem.
[6 empty] | -- | 2018-11-20 10:12 | 2018-11-29 17:24 | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 07:12 | -- | -- | -- | OSPD | S/D by KHEP for AMP work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.0055556 | 0 | 0 | 1900-01-08 07:12 | -- | -- | -- |  |  |  | 720 | 515 | 2.7 | 1390.5 | 1390.2425 | 99.9815
65 | 85 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- | 2018-11-17 11:28 | 2018-11-18 17:19 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 05:51 | -- | -- | -- | OSPD | S/D by KHEP for AMP work.
|  | 7: 2018-11-30 21:30; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.10417 | OSFD | Forced S/D by THDC to avoid Bus fault due to flashover of strung bus insulator at KHEP s/yard.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:21 | -- | -- | -- |  |  |  | 720 | 515 | 2.7 | 1390.5 | 1390.5 | 100
66 | 86 | 2: NR140065; 3: 400KV KOTESHWR-TEHRI-I; 4: 14.463; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 633 | 14.463 | 9155.079 | 9155.079 | 100
67 | 87 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | 2018-11-29 12:22 | 2018-11-29 17:21 |  |  |  | 0.20764 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attend broken R-Phase jumper at Loc.No. 30.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.20764 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 633 | 16.49 | 10438.17 | 10365.9243 | 99.3079
68 | 88 | 2: NR140176; 3: 400KV MORADABD-HAPUR(UP); 4: 106.85; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 106.85 | 55027.75 | 55027.75 | 100
68 | 89 | 2: NR140177; 3: 400KV MURADNGR-HAPUR(UP); 4: 26.65; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 26.65 | 13724.75 | 13724.75 | 100
69 | 90 | NR140165 | 400KV MEERUT-BAGPAT-I | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 70.976 | 36552.64 | 36552.64 | 100
70 | 91 | NR140166 | 400KV MEERUT-BAGPAT-II | 70.976 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 70.976 | 36552.64 | 36552.64 | 100
71 | 92 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
72 | 93 | 2: NR140130; 3: 400KV MEERUT-BAREILLY-II; 4: 66.009; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
73 | 94 | 2: NR140077; 3: 400KV MEERUT-KOTESHWR-I; 4: 178.69; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 678 | 178.69 | 121151.82 | 121151.82 | 100
74 | 95 | 2: NR140099; 3: 400KV MEERUT-KOTESHWR-II; 4: 175.63; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 673 | 175.63 | 118198.99 | 118198.99 | 100
75 | 96 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | 2018-11-08 21:27 | 2018-11-14 09:27 |  |  |  | 0 | 0 | 0 | 1900-01-04 12:00 |  |  |  | LVRD | Hand tripped for voltage regulation. MND-427 KV
|  | 7: 2018-11-16 01:11; 8: 2018-11-16 08:23; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.3 | LVRD | Hand tripped for voltage regulation. MRT=427kv.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 19:12 | 0 | 0 | 0 |  |  |  | 720 | 515 | 59.868 | 30832.02 | 30832.02 | 100
76 | 97 | 2: NR140079; 3: 400KV MEERUT-MND-II; 4: 59.868; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 59.868 | 30832.02 | 30832.02 | 100
77 | 98 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | 2018-11-16 01:11 | 2018-11-16 07:55 |  |  |  | 0 | 0 | 0 | 0.28056 |  |  |  | LVRD | Hand tripped for voltage regulation. MRT=427kv.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.28056 | 0 | 0 | 0 |  |  |  | 720 | 515 | 54.298 | 27963.47 | 27963.47 | 100
78 | 99 | 2: NR140131; 3: 400KV MEERUT-MND-IV; 4: 54.298; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 54.298 | 27963.47 | 27963.47 | 100
79 | 100 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | 2018-11-13 13:43 | 2018-11-13 19:55 |  |  |  | 0 | 0 | 0 | 0.25833 |  |  |  | OSFD | Emergency S/D by UPPCL for attending oil leakage in Y-ph CT at Mzfrngr end.
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; 9: --; 10: --; 11: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.25833 |  |  |  | 720 | 515 | 37.38 | 19250.7 | 19250.7 | 100
80 | 101 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- | 2018-11-29 12:32 | 2018-11-29 18:25 | -- | -- | -- | 0 | 0 | 0 | 0.24514 | -- | -- | -- | OSPD | S/D by RRVPNL for genaral maintenace work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.24514 | -- | -- | -- |  |  |  | 720 | 515 | 76.018 | 39149.27 | 39149.27 | 100
81 | 102 | NR140139 | 400KV NAVADA(HVPN)-GR.NOIDA | 30.15 | NR1 | -- | 2018-11-01 18:53 | 2018-11-01 23:08 | -- | -- | -- | 0 | 0 | 0 | 0.17708 | -- | -- | -- | LPRD | Hand tripped for power regulation.
|  | 7: 2018-11-02 06:36; 8: 2018-11-02 08:54; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.095833 | LPRD | Hand tripped for power regulation.
|  | 7: 2018-11-02 18:21; 8: 2018-11-02 22:56; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.19097 | LPRD | Hand tripped for power regulation.
|  | 7: 2018-11-03 18:18; 8: 2018-11-03 23:03; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.19792 | LPRD | Hand tripped for power regulation.
|  | 7: 2018-11-05 17:46; 8: 2018-11-06 08:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.61181 | LPRD | Hand tripped for power regulation.
|  | 7: 2018-11-16 10:08; 8: 2018-11-23 18:48; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-06 08:40 | OSPD | S/D by UPPCL for diversion of towers due to DFCC work.
|  | 7: 2018-11-23 18:48; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-06 05:12 | LCSD | S/D continued by NHAI for diversion of towers due to DFCC work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 20:26 | -- | -- | -- |  |  |  | 720 | 691 | 30.15 | 20833.65 | 20833.65 | 100
82 | 104 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 67.041 | 34526.115 | 34526.115 | 100
83 |  | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 67.041 | 34526.115 | 34526.115 | 100
84 | 105 | NR140183 | 400KV NIMRANA-BABAI(RRVPNL) | 81 | NR1 | -- | 2018-11-03 13:20 | 2018-11-03 17:49 | -- | -- |  | 0.18681 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for insulator cleaning work by PGCIL
|  | 7: 2018-11-04 10:02; 8: 2018-11-04 11:49; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.074306 | OSFD | Forced S/D by RRVPNL to attend isolator hotspot at Babai S/yard.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.18681 | 0 | 0 | 0.074306 | -- | -- | -- |  |  |  | 720 | 515 | 81 | 41715 | 41455.2469 | 99.3773
85 | 106 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- | 2018-11-01 | 2018-11-01 08:02 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | -- | -- | -- | LVRD | Hand tripped for voltage regulation. Nmrn-430 KV. Out since 31/10/2018 9:10:00 PM
|  | 7: 2018-11-01 19:58; 8: 2018-11-02 07:54; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49722 | LVRD | Hand tripped for voltage regulation. Nmrn-430 KV
|  | 7: 2018-11-02 07:54; 8: 2018-11-02 19:29; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.48264 | LCSD | S/D for polymer insulator replacement work.
|  | 7: 2018-11-02 21:08; 8: 2018-11-03 06:48; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40278 | LVRD | Hand tripped for voltage regulation. Nmrn-428 KV
|  | 7: 2018-11-03 19:49; 8: 2018-11-04 07:23; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.48194 | LVRD | Hand tripped for voltage regulation. Sikar-419 KV
|  | 7: 2018-11-04 20:20; 8: 2018-11-05 08:32; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.50833 | LVRD | Hand tripped for voltage regulation. Sikar-419 KV
|  | 7: 2018-11-05 19:49; 8: 2018-11-06 08:10; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.51458 | LVRD | Hand tripped for voltage regulation. Sikar-419 KV
|  | 7: 2018-11-06 16:04; 8: 2018-11-07 08:23; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.67986 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-07 13:29; 8: 2018-11-08 05:32; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.66875 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-08 13:15; 8: 2018-11-09 07:10; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.74653 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-09 13:06; 8: 2018-11-10 06:49; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.73819 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-10 20:14; 8: 2018-11-11 06:29; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42708 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-11 19:32; 8: 2018-11-12 06:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44375 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-12 20:18; 8: 2018-11-13 09:26; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.54722 | LVRD | Hand tripped for voltage regulation.Nmrn-428 KV
|  | 7: 2018-11-13 20:31; 8: 2018-11-14 09:22; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.53542 | LVRD | Hand tripped for voltage regulation.Nmrn-431 KV
|  | 7: 2018-11-14 19:52; 8: 2018-11-15 07:08; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46944 | LVRD | Hand tripped for voltage regulation.Nmrn-431 KV
|  | 7: 2018-11-15 20:05; 8: 2018-11-16 07:10; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46181 | LVRD | Hand tripped for voltage regulation.Nmrn-431 KV
|  | 7: 2018-11-16 19:52; 8: 2018-11-17 07:16; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.475 | LVRD | Hand tripped for voltage regulation.Nmrn-427 KV
|  | 7: 2018-11-17 20:46; 8: 2018-11-18 07:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43403 | LVRD | Hand tripped for voltage regulation.Nmrn-429 KV
|  | 7: 2018-11-18 20:13; 8: 2018-11-19 06:32; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42986 | LVRD | Hand tripped for voltage regulation.Nmrn-431 KV
|  | 7: 2018-11-19 20:30; 8: 2018-11-20 06:26; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.41389 | LVRD | Hand tripped for voltage regulation.Nmrn-430 KV
|  | 7: 2018-11-20 19:19; 8: 2018-11-21 09:37; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.59583 | LVRD | Hand tripped for voltage regulation.Nmrn-428KV
|  | 7: 2018-11-21 19:40; 8: 2018-11-22 07:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.49097 | LVRD | Hand tripped for voltage regulation.Nmrn-428KV
|  | 7: 2018-11-22 19:24; 8: 2018-11-23 06:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.46667 | LVRD | Hand tripped for voltage regulation.Nmrn-428KV
|  | 7: 2018-11-23 19:42; 8: 2018-11-24 06:35; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45347 | LVRD | Hand tripped for voltage regulation.Nmrn-428KV
|  | 7: 2018-11-24 20:40; 8: 2018-11-25 07:24; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.44722 | LVRD | Hand tripped for voltage regulation.Nmrn-428KV
|  | 7: 2018-11-25 14:07; 8: 2018-11-26 06:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.69167 | LVRD | Hand tripped for voltage regulation.Nmrn-428KV
|  | 7: 2018-11-26 20:01; 8: 2018-11-27 06:56; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45486 | LVRD | Hand tripped for voltage regulation.Nmrn-429KV
|  | 7: 2018-11-27 19:46; 8: 2018-11-28 07:58; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.50833 | LVRD | Hand tripped for voltage regulation.Nmrn-427KV
|  | 7: 2018-11-28 19:47; 8: 2018-11-29 06:38; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45208 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-29 19:10; 8: 2018-11-30 07:34; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.51667 | LVRD | Hand tripped for voltage regulation. Sikar-426 KV
|  | 7: 2018-11-30 19:34; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.18472 | LVRD | Hand tripped for voltage regulation. Sikar-426 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 22:56 | -- | -- | -- |  |  |  | 720 | 515 | 175.859 | 90567.385 | 90567.385 | 100
86 | 107 | 2: NR140170; 3: 400KV RAPPC-CHITTOR(RJ)-I; 4: 155.15; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 515 | 155.15 | 79902.25 | 79902.25 | 100
90 | 108 | 2: NR140175; 3: 400KV ROORKEE -DEHRADUN; 4: 79.7; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 79.7 | 54753.9 | 54753.9 | 100
87 | 109 | NR140161 | 400KV ROORKI-KASHIPUR-I | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 150.832 | 103621.584 | 103621.584 | 100
88 | 110 | NR140162 | 400KV ROORKI-KASHIPUR-II | 150.832 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 150.832 | 103621.584 | 103621.584 | 100
89 | 111 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | 2018-11-10 01:38 | 2018-11-10 02:00 |  |  |  | 0 | 0.015278 | 0 | 0 |  |  |  | OMSU | Line tripped on R-N fault in UPPCL portion, FLR-RRK-68.6Km, If-5.9KA.
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.015278 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.1 | 1081.5 | 1081.5 | 100
91 | 112 | 2: NR140087; 3: 400KV ROORKI-RISHIKESH; 4: 2.1; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 515 | 2.1 | 1081.5 | 1081.5 | 100
92 | 113 | NR140167 | 400KV ROORKI-SAHARANPUR-I | 36.535 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 687 | 36.535 | 25099.545 | 25099.545 | 100
92 | 114 | NR140184 | 400KV SIKAR-BABAI(RRVPNL) | 94.43 | NR1 | -- | 2018-11-01 09:58 | 2018-11-01 17:03 | -- | -- | -- | 0 | 0 | 0 | 0.29514 | -- | -- | -- | LCSD | S/D for polymer insulator replacement work.
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.29514 | -- | -- | -- |  |  |  | 720 | 515 | 94.43 | 48631.45 | 48631.45 | 100
94 | 115 | 2: NR140155; 3: 400KV SIKAR-RATANGARH-I; 4: 76.48; 5: NR1; 7: 2018-11-01; 8: 2018-11-01 07:03; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.29375 | LVRD | Hand tripped for voltage regulation. Rtngrh-425 KV. Out since 31/10/2018 7:41:00 PM
|  | 7: 2018-11-01 13:12; 8: 2018-11-02 06:21; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.71458 | LVRD | Hand tripped for voltage regulation. Rtngrh-425 KV
|  | 7: 2018-11-04 15:27; 8: 2018-11-06 06:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 15:00 | LVRD | Hand tripped for voltage regulation. Rtngrh-425 KV
|  | 7: 2018-11-07 21:41; 8: 2018-11-08 06:32; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36875 | LVRD | Hand tripped for voltage regulation.Sikar-428kv.
|  | 7: 2018-11-08 15:57; 8: 2018-11-09 05:35; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.56806 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-09 20:18; 8: 2018-11-10 06:29; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42431 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-10 14:10; 8: 2018-11-11 06:02; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.66111 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-11 14:06; 8: 2018-11-12 06:05; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.66597 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-12 19:25; 8: 2018-11-13 05:40; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.42708 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-13 19:17; 8: 2018-11-14 06:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47153 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-14 16:16; 8: 2018-11-15 06:24; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.58889 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-16 18:49; 8: 2018-11-18 06:29; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 11:40 | LVRD | Hand tripped for voltage regulation. Sikar-416 KV
|  | 7: 2018-11-18 15:25; 8: 2018-11-19 05:32; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.58819 | LVRD | Hand tripped for voltage regulation. Sikar-426 KV
|  | 7: 2018-11-19 16:51; 8: 2018-11-20 06:45; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.57917 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-22 16:12; 8: 2018-11-23 06:27; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.59375 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-23 19:52; 8: 2018-11-25 09:07; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 13:15 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-25 21:07; 8: 2018-11-26 05:46; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36042 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-26 20:15; 8: 2018-11-27 05:58; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40486 | LVRD | Hand tripped for voltage regulation. Sikar-426 KV
|  | 7: 2018-11-27 18:09; 8: 2018-11-28 06:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.50139 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-28 20:24; 8: 2018-11-29 06:10; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40694 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-29 19:10; 8: 2018-11-30 06:31; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.47292 | LVRD | Hand tripped for voltage regulation. Sikar-426 KV
|  | 7: 2018-11-30 19:49; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.17431 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-12 22:18 | -- | -- | -- |  |  |  | 720 | 515 | 76.48 | 39387.2 | 39387.2 | 100
95 | 116 | 2: NR140156; 3: 400KV SIKAR-RATANGARH-II; 4: 76.48; 5: NR1; 7: 2018-11-02 17:52; 8: 2018-11-03 07:18; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.55972 | LVRD | Hand tripped for voltage regulation. Rtngrh-425 KV
|  | 7: 2018-11-03 15:21; 8: 2018-11-04 06:04; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.61319 | LVRD | Hand tripped for voltage regulation. Sikar-419 KV
|  | 7: 2018-11-06 15:13; 8: 2018-11-07 06:15; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.62639 | LVRD | Hand tripped for voltage regulation.Sikar-425 KV
|  | 7: 2018-11-07 13:28; 8: 2018-11-08 06:45; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.72014 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-08 21:13; 8: 2018-11-09 06:12; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.37431 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-09 13:05; 8: 2018-11-10 06:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.73472 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-10 20:43; 8: 2018-11-11 05:55; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.38333 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-11 20:17; 8: 2018-11-12 07:08; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45208 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-12 21:02; 8: 2018-11-13 05:41; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.36042 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-13 19:47; 8: 2018-11-14 06:37; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45139 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-15 17:08; 8: 2018-11-16 06:36; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.56111 | LVRD | Hand tripped for voltage regulation. Sikar-425 KV
|  | 7: 2018-11-17 17:07; 8: 2018-11-18 09:54; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.69931 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-18 19:50; 8: 2018-11-19 05:33; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40486 | LVRD | Hand tripped for voltage regulation. Sikar-426 KV
|  | 7: 2018-11-19 20:23; 8: 2018-11-20 06:46; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.43264 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-20 19:23; 8: 2018-11-21 06:18; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45486 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-21 19:47; 8: 2018-11-22 06:47; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45833 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-24 20:25; 8: 2018-11-26 06:34; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 10:09 | LVRD | Hand tripped for voltage regulation. Sikar-431 KV
|  | 7: 2018-11-26 13:12; 8: 2018-11-27 05:59; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.69931 | LVRD | Hand tripped for voltage regulation. Sikar-422 KV
|  | 7: 2018-11-27 20:29; 8: 2018-11-28 06:12; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.40486 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-28 19:14; 8: 2018-11-29 06:15; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.45903 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  | 7: 2018-11-29 20:01; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 03:59 | LVRD | Hand tripped for voltage regulation. Sikar-424 KV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-11 10:32 | -- | -- | -- |  |  |  | 720 | 515 | 76.48 | 39387.2 | 39387.2 | 100
117
220KV LINES
1 | 118 | 2: NR122001; 3: 220KV ANTA-BHIL-I; 4: 186.667; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 186.667 | 24640.044 | 24640.044 | 100
2 | 119 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | 2018-11-16 23:10 | 2018-11-16 23:10 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on R-N fault. FLR, Anta-44.5KM/3.18KA, Bhil-173.4KM/1.5KA
|  | 7: 2018-11-18 09:52; 8: 2018-11-18 15:52; Hrs:Min 12: 0.25; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Emergency S/D by Kota for replacement of flash over R-Phase jumper at Loc.no.140
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.25 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 186.667 | 24640.044 | 24434.7103 | 99.1667
3 | 120 | NR122046 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- | 2018-11-16 10:25 | 2018-11-16 15:30 | -- | -- | -- | 0 | 0 | 0 | 0.21181 | -- | -- | -- | OSPD | S/D by RRVPNL for AMP work.
|  | 7: 2018-11-21 12:25; 8: 2018-11-21 13:48; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.057639 | OSPD | S/D by RRVPNL for installation of Busbar scheme.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.26944 | -- | -- | -- |  |  |  | 720 | 132 | 180.287 | 23797.884 | 23797.884 | 100
4 | 121 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- | 2018-11-02 22:10 | 2018-11-02 22:10 | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | LART | A/R on R-N fault.FLR-RAPPC-42.85km,IF-3.12KA
|  | 7: 2018-11-03 13:52; 8: 2018-11-03 17:55; Hrs:Min 12: 0.16875; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Emergency S/D by PGCIL for replacement of faulty R phase polymer insulator.
|  | 7: 2018-11-09 06:04; 8: 2018-11-09 06:04; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | LART | Line A/R on Y-N fault, FLR-RAPPC- 64.5Km, Anta-19.81Km,
|  | 7: 2018-11-10 10:59; 8: 2018-11-10 17:07; Hrs:Min 12: 0.25556; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | S/d for replacement of damage insulator at Loc.No-184.
|  | 7: 2018-11-27 06:23; 8: 2018-11-27 06:23; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | LART | Line A/R at R-N fault. FLR- RAPPC- 64.2 km/2.34 kA, Anta-21 km.
|  | 7: 2018-11-29 15:07; 8: 2018-11-29 19:04; Hrs:Min 12: 0.16458; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | S/D for replacement of flash over insulator string.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.58889 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 87.544 | 11468.264 | 11243.1462 | 98.037
5 | 122 | 2: NR122005; 3: 220KV ANTA-S.MDHPR; 4: 102.164; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 102.164 | 13485.648 | 13485.648 | 100
6 | 123 | 2: NR122008; 3: 220KV BASSI-BAGRU; 4: 35.353; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 35.353 | 4631.243 | 4631.243 | 100
7 | 124 | 2: NR122009; 3: 220KV BASSI-DAUSA-I; 4: 20.109; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100
8 | 125 | 2: NR122010; 3: 220KV BASSI-DAUSA-II; 4: 20.109; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 20.109 | 2634.279 | 2634.279 | 100
9 | 126 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | 2018-11-23 10:19 | 2018-11-23 19:00 |  |  |  | 0 | 0 | 0 | 0.36181 |  |  |  | LCSD | S/D for polymer insulator replacement work.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.36181 | -- | -- | -- |  |  |  | 720 | 131 | 22.478 | 2944.618 | 2944.618 | 100
10 | 127 | 2: BILHY2201; 3: 220KV FGPP-PALLA-I; 4: 15.69; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 15.69 | 2055.39 | 2055.39 | 100
11 | 128 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[9 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 15.69 | 2055.39 | 2055.39 | 100
12 | 129 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 17.691 | 2317.521 | 2317.521 | 100
13 | 130 | 2: BILHY2204; 3: 220KV FGPP-SPUR-II; 4: 17.691; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 17.691 | 2317.521 | 2317.521 | 100
14 | 131 | 2: NR122014; 3: 220KV HIRAPURA-IG NAGAR; 4: 24.875; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  | 3: SUB TOTAL; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 131 | 24.875 | 3258.625 | 3258.625 | 100
15 | 132 | 2: NR122015; 3: 220KV HIRAPURA-SANGANER; 4: 12; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  | 3: SUB TOTAL; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 131 | 12 | 1572 | 1572 | 100
16 | 133 | 2: NR222004; 3: 220KV HISAR-HISAR I/A-I; 4: 132; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 132 | 13.77 | 1817.64 | 1817.64 | 100
17 | 134 | NR222005 | 220KV HISAR-HISAR I/A-II | 132 | NR1 | -- | 2018-11-01 15:08 | 2018-11-01 16:12 |  |  |  | 0 | 0.044444 | 0 | 0 |  |  |  | OMSU | A/R at Hissar(PG) but tripped from Hissar(IA) HVPN end due to non A/reclose on B-N fault. Hissar(PG)-4.8KM,IF-11.4 KA.
|  | 7: 2018-11-02 10:58; 8: 2018-11-02 13:30; Hrs:Min 12: 0.10556; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | S/D for replacement of B-phase flash over insulator at Loc.no-30
[12 empty] | 0 | 0 | 0 | 0
|  | 3: SUB TOTAL; 6: --; Hrs:Min 12: 0.10556; Hrs:Min 13: 0.044444; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 132 | 13.77 | 1817.64 | 1811.2446 | 99.6481
18 | 135 | 2: NR122047; 3: 220KV LALSOT-DAUSA; 4: 28.02; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 28.02 | 3698.64 | 3698.64 | 100
19 | 136 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 2.316 | 305.712 | 305.712 | 100
20 | 137 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 9.254 | 1221.528 | 1221.528 | 100
21 | 138 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- | 2018-11-02 13:35 | 2018-11-02 15:42 | -- | -- | -- | 0 | 0 | 0 | 0.088194 | -- | -- | -- | OSFD | Emergency S/D by UPPCL to attend Hot-spot at Nara end.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.088194 | -- | -- | -- |  |  |  | 720 | 132 | 2.316 | 305.712 | 305.712 | 100
22 |  | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 8.234 | 1086.888 | 1086.888 | 100
23 | 139 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- | 2018-11-25 11:23 | 2018-11-25 13:40 |  |  |  | 0 | 0.095139 | 0 | 0 |  |  |  | SBBU | Tripped on Busbar protn opted at Simbholi/UPPCL.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.095139 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 9.254 | 1221.528 | 1221.528 | 100
24 | 140 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | 2018-11-06 09:03 | 2018-11-06 17:12 |  |  |  | 0.33958 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for replacement of snapped conductor at loc-07.
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.33958 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 128.833 | 16877.123 | 16686.0833 | 98.8681
25 | 141 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | 2018-11-01 08:30 | 2018-11-02 20:28 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:58 |  |  |  | OSPD | S/D by RRVPNL for AMP.
|  | 7: 2018-11-14 11:38; 8: 2018-11-14 17:38; Hrs:Min 12: 0.25; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Forced S/D for replacement of B ph CVT at Chittaurgrh.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.25 | 0 | 0 | 1899-12-31 11:58 | -- | -- | -- |  |  |  | 720 | 131 | 128.833 | 16877.123 | 16736.4803 | 99.1667
26 | 142 | 2: NR122029; 3: 220KV RAPPB-RAPPC; 4: 0.175; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 131 | 0.175 | 22.925 | 22.925 | 100
27 | 143 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- | 2018-11-03 09:45 | 2018-11-04 20:00 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 10:15 | -- | -- | -- | OSPD | S/D by RAPPB with main Bus-II for maintenance work.
|  | 7: 2018-11-05 21:45; 8: 2018-11-05 22:10; Hrs:Min 12: 0; Hrs:Min 13: 0.017361; Hrs:Min 14: 0; Hrs:Min 15: 0 | OMSU | A/R at RAPB & trip from udaipur/RRVPNL end due to A/R relay problem at RRVPNL due to B-N fault. RAPB=53.81km.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.017361 | 0 | 1899-12-31 10:15 | -- | -- | -- |  |  |  | 720 | 131 | 230.297 | 30168.907 | 30168.907 | 100
28 | 144 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | 2018-11-14 11:05 | 2018-11-14 13:35 |  |  |  | 0 | 0 | 0 | 0.10417 |  |  |  | OSPD | S/D by RRVPNL for AMP work at their end.
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.10417 | -- | -- | -- |  |  |  | 720 | 132 | 106.243 | 14024.076 | 14024.076 | 100
29 | 145 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 2.83 | 373.56 | 373.56 | 100
30 | 146 | 2: NR122044; 3: 220KV SIKAR-RATANGARH-II; 4: 2.83; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 2.83 | 373.56 | 373.56 | 100
31 | 147 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- | 2018-11-14 09:08 | 2018-11-14 19:13 | -- | -- |  | 0.42014 | 0 | 0 | 0 | -- | -- | -- | OSFT | Forced S/D by Powergrid to attend CT & isolator connector hotspot
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.42014 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 3 | 396 | 390.4542 | 98.5995
32 | 148 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- | 2018-11-13 11:14 | 2018-11-13 18:37 | -- | -- | -- | 0.30764 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for attending hot spot in CT & isolator terminal connector at POWERGRID end
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.30764 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 132 | 3 | 396 | 391.9392 | 98.9745
1637.99 | bar: 6
|  | 2: Lines; 3: TOTAL FOR T/LS; Hrs:Min 12: 1900-01-10 05:26; Hrs:Min 13: 0.69306; Hrs:Min 14: 1900-01-01 03:50; Hrs:Min 15: 1901-06-10 17:10 | [6 empty] | 8679939.025 | 8670400.278 | 99.8901
%'(HVDC)
E |  | 3: 765/400 KV ICT'S; 6: -- |  |  |  |  | MVA |  | Weitage Factor
1 | 149 | NR1ICT86 | 765/400KV ICT-I AJMER | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
1 | 150 | NR1ICT87 | 765/400KV ICT-II AJMER | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
7 | 151 | NR2ICT46 | 765/400KV ICT-I BHIWANI | 1500 | NR1 |  | 2018-11-15 09:23 | 2018-11-15 21:21 |  |  |  | 0 | 0 | 0 | 0.49861 | -- | -- | -- | SCSD | S/D for polymer insulator replacement in s/yard.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.49861 | -- | -- | -- |  |  |  | 720 | 1000 |  | 1000 | 1000 | 100
8 | 152 | NR2ICT48 | 765/400KV ICT-II BHIWANI | 1500 | NR1 |  | 2018-11-16 09:44 | 2018-11-16 20:07 |  |  |  | 0 | 0 | 0 | 0.43264 | -- | -- | -- | SCSD | S/D for polymer insulator replacement in S/Y.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.43264 | -- | -- | -- |  |  |  | 720 | 1000 |  | 1000 | 1000 | 100
8 | 153 | NR1ICT88 | 765/400KV ICT-I CHITTORGRH | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1000 |  | 1000 | 1000 | 100
8 | 154 | NR1ICT89 | 765/400KV ICT-II CHITTORGRH | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1000 |  | 1000 | 1000 | 100
1 | 155 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
2 | 156 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
3 | 157 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
4 | 158 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
5 | 159 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | 2018-11-06 12:51 | 2018-11-06 13:35 |  |  |  | 0 | 0 | 0 | 0.030556 | -- | -- | -- | LVRD | S/D for tap changing from 12 to 15 for voltage regulation as per NRLDC instruction
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.030556 | -- | -- | -- |  |  |  | 720 | 1500 |  | 1500 | 1500 | 100
6 | 160 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | 2018-11-06 13:37 | 2018-11-06 13:55 |  |  |  | 0 | 0 | 0 | 0.0125 |  |  |  | LVRD | S/D for tap changing from 12 to 15 for voltage regulation as per NRLDC instruction
|  | 7: 2018-11-26 09:20; 8: 2018-11-26 19:03; Hrs:Min 12: 0.40486; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSPT | S/D taken for general maintenance and AMP work.
|  | 7: 2018-11-27 09:33; 8: 2018-11-27 19:18; Hrs:Min 12: 0.40625; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSPT | S/D taken for AMP work and polymer replacement work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.81111 | 0 | 0 | 0.0125 | 0 | 0 | 0 |  |  |  | 720 | 1500 |  | 1500 | 1459.4444 | 97.2963
F | 161 | 3: 400/220 KV ICT'S; 5: NR1; 6: --
4 |  | 2: NR1ICT75; 3: 500MVA ICT-I BAGPAT; 4: 315; 5: NR1; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
5 | 162 | 2: NR1ICT78; 3: 500MVA ICT-II BAGPAT; 4: 315; 5: NR1; 7: 2018-11-27 11:42; 8: 2018-11-27 12:15; Hrs:Min 12: 0.022917; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 | OSFT | Emergency S/D taken for refilling of SF6.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.022917 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 499.6181 | 99.9236
6 | 163 | 2: NR2ICT08; 3: 315MVA ICT-I BAHADURGARH; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
7 | 164 | 2: NR2ICT42; 3: 500MVA ICT-II BAHADURGARH; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 500 |  | 500 | 500 | 100
1 | 165 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | 2018-11-12 10:07 | 2018-11-12 18:49 |  |  |  | 0 | 0 | 0 | 0.3625 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.3625 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
2 | 166 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | 2018-11-17 09:29 | 2018-11-17 19:02 |  |  |  | 0 | 0 | 0 | 0.39792 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.39792 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
3 | 167 | 2: NR1ICT68; 3: 500MVA ICT-III BASSI; 4: 500; 5: NR1; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
8 | 168 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | 2018-11-01 | 2018-11-15 16:54 |  |  |  | 0 | 0 | 0 | 1900-01-13 16:54 |  |  |  | SCSD | S/D continued after Y-ph OLTC chamber failed & Y-ph Bushing damaged. Out since 02-09-2018 16:22:00
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-13 16:54 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
9 | 169 | 2: NR1ICT06; 3: 315MVA ICT-I BHINMAL; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
10 | 170 | 2: NR1ICT07; 3: 315MVA ICT-II BHINMAL; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
11 | 171 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | 2018-11-24 08:14 | 2018-11-24 09:18 |  |  |  | 0 | 0.044444 | 0 | 0 |  |  |  | OMSU | ICT tripped on 220kv bus bar-2 prot. Oprated due to dead line fault by jumpher snaping at loc no 20 of 220KV BHIWADI-KHUSHKHERA-II line.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.044444 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
12 | 172 | 2: NR1ICT09; 3: 315MVA ICT-II BHIWADI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
13 | 173 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | 2018-11-24 08:14 | 2018-11-24 09:43 |  |  |  | 0 | 0.061806 | 0 | 0 |  |  |  | OMSU | ICT tripped on 220kv bus bar-2 prot. Oprated due to dead line fault by jumpher snaping at loc no 20 of 220KV BHIWADI-KHUSHKHERA-II line.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.061806 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
14 | 174 | 2: NR2ICT49; 3: 315MVA ICT-I BHIWANI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
15 | 175 | 2: NR2ICT50; 3: 315MVA ICT-II BHIWANI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
16 | 176 | 2: NR1ICT71; 3: 500MVA ICT-I BLBGARH; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
17 | 177 | 2: NR1ICT79; 3: 500MVA ICT-II BLBGARH; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
18 | 178 | NR1ICT83 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | 2018-11-21 11:53 | 2018-11-21 18:29 |  |  |  | 0.275 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend oil leakage in R ph CVT in 220kv side.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.275 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 312.1125 | 99.0833
19 | 179 | NR1ICT84 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
19 | 180 | NR1ICT81 | 315MVA ICT-I DEHRADUN | 315 | NR1 | -- | 2018-11-13 17:33 | 2018-11-13 17:44 | -- | -- | -- | 0 | 0 | 0 | 0.0076389 | -- | -- | -- | LVRD | S/D for tap changing from 09 to 11 for voltage regulation as per NRLDC instruction
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.0076389 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
19 | 181 | NR1ICT82 | 315MVA ICT-II DEHRADUN | 315 | NR1 | -- | 2018-11-13 17:20 | 2018-11-13 17:25 | -- | -- | -- | 0 | 0 | 0 | 0.0034722 | -- | -- | -- | LVRD | S/D for tap changing from 09 to 11 as per NRLDC instruction
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.0034722 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
20 | 182 | 2: NR1ICT42; 3: 315MVA ICT-I GURGAON; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
21 | 183 | 2: NR1ICT51; 3: 315MVA ICT-II GURGAON; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
21 | 184 | 2: NR1ICT85; 3: 500MVA ICT-III GURGAON; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
21 | 185 | 2: NR1ICT90; 3: 500MVA ICT-III GURGAON; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
22 | 186 | NR2ICT09 | 315MVA ICT-I HISAR | 315 | NR1 | -- | 2018-11-21 10:54 | 2018-11-21 18:59 |  |  |  | 0 | 0 | 0 | 0.33681 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
|  | 7: 2018-11-22 10:38; 8: 2018-11-22 17:25; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.28264 | SCSD | S/D for polymer insulator replacement in S/Y.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.61944 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
23 | 187 | 2: NR2ICT10; 3: 315MVA ICT-II HISAR; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
24 | 188 | 2: NR2ICT34; 3: 315MVA ICT-III HISAR; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
25 | 189 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | 2018-11-26 10:32 | 2018-11-26 17:22 |  |  |  | 0.28472 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.28472 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 495.2546 | 99.0509
26 | 190 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | 2018-11-28 10:30 | 2018-11-28 19:07 |  |  |  | 0.35903 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP work
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.35903 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 494.0162 | 98.8032
26 | 191 | NR1ICT93 | 500MVA ICT-II TUGHLKBD | 500 | NR1 | -- | 2018-11-30 15:26 | 2018-11-30 16:29 |  |  |  | 0.04375 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend abnormal sound in CT wireing.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.04375 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 499.2708 | 99.8542
27 | 192 | 2: NR2ICT53; 3: 315MVA ICT-I JIND; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
28 | 193 | 2: NR2ICT54; 3: 315MVA ICT-II JIND; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
29 | 194 | 2: NR1ICT16; 3: 315MVA ICT-I KANKROLI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
30 | 195 | 2: NR1ICT17; 3: 315MVA ICT-II KANKROLI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
31 | 196 | 2: NR1ICT18; 3: 315MVA ICT-III KANKROLI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 315 |  | 315 | 315 | 100
32 | 197 | 2: NR1ICT21; 3: 315MVA ICT-I KOTA; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 315 |  | 315 | 315 | 100
33 | 198 | 2: NR1ICT22; 3: 315MVA ICT-II KOTA; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 315 |  | 315 | 315 | 100
34 | 199 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | 2018-11-21 11:04 | 2018-11-21 22:43 |  |  |  | 0 | 0 | 0 | 0.48542 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.48542 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
35 | 200 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | 2018-11-22 09:57 | 2018-11-22 22:29 |  |  |  | 0 | 0 | 0 | 0.52222 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.52222 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
36 | 201 | 2: NR1ICT24; 3: 315MVA ICT-I MAHRANIBAG; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
37 | 202 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | 2018-11-27 07:06 | 2018-11-27 09:30 |  |  |  | 0 | 0 | 0 | 0.1 |  |  |  | SPRD | Hand tripped for power regulation .
|  | 7: 2018-11-27 18:10; 8: 2018-11-27 21:43; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.14792 | SPRD | Hand tripped for power regulation .
|  | 7: 2018-11-28 06:46; 8: 2018-11-30 09:28; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 02:42 | SPRD | Transformer hand tripped for Power regulation on RLDC instruction.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:39 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
38 | 203 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | 2018-11-26 18:18 | 2018-11-26 18:50 |  |  |  | 0 | 0 | 0 | 0.022222 |  |  |  | SPRD | Transformer hand tripped for Power regulation on RLDC instruction.
|  | 7: 2018-11-27 07:05; 8: 2018-11-27 12:31; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.22639 | SPRD | Transformer hand tripped for Power regulation on RLDC instruction.
|  | 7: 2018-11-27 18:10; 8: 2018-11-27 21:11; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0.12569 | SPRD | Transformer hand tripped for Power regulation on RLDC instruction.
|  | 7: 2018-11-28 06:47; 8: 2018-11-29 10:19; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 03:32 | SPRD | Transformer hand tripped for Power regulation on RLDC instruction.
|  | 7: 2018-11-29 17:36; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1899-12-31 06:24 | SPRD | Transformer hand tripped for Power regulation on RLDC instruction.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 18:55 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
39 | 204 | 2: NR1ICT46; 3: 500MVA ICT-IV MAHRANIBAG; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
40 | 205 | 2: NR1ICT72; 3: 315MVA ICT-I MANDOLA; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
41 | 206 | 2: NR1ICT80; 3: 500MVA ICT-II MANDOLA; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
42 | 207 | 2: NR1ICT73; 3: 315MVA ICT-III MANDOLA; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
43 | 208 | NR1ICT74 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | 2018-11-09 14:27 | 2018-11-09 17:50 |  |  |  | 0 | 0.14097 | 0 | 0 |  |  |  | OMSU | S/D by DTL for replacement of demage Male-female contact assembly of 220KV line isolator of ICT-4 in their s/yard..
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.14097 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
44 | 209 | 2: NR1ICT58; 3: 500MVA ICT-I MANESAR; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 500 |  | 500 | 500 | 100
45 | 210 | 2: NR1ICT61; 3: 500MVA ICT-II MANESAR; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 500 |  | 500 | 500 | 100
46 | 211 | 2: NR1ICT32; 3: 315MVA ICT-I MEERUT; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 316 |  | 316 | 316 | 100
47 | 212 | 2: NR1ICT33; 3: 315MVA ICT-II MEERUT; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
48 | 213 | 2: NR1ICT34; 3: 315MVA ICT-III MEERUT; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
49 | 214 | 2: NR1ICT69; 3: 500MVA ICT-IV MEERUT; 4: 500; 5: NR1; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 500 |  | 500 | 500 | 100
50 | 215 | 2: NR1ICT35; 3: 315MVA ICT-I MUZFRNGR; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 315 |  | 315 | 315 | 100
51 | 216 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | 2018-11-22 11:17 | 2018-11-22 20:13 |  |  |  | 0.37222 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend isolator hotspot at Nimrana
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.37222 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 493.7963 | 98.7593
52 | 217 | 2: NR1ICT50; 3: 315MVA ICT-II NIMRANA; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 315 |  | 315 | 315 | 100
53 | 218 | 2: NR1ICT36; 3: 315MVA ICT-I ROORKI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
54 | 219 | 2: NR1ICT37; 3: 315MVA ICT-II ROORKI; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
57 | 220 | NR1ICT76 | 315MVA ICT-I SAHARANPUR | 500 | NR1 | -- | 2018-11-28 11:07 | 2018-11-28 17:10 |  |  |  | 0.25208 | 0 | 0 | 0 |  |  |  | OSPT | S/D for the commissioning of transformer impedance relay
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.25208 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 312.3531 | 99.1597
58 | 221 | NR1ICT77 | 315MVA ICT-II SAHARANPUR | 500 | NR1 | -- | 2018-11-29 10:20 | 2018-11-29 16:03 |  |  |  | 0.23819 | 0 | 0 | 0 |  |  |  | OSPT | S/D for the commissioning of transformer impedance relay
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.23819 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 312.499 | 99.206
55 | 222 | 2: NR1ICT56; 3: 315MVA ICT-I SIKAR; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
56 | 223 | 2: NR1ICT52; 3: 315MVA ICT-II SIKAR; 4: 315; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
57 | 224 | 2: NR1ICT91; 3: 500MVA ICT-III SIKAR; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
59 | 225 | 2: NR2ICT36; 3: 315MVA ICT-I SONIPAT; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
60 | 226 | 2: NR2ICT35; 3: 315MVA ICT-II SONIPAT; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 315 |  | 315 | 315 | 100
60 | 227 | 2: NR1ICT92; 3: 500MVA ICT-I TUGHLKBD; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
60 | 228 | NR1ICT93 | 500MVA ICT-II TUGHLKBD | 500 | NR1 | -- | 2018-11-30 15:26 | 2018-11-30 16:29 |  |  |  | 0.04375 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend abnormal sound in CT wireing.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.04375 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 499.2708 | 99.8542
60 | 229 | 2: NR1ICT94; 3: 500MVA ICT-IV TUGHLKBD; 4: 500; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 500 |  | 500 | 500 | 100
TOTAL FOR ICTs
1 | 230 | 2: NR1SVC-01; 3: +400/-300MVAR SVC KANKROLI; 4: 700; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | TOTAL FOR SVC |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 700 |  | 700 | 700 | 100
M |  | 3: Bus & Switch Line Reactor; 6: -- |  |  |  |  | MVAR |  | OHxMVARxMF | THMxMVARxMF
2 | 231 | 2: NR1BRT66; 3: 125MVAR B/Reactor AJMER; 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
2 | 232 | NR1BRT67 | 240MVAR B/Reactor AJMER-765 | 240 | NR1 | -- | 2018-11-27 09:26 | 2018-11-27 21:06 |  |  |  | 0 | 0 | 0 | 0.48611 |  |  |  | SVRD | Hand tripped for voltage regulation. Ajmer- 742 kV
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.48611 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
2 | 233 | NR1SRT31 | 240MVAR S/R AJMER-I Line at CHITTOR | 240 | NR1 | -- | 2018-11-23 07:45 | 2018-11-27 10:47 |  |  |  | 0 | 0 | 0 | 1900-01-03 03:02 |  |  |  | SVRD | Hand tripped for voltage regulation.(Test charge of L/Reactor of Banaskhatha-1 & 2 line )
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 03:02 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
2 | 234 | NR1SRT32 | 240MVAR S/R AJMER-II Line at CHITTOR | 240 | NR1 | -- | 2018-11-23 07:46 | 2018-11-27 10:54 |  |  |  | 0 | 0 | 0 | 1900-01-03 03:08 |  |  |  | SVRD | Hand tripped for voltage regulation.(Test charge of L/Reactor of Banaskhatha-1 & 2 line )
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 03:08 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
1 | 235 | 2: NR1BRT57; 3: 125MVAR B/Reactor-I BAGPAT; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
2 | 236 | NR1BRT04 | 50MVAR B/Reactor-I BASSI | 50 | NR1 | -- | 2018-11-02 09:44 | 2018-11-02 18:46 |  |  |  | 0 | 0 | 0 | 0.37639 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.37639 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
3 | 237 | NR1BRT53 | 50MVAR B/Reactor-II BASSI | 50 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[6 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
4 | 238 | 2: NR1BRT54; 3: 50MVAR B/Reactor-III BASSI; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
5 | 239 | NR1BRT60 | 125MVAR B/Reactor-IV BASSI | 125 | NR1 | -- | 2018-11-03 09:42 | 2018-11-03 18:05 |  |  |  | 0 | 0 | 0 | 0.34931 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.34931 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
6 | 240 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- | 2018-11-08 07:41 | 2018-11-08 14:45 | -- | -- | -- | 0 | 0 | 0 | 0.29444 | -- | -- | -- | SVRD | Hand tripped for voltage regulation on standing instruction<395kv.
[12 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.29444 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
7 | 241 | 2: NR1BRT15; 3: 80MVAR B/Reactor BHIWADI; 4: 80; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 80 |  | 80 | 80 | 100
8 | 242 | 2: NR2BRT27; 3: 240MVAR B/Reactor-I BHIWANI; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
9 | 243 | 2: NR2BRT28; 3: 240MVAR B/Reactor-II BHIWANI; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
10 | 244 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
10 | 245 | NR1BRT68 | 125MVAR B/Reactor CHITTORGRH | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
10 | 246 | NR1BRT69 | 240MVAR B/Reactor CHITTORGRH-765 | 240 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
11 | 247 | NR1BRT63 | 80MVAR B/Reactor-I DEHRADUN | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
11 | 248 | NR2BRT03 | 50MVAR B/Reactor HISAR | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
12 | 249 | NR2BRT22 | 125MVAR B/Reactor HISAR | 125 | NR1 | -- | 2018-11-19 09:20 | 2018-11-19 18:38 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | LCSD | S/D for insulator replacement work.
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.3875 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
13 | 250 | 2: NR1BRT37; 3: 125MVAR B/Reactor-I JAIPUR(S); 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
14 | 251 | 2: NR1BRT62; 3: 125MVAR B/Reactor-II JAIPUR(S); 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 125 |  | 125 | 125 | 100
14 | 252 | 2: NR1BRT31; 3: 240MVAR B/Reactor-I JHATIKALA-765; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100
15 | 253 | 2: NR1BRT52; 3: 240MVAR B/Reactor-II JHATIKALA-765; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
16 | 254 | 2: NR2BRT35; 3: 125MVAR Bus/eactor JIND; 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
17 | 255 | 2: NR1BRT08; 3: 50MVAR B/Reactor KANKROLI; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
17 | 256 | NR1BRT64 | 125MVAR B/Reactor Koteshwr HEP | 125 | NR1 | -- | 2018-11-01 | 2018-11-30 18:39 |  |  |  | 1900-01-28 18:39 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D for attending severe oil leakage from Bushing.
|  | 7: 2018-11-30 18:55; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0.21181; Hrs:Min 14: 0; Hrs:Min 15: 0 | SEFU | Tripped due to insulator string blast of bay isolator at KHEP (The bay belongs to KHEP). Reactor is ready for service.
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 1900-01-28 18:39 | 0.21181 | 0 | 0 | -- | -- | -- |  |  |  | 714.9167 | 125 |  | 125 | 0.046625 | 0.0373
18 | 257 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | 2018-11-08 07:39 | 2018-11-08 14:49 |  |  |  | 0 | 0 | 0 | 0.29861 |  |  |  | SVRD | Hand tripped for voltage regulation on standing instruction<395kv.
[6 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.29861 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
19 | 258 | 2: NR1BRT09; 3: 80MVAR B/Reactor-I KOTA; 4: 80; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 80 |  | 80 | 80 | 100
20 | 259 | 2: NR1BRT55; 3: 50MVAR B/Reactor-II KOTA; 4: 50; 5: NR1; 6: -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
21 | 260 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | 2018-11-23 08:29 | 2018-11-23 18:18 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | SCSD | S/D for polymer insulator replacement in S/Y.
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.40903 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
22 | 261 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- | 2018-11-28 09:39 | 2018-12-01 | -- | -- | -- | 1900-01-01 14:21 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for replacement of 03 no of isolator with new isolator.S/D by 04/12/18
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 1900-01-01 14:21 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 45.6701 | 91.3403
23 | 262 | 2: NR1BRT30; 3: 125MVAR B/Reactor MANESAR; 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0; Hrs:Min 16: 2016-05-20 07:36
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 2016-05-28 18:19 | 0 | 0 |  |  |  | 720 | 125 |  | 125 | 125 | 100
23 | 263 | 2: NR1BRT65; 3: 125MVAR B/Reactor-II MANESAR; 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0; Hrs:Min 16: 2016-05-20 07:36
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 2016-05-28 18:19 | 0 | 0 |  |  |  | 720 | 125 |  | 125 | 125 | 100
24 | 264 | 2: NR1BRT41; 3: 240MVAR B/Reactor-I MEERUT-765; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 2249-03-17 20:14 | 0 | 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100
25 | 265 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 50 |  | 50 | 50 | 100
26 | 266 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
27 | 267 | 2: NR1BRT51; 3: 240MVAR B/Reactor-I PHAGI(JPR)-765; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100
28 | 268 | 2: NR1BRT48; 3: 125MVAR B/Reactor-I RATANGARH(RJ); 4: 125; 5: NR1; 6: -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
29 | 269 | NR1BRT40 | 125MVAR B/Reactor ROORKI | 125 | NR1 | -- | 2018-11-13 11:18 | 2018-11-13 12:39 | -- | -- | -- | 0.05625 | 0 | 0 | 0 | -- | -- | -- | OSFT | Emergency S/D for attending problem in CSD relay
[12 empty] | 0 | 0 | 0 | 0
[6 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.05625 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 124.7656 | 99.8125
40 | 270 | 2: NR1BRT58; 3: 50MVAR B/Reactor-I SAHARANPUR; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100
41 | 271 | 2: NR1BRT59; 3: 50MVAR B/Reactor-II SAHARANPUR; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100
30 | 272 | 2: NR1BRT29; 3: 80MVAR B/Reactor SIKAR; 4: 80; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 80 |  | 80 | 80 | 100
31 | 273 | 2: NR2BRT13; 3: 125MVAR B/Reactor-I SONIPAT; 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
31 | 274 | 2: NR1BRT61; 3: 125MVAR B/Reactor-II SONIPAT; 4: 125; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 125 |  | 125 | 125 | 100
32 | 275 | 2: NR2BRT29; 3: BHIWANI 240MVAR S/R MEERUT line; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100
33 | 276 | 2: NR1SRT06; 3: BHINML 50MVAR S/R KANKROLI; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100
34 | 277 | 2: NR1SRT19; 3: JHATIKALA 240MVAR S/R AGRA Line; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100
35 | 278 | 2: NR1SRT09; 3: MEERUT 50MVAR S/R Kotesh-I LINE; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100
35 | 279 | NR1SRT33 | 330MVAR S/R ALIGARH Line at JHATIKALA | 330 | NR1 | -- | 2018-11-02 11:01 | 2018-11-06 19:15 |  |  |  | 1900-01-03 08:14 | 0 | 0 | 0 |  |  |  | OSFT | Hand tripped due flash over in L/R of B phase pole CB at Jhatikra end
[12 empty] | 0 | 0 | 0 | 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-03 08:14 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 330 |  | 330 | 282.2264 | 85.5231
36 | 280 | 2: NR1SRT10; 3: MEERUT 50MVAR S/R Kotesh Ckt-II; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100
37 | 281 | 2: NR1SRT21; 3: MEERUT 240MVAR S/R AGRA line; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 240 |  | 240 | 240 | 100
38 | 282 | 2: NR1SRT22; 3: SIKAR 50MVAR S/R AGRA Ckt-I; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100
39 | 283 | 2: NR1SRT23; 3: SIKAR 50MVAR S/R AGRA Ckt-II; 4: 50; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0 |  |  |  | 720 | 50 |  | 50 | 50 | 100
42 | 284 | NR1BRT69 | 240MVAR B/Reactor CHITTORGRH-765 | 240 | NR1 | -- | 2018-11-09 09:29 | 2018-11-09 21:56 |  |  |  | 0 | 0 | 0 | 0.51875 |  |  |  | SVRD | Hand tripped for voltage regulation<745kv.
|  | 7: 2018-11-22 12:06; 8: 2018-11-25 00:22; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-01 12:16 | SVRD | Hand tripped for voltage regulation.(Test charge of L/Reactor of Banaskhatha-1 & 2 line )
|  | 7: 2018-11-27 09:24; 8: 2018-12-01; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-02 14:36 | SVRD | Hand tripped for voltage regulation. Chittorgarh- 741 kV
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 15:19 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
42 | 285 | 2: NR1SRT27; 3: PHAGI(JPR)240MVAR S/R BHIWANI-I; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
43 | 286 | 2: NR1SRT28; 3: PHAGI(JPR) 240MVAR S/R BHIWANI-II Line; 4: 240; 5: NR1; 6: --; Hrs:Min 12: 0; Hrs:Min 13: 0; Hrs:Min 14: 0; Hrs:Min 15: 0
|  |  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 720 | 240 |  | 240 | 240 | 100
|  | 3: TOTAL FOR BUS REACTORS; Hrs:Min 12: 1900-03-13 13:10; Hrs:Min 13: 0.42361; Hrs:Min 14: 0; Hrs:Min 15: 1900-01-16 12:10 | [6 empty] | 6590 | 6412.7088 |  | %
Note on D10: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on D462: LILO of Moradabad-Muradnagar by UP at HAPUR
Note on D464: LILO of Moradabad-Muradnagar by UP at HAPUR
Note on D600: DOC-11-02-15
Note on D682: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14
Note on D830: Charged-01.08.17
Note on D832: Charged-01.08.17