## SOP DATA NR1 August-15
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.06.2015 to 30.06.2015
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [17 empty] | NRPC | [6 empty] | 0
1 | NR176505 | 765 KV AGRA- MEERUT | 267.628 | NR1 | -- | 2015-08-19 08:44 | 2015-08-19 19:26 |  |  |  | 0 | 0 | 0 | 0.44583 |  |  |  | OSPD | S/D by UPPCL for crossing of their 765kV Gr. Noida- Mainpuri Line. | [7 empty] | 744
[6 empty] | 2015-08-20 08:08 | 2015-08-20 18:57 |  |  |  | 0 | 0 | 0 | 0.45069 |  |  |  | OSPD | S/D by UPPCL for crossing of their 765kV Gr. Noida- Mainpuri Line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.89653 | [6 empty] | 744 | 1779 | 267.628 | 476110.212 | 476110.212 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR1 | -- | 2015-08-01 12:02 | 2015-08-01 12:29 |  |  |  | 0.01875 | 0 | 0 | 0 |  |  |  | SRET | Tripped due to L/Reactor REF mal-operated at Agra.
[6 empty] | 2015-08-29 13:11 | 2015-08-29 13:22 |  |  |  | 0.0076389 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/Reactor in service at Agra.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.026389 | 0 | 0 | 0 | [6 empty] | 744 | 1779 | 267.628 | 476110.212 | 475704.921 | 99.9149
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR1 | -- | 2015-08-01 08:49 | 2015-08-01 19:22 |  |  |  | 0.43958 | 0 | 0 | 0 |  |  |  | OSPT | S/D for attending hot spot at Loc.649 & jumper tightening.
[6 empty] | 2015-08-06 12:03 | 2015-08-06 14:12 |  |  |  | 0.089583 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending sparking in jumper at loc no. 362.
[6 empty] | 2015-08-15 13:06 | 2015-08-17 10:20 |  |  |  | 0 | 0 | 0 | 1899-12-31 21:14 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-805 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.52917 | 0 | 0 | 1899-12-31 21:14 | [6 empty] | 744 | 1210 | 334.8 | 405108 | 398192.85 | 98.293
4 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
5 | NR176503 | 765KV FATEHPUR-GAYA | 484.6 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1070 | 484.6 | 518522 | 518522 | 100
6 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1067 | 355.008 | 378793.536 | 378793.536 | 100
7 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
8 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR1 | -- | 2015-08-09 13:15 | 2015-08-09 19:04 |  |  |  | 0 | 0.24236 | 0 | 0 |  |  |  | OMSU | Tripped on R-N fault due to Kite thread. FLR:Brly-19km, Lko-231km. Charged after patrolling & removing the kite.
[5 empty] | -- | 2015-08-27 12:30 | 2015-08-27 20:25 |  |  |  | 0 | 0 | 0 | 0.32986 |  |  |  | LCSD | S/D for jumpering and Bus stability test for charging of 765kV ICT-II at Bareilly.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.24236 | 0 | 0.32986 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 256393.647 | 100
9 | NR176508 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1155 | 271.571 | 313664.505 | 313664.505 | 100
B |  | 400 KV TRANS LINES |  |  | --
1 | NR140001 | 400KV AGRA-AGRA(UP)-I | 29.982 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR1 | -- | 2015-08-10 10:29 | 2015-08-10 13:01 | -- | -- | -- | 0.10556 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for L/Reactor faulty bushing replacement at Agra.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10556 | 0 | 0 | 0 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61153.4599 | 99.6595
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR1 | -- | 2015-08-01 02:31 | 2015-08-04 09:54 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 07:23 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Bassi-430 KV
[6 empty] | 2015-08-12 02:31 | 2015-08-14 11:26 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:55 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428kv.
[6 empty] | 2015-08-15 11:55 | 2015-08-15 12:00 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection at Bassi>435kv.
[6 empty] | 2015-08-15 12:00 | 2015-08-23 10:56 |  |  |  | 0 | 0 | 0 | 1900-01-06 22:56 |  |  |  | LVRD | Line kept open for Voltage regulation.Agra-432KV.
[5 empty] | -- | 2015-08-23 18:04 | 2015-08-24 09:38 | -- | -- | -- | 0 | 0 | 0 | 0.64861 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-432 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.0034722 | 1900-01-13 06:48 | [6 empty] | 743.9167 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR1 | -- | 2015-08-12 00:18 | 2015-08-14 11:13 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 10:55 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bhiwadi-428kv.
[6 empty] | 2015-08-14 23:18 | 2015-08-17 09:14 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:56 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-08-18 00:57 | 2015-08-18 14:30 |  |  |  | 0 | 0 | 0 | 0.56458 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-08-19 00:15 | 2015-08-19 09:40 |  |  |  | 0 | 0 | 0 | 0.39236 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-08-21 11:55 | 2015-08-21 15:37 |  |  |  | 0.15417 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend burnt Y-Ph Jumpher hot spot at Bhiwadi.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.15417 | 0 | 0 | 1900-01-04 19:49 | [6 empty] | 744 | 515 | 209.51 | 107897.65 | 107361.0622 | 99.5027
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2015-08-09 09:17 | 2015-08-10 22:19 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 13:02 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-435 KV
[6 empty] | 2015-08-14 17:12 | 2015-08-14 20:27 | -- | -- | -- | 0 | 0 | 0 | 0.13542 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 16:17 | -- | -- | -- |  |  |  | 744 | 307 | 253.823 | 77923.661 | 77923.661 | 100
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2015-08-15 00:39 | 2015-08-17 09:19 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:40 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[5 empty] | -- | 2015-08-19 03:18 | 2015-08-23 12:49 |  |  |  | 0 | 0 | 0 | 1900-01-03 09:31 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 18:11 | -- | -- | -- |  |  |  | 744 | 307 | 253.823 | 77923.661 | 77923.661 | 100
11 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2015-08-01 | 2015-08-04 10:03 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 10:03 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV. Out since 30.07.15 at 0545hrs
[5 empty] | -- | 2015-08-14 17:13 | 2015-08-14 19:54 | -- | -- | -- | 0 | 0 | 0 | 0.11181 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[5 empty] | -- | 2015-08-14 23:14 | 2015-08-18 15:52 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 16:38 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-08-18 17:14 | 2015-08-19 12:33 |  |  |  | 0 | 0 | 0 | 0.80486 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-08-21 08:43 | 2015-08-21 23:15 | -- | -- | -- | 0 | 0 | 0 | 0.60556 | -- | -- | -- | LCSD | S/D for polymer insulator string installation work. (tension)
[6 empty] | 2015-08-23 04:59 | 2015-08-23 11:11 | -- | -- | -- | 0 | 0 | 0 | 0.25833 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-08-23 17:09 | 2015-08-24 09:31 | -- | -- | -- | 0 | 0 | 0 | 0.68194 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-08-29 18:41 | 2015-08-30 13:20 |  |  |  | 0 | 0 | 0 | 0.77708 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-432 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 08:26 | -- | -- | -- |  |  |  | 744 | 568 | 393.9 | 223735.2 | 223735.2 | 100
12 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2015-08-08 03:12 | 2015-08-14 12:26 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 09:14 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-431 KV
[5 empty] | -- | 2015-08-15 12:50 | 2015-08-17 10:43 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 21:53 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Sikar-432 KV
[5 empty] | -- | 2015-08-20 09:09 | 2015-08-20 19:13 | -- | -- | -- | 0 | 0 | 0 | 0.41944 | -- | -- | -- | LCSD | S/D for polymer insulator string installation work. (tension)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 17:11 | -- | -- | -- |  |  |  | 744 | 568 | 393.9 | 223735.2 | 223735.2 | 100
13 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR1 | -- | [15 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
14 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
15 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 155.932 | 80304.98 | 80304.98 | 100
16 | NR140012 | 400KV ALLD-KNP-II | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 224 | 115360 | 115360 | 100
17 | NR140019 | 400KV BALIA-MAU-I | 13 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
18 | NR140020 | 400KV BALIA-MAU-II | 13 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
19 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR1 | -- | 2015-08-07 11:10 | 2015-08-07 15:14 |  |  |  | 0.16944 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking oil sample of bushing of L/R at Sohawal
[6 empty] | 2015-08-27 09:25 | 2015-08-27 18:38 |  |  |  | 0 | 0 | 0 | 0.38403 |  |  |  | LCSD | S/D for OPGW strining work. Diomond ring formation at crossing of 800kv HVDC BNC-Agra line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.16944 | 0 | 0 | 0.38403 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 51735.6623 | 99.4534
20 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR1 | -- | 2015-08-10 16:10 | 2015-08-10 17:25 |  |  |  | 0.052083 | 0 | 0 | 0 |  |  |  | OSPT | S/D for implementation of NGR bypass scheme at Balia.
[6 empty] | 2015-08-24 17:26 | 2015-08-24 19:22 |  |  |  | 0.080556 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending hot spot at loc. 289 by Balia.
[6 empty] | 2015-08-27 09:48 | 2015-08-27 18:38 |  |  |  | 0 | 0 | 0 | 0.36806 |  |  |  | LCSD | S/D for OPGW strining work. Diomond ring formation at crossing of 800kv HVDC BNC-Ahra line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.13264 | 0 | 0 | 0.36806 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 51797.4244 | 99.5721
21 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR1 | -- | [15 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
22 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR1 | [16 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
23 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
24 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR1 | -- | 2015-08-02 12:15 | 2015-08-02 12:38 |  |  |  | 0 | 0.015972 | 0 | 0 |  |  |  | OMSU | CB A/trip at UPPCL end. Line remain charged from Bareilly (PG) end. No flag/facia informed by UPPCL.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.015972 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
25 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR1 | -- | 2015-08-16 17:15 | 2015-08-16 18:29 | -- | -- | -- | 0 | 0 | 0 | 0.051389 | -- | -- | -- | OSPD | S/D by UPPCL for taking L/R out due to low oil level alarm.
[6 empty] | 2015-08-16 22:34 | 2015-08-16 23:13 |  |  |  | 0 | 0.027083 | 0 | 0 |  |  |  | OMSU | Tripped on L/reactor protection relay mal-operated at Lko(UP) end while L/R out of service.
[6 empty] | 2015-08-18 12:41 | 2015-08-18 14:23 |  |  |  | 0 | 0 | 0 | 0.070833 |  |  |  | OSPD | S/D by UPPCL for taking L/R into service at Lucknow(UP).
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.027083 | 0 | 0.12222 | -- | -- | -- |  |  |  | 744 | 331 | 278.76 | 92269.56 | 92269.56 | 100
26 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
27 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR1 | -- | 2015-08-27 13:42 | 2015-08-27 15:40 |  |  |  | 0 | 0.081944 | 0 | 0 |  |  |  | OMSU | Tripped due to Bus protection mal-operation at Moradabad during ICT-II protn testing by UPPCL. D/T recd at Brly.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.081944 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
28 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR1 | -- | 2015-08-25 05:45 | 2015-08-25 10:31 | -- | -- | -- | 0 | 0 | 0 | 0.19861 | -- | -- | -- | LCSD | S/D for OPGW installation work under ULDC scheme.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.19861 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
29 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR1 | [16 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 | 100
30 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR1 |  | 2015-08-03 09:19 | 2015-08-03 20:49 |  |  |  | 0 | 0 | 0 | 0.47917 |  |  |  | LCSD | S/D for Erection of new 400kv Roorki D/C bay equipments at Kashipur(Uttaranchal) end.
[6 empty] | 2015-08-04 09:34 | 2015-08-04 10:05 |  |  |  | 0 | 0.021528 | 0 | 0 |  |  |  | OMSU | Trip on D/T recd at BLY due to wrong operation at Kashipur during isolation of ckt-II for s/d. Bus Protn oprtd.
[6 empty] | 2015-08-11 11:45 | 2015-08-11 16:55 |  |  |  | 0 | 0.21528 | 0 | 0 |  |  |  | OMSU | Tripped due to Sparking/ burning of gantry jumper at Kashipur (Uttaranchal ) end.
[6 empty] | 2015-08-17 12:30 | 2015-08-17 13:22 |  |  |  | 0 | 0.036111 | 0 | 0 |  |  |  | OMSU | Tripped on R-N fault due to kite thread. FLR:Brly-4 km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.27292 | 0 | 0.47917 | -- | -- | -- |  |  |  | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
31 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR1 |  | 2015-08-04 09:34 | 2015-08-04 21:30 |  |  |  | 0 | 0 | 0 | 0.49722 |  |  |  | LCSD | S/D for Erection of new 400kv Roorki D/C bay equipments at Kashipur(Uttaranchal) end.
[6 empty] | 2015-08-11 12:04 | 2015-08-11 16:36 |  |  |  | 0 | 0.18889 | 0 | 0 |  |  |  | OMSU | Line tripped on B-Y fault caused due to Kite thread. Charged after patrolling. FLR:Bareilly-102 km
[6 empty] | 2015-08-19 17:39 | 2015-08-19 18:15 |  |  |  | 0 | 0.025 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-B fault caused due to kite thread. FLR:Brly-16km, Kashipur-80km.
[6 empty] | 2015-08-21 14:03 | 2015-08-21 18:16 |  |  |  | 0.17569 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend hot spot in Y-Ph Jumpher at loc. No. 61A/0.
[6 empty] | 2015-08-28 15:58 | 2015-08-28 22:31 |  |  |  | 0.27292 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend hotspot in R-ph Bus isolator at BLY.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.44861 | 0.21389 | 0 | 0.49722 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 68952.284 | 98.5529
32 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- | 2015-08-03 22:40 | 2015-08-04 18:35 | -- | -- | -- | 0.82986 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D by BASSI for Y-Ph CVT repacement due to secondary winding burnt.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.82986 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 416 | 235 | 97760 | 95142.9928 | 97.323
33 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 47.762 | 24597.43 | 24597.43 | 100
34 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 48.99 | 25229.85 | 25229.85 | 100
35 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- | 2015-08-12 03:55 | 2015-08-12 10:35 | -- | -- | -- | 0 | 0 | 0 | 0.27778 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bassi-425kv
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.27778 | -- | -- | -- |  |  |  | 744 | 515 | 37.164 | 19139.46 | 19139.46 | 100
36 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 37.164 | 19139.46 | 19139.46 | 100
37 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 247 | 106.153 | 26219.791 | 26219.791 | 100
38 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 48.432 | 33272.784 | 33272.784 | 100
39 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 48.432 | 33272.784 | 33272.784 | 100
40 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 82.8 | 42642 | 42642 | 100
41 | NR140033 | 400KV BHIWADI-HISAR | 211.547 | NR1 | -- | 2015-08-08 07:07 | 2015-08-08 20:13 | -- | -- | -- | 0 | 0 | 0 | 0.54583 | -- | -- | -- | LCSD | S/D for stringing of 765kV Bhiwani-Phagi D/C line.
[6 empty] | 2015-08-15 12:42 | 2015-08-18 14:28 |  |  |  | 0 | 0 | 0 | 1900-01-02 01:46 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Bhi-428 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 14:52 | -- | -- | -- |  |  |  | 744 | 403 | 211.547 | 85253.441 | 85253.441 | 100
42 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 132.428 | 68200.42 | 68200.42 | 100
43 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 48.428 | 24940.42 | 24940.42 | 100
44 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- | 2015-08-12 00:24 | 2015-08-17 09:32 | -- | -- |  | 0 | 0 | 0 | 1900-01-04 09:08 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bhiwadi-428kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-04 09:08 | -- | -- | -- |  |  |  | 744 | 515 | 48.428 | 24940.42 | 24940.42 | 100
45 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | 2015-08-25 12:06 | 2015-08-25 15:03 |  |  |  | 0 | 0 | 0 | 0.12292 |  |  |  | LCSD | S/D for jumper opening for isolator retrofitment under Add Cap at BLB end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.12292 | -- | -- | -- |  |  |  | 744 | 515 | 42.7 | 21990.5 | 21990.5 | 100
46 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | 2015-08-21 09:16 | 2015-08-21 14:10 |  |  |  | 0.20417 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend hot spot in Y-Ph line isolator at Blb.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.20417 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 60.68 | 41929.88 | 41653.7289 | 99.3414
47 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
48 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR1 | -- | 2015-08-09 08:58 | 2015-08-10 10:15 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 01:17 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Mnp-431 KV
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 01:17 | -- | -- | -- |  |  |  | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
49 | NR140138 | 400KV BLBGRH-NAVADA | 12.55 | NR1 | -- | 2015-08-06 10:32 | 2015-08-06 17:20 | -- | -- |  | 0 | 0 | 0 | 0.28333 | -- | -- | -- | OSPD | S/D by HVPNL for their bay eqpmt AMP work at Nawada.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.28333 | -- | -- | -- |  |  |  | 744 | 691 | 12.55 | 8672.05 | 8672.05 | 100
50 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 13.256 | 9159.896 | 9159.896 | 100
51 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- | 2015-08-03 02:08 | 2015-08-03 02:22 | -- | -- |  | 0.0097222 | 0 | 0 | 0 | -- | -- | -- | LEFT | Line tripped on Y-N fault in reclaim time. FLR:Dadri-21.9km
[5 empty] | -- | 2015-08-25 10:52 | 2015-08-25 11:43 | -- | -- |  | 0.035417 | 0 | 0 | 0 | -- | -- | -- | OMST | Tripped on to Bus Bar-I protn at Mhrnbg during isolation of ICT-II for S/D.
[5 empty] | -- | 2015-08-29 12:09 | 2015-08-29 16:19 | -- | -- |  | 0 | 0.17361 | 0 | 0 | -- | -- | -- | OMSU | A/R & Trip on B-N fault due to kite thread. Charged after removal of same. FLR:Mbagh=7.6km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.045139 | 0.17361 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 54.36 | 37562.76 | 37508.0651 | 99.8544
52 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 46.3 | 31993.3 | 31993.3 | 100
53 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 46.3 | 31993.3 | 31993.3 | 100
54 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 33.098 | 17045.47 | 17045.47 | 100
55 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | 2015-08-04 10:30 | 2015-08-04 17:32 |  |  |  | 0.29306 | 0 | 0 | 0 |  |  |  | OSPT | S/D for protn testing & polluted insulator replacement work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.29306 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 112.322 | 57845.83 | 57298.9899 | 99.0547
56 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- | 2015-08-05 17:16 | 2015-08-05 20:02 | -- | -- |  | 0 | 0 | 0 | 0.11528 | -- | -- | -- | OSPD | S/D by BBMB to attend hotspot in Bus Clamp at their s/s.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.11528 | -- | -- | -- |  |  |  | 744 | 515 | 117 | 60255 | 60255 | 100
57 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR1 | -- | 2015-08-14 06:45 | 2015-08-14 07:45 | -- | -- | -- | 0.041667 | 0 | 0 | 0 | -- | -- | -- | LEFT | Line tripped only from Fatehpur on B-N fault during reclaim time. FLR-Ftpr-1.6Km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.041667 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 121799.989 | 99.8656
58 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
59 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
60 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
61 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- | 2015-08-15 12:59 | 2015-08-16 22:20 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:21 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Manesher-426 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:21 | -- | -- | -- |  |  |  | 744 | 687 | 23.462 | 16118.394 | 16118.394 | 100
62 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 23.462 | 16118.394 | 16118.394 | 100
63 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | 2015-08-01 | 2015-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-30 |  |  |  | OSPD | S/D by DTL for maintenance work at Bmnoli end. Open since 16.03.15 at 13:04hrs.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- |  |  |  | 744 | 687 | 6.106 | 4194.822 | 4194.822 | 100
64 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 6.106 | 4194.822 | 4194.822 | 100
65 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 6.782 | 4659.234 | 4659.234 | 100
66 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 6.782 | 4659.234 | 4659.234 | 100
67 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- | 2015-08-13 11:17 | 2015-08-13 15:40 | -- | -- | -- | 0.18264 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for testing of L/R bushing and CSD relay commissioning at Kankroli.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.18264 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 225 | 201.2 | 45270 | 45003.2883 | 99.4108
68 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2015-08-01 02:27 | 2015-08-01 02:32 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | -- | -- | -- | GOVC | Tripped on O/Voltage protn at Jodhpur. DT received at Kank
[6 empty] | 2015-08-01 02:32 | 2015-08-01 06:52 |  |  |  | 0 | 0 | 0 | 0.18056 |  |  |  | LVRD | Line kept open for Voltage regulation. Kankroli-430kv
[6 empty] | 2015-08-01 14:08 | 2015-08-01 21:47 |  |  |  | 0 | 0 | 0 | 0.31875 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Jodhpr>440 kV
[6 empty] | 2015-08-07 04:21 | 2015-08-07 08:40 |  |  |  | 0 | 0 | 0 | 0.17986 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Jodhpur-430 KV
[6 empty] | 2015-08-13 14:50 | 2015-08-13 17:20 |  |  |  | 0.10417 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending hot spot at loc. No. 476.
[6 empty] | 2015-08-13 17:20 | 2015-08-14 09:45 |  |  |  | 0 | 0 | 0 | 0.68403 |  |  |  | LVRD | Line kept open for Voltage regulation.
[6 empty] | 2015-08-14 09:58 | 2015-08-14 10:22 |  |  |  | 0 | 0 | 0 | 0.016667 |  |  |  | OSFD | Hand tripped by Jodhpur RRVNL end due to isolator sparking.
[6 empty] | 2015-08-14 10:51 | 2015-08-14 18:01 |  |  |  | 0 | 0 | 0 | 0.29861 |  |  |  | OSFD | Lind hand tripped for forced s/d by Jodhpur RRVNL end due to sparking in line isolator.
[6 empty] | 2015-08-16 00:23 | 2015-08-17 09:25 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:02 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Jodhpur-434KV
[6 empty] | 2015-08-22 21:55 | 2015-08-22 22:23 |  |  |  | 0 | 0.019444 | 0 | 0 |  |  |  | OMSU | CB auto tripped at Jodhpur, RRVPNL end only. Line remain charged from KNK-PG end. No flag/facia reported.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10417 | 0.019444 | 0.0034722 | 1900-01-02 01:19 | -- | -- | -- |  |  |  | 743.9167 | 515 | 187.965 | 96801.975 | 96476.6631 | 99.6639
69 | NR140050 | 400KV KANKROLI-RAPPC-I | 198.54 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 395 | 198.54 | 78423.3 | 78423.3 | 100
70 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- | 2015-08-12 16:35 | 2015-08-12 17:40 | -- | -- |  | 0.045139 | 0 | 0 | 0 | -- | -- | -- | OSFT | Forced S/D due to abnormal sound in L/R at Kankroli.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.045139 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 395 | 198.54 | 78423.3 | 78309.1084 | 99.8544
71 | NR140052 | 400KV KNP-AGRA | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0 |  |  |  | LCSD
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 291 | 240 | 69840 | 69840 | 100
72 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR1 | -- | 2015-08-08 13:53 | 2015-08-08 13:58 |  |  |  | 0 | 0.0034722 | 0 | 0 |  |  |  | OMSU | Tripped on Y-N fault due o snapping of pilot rope during OPGW stringing work under ULDC scheme.
[6 empty] | 2015-08-08 13:58 | 2015-08-08 18:48 |  |  |  | 0 | 0 | 0 | 0.20139 |  |  |  | LCSD | S/D for OPGW stringing work under ULDC scheme.
[5 empty] | -- | 2015-08-24 09:45 | 2015-08-24 22:35 |  |  |  | 0 | 0 | 0 | 0.53472 |  |  |  | LCSD | S/D for OPGW installation work under ULDC scheme.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.0034722 | 0 | 0.73611 | -- | -- | -- |  |  |  | 744 | 515 | 72.6 | 37389 | 37389 | 100
73 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.2 | 37698 | 37698 | 100
74 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR1 | -- | 2015-08-03 14:02 | 2015-08-03 19:35 | -- | -- |  | 0 | 0 | 0 | 0.23125 | -- | -- | -- | LCSD | S/D for tie bay jumpering after Isolator retrofitment work under Add Cap at BLB end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.23125 | -- | -- | -- |  |  |  | 744 | 342 | 385.69 | 131905.98 | 131905.98 | 100
75 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR1 | -- | 2015-08-01 15:14 | 2015-08-01 17:53 | -- | -- |  | 0.11042 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for CSD relay testing/ commissioning at Blb end.
[6 empty] | 2015-08-14 12:27 | 2015-08-14 16:17 |  |  |  | 0.15972 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend hot spot on loc no. 932 by Blb.
[6 empty] | 2015-08-27 13:41 | 2015-08-27 17:56 |  |  |  | 0.17708 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D to attend sparking in FSC bypass isolator at BLB.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.44722 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 131917.7207 | 98.5573
76 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
77 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 107.079 | 55145.685 | 55145.685 | 100
78 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 107.1 | 55156.5 | 55156.5 | 100
79 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 5.922 | 3049.83 | 3049.83 | 100
80 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR1 | -- | 2015-08-10 17:31 | 2015-08-10 19:02 |  |  |  | 0 | 0 | 0 | 0.063194 |  |  |  | OSPD | S/D by UPPCL for attending CT clamp hot spot at Panki.
[5 empty] | -- | 2015-08-19 09:06 | 2015-08-19 16:15 |  |  |  | 0 | 0 | 0 | 0.29792 |  |  |  | OSPD | S/D by UPPCL for attending CT clamp hot spot at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.36111 | -- | -- | -- |  |  |  | 744 | 515 | 5.86 | 3017.9 | 3017.9 | 100
81 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 179.711 | 92551.165 | 92551.165 | 100
82 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- | 2015-08-01 | 2015-08-04 10:06 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 10:06 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Merta-430 KV. Out since 23.07.15 at 0354hrs
[6 empty] | 2015-08-05 00:32 | 2015-08-07 15:55 |  |  |  | 0 | 0 | 0 | 1900-01-01 15:23 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-430 KV
[6 empty] | 2015-08-07 18:37 | 2015-08-13 11:02 |  |  |  | 0 | 0 | 0 | 1900-01-04 16:25 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-432 KV
[6 empty] | 2015-08-14 03:59 | 2015-08-14 11:54 |  |  |  | 0 | 0 | 0 | 0.32986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Kota-426kv.
[6 empty] | 2015-08-14 18:49 | 2015-08-18 10:04 |  |  |  | 0 | 0 | 0 | 1900-01-02 15:15 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-430 KV
[6 empty] | 2015-08-19 03:16 | 2015-08-19 08:22 |  |  |  | 0 | 0 | 0 | 0.2125 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 22:10 | -- | -- | -- |  |  |  | 744 | 309 | 255.56 | 78968.04 | 78968.04 | 100
83 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | 2015-08-06 11:22 | 2015-08-06 16:48 |  |  |  | 0.22639 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for attending Y-ph line isolator sparking at Kota
[6 empty] | 2015-08-16 03:00 | 2015-08-16 09:22 |  |  |  | 0 | 0 | 0 | 0.26528 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Kota-432 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.22639 | 0 | 0 | 0.26528 | -- | -- | -- |  |  |  | 744 | 515 | 50.5 | 26007.5 | 25817.5707 | 99.2697
84 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- | 2015-08-28 13:07 | 2015-08-28 14:56 | -- | -- | -- | 0 | 0 | 0 | 0.075694 | -- | -- | -- | OSFD | Forced S/D by KHEP due to problem in their generation unit.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.075694 | -- | -- | -- |  |  |  | 744 | 515 | 2.7 | 1390.5 | 1390.5 | 100
85 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.7 | 1390.5 | 1390.5 | 100
86 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 633 | 14.463 | 9155.079 | 9155.079 | 100
87 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 633 | 16.49 | 10438.17 | 10438.17 | 100
88 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
89 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
90 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR1 | -- | [15 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
91 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR1 | -- | [15 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
92 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
93 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR1 | -- | 2015-08-25 06:02 | 2015-08-25 10:30 |  |  |  | 0 | 0 | 0 | 0.18611 |  |  |  | LCSD | S/D for OPGW installation work under ULDC scheme.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.18611 | -- | -- | -- |  |  |  | 744 | 371 | 169.785 | 62990.235 | 62990.235 | 100
94 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 169.729 | 87410.435 | 87410.435 | 100
95 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
96 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
97 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
98 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
99 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR1 | -- | 2015-08-05 17:21 | 2015-08-05 17:56 | -- | -- | -- | 0 | 0.024306 | 0 | 0 | -- | -- | -- | OMSU | Trip on Y-B fault caused due to kite thread, LKO=26km.
[6 empty] | 2015-08-06 13:32 | 2015-08-06 13:58 | -- | -- | -- | 0 | 0.018056 | 0 | 0 | -- | -- | -- | OMSU | Line tripped B-Y fault, dist. LKO-23.1 kms, due to kite thread reported by TL staff
[6 empty] | 2015-08-06 17:19 | 2015-08-06 17:53 | -- | -- | -- | 0 | 0.023611 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on B-Y fault caused by Kite thread. FLR:LKO-21.9km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.065972 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
100 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 133.5 | 68752.5 | 68752.5 | 100
101 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- | 2015-08-23 11:10 | 2015-08-23 11:42 | -- | -- | -- | 0 | 0.022222 | 0 | 0 | -- | -- | -- | OMSU | Trip on R-N fault caused by Kite thread. MRT=23.2km, BLY=269km.
[6 empty] | 2015-08-23 13:36 | 2015-08-23 17:30 | -- | -- | -- | 0 | 0.1625 | 0 | 0 | -- | -- | -- | OMSU | Tripped on R-N fault caused by Kite thread, MRT=11.2km. Charged after patrolling.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.18472 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
102 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
103 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 678 | 178.69 | 121151.82 | 121151.82 | 100
104 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 673 | 175.63 | 118198.99 | 118198.99 | 100
105 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 59.868 | 30832.02 | 30832.02 | 100
106 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | [15 empty] | 744 | 515 | 59.868 | 30832.02 | 30832.02 | 100
107 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 54.298 | 27963.47 | 27963.47 | 100
108 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 54.298 | 27963.47 | 27963.47 | 100
109 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 37.38 | 19250.7 | 19250.7 | 100
110 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 76.018 | 39149.27 | 39149.27 | 100
111 | NR140139 | 400KV NAVADA-GR.NOIDA | 30.15 | NR1 | -- | 2015-08-01 10:22 | 2015-08-01 18:13 | -- | -- | -- | 0 | 0 | 0 | 0.32708 | -- | -- | -- | OSPD | S/D by HVPNL for AMP work at Nawada
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.32708 | -- | -- | -- |  |  |  | 744 | 691 | 30.15 | 20833.65 | 20833.65 | 100
112 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 67.041 | 34526.115 | 34526.115 | 100
113 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- | 2015-08-15 12:56 | 2015-08-16 22:26 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:30 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Neem-428 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:30 | -- | -- | -- |  |  |  | 744 | 515 | 67.041 | 34526.115 | 34526.115 | 100
114 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 175.859 | 90567.385 | 90567.385 | 100
115 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- | 2015-08-12 00:24 | 2015-08-12 10:35 | -- | -- | -- | 0 | 0 | 0 | 0.42431 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Bhiwadi-428kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.42431 | -- | -- | -- |  |  |  | 744 | 515 | 175.859 | 90567.385 | 90567.385 | 100
116 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR1 | -- | 2015-08-15 19:48 | 2015-08-15 20:23 | -- | -- | -- | 0.024306 | 0 | 0 | 0 | -- | -- | -- | LEFT | Line tripped on B-N fault in eclaim time. FLR:Alld-140Kms
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.024306 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 120818.2831 | 99.9216
117 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
118 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | 2015-08-14 09:45 | 2015-08-14 10:30 |  |  |  | 0 | 0.03125 | 0 | 0 |  |  |  | OMSU | Line A/R at Roorkee but tripped at Muzfrngr on Y-N fault in UPCL portion. FLR: Roorkee-20.85 km.
[5 empty] | -- | 2015-08-18 03:41 | 2015-08-18 04:08 |  |  |  | 0 | 0.01875 | 0 | 0 |  |  |  | OMSU | A/R from Roorkee but tripped at Mzfrngr(UP) on Y-N fault in UPPCL portion. FLR:Roork-12km.
[6 empty] | 2015-08-24 02:56 | 2015-08-24 03:19 |  |  |  | 0 | 0.015972 | 0 | 0 |  |  |  | OMSU | A/R at Roorki but Trip from Mzfrtngr end due to R-N fault in UPPCL portion. Roorki=54km.
[5 empty] | -- | 2015-08-31 14:09 | 2015-08-31 14:36 |  |  |  | 0 | 0.01875 | 0 | 0 |  |  |  | OMSU | Line A/R at Roorkee but tripped at Muzfernagar end on B-N fault in UPPCL portion, FLR:Roorkee-15km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.084722 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.1 | 1081.5 | 1081.5 | 100
119 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.1 | 1081.5 | 1081.5 | 100
120 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 |  | 2015-08-01 | 2015-08-02 10:24 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:24 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-430 KV. Out since 30.07.15 at 2206hrs
[6 empty] | 2015-08-03 02:47 | 2015-08-03 08:21 |  |  |  | 0 | 0 | 0 | 0.23194 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-430 KV
[6 empty] | 2015-08-03 13:34 | 2015-08-04 08:38 |  |  |  | 0 | 0 | 0 | 0.79444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-420kv.
[6 empty] | 2015-08-06 10:08 | 2015-08-06 20:10 |  |  |  | 0 | 0 | 0 | 0.41806 |  |  |  | OSPD | S/D by RRVPNL to attend Bus Jumper hot spot at Ratangrh.
[6 empty] | 2015-08-12 00:12 | 2015-08-12 08:31 |  |  |  | 0 | 0 | 0 | 0.34653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ratangarh-420kv.
[6 empty] | 2015-08-15 16:53 | 2015-08-17 09:46 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:53 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-430 KV
[6 empty] | 2015-08-23 18:20 | 2015-08-24 09:24 |  |  |  | 0 | 0 | 0 | 0.62778 |  |  |  | LVRD | Line hand tripped for Voltage regulation Ratangarh-432 KV
[6 empty] | 2015-08-26 10:20 | 2015-08-26 20:04 |  |  |  | 0.40556 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending HOT SPOT and jumper tightening work.
[6 empty] | 2015-08-27 09:04 | 2015-08-27 20:41 |  |  |  | 0.48403 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending HOT SPOT and jumper tightening work.
[6 empty] | 2015-08-29 18:15 | 2015-08-29 23:42 |  |  |  | 0 | 0 | 0 | 0.22708 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar=418kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.88958 | 0 | 0 | 1900-01-04 18:47 | -- | -- | -- |  |  |  | 744 | 515 | 76.48 | 39387.2 | 38256.9356 | 97.1304
121 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 |  | 2015-08-01 | 2015-08-19 10:18 |  |  |  | 0 | 0 | 0 | 1900-01-17 10:18 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-432 KV. Out since 30.07.15 at 0334hrs
[6 empty] | 2015-08-21 18:27 | 2015-08-22 06:33 |  |  |  | 0 | 0 | 0 | 0.50417 |  |  |  | LVRD | Line hand tripped for Voltage regulation.R/Garh-428 KV
[6 empty] | 2015-08-22 18:30 | 2015-08-23 11:08 |  |  |  | 0 | 0 | 0 | 0.69306 |  |  |  | LVRD | Line hand tripped for Voltage regulation Ratangarh-432 KV
[6 empty] | 2015-08-28 09:06 | 2015-08-28 18:33 |  |  |  | 0.39375 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending HOT SPOT and jumper tightening work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.39375 | 0 | 0 | 1900-01-18 15:02 | -- | -- | -- |  |  |  | 744 | 515 | 76.48 | 39387.2 | 38886.919 | 98.7298
122 | NR140091 | 400KV SING-ALLD-I | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 332 | 224 | 74368 | 74368 | 100
123 | NR140092 | 400KV SING-ALLD-II | 202 | NR1 | -- | [15 empty] | 744 | 306 | 202 | 61812 | 61812 | 100
124 | NR140093 | 400KV SING-ANPARA | 25.057 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 25.057 | 12904.355 | 12904.355 | 100
125 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 236 | 330.953 | 78104.908 | 78104.908 | 100
126 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 337 | 408.6 | 137698.2 | 137698.2 | 100
127 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR1 | -- | 2015-08-07 11:37 | 2015-08-07 16:46 | -- | -- |  | 0.21458 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for Demo of Off Line fault locator test kit.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.21458 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 42.026 | 21643.39 | 21493.5735 | 99.3078
128 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR1 | -- | 2015-08-05 09:02 | 2015-08-05 23:08 | -- | -- |  | 0 | 0 | 0 | 0.5875 | -- | -- | -- | OSPD | S/D by SING/NTPC for faulty CT replacement work.
[6 empty] | 2015-08-10 18:06 | 2015-08-10 18:27 | -- | -- |  | 0 | 0.014583 | 0 | 0 | -- | -- | -- | SRMU | Tripped only from Rihand-NTPC end due to O/Voltage relay mal-operation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.014583 | 0 | 0.5875 | [6 empty] | 744 | 515 | 43.952 | 22635.28 | 22635.28 | 100
129 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR1 | -- | 2015-08-11 10:30 | 2015-08-11 21:54 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | OSPD | S/D Taken by NTPC for replacement of faulty CT at Sing.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.475 | -- | -- | -- |  |  |  | 744 | 515 | 3.341 | 1720.615 | 1720.615 | 100
130 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR1 | -- | 2015-08-12 10:37 | 2015-08-12 20:21 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | OSPD | S/D Taken by NTPC for replacement of faulty CT at Sing.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.40556 | -- | -- | -- |  |  |  | 744 | 515 | 3.317 | 1708.255 | 1708.255 | 100
131 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | 2015-08-04 20:03 | 2015-08-04 20:40 |  |  |  | 0.025694 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D by Kankroli end due to sparking observed in main bay isolator.
[6 empty] | 2015-08-04 21:21 | 2015-08-04 21:44 |  |  |  | 0 | 0 | 0.015972 | 0 |  |  |  | GOVC | Tripped on O/Voltage protn, Kank=437kv.
[6 empty] | 2015-08-12 15:00 | 2015-08-12 20:00 |  |  |  | 0.20833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for ten delta measurement on various frequencies for healthiness of LR bushings at Kankroli.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.23403 | 0 | 0.015972 | 0 | -- | -- | -- |  |  |  | 743.6167 | 236 | 233.707 | 55154.852 | 54738.2578 | 99.2447
132 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 272 | 142.8 | 38841.6 | 38841.6 | 100
[5 empty] | -- | [17 empty] | 18399.672
|  | 220 KV TRANS LINES |  |  | --
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR1 | -- | [15 empty] | 744 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
5 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | 2015-08-01 | 2015-08-04 09:55 |  |  |  | 0 | 0 | 0 | 1900-01-02 09:55 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Out since 26.07.15 at 0433hrs
[6 empty] | 2015-08-25 11:15 | 2015-08-25 13:40 |  |  |  | 0 | 0.10069 | 0 | 0 |  |  |  | SBBU | Tripped on Bus Bar protn operated at Bhil(RRVPNL) due to fire in wave trap of their interconnector line.
[6 empty] | 2015-08-27 17:50 | 2015-08-27 18:35 |  |  |  | 0 | 0.03125 | 0 | 0 |  |  |  | OMSU | Line tripped only at Bhilwara end due to station DC E/fault in RRVPNL S/S
[6 empty] | 2015-08-28 12:52 | 2015-08-28 19:57 |  |  |  | 0 | 0 | 0 | 0.29514 |  |  |  | OSPD | S/D by RRVPNL to attend TBC problem at Bhilwara.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.13194 | 0 | 1900-01-02 17:00 | -- | -- | -- |  |  |  | 744 | 132 | 186.667 | 24640.044 | 24640.044 | 100
6 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | 2015-08-13 05:15 | 2015-08-13 18:26 |  |  |  | 0 | 0.54931 | 0 | 0 |  |  |  | OMSU | Line tripped due to A/R problem at Anta on R-N transient fault. FLR:Anta-45.29km
[6 empty] | 2015-08-25 11:15 | 2015-08-25 13:40 |  |  |  | 0 | 0.10069 | 0 | 0 |  |  |  | SBBU | Tripped on Bus Bar protn operated at Bhil(RRVPNL) due to fire in wave trap of their interconnector line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.65 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 186.667 | 24640.044 | 24640.044 | 100
7 | NR122038 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 180.287 | 23797.884 | 23797.884 | 100
8 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- | 2015-08-06 22:07 | 2015-08-06 22:53 | -- | -- |  | 0 | 0.031944 | 0 | 0 | -- | -- | -- | OMSU | Line tripped due to A/R problem at RAPP during Y-N transient fault, FLR:Anta-40.06 kms
[6 empty] | 2015-08-08 22:09 | 2015-08-08 22:38 | -- | -- |  | 0 | 0.020139 | 0 | 0 | -- | -- | -- | OMSU | A/R from RAPPC but tripped only at Anta due to A/R relay problem on Y-N fault. FLR, Anta-19.36km, RAPP-63.96km
[6 empty] | 2015-08-15 18:11 | 2015-08-15 18:44 | -- | -- |  | 0 | 0.022917 | 0 | 0 | -- | -- | -- | OMSU | Line A/R at Rapp-C but tripped from Anta NTPC due to A/R problem on Y-N transient fault. FLR:Anta-40.43 kms
[6 empty] | 2015-08-20 15:39 | 2015-08-20 18:20 | -- | -- |  | 0 | 0.11181 | 0 | 0 | -- | -- | -- | OMSU | CB auto tripped at Anta during shifting of line on transfer bus by NTPC. Remain charged from RAPPC end.
[5 empty] | -- | 2015-08-27 10:50 | 2015-08-27 19:07 | -- | -- |  | 0.34514 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for replacement of insulator strings due to flashover.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.34514 | 0.18681 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 87.544 | 11468.264 | 11340.5819 | 98.8866
9 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 102.164 | 13485.648 | 13485.648 | 100
10 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
11 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
12 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | 2015-08-27 12:11 | 2015-08-27 17:49 |  |  |  | 0 | 0 | 0 | 0.23472 |  |  |  | OSPD | S/D by RRVPNL to attend isolator clamp hot spot at Bagru.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.23472 | -- | -- | -- |  |  |  | 744 | 131 | 35.353 | 4631.243 | 4631.243 | 100
13 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 20.109 | 2634.279 | 2634.279 | 100
14 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 20.109 | 2634.279 | 2634.279 | 100
15 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 22.478 | 2944.618 | 2944.618 | 100
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 109 | 234.59 | 25570.31 | 25570.31 | 100
17 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 156 | 59.01 | 9205.56 | 9205.56 | 100
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR1 | -- | 2015-08-13 12:51 | 2015-08-13 16:36 | -- | -- |  | 0 | 0 | 0 | 0.15625 | -- | -- | -- | OSPD | S/D by UPPCL for maintanance at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.15625 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
21 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
22 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | 2015-08-06 09:50 | 2015-08-06 16:09 |  |  |  | 0 | 0 | 0 | 0.26319 |  |  |  | OSPD | S/D by NHPC for attending hot spot in R-ph CB at FGPP.
[6 empty] | 2015-08-11 10:55 | 2015-08-11 17:30 |  |  |  | 0 | 0 | 0 | 0.27431 |  |  |  | OSPD | S/D taken by FGPP for Bay Equipment Maintenance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.5375 | -- | -- | -- |  |  |  | 744 | 131 | 15.69 | 2055.39 | 2055.39 | 100
23 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- | 2015-08-24 11:46 | 2015-08-24 17:12 | -- | -- |  | 0 | 0 | 0 | 0.22639 | -- | -- | -- | OSFD | S/D by NTPC for attending hot spot in CT at FGPP end.
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.22639 | -- | -- | -- |  |  |  | 744 | 131 | 15.69 | 2055.39 | 2055.39 | 100
24 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- | 2015-08-14 09:08 | 2015-08-14 19:17 | -- | -- |  | 0 | 0 | 0 | 0.42292 | -- | -- | -- | OSPD | S/D by NTPC for bay maint work at FGPP end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.42292 | -- | -- | -- |  |  |  | 744 | 131 | 17.691 | 2317.521 | 2317.521 | 100
25 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | 2015-08-17 09:42 | 2015-08-17 18:52 |  |  |  | 0 | 0 | 0 | 0.38194 |  |  |  | OSPD | S/D by NTPC for bay maintenance work at FGPP end
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.38194 | -- | -- | -- |  |  |  | 744 | 131 | 17.691 | 2317.521 | 2317.521 | 100
26 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | [15 empty] | 744 | 131 | 24.875 | 3258.625 | 3258.625 | 100
27 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [15 empty] | 744 | 131 | 12 | 1572 | 1572 | 100
28 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR1 | -- | 2015-08-10 10:20 | 2015-09-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-20 13:40 | -- | -- | -- | OSPD | S/D by UPPCL for line diversion work in their portion.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-20 13:40 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
29 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR1 | -- | 2015-08-11 05:11 | 2015-08-11 05:42 |  |  |  | 0 | 0.021528 | 0 | 0 |  |  |  | OMSU | A/R from Knp but tripped at Naubasta (UP) due to A/R problem on B-N fault. FLR:Knp-2.315km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.021528 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
30 | NR122018 | 220KV KNP-PANKI-I | 10.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
31 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR1 | -- | 2015-08-13 14:30 | 2015-08-13 20:08 | -- | -- | -- | 0.23472 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for attend hot-spot in R&Y Ph isolator at Kanpur.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.23472 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1931.9205 | 99.2428
32 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
33 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
34 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
35 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
36 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 28.02 | 3698.64 | 3698.64 | 100
37 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- | 2015-08-03 18:17 | 2015-08-03 22:44 | -- | -- | -- | 0 | 0.18542 | 0 | 0 | -- | -- | -- | OMSU | Line A/R at Meerut but trip from Modipuram-UP end on B-N fault in their section. Meerut- 4.8 km
[6 empty] | 2015-08-04 08:45 | 2015-08-04 13:32 |  |  |  | 0 | 0 | 0 | 0.19931 |  |  |  | OSPD | S/D by UPPCL for mntc work in their portion.
[6 empty] | 2015-08-04 19:33 | 2015-08-05 01:46 |  |  |  | 0 | 0 | 0 | 0.25903 |  |  |  | LPRD | Line hand tripped for Power regulation.
[6 empty] | 2015-08-06 10:20 | 2015-08-06 13:16 | -- | -- | -- | 0 | 0 | 0 | 0.12222 | -- | -- | -- | OSPD | S/D by UPPCL to attend hotspot at Modipuram end.
[6 empty] | 2015-08-09 22:10 | 2015-08-09 22:23 | -- | -- | -- | 0 | 0 | 0 | 0.0090278 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
[6 empty] | 2015-08-10 21:21 | 2015-08-10 21:30 | -- | -- | -- | 0 | 0 | 0 | 0.00625 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
[6 empty] | 2015-08-12 20:17 | 2015-08-12 22:31 | -- | -- | -- | 0 | 0 | 0 | 0.093056 | -- | -- | -- | LPRD | Line hand tripped for Power regulation.
[6 empty] | 2015-08-13 21:12 | 2015-08-13 23:36 | -- | -- | -- | 0 | 0 | 0 | 0.1 | -- | -- | -- | LPRD | Line hand tripped for Power regulation on RLDC instruction.
[6 empty] | 2015-08-25 15:59 | 2015-08-25 18:44 |  |  |  | 0 | 0 | 0 | 0.11458 |  |  |  | LPRD | Line hand tripped for Power regulation
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.18542 | 0 | 0.90347 | -- | -- | -- |  |  |  | 744 | 132 | 2.316 | 305.712 | 305.712 | 100
38 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- | 2015-08-04 19:33 | 2015-08-05 01:45 | -- | -- | -- | 0 | 0 | 0 | 0.25833 | -- | -- | -- | LPRD | Line hand tripped for Power regulation.
[5 empty] | -- | 2015-08-05 19:20 | 2015-08-05 20:05 | -- | -- | -- | 0 | 0 | 0 | 0.03125 | -- | -- | -- | OSPD | S/D by UPPCL to attend hotspot at Modipuram end.
[5 empty] | -- | 2015-08-09 22:10 | 2015-08-09 22:54 | -- | -- | -- | 0 | 0 | 0 | 0.030556 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
[5 empty] | -- | 2015-08-10 21:21 | 2015-08-10 21:30 | -- | -- | -- | 0 | 0 | 0 | 0.00625 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
[5 empty] | -- | 2015-08-12 20:17 | 2015-08-12 22:31 | -- | -- | -- | 0 | 0 | 0 | 0.093056 | -- | -- | -- | LPRD | Line hand tripped for Power regulation.
[5 empty] | -- | 2015-08-13 21:12 | 2015-08-13 23:36 | -- | -- | -- | 0 | 0 | 0 | 0.1 | -- | -- | -- | LPRD | Line hand tripped for Power regulation.
[5 empty] | -- | 2015-08-23 21:00 | 2015-08-23 21:28 | -- | -- | -- | 0 | 0.019444 | 0 | 0 | -- | -- | -- | OMSU | Tripped on Y-N fault in UPPCL portion. MRT=9.3km
[5 empty] | -- | 2015-08-25 15:59 | 2015-08-25 18:44 | -- | -- | -- | 0 | 0 | 0 | 0.11458 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.019444 | 0 | 0.63403 | -- | -- | -- |  |  |  | 744 | 132 | 9.254 | 1221.528 | 1221.528 | 100
39 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 2.316 | 305.712 | 305.712 | 100
40 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- | 2015-08-17 12:01 | 2015-08-17 15:49 | -- | -- | -- | 0 | 0 | 0 | 0.15833 | -- | -- | -- | OSPD | S/D by UPPCL for bay maintenance work at Shtbdngr end
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.15833 | -- | -- | -- |  |  |  | 744 | 132 | 8.234 | 1086.888 | 1086.888 | 100
41 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- | 2015-08-02 09:51 | 2015-08-02 10:55 | -- | -- |  | 0 | 0.044444 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on B-N fault in UPPCL portion. FLR: Meerut-9.7km .
[5 empty] | -- | 2015-08-08 14:23 | 2015-08-08 16:09 | -- | -- |  | 0 | 0.073611 | 0 | 0 | -- | -- | -- | OMSU | Tripped on R-N fault in UPPCL portion. FLR:Mrt-52.2km.
[5 empty] | -- | 2015-08-27 08:45 | 2015-08-27 10:37 | -- | -- |  | 0 | 0.077778 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on B-N fault in UPPCL portion. ,FLR:Mrt-47.8km, Smbholi-9.75km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.19583 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 9.254 | 1221.528 | 1221.528 | 100
42 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR1 | -- | 2015-08-22 18:18 | 2015-08-22 18:59 |  |  |  | 0 | 0.028472 | 0 | 0 |  |  |  | OMSU | Line tripped due o snapping of pilot rope during OPGW work between LOC no. 164 to 165 under ULDC scheme.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.028472 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 156 | 177.88 | 27749.28 | 27749.28 | 100
43 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
44 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
45 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 128.833 | 16877.123 | 16877.123 | 100
46 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | 2015-08-25 12:53 | 2015-08-25 13:41 |  |  |  | 0 | 0.033333 | 0 | 0 |  |  |  | OMSU | Tripped on B-N fault in RRVPNL portion. FLR:RAPP-132.9km, Line length-128km.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.033333 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 128.833 | 16877.123 | 16877.123 | 100
47 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 0.175 | 22.925 | 22.925 | 100
48 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 230.297 | 30168.907 | 30168.907 | 100
49 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 106.243 | 14024.076 | 14024.076 | 100
50 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 2.83 | 373.56 | 373.56 | 100
51 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 2.83 | 373.56 | 373.56 | 100
52 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
53 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
54 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR1 | -- | 2015-08-17 13:55 | 2015-08-17 18:00 | -- | -- | -- | 0.17014 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for facilitate jumper rectification work in 220KV TNKPR-SITARGANJ line in LILO portion.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.17014 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 105.72 | 13955.04 | 13878.4498 | 99.4512
55 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR1 | -- | 2015-08-03 10:31 | 2015-08-03 11:16 |  |  |  | 0 | 0 | 0 | 0.03125 |  |  |  | OSFD | Line S/D by NHPC to attend HOT spot & CB problem at Tanakpur End.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.03125 | -- | -- | -- |  |  |  | 744 | 132 | 106 | 13992 | 13992 | 100
56 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR1 | Jumper Failure | 2015-08-17 08:54 | 2015-08-17 18:03 |  |  | 0.38125 | 0.38125 | 0 | 0 | 0 | 2 | N | -1.6187 | LHWT | Tripped on R-Y fault due to Jumper broken at Loc. 23.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.38125 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 42.55 | 5616.6 | 5547.5249 | 98.7702
57 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
58 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
59 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 42.5 | 5610 | 5610 | 100
[5 empty] | -- | [17 empty] | 3441.839
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR1 | -- | [15 empty] | 744 | 50 | 58 | 2900 | 2900 | 100
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-12 17:54 | 1900-01-04 16:58 | 0.045833 | 1900-12-14 16:14 | [8 empty] | 21899.511 | 10895483.238 | 10876832.287 | 99.8288 | %
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | #VALUE! | % (AC) | 85.8323 | [6 empty] | %'(HVDC)
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 400/765KV ICT-I AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR1 | -- | 2015-08-05 14:55 | 2015-08-05 16:19 |  |  |  | 0 | 0 | 0 | 0.058333 | -- | -- | -- | LVRD | S/D to change Tap position from 20 to 18 for voltage regulation by NRLDC.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.058333 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR1 | -- | 2015-08-05 16:25 | 2015-08-05 17:10 | -- | -- |  | 0 | 0 | 0 | 0.03125 | -- | -- | -- | LVRD | S/D to change Tap position from 20 to 18 for voltage regulation by NRLDC.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.03125 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
13 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
14 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR1 | -- | 2015-08-07 11:50 | 2015-08-07 20:01 | -- | -- |  | 0 | 0 | 0 | 0.34097 | -- | -- | -- | SCSD | S/D for erection of bushing of new 765kv ICT-II R-ph unit under construcion.
[5 empty] | -- | 2015-08-27 12:30 | 2015-08-27 19:12 | -- | -- |  | 0 | 0 | 0 | 0.27917 | -- | -- | -- | SCSD | S/D for jumpering and Bus stability test for charging of 765kV ICT-II at Bareilly.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.62014 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
F |  | 400/220 KV ICT'S |  | NR1 | --
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR1 | [16 empty] | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | 2015-08-21 09:35 | 2015-08-21 18:21 |  |  |  | 0.36528 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP and bushing tan delta measurement.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.36528 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 311.2883 | 98.8217
5 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | 2015-08-23 09:22 | 2015-08-23 20:07 |  |  |  | 0.44792 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP and bushing tan delta measurement.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.44792 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 310.4486 | 98.5551
6 | NR1ICT68 | 500MVA ICT-III BASSI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
7 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
8 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
10 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
13 | NR1ICT10 | 315MVA ICT-I BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
14 | NR1ICT11 | 315MVA ICT-II BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
15 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
16 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
17 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
18 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
19 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
20 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
21 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
22 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | 2015-08-01 10:58 | 2015-08-01 19:07 |  |  |  | 0.33958 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP work along with GIS bay.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.33958 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 311.5494 | 98.9046
23 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
24 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
25 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
26 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
27 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
28 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
29 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
30 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
31 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
32 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
33 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
34 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
35 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
36 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | 2015-08-25 10:52 | 2015-08-25 11:10 |  |  |  | 0.0125 | 0 | 0 | 0 |  |  |  | OMST | Tripped on to Bus Bar-I protn at Mhrnbg during isolation of ICT-II for S/D.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.0125 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 314.873 | 99.9597
37 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | 2015-08-25 10:34 | 2015-08-25 20:10 |  |  |  | 0.4 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP and bushing tan delta measurement.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.4 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 310.9355 | 98.7097
38 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | 2015-08-27 11:40 | 2015-08-27 19:49 |  |  |  | 0.33958 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP and bushing tan delta measurement.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.33958 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 494.5228 | 98.9046
39 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | 2015-08-25 10:52 | 2015-08-25 11:12 |  |  |  | 0.013889 | 0 | 0 | 0 |  |  |  | OMST | Tripped on to Bus Bar-I protn at Mhrnbg during isolation of ICT-II for S/D.
[6 empty] | 2015-08-26 11:35 | 2015-08-26 17:42 |  |  |  | 0.25486 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP and bushing tan delta measurement.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.26875 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 495.6653 | 99.1331
40 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
41 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
42 | NR1ICT28 | 315MVA ICT-I MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
43 | NR1ICT29 | 315MVA ICT-II MANDOLA | 315 | NR1 | -- | 2015-08-14 06:27 | 2015-08-14 11:11 |  |  |  | 0.19722 | 0 | 0 | 0 |  |  |  | OSPT | S/D to attend hot spot in R-Ph isolator.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.19722 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 312.996 | 99.3638
44 | NR1ICT30 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
45 | NR1ICT31 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
46 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
47 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
48 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 316 |  | 316 | 316 | 100
49 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
50 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
51 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | [17 empty] | 744 | 500 |  | 500 | 500 | 100
52 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
53 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
54 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
55 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
56 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
57 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR1 | [16 empty] | 744 | 500 |  | 500 | 500 | 100
58 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR1 | [16 empty] | 744 | 500 |  | 500 | 500 | 100
59 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
60 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
61 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
62 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR1 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 | -- | 2015-08-22 17:20 | 2015-09-01 |  |  |  | 0 | 0 | 1900-01-08 06:40 | 0 |  |  |  | LNCC | Differential, REF, PRD, Buchholz & other ICT protn trip due to striking of lightning surge on Y-ph unit near LV bushing during strong thunderstorm.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1900-01-08 06:40 | 0 | -- | -- | -- |  |  |  | 521.3333 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR1 | -- | 2015-08-06 09:19 | 2015-08-06 10:59 |  |  |  | 0 | 0.069444 | 0 | 0 |  |  |  | OMSU | ICT tripped due to fire/ Bus fault at 132KV UPPCL yard.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.069444 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR1 | -- | 2015-08-06 09:19 | 2015-08-06 11:08 |  |  |  | 0 | 0.075694 | 0 | 0 |  |  |  | OMSU | ICT tripped due to fire/ Bus fault at 132KV UPPCL yard.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.075694 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR1 | -- | 2015-08-06 09:19 | 2015-08-06 11:12 |  |  |  | 0 | 0.078472 | 0 | 0 |  |  |  | OMSU | ICT tripped due to fire/ Bus fault at 132KV UPPCL yard.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.078472 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
--
83 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 1900-01-03 17:48 | 0.44722 | 1900-01-17 13:20 | 1899-12-31 10:04 | [7 empty] | 46451 |  | 46451 | 46423.2789 | 99.9403 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR1 | -- | 2015-08-30 10:09 | 2015-08-30 11:42 |  |  |  | 0.064583 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend control panel system failure alarm at Dadri.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.064583 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 609976.5625 | 99.7917
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR1 | -- | 2015-08-10 11:05 | 2015-08-10 22:56 |  |  |  | 0.49375 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend level-3 thyrestor failure alarm at Rh termial.
[6 empty] | 2015-08-31 08:40 | 2015-08-31 22:55 |  |  |  | 0.59375 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend level-3 thyrestor failure alarm at Rh termial.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 02:06 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 589806.9556 | 96.4919
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR1 | -- | 2015-08-21 10:21 | 2015-08-21 23:09 |  |  |  | 0 | 0 | 0 | 0.53333 |  |  |  | OSPD | S/D with E/Electrode line by HVPNL for stringing of their 220kv Rangla-Rajpur line. P-II kept in metallic reurn mode.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.53333 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 1899-12-31 03:39 | 0 | 0 | 0.53333 | [8 empty] | 3209.572 | 3196965 | 3174248.5181 | 99.2894 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I | 250 | NR1 | -- | 2015-08-06 12:42 | 2015-09-01 |  |  | 25 | 1900-01-24 11:18 | 0 | 0 | 0 | 25 | N | -95 | OMST | Tripped on DC over curent protection. Out due to major components failure in valve hall. Expected by 15-10-15.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-24 11:18 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 44.5901 | 17.836
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-24 11:18 | 0 | 0 | 0 | [9 empty] | 500 | 294.5901 | 58.918 | %
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 280 | 280 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 50MVAR B/Reactor-I BAREILLY | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
16 | NR1BRT04 | 50MVAR B/Reactor BASSI | 50 | NR1 | -- | 2015-08-28 10:54 | 2015-08-28 18:19 |  |  |  | 0 | 0 | 0 | 0.30903 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.30903 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
17 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- | 2015-08-20 08:56 | 2015-08-29 18:44 | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 09:48 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2015-08-30 07:53 | 2015-08-30 18:06 |  |  |  | 0 | 0 | 0 | 0.42569 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-08 20:01 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
18 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
19 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
20 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
21 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
22 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
23 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 330 |  | 330 | 330 | 100
24 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
25 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
26 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
27 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
28 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
29 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | 2015-08-24 08:46 | 2015-08-24 17:58 |  |  |  | 0 | 0 | 0 | 0.38333 |  |  |  | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[5 empty] | -- | 2015-08-25 08:59 | 2015-08-25 21:46 |  |  |  | 0 | 0 | 0 | 0.53264 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[5 empty] | -- | 2015-08-27 10:12 | 2015-08-27 20:41 |  |  |  | 0 | 0 | 0 | 0.43681 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[5 empty] | -- | 2015-08-28 10:03 | 2015-08-28 20:37 |  |  |  | 0 | 0 | 0 | 0.44028 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2015-08-30 11:14 | 2015-08-30 20:45 |  |  |  | 0 | 0 | 0 | 0.39653 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 04:33 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
30 | NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
31 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | 2015-08-31 00:07 | 2015-09-01 |  |  |  | 0 | 0 | 0 | 0.99514 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.99514 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
32 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
33 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
34 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
35 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
36 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
37 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
38 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
39 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
40 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- | 2015-08-01 | 2015-09-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
41 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- | 2015-08-31 10:55 | 2015-09-01 | -- | -- | -- | 0 | 0 | 0 | 0.54514 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.54514 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
42 | NR1BRT48 | 125MVAR B/Reactor-I RATANGARH(RJ) | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
43 | NR1BRT40 | 125MVAR B/Reactor Roorki | 125 | NR1 | -- | 2015-08-01 | 2015-08-15 14:09 | -- | -- | -- | 0 | 0 | 0 | 1900-01-13 14:09 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[6 empty] | 2015-08-15 19:14 | 2015-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-15 04:46 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-29 18:55 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
44 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJAHANPUR | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
45 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | 2015-08-31 10:55 | 2015-09-01 |  |  |  | 0 | 0 | 0 | 0.54514 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.54514 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
46 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR1 | -- | [15 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
47 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR1 | -- | [15 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
48 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
49 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
50 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
51 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
52 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
53 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
54 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
55 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
56 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
57 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
58 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
59 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR1 | -- | [15 empty] | 744 | 330 |  | 330 | 330 | 100
60 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
61 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
62 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
63 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
64 | NR1SRT24 | GORAKH 80MVAR S/R BARH-I LINE | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
65 | NR1SRT25 | GORAKH 80MVAR S/R BARH-II LINE | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
66 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
67 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
68 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
69 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
70 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
71 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
72 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
73 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
74 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
75 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
76 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
77 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
78 | NR1SRT27 | PHAGI(JPR)240MVAR S/R BHIWANI-I | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 1900-05-31 09:54 | [9 empty] | 9823.4 | 9823.4 |  | %
|  | TOTAL | [8 empty] | 1900-02-13 02:39 | 1900-01-05 03:42 | 1900-01-17 14:26 | 1901-05-18 01:00
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L15:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M15:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N15:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O15:[Deemed Available, row above])
Note on C128: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C396: DOC-11-02-15
Note on C520: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14
Note on C716: DOC-15/06/14
Note on C717: DOC-26/09/14