## SOP DATA NR1 MAY-15
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-I
NAME OF REGION : NRTS-I
Availability calculation for the Period : From 01.06.2015 to 30.06.2015
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [24 empty] | 0
1 | NR176505 | 765 KV AGRA- MEERUT | 267.628 | NR1 | -- | 2015-07-12 12:07 | 2015-07-12 12:45 |  |  |  | 0 | 0 | 0 | 0.026389 |  |  |  | LVRD | Line hand tripped for Voltage regulation.MRT-805 KV | NRPC | [6 empty] | 744
[6 empty] | 2015-07-21 16:30 | 2015-07-21 21:39 |  |  |  | 0.21458 | 0 | 0 | 0 |  |  |  | OSFT | S/D for tightening of wave trap jumper at Agra.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.21458 | 0 | 0 | 0.026389 | [6 empty] | 744 | 1779 | 267.628 | 476110.212 | 472814.5566 | 99.3078
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | 2015-07-13 12:52 | 2015-07-13 16:40 |  |  |  | 0.15833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for attending hot spot in R-Ph jumper on Loc no-678.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.15833 | 0 | 0 | 0 | [6 empty] | 744 | 1747 | 253.076 | 442123.772 | 439865.6129 | 99.4892
5 | NR176503 | 765KV FATEHPUR-GAYA | 484.6 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1070 | 484.6 | 518522 | 518522 | 100
6 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR1 | -- | 2015-07-07 17:15 | 2015-07-07 18:04 |  |  |  | 0 | 0.034028 | 0 | 0 |  |  |  | OMSU | Tripped on L/Reactor PRV Mal-opeartion at Fthpur due to moisture developed during Rain.
[5 empty] | -- | 2015-07-15 07:04 | 2015-07-15 08:39 | -- | -- | -- | 0 | 0.065972 | 0 | 0 | -- | -- | -- | OMSU | L/Reactor PRV relay mall operated at Fatehpur. Charged without line reactor.
[6 empty] | 2015-07-15 16:17 | 2015-07-15 16:54 | -- | -- | -- | 0.025694 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for taking L/R in service at Fatehpur.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.025694 | 0.1 | 0 | 0 | [6 empty] | 744 | 1067 | 355.008 | 378793.536 | 378479.5718 | 99.9171
7 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
8 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR1 | -- | 2015-07-01 09:06 | 2015-07-01 20:26 |  |  |  | 0.47222 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line maintenance/ missing part fixing work.
[5 empty] | -- | 2015-07-02 08:53 | 2015-07-02 21:57 |  |  |  | 0.54444 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line maintenance/ missing part fixing work.
[5 empty] | -- | 2015-07-03 15:34 | 2015-07-03 21:59 |  |  |  | 0 | 0 | 0 | 0.26736 |  |  |  | LCSD | S/D for erection & comisioning of 765kv B/Reactor at BLY.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 00:24 | 0 | 0 | 0.26736 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 247985.0381 | 96.7204
B |  | 400 KV TRANS LINES |  |  | --
1 | NR140001 | 400KV AGRA-AGRA(UP)-I | 29.982 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR1 | -- | 2015-07-07 08:55 | 2015-07-07 22:55 | -- | -- | -- | 0.58333 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for L/R bushing replacement at Agra.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.58333 | 0 | 0 | 0 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 60207.7312 | 98.1183
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR1 | -- | 2015-07-04 19:01 | 2015-07-04 19:05 |  |  |  | 0.0027778 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/Reactor in service at Agra.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.0027778 | 0 | 0 | 0 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61356.9016 | 99.991
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR1 | -- | 2015-07-07 09:46 | 2015-07-10 22:47 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 13:01 | -- | -- | -- | LCSD | S/D for retro-fitment of all relay panels under Addcap after completion of 25 yrs at Bassi.
[5 empty] | -- | 2015-07-28 03:24 | 2015-07-28 10:06 | -- | -- | -- | 0 | 0 | 0 | 0.27917 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 19:43 | [6 empty] | 744 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR1 | -- | 2015-07-01 03:32 | 2015-07-03 08:58 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 05:26 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-431 kV
[6 empty] | 2015-07-11 02:04 | 2015-07-13 09:03 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:59 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-436 KV
[6 empty] | 2015-07-19 03:10 | 2015-07-20 13:03 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:53 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-433 KV
[6 empty] | 2015-07-26 03:26 | 2015-07-27 09:45 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:19 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-06 04:37 | [6 empty] | 744 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2015-07-11 02:08 | 2015-07-13 11:47 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:39 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-436 KV
[6 empty] | 2015-07-15 10:40 | 2015-07-15 11:06 | -- | -- | -- | 0.018056 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for implementation of L/R NGR bypass scheme at Jpr-s.
[6 empty] | 2015-07-15 13:02 | 2015-07-15 13:12 | -- | -- | -- | 0.0069444 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for implementation of L/R NGR bypass scheme at Jpr-s.
[6 empty] | 2015-07-26 01:06 | 2015-07-27 10:19 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:13 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.025 | 0 | 0 | 1900-01-02 18:52 | -- | -- | -- |  |  |  | 744 | 307 | 253.823 | 77923.661 | 77860.8193 | 99.9194
10 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2015-07-15 14:50 | 2015-07-15 14:58 | -- | -- | -- | 0.0055556 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for implementation of L/R NGR bypass scheme at Jpr-s.
[5 empty] | -- | 2015-07-15 17:10 | 2015-07-15 17:52 |  |  |  | 0.029167 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for taking L/R in service after NGR by pass at Jaipur-s
[6 empty] | 2015-07-19 04:26 | 2015-07-21 11:17 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:51 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-433 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.034722 | 0 | 0 | 1900-01-01 06:51 | -- | -- | -- |  |  |  | 744 | 307 | 253.823 | 77923.661 | 77836.3809 | 99.888
11 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2015-07-08 04:35 | 2015-07-13 12:52 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 08:17 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-431 KV
[5 empty] | -- | 2015-07-19 02:21 | 2015-07-21 12:14 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:53 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-433 KV
[5 empty] | -- | 2015-07-22 04:02 | 2015-07-22 10:05 | -- | -- | -- | 0 | 0 | 0 | 0.25208 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-07-26 00:10 | 2015-07-27 10:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:34 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-07-30 05:45 | 2015-08-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 18:15 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 05:02 | -- | -- | -- |  |  |  | 744 | 568 | 393.9 | 223735.2 | 223735.2 | 100
12 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2015-07-12 04:25 | 2015-07-13 09:15 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:50 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-431 KV
[5 empty] | -- | 2015-07-14 03:37 | 2015-07-14 17:19 | -- | -- | -- | 0 | 0 | 0 | 0.57083 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[5 empty] | -- | 2015-07-23 11:57 | 2015-07-23 19:32 | -- | -- | -- | 0.31597 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for replacement of faulty B-ph CVT at Agra.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.31597 | 0 | 0 | 1899-12-31 18:32 | -- | -- | -- |  |  |  | 744 | 568 | 393.9 | 223735.2 | 221454.7449 | 98.9807
13 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR1 | -- | [15 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
14 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
15 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 155.932 | 80304.98 | 80304.98 | 100
16 | NR140012 | 400KV ALLD-KNP-II | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 224 | 115360 | 115360 | 100
17 | NR140019 | 400KV BALIA-MAU-I | 13 | NR1 | -- | 2015-07-05 16:34 | 2015-07-05 17:04 | -- | -- |  | 0 | 0.020833 | 0 | 0 | -- | -- | -- | OMSU | CB A/trip only at Mau-UPPCL end. No flag/facia reported. Line remain charged from Balia end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.020833 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
18 | NR140020 | 400KV BALIA-MAU-II | 13 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
19 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR1 | -- | 2015-07-02 09:07 | 2015-07-04 18:33 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:26 |  |  |  | LCSD | S/D for FSC erection work at Soahwal.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:26 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 52020.001 | 100
20 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 52020.001 | 100
21 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR1 | -- | [15 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
22 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR1 | [16 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
23 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
24 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
25 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR1 | -- | 2015-07-23 16:15 | 2015-07-23 16:31 | -- | -- | -- | 0.011111 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for isolating L/R to implement NGR bypass at Bareily.
[6 empty] | 2015-07-23 17:37 | 2015-07-23 17:43 |  |  |  | 0.0041667 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking in L/R after NGR bypassing at Bareily.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.015278 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 331 | 278.76 | 92269.56 | 92224.0867 | 99.9507
26 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR1 | -- | 2015-07-12 10:03 | 2015-07-12 10:46 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | OMSU | CB autotrip at MBD/UPPCL end only. Remain charged from BLY. No flag/facia reported.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.029861 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
27 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
28 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR1 | -- | 2015-07-14 10:14 | 2015-07-14 19:43 | -- | -- | -- | 0 | 0 | 0 | 0.39514 | -- | -- | -- | OSFD | S/D taken by Rosa-UPPCL to attend hot spot at loc -29.
[6 empty] | 2015-07-21 16:40 | 2015-07-21 17:33 |  |  |  | 0 | 0.036806 | 0 | 0 |  |  |  | OMSU | CB A/Trip at Roja-UPPCL end only. No flag facia reported. Line remain charged from Bareilly.
[6 empty] | 2015-07-21 19:42 | 2015-07-21 20:41 |  |  |  | 0 | 0.040972 | 0 | 0 |  |  |  | OMSU | CB A/Trip at Roja-UPPCL end only. No flag facia reported. Line remain charged from Bareilly.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.077778 | 0 | 0.39514 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
29 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR1 | [16 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 | 100
30 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR1 |  | 2015-07-12 07:11 | 2015-07-12 08:23 |  |  |  | 0 | 0.05 | 0 | 0 |  |  |  | SBBU | Busbar protn opted at Kashipur/PITCUL stn.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.05 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
31 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR1 |  | 2015-07-12 07:11 | 2015-07-12 14:14 |  |  |  | 0 | 0.29375 | 0 | 0 |  |  |  | SBBU | Busbar protn opted at Kashipur/PITCUL stn. Remain out in want of clearance from PITCUL.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.29375 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
32 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 416 | 235 | 97760 | 97760 | 100
33 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 47.762 | 24597.43 | 24597.43 | 100
34 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | -- | 2015-07-14 08:31 | 2015-07-16 15:48 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:17 |  |  |  | LCSD | S/D for retro-fitment of all relay panels under Addcap after completion of 25 yrs at Bassi.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 07:17 | -- | -- | -- |  |  |  | 744 | 515 | 48.99 | 25229.85 | 25229.85 | 100
35 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | -- | 2015-07-04 11:51 | 2015-07-04 12:53 | -- | -- | -- | 0.043056 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D to attend hotspot in B-ph line isolator at Jaipur(S).
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.043056 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 37.164 | 19139.46 | 19112.8774 | 99.8611
36 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 37.164 | 19139.46 | 19139.46 | 100
37 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- | 2015-07-01 11:58 | 2015-07-01 13:10 | -- | -- | -- | 0.05 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D to attend sparking in R-Ph line isolator at Bassi.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.05 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 247 | 106.153 | 26219.791 | 26177.501 | 99.8387
38 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 48.432 | 33272.784 | 33272.784 | 100
39 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 48.432 | 33272.784 | 33272.784 | 100
40 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | 2015-07-22 08:21 | 2015-07-22 19:17 |  |  |  | 0 | 0 | 0 | 0.45556 |  |  |  | LCSD | S/D for stringing of 765kv KNP-Jhatikala line.
[6 empty] | 2015-07-23 08:35 | 2015-07-23 19:38 |  |  |  | 0 | 0 | 0 | 0.46042 |  |  |  | LCSD | S/D for stringing of 765kv KNP-Jhatikala line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.91597 | -- | -- | -- |  |  |  | 744 | 515 | 82.8 | 42642 | 42642 | 100
41 | NR140033 | 400KV BHIWADI-HISAR | 211.547 | NR1 | -- | 2015-07-11 04:01 | 2015-07-13 12:16 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:15 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.BWD-431 KV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:15 | -- | -- | -- |  |  |  | 744 | 403 | 211.547 | 85253.441 | 85253.441 | 100
42 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 132.428 | 68200.42 | 68200.42 | 100
43 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2015-07-12 04:29 | 2015-07-13 12:32 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:03 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.BWD-431 KV
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:03 | -- | -- | -- |  |  |  | 744 | 515 | 48.428 | 24940.42 | 24940.42 | 100
44 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | -- | 2015-07-26 03:44 | 2015-07-27 10:10 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 06:26 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.BWD-428 KV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 06:26 | -- | -- | -- |  |  |  | 744 | 515 | 48.428 | 24940.42 | 24940.42 | 100
45 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 42.7 | 21990.5 | 21990.5 | 100
46 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 60.68 | 41929.88 | 41929.88 | 100
47 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR1 | -- | 2015-07-11 04:12 | 2015-07-13 11:18 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 07:06 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.MNP-432 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 07:06 | -- | -- | -- |  |  |  | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
48 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR1 | -- | 2015-07-26 11:40 | 2015-07-27 09:50 | -- | -- |  | 0 | 0 | 0 | 0.92361 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.MNP-428 KV
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.92361 | -- | -- | -- |  |  |  | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
49 | NR140138 | 400KV BLBGRH-NAVADA | 12.55 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 12.55 | 8672.05 | 8672.05 | 100
50 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | -- | 2015-07-13 07:15 | 2015-07-13 08:00 | -- | -- |  | 0 | 0.03125 | 0 | 0 | -- | -- | -- | SBBU | Bus Bar Protection operated at Gr. Noida UPPCL end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.03125 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 13.256 | 9159.896 | 9159.896 | 100
51 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | -- | 2015-07-29 15:52 | 2015-07-29 17:50 | -- | -- |  | 0 | 0.081944 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on R-Y fault due to kite thread, reported by Mahranibag, FLR:Dadri-54.2km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.081944 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 54.36 | 37562.76 | 37562.76 | 100
52 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 46.3 | 31993.3 | 31993.3 | 100
53 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 46.3 | 31993.3 | 31993.3 | 100
54 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2015-07-13 16:24 | 2015-07-13 16:52 | -- | -- |  | 0 | 0.019444 | 0 | 0 | -- | -- | -- | OMSU | Tripped at Dadri-NTPC on CVT fuse failure.
[5 empty] | -- | 2015-07-13 16:52 | 2015-07-14 03:04 | -- | -- |  | 0 | 0 | 0 | 0.425 | -- | -- | -- | OSFD | Forced S/D Taken by NTPC-Dadri for CVT testing.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.019444 | 0 | 0.425 | -- | -- | -- |  |  |  | 744 | 515 | 33.098 | 17045.47 | 17045.47 | 100
55 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 | -- | 2015-07-29 08:26 | 2015-07-29 09:22 |  |  |  | 0 | 0.038889 | 0 | 0 |  |  |  | OMSU | Line A/R at Dadri-NTPC but tripped from Panipat-BBMB due to A/R problem on B-N fault, Dadri-26.38km, Pnpt-84km
[6 empty] | 2015-07-30 05:36 | 2015-07-30 06:16 |  |  |  | 0 | 0.027778 | 0 | 0 |  |  |  | OMSU | Line A/R at Dadri-NTPC but tripped from Panipat-BBMB due to A/R problem on B-N fault. Dad-85.7km,Pnpt-24.54km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.066667 | 0 | 0 | [6 empty] | 744 | 515 | 112.322 | 57845.83 | 57845.83 | 100
56 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 117 | 60255 | 60255 | 100
57 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR1 | -- | 2015-07-05 11:44 | 2015-07-05 12:03 | -- | -- | -- | 0 | 0.013194 | 0 | 0 | -- | -- | -- | OMSU | NGR bucholz operated in L/R at Mainpuri end.
[6 empty] | 2015-07-07 09:55 | 2015-07-07 16:52 |  |  |  | 0.28958 | 0 | 0 | 0 |  |  |  | OSPT | S/D for attending hot spot in B-ph L/R jumper at Mnp end.
[6 empty] | 2015-07-10 16:57 | 2015-07-10 18:05 |  |  |  | 0.047222 | 0 | 0 | 0 |  |  |  | SRET | Line reactor REF protection operated at MNP.
[6 empty] | 2015-07-11 08:26 | 2015-07-13 11:06 |  |  |  | 0 | 0 | 0 | 1900-01-01 02:40 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-432KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.33681 | 0.013194 | 0 | 1900-01-01 02:40 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 120638.8182 | 98.9135
58 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR1 | -- | 2015-07-22 11:27 | 2015-07-22 14:48 | -- | -- | -- | 0.13958 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D to attend the R-phase line isolator hot spot at Mainpuri.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.13958 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 121414.7535 | 99.5497
59 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
60 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
61 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 23.462 | 16118.394 | 16118.394 | 100
62 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 23.462 | 16118.394 | 16118.394 | 100
63 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | 2015-07-01 | 2015-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-30 |  |  |  | OSPD | S/D by DTL for maintenance work at Bmnoli end. Open since 16.03.15 at 13:04hrs.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- |  |  |  | 744 | 687 | 6.106 | 4194.822 | 4194.822 | 100
64 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | 2015-07-07 19:01 | 2015-07-07 19:35 |  |  |  | 0 | 0.023611 | 0 | 0 |  |  |  | OMSU | Tripped only from Bamnoli (DTL) end on relay maloperation
[6 empty] | 2015-07-13 19:06 | 2015-07-13 19:17 |  |  |  | 0 | 0.0076389 | 0 | 0 |  |  |  | OMSU | Tripped only at Bamnoli-DTL end due to relay mal operation.
[6 empty] | 2015-07-21 15:31 | 2015-07-21 21:05 |  |  |  | 0 | 0.23194 | 0 | 0 |  |  |  | OMSU | Line tripped due to snapping of Y-ph conductor on ERS at Bhamnauli DTL end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.26319 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 6.106 | 4194.822 | 4194.822 | 100
65 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 6.782 | 4659.234 | 4659.234 | 100
66 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 6.782 | 4659.234 | 4659.234 | 100
67 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 225 | 201.2 | 45270 | 45270 | 100
68 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 | -- | 2015-07-11 11:12 | 2015-07-11 14:09 | -- | -- | -- | 0 | 0 | 0 | 0.12292 | -- | -- | -- | OSPD | S/D by RRVPNL to attend isolator hotspot at Jodhpur.
[6 empty] | 2015-07-22 15:04 | 2015-07-22 16:07 |  |  |  | 0.04375 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend the hot spot at loc no. 132 by Kankroli.
[6 empty] | 2015-07-23 04:18 | 2015-07-23 07:17 |  |  |  | 0 | 0 | 0 | 0.12431 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Jodhpur-430 KV
[6 empty] | 2015-07-24 01:27 | 2015-07-24 06:40 |  |  |  | 0 | 0 | 0 | 0.21736 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Jodhpur-430 KV
[6 empty] | 2015-07-25 02:10 | 2015-07-30 20:30 |  |  |  | 0 | 0 | 0 | 1900-01-04 18:20 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Kankroli-427kv.
[6 empty] | 2015-07-31 04:20 | 2015-07-31 04:25 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on O/Voltage protn at Jodhpur. D/T recd at Kota
[6 empty] | 2015-07-31 04:25 | 2015-07-31 06:01 |  |  |  | 0 | 0 | 0 | 0.066667 |  |  |  | LVRD | Line kept open for Voltage regulation. Jodhpur=434kv
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.04375 | 0 | 0.0034722 | 1900-01-05 07:05 | -- | -- | -- |  |  |  | 743.9167 | 515 | 187.965 | 96801.975 | 96665.344 | 99.8589
69 | NR140050 | 400KV KANKROLI-RAPPC-I | 198.54 | NR1 | -- | 2015-07-08 18:01 | 2015-07-08 18:37 |  |  |  | 0 | 0.025 | 0 | 0 |  |  |  | OMSU | Line A/R at Kank but tripped due to relay problem at RAPPC during B-N transient fault. FLR:Knk-178.4km.
[5 empty] | -- | 2015-07-27 00:10 | 2015-07-27 11:45 |  |  |  | 0 | 0 | 0 | 0.48264 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Kank-428 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.025 | 0 | 0.48264 | -- | -- | -- |  |  |  | 744 | 395 | 198.54 | 78423.3 | 78423.3 | 100
70 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 395 | 198.54 | 78423.3 | 78423.3 | 100
71 | NR140052 | 400KV KNP-AGRA | 240 | NR1 | -- | 2015-07-06 08:20 | 2015-07-06 17:24 |  |  |  | 0 | 0 | 0 | 0.37778 |  |  |  | LCSD | S/D for stringing work of 765 KV KNP-Jhatikra line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.37778 | -- | -- | -- |  |  |  | 744 | 291 | 240 | 69840 | 69840 | 100
72 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR1 | -- | 2015-07-27 10:43 | 2015-07-27 21:10 |  |  |  | 0 | 0 | 0 | 0.43542 |  |  |  | LCSD | S/D for stringing of 765kv KNP-Jhatikala line.
[5 empty] | -- | 2015-07-28 07:48 | 2015-07-28 18:17 |  |  |  | 0 | 0 | 0 | 0.43681 |  |  |  | LCSD | S/D for stringing of 765kv KNP-Jhatikala line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.87222 | -- | -- | -- |  |  |  | 744 | 515 | 72.6 | 37389 | 37389 | 100
73 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR1 | -- | 2015-07-27 10:52 | 2015-07-27 21:13 | -- | -- |  | 0 | 0 | 0 | 0.43125 | -- | -- | -- | LCSD | S/D for stringing of 765kv KNP-Jhatikala line.
[6 empty] | 2015-07-28 07:48 | 2015-07-28 18:18 |  |  |  | 0 | 0 | 0 | 0.4375 |  |  |  | LCSD | S/D for stringing of 765kv KNP-Jhatikala line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.86875 | -- | -- | -- |  |  |  | 744 | 515 | 73.2 | 37698 | 37698 | 100
74 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR1 | -- | 2015-07-01 10:08 | 2015-07-01 19:44 | -- | -- |  | 0.4 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for replacement of Y-Ph defective CT at Kanpur.
[6 empty] | 2015-07-12 09:33 | 2015-07-14 07:59 |  |  |  | 0 | 0 | 0 | 1899-12-31 22:26 |  |  |  | LVRD | Line hand tripped for Voltage regulation.BLB-431 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.4 | 0 | 0 | 1899-12-31 22:26 | -- | -- | -- |  |  |  | 744 | 342 | 385.69 | 131905.98 | 130203.9674 | 98.7097
75 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR1 | -- | 2015-07-02 10:13 | 2015-07-02 15:35 | -- | -- |  | 0 | 0 | 0 | 0.22361 | -- | -- | -- | LCSD | S/D for L/reactor CSD relay retrofitment at BLB.
[6 empty] | 2015-07-21 11:17 | 2015-07-21 11:27 |  |  |  | 0.0069444 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R out for NGR bypassing at BLB.
[6 empty] | 2015-07-21 16:48 | 2015-07-21 16:59 |  |  |  | 0.0076389 | 0 | 0 | 0 |  |  |  | OSPT | S/D for L/R taking in service after NGR bypass at Blb
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.014583 | 0 | 0 | 0.22361 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 133785.7255 | 99.953
76 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR1 | -- | 2015-07-21 17:13 | 2015-07-21 17:24 | -- | -- | -- | 0.0076389 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for L/R out of service for NGR bypass at BLB
[6 empty] | 2015-07-21 18:16 | 2015-07-21 18:36 |  |  |  | 0.013889 | 0 | 0 | 0 |  |  |  | OSPT | S/D for L/R taking in service after NGR bypass at Blb
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.021528 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 133755.7415 | 99.9306
77 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR1 | -- | 2015-07-14 15:42 | 2015-07-14 17:40 | -- | -- | -- | 0.081944 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for isolator de-jumpering for retrofitment at KNP.
[5 empty] | -- | 2015-07-24 16:55 | 2015-07-24 17:10 | -- | -- | -- | 0.010417 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for Jumpering between isolator and Jack Bus at Kanpur but could not be availed due to heavy rain.
[5 empty] | -- | 2015-07-25 14:47 | 2015-07-25 18:05 | -- | -- | -- | 0.1375 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for Jumpering between isolator and Jack Bus at KNP.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.22986 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 107.079 | 55145.685 | 54736.7867 | 99.2585
78 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 107.1 | 55156.5 | 55156.5 | 100
79 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 5.922 | 3049.83 | 3049.83 | 100
80 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR1 | -- | [15 empty] | 744 | 515 | 5.86 | 3017.9 | 3017.9 | 100
81 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- | 2015-07-04 15:45 | 2015-07-04 16:11 | -- | -- | -- | 0.018056 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for L/Reactor isolation at Kota for bushing DGA.
[6 empty] | 2015-07-27 04:01 | 2015-07-27 04:40 |  |  |  | 0 | 0 | 0.027083 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection. Kota-435KV
[6 empty] | 2015-07-28 03:58 | 2015-07-28 04:03 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection. Kota=437kv
[6 empty] | 2015-07-28 04:03 | 2015-07-28 06:47 |  |  |  | 0 | 0 | 0 | 0.11389 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.018056 | 0 | 0.030556 | 0.11389 | [6 empty] | 743.2667 | 515 | 179.711 | 92551.165 | 92497.2066 | 99.9417
82 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- | 2015-07-01 18:08 | 2015-07-02 21:50 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 03:42 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation.Merta-425kV
[6 empty] | 2015-07-05 11:49 | 2015-07-05 15:50 |  |  |  | 0.16736 | 0 | 0 | 0 |  |  |  | OSPT | S/D for repairing of R-phase jumper at loc no. 434
[6 empty] | 2015-07-09 01:00 | 2015-07-09 07:29 |  |  |  | 0 | 0 | 0 | 0.27014 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Kota-425 KV
[6 empty] | 2015-07-10 17:40 | 2015-07-14 08:32 |  |  |  | 0 | 0 | 0 | 1900-01-02 14:52 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Kota-425 KV
[6 empty] | 2015-07-18 18:20 | 2015-07-21 12:12 |  |  |  | 0 | 0 | 0 | 1900-01-01 17:52 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-422KV
[6 empty] | 2015-07-21 18:31 | 2015-07-22 10:24 |  |  |  | 0 | 0 | 0 | 0.66181 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-424KV
[6 empty] | 2015-07-23 03:54 | 2015-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-07 20:06 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-430KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.16736 | 0 | 0 | 1900-01-16 06:54 | -- | -- | -- |  |  |  | 744 | 309 | 255.56 | 78968.04 | 78541.7116 | 99.4601
83 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | -- | 2015-07-26 03:47 | 2015-07-26 03:52 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on O/Voltage protection. Kota>435kv. due to continuous rain and load crash in Rajasthan.
[6 empty] | 2015-07-26 03:52 | 2015-07-26 07:51 |  |  |  | 0 | 0 | 0 | 0.16597 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage.
[5 empty] | -- | 2015-07-26 16:45 | 2015-07-26 16:50 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection. Kota-434KV.
[5 empty] | -- | 2015-07-26 16:50 | 2015-07-26 21:28 |  |  |  | 0 | 0 | 0 | 0.19306 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage.
[5 empty] | -- | 2015-07-27 02:09 | 2015-07-27 02:14 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection. Kota-436KV
[5 empty] | -- | 2015-07-27 02:14 | 2015-07-27 05:50 |  |  |  | 0 | 0 | 0 | 0.15 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage.
[5 empty] | -- | 2015-07-27 23:13 | 2015-07-27 23:17 |  |  |  | 0 | 0 | 0.0027778 | 0 |  |  |  | GOVC | Tripped on O/ Voltage protection. RAPC 438KV
[5 empty] | -- | 2015-07-27 23:17 | 2015-07-28 10:23 |  |  |  | 0 | 0 | 0 | 0.4625 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage.
[5 empty] | -- | 2015-07-28 10:59 | 2015-07-28 11:05 |  |  |  | 0 | 0 | 0.0041667 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection. RAPC- 435KV
[5 empty] | -- | 2015-07-28 11:05 | 2015-07-29 10:23 |  |  |  | 0 | 0 | 0 | 0.97083 |  |  |  | LVRD | Kept open for V/Regulation. RAPC=437kv.
[5 empty] | -- | 2015-07-30 01:59 | 2015-07-30 02:05 |  |  |  | 0 | 0 | 0.0041667 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection at RAPPC>436kv.
[5 empty] | -- | 2015-07-30 02:05 | 2015-07-30 16:25 |  |  |  | 0 | 0 | 0 | 0.59722 |  |  |  | LVRD | Line kept open for Voltage regulation.Kota-430 KV
[5 empty] | -- | 2015-07-30 16:25 | 2015-07-30 18:15 |  |  |  | 0.076389 | 0 | 0 | 0 |  |  |  | OSPT | S/D for testing of CVT at Kota.
[5 empty] | -- | 2015-07-30 18:15 | 2015-07-30 20:25 |  |  |  | 0 | 0.090278 | 0 | 0 |  |  |  | OMSU | Charging delay by RAPPC after issue of NRLDC code.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.076389 | 0.090278 | 0.021528 | 1900-01-01 12:57 | -- | -- | -- |  |  |  | 743.4833 | 515 | 50.5 | 26007.5 | 25943.3689 | 99.7534
84 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.7 | 1390.5 | 1390.5 | 100
85 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.7 | 1390.5 | 1390.5 | 100
86 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 633 | 14.463 | 9155.079 | 9155.079 | 100
87 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 633 | 16.49 | 10438.17 | 10438.17 | 100
88 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
89 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
90 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR1 | -- | [15 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
91 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR1 | -- | [15 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
92 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
93 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR1 | -- | 2015-07-31 11:41 | 2015-07-31 11:44 |  |  |  | 0.0020833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for L/R NGR bypassing work at Lucknow
[6 empty] | 2015-07-31 17:58 | 2015-07-31 18:02 |  |  |  | 0.0027778 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R in service after bypassing NGR.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.0048611 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 371 | 169.785 | 62990.235 | 62980.3575 | 99.9843
94 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR1 |  | 2015-07-11 20:39 | 2015-07-11 21:08 |  |  |  | 0.020139 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault in reclaim time. FLR:LKO=126km, Shjpur=9.25km.
[6 empty] | 2015-07-12 01:54 | 2015-07-12 16:32 |  |  |  | 0.60972 | 0 | 0 | 0 |  |  |  | OSFT | Forced s/d due to multiple A/R on B-N fault at same distance. Charged after patrolling. Sjhanpur=9.02km.
[6 empty] | 2015-07-22 15:05 | 2015-07-22 18:00 |  |  |  | 0.12153 | 0 | 0 | 0 |  |  |  | OSPT | S/D for OFF line fault locator testing demo at Lucknow.
[6 empty] | 2015-07-30 15:41 | 2015-07-30 15:52 |  |  |  | 0.0076389 | 0 | 0 | 0 |  |  |  | OSPT | S/D for L/R NGR bypassing work at Lucknow
[6 empty] | 2015-07-30 17:21 | 2015-07-30 17:38 |  |  |  | 0.011806 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R in service after bypassing NGR at Lko.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.77083 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 169.729 | 87410.435 | 85236.9228 | 97.5134
95 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
96 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
97 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR1 | -- | 2015-07-08 09:50 | 2015-07-10 19:41 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:51 | -- | -- | -- | OSPD | S/D by UPPCL for installation of polymer insulator string.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:51 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
98 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
99 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
100 | NR140076 | 400KV MBAD-MURADNGR | 133.5 | NR1 | -- | 2015-07-12 07:01 | 2015-07-12 08:16 |  |  |  | 0 | 0.052083 | 0 | 0 |  |  |  | OMSU | Tripped due to A/R problem at UPPCL during R-N transient fault. FLR:MBD=82.6km, Mngr=36.65km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.052083 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 133.5 | 68752.5 | 68752.5 | 100
101 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
102 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
103 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | -- | 2015-07-12 22:43 | 2015-07-13 13:00 |  |  |  | 0.59514 | 0 | 0 | 0 |  |  |  | OSFT | Hand tripped due to sparking and damage of B-ph conductor near gantry at Koteshwar.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.59514 | 0 | 0 | 0 | [6 empty] | 744 | 678 | 178.69 | 121151.82 | 118825.9439 | 98.0802
104 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 673 | 175.63 | 118198.99 | 118198.99 | 100
105 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 59.868 | 30832.02 | 30832.02 | 100
106 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 | -- | [15 empty] | 744 | 515 | 59.868 | 30832.02 | 30832.02 | 100
107 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 54.298 | 27963.47 | 27963.47 | 100
108 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | -- | 2015-07-12 09:49 | 2015-07-13 17:23 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:34 |  |  |  | LVRD | Line hand tripped for Voltage regulation.MRT-431 KV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:34 | 0 | 0 | 0 |  |  |  | 744 | 515 | 54.298 | 27963.47 | 27963.47 | 100
109 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | -- | 2015-07-12 08:46 | 2015-07-12 09:35 |  |  |  | 0 | 0.034028 | 0 | 0 |  |  |  | OMSU | CB autotrip at Muzaferngr/UPPCL end only. Remain charged from MRT. No flag/facia reported.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.034028 | 0 | 0 | [6 empty] | 744 | 515 | 37.38 | 19250.7 | 19250.7 | 100
110 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 76.018 | 39149.27 | 39149.27 | 100
111 | NR140139 | 400KV NAVADA-GR.NOIDA | 30.15 | NR1 | -- | 2015-07-01 09:18 | 2015-07-01 20:30 | -- | -- | -- | 0.46667 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for jumpher tightening work on new tower at loc.68.
[6 empty] | 2015-07-13 07:15 | 2015-07-13 08:11 |  |  |  | 0 | 0.038889 | 0 | 0 |  |  |  | SBBU | Bus Bar Protection operated at Gr. Noida UPPCL end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.46667 | 0.038889 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 30.15 | 20833.65 | 20520.0252 | 98.4946
112 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 67.041 | 34526.115 | 34526.115 | 100
113 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 67.041 | 34526.115 | 34526.115 | 100
114 | NR140108 | 400KV NIMRANA-SIKAR-I | 175.859 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 175.859 | 90567.385 | 90567.385 | 100
115 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 175.859 | 90567.385 | 90567.385 | 100
116 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
117 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
118 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | 2015-07-05 13:06 | 2015-07-05 13:40 |  |  |  | 0 | 0.023611 | 0 | 0 |  |  |  | OMSU | Line A/R at Roorkee but tripped from Muzfrngr on Y-N fault in UPPCL portion. FLR:Roorkee-48km
[5 empty] | -- | 2015-07-06 08:55 | 2015-07-06 09:24 |  |  |  | 0 | 0.020139 | 0 | 0 |  |  |  | OMSU | Line tripped Due to PLCC malfunction at Muzaffarngr-UP. D/T received at Roorkee.
[5 empty] | -- | 2015-07-12 08:46 | 2015-07-12 09:33 |  |  |  | 0 | 0.032639 | 0 | 0 |  |  |  | OMSU | Tripped on R-N Fault in UPPCL portion. Roorki=60.9km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.076389 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.1 | 1081.5 | 1081.5 | 100
119 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 2.1 | 1081.5 | 1081.5 | 100
120 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 |  | 2015-07-01 | 2015-07-01 13:39 |  |  |  | 0 | 0 | 0 | 0.56875 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Rtngrh-425kV. Open since 13:06hrs of 30/6/15.
[6 empty] | 2015-07-01 16:44 | 2015-07-03 09:01 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:17 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Rtngrh-425kV
[6 empty] | 2015-07-03 18:03 | 2015-07-04 07:13 |  |  |  | 0 | 0 | 0 | 0.54861 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Rtngrh-425kV
[6 empty] | 2015-07-05 18:47 | 2015-07-06 07:29 |  |  |  | 0 | 0 | 0 | 0.52917 |  |  |  | LVRD | Line hand tripped for Voltage regulation , Sikar-430 KV
[6 empty] | 2015-07-08 02:28 | 2015-07-12 07:24 |  |  |  | 0 | 0 | 0 | 1900-01-03 04:56 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421 KV
[6 empty] | 2015-07-12 12:35 | 2015-07-14 09:45 |  |  |  | 0 | 0 | 0 | 1899-12-31 21:10 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421 KV
[6 empty] | 2015-07-14 18:57 | 2015-07-15 07:50 |  |  |  | 0 | 0 | 0 | 0.53681 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-418 KV
[6 empty] | 2015-07-18 17:16 | 2015-07-21 07:01 |  |  |  | 0 | 0 | 0 | 1900-01-01 13:45 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-421 KV
[6 empty] | 2015-07-22 03:14 | 2015-07-22 10:10 |  |  |  | 0 | 0 | 0 | 0.28889 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-428 KV
[6 empty] | 2015-07-22 17:23 | 2015-07-23 08:17 |  |  |  | 0 | 0 | 0 | 0.62083 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Agra-430 KV
[6 empty] | 2015-07-24 16:59 | 2015-07-30 08:26 |  |  |  | 0 | 0 | 0 | 1900-01-04 15:27 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Merta-430 KV
[6 empty] | 2015-07-30 22:06 | 2015-08-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 01:54 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sikar-430 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-19 03:43 | -- | -- | -- |  |  |  | 744 | 515 | 76.48 | 39387.2 | 39387.2 | 100
121 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 |  | 2015-07-30 03:34 | 2015-08-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 20:26 |  |  |  | LVRD | Line hand tripped for Voltage regulation.Sikar-432 KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 20:26 | -- | -- | -- |  |  |  | 744 | 515 | 76.48 | 39387.2 | 39387.2 | 100
122 | NR140091 | 400KV SING-ALLD-I | 224 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 332 | 224 | 74368 | 74368 | 100
123 | NR140092 | 400KV SING-ALLD-II | 202 | NR1 | -- | [15 empty] | 744 | 306 | 202 | 61812 | 61812 | 100
124 | NR140093 | 400KV SING-ANPARA | 25.057 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 25.057 | 12904.355 | 12904.355 | 100
125 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 236 | 330.953 | 78104.908 | 78104.908 | 100
126 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 337 | 408.6 | 137698.2 | 137698.2 | 100
127 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR1 | -- | 2015-07-29 21:59 | 2015-07-29 22:20 | -- | -- |  | 0 | 0.014583 | 0 | 0 | -- | -- | -- | OMSU | CB A/trip only at Singrauli end during CT testing of ckt-II after replacement work by NTPC.
[5 empty] | -- | 2015-07-29 23:01 | 2015-07-29 23:20 | -- | -- |  | 0 | 0.013194 | 0 | 0 | -- | -- | -- | OMSU | CB A/trip only at Singrauli end during CT testing of ckt-II after replacement work by NTPC.
[5 empty] | -- | 2015-07-29 23:23 | 2015-07-29 23:56 | -- | -- |  | 0 | 0.022917 | 0 | 0 | -- | -- | -- | OMSU | CB A/trip only at Singrauli end during CT testing of ckt-II after replacement work by NTPC.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.050694 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 42.026 | 21643.39 | 21643.39 | 100
128 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR1 | -- | 2015-07-29 11:00 | 2015-07-30 01:02 | -- | -- |  | 0 | 0 | 0 | 0.58472 | -- | -- | -- | OSPD | S/D by NTPC-Singrauli for faulty CT replacement work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.58472 | -- | -- | -- |  |  |  | 744 | 515 | 43.952 | 22635.28 | 22635.28 | 100
129 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 3.341 | 1720.615 | 1720.615 | 100
130 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 3.317 | 1708.255 | 1708.255 | 100
131 | N-W40003 | 400KV KANKROLI-ZERDA-I | 233.707 | NR1 | -- | 2015-07-28 01:43 | 2015-07-28 01:47 |  |  |  | 0 | 0 | 0.0027778 | 0 |  |  |  | GOVC | Tripped on O/ Voltage protection at Zerda>439kv. D/T recd at Kankroli.
[6 empty] | 2015-07-28 01:47 | 2015-07-29 10:07 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:20 |  |  |  | LVRD | Line kept open for V/regulation due to high grid voltage. | N-1736
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.0027778 | 1899-12-31 08:20 | -- | -- | -- |  |  |  | 743.9333 | 236 | 233.707 | 55154.852 | 55154.852 | 100
132 | N-W40004 | 400KV BHINMAL-ZERDA | 142.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 272 | 142.8 | 38841.6 | 38841.6 | 100
[5 empty] | -- | [17 empty] | 18194.993
|  | 220 KV TRANS LINES |  |  | --
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR1 | -- | 2015-07-05 10:28 | 2015-07-05 12:38 | -- | -- |  | 0 | 0.090278 | 0 | 0 | -- | -- | -- | SBBU | Bus Bar trip due to fire in s/y at Jhusi-UPPCL s/s.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.090278 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR1 | -- | [15 empty] | 744 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR1 | -- | 2015-07-07 11:10 | 2015-07-07 18:40 |  |  |  | 0 | 0 | 0 | 0.3125 |  |  |  | OSPD | S/D for by UPPCL for Jumpet tightening at Rewa-Road end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.3125 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
5 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | 2015-07-06 06:52 | 2015-07-08 21:25 |  |  |  | 0 | 0 | 0 | 1900-01-01 14:33 |  |  |  | OSPD | S/D by NTPC-Anta for annual bay equipmnt maintenance.
[6 empty] | 2015-07-26 04:33 | 2015-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-04 19:27 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Anta>240kv, due to continuous rain and load crash in Rajasthan.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-07 10:00 | -- | -- | -- |  |  |  | 744 | 132 | 186.667 | 24640.044 | 24640.044 | 100
6 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | 2015-07-15 07:12 | 2015-07-17 21:40 |  |  |  | 0 | 0 | 0 | 1900-01-01 14:28 |  |  |  | OSPD | S/D by NTPC for bay eqpmnt maintenance work at Anta.
[6 empty] | 2015-07-27 02:45 | 2015-07-27 08:41 |  |  |  | 0 | 0 | 0 | 0.24722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Anta>245kv, due to continuous rain and load crash in Rajasthan.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 20:24 | -- | -- | -- |  |  |  | 744 | 132 | 186.667 | 24640.044 | 24640.044 | 100
7 | NR122038 | 220KV ANTA-LALSOT | 180.287 | NR1 | -- | 2015-07-20 08:26 | 2015-07-22 12:57 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 04:31 | -- | -- | -- | OSPD | S/D by NTPC for annual bay eqpmnt mntc at Anta.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 04:31 | -- | -- | -- |  |  |  | 744 | 132 | 180.287 | 23797.884 | 23797.884 | 100
8 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- | 2015-07-11 06:02 | 2015-07-11 07:43 | -- | -- |  | 0 | 0.070139 | 0 | 0 | -- | -- | -- | OMSU | Line A/R at RAPPC but tripped from Anta due to A/R relay problem on B-N transient fault. FLR-20.82Km.
[5 empty] | -- | 2015-07-23 14:58 | 2015-07-23 17:24 | -- | -- |  | 0 | 0.10139 | 0 | 0 | -- | -- | -- | OMSU | Line tripped only from Anta-NTPC due to A/R relay problem during B-N transient fault. FLR:Anta-52.3km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.17153 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 87.544 | 11468.264 | 11468.264 | 100
9 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 102.164 | 13485.648 | 13485.648 | 100
10 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR1 | -- | 2015-07-05 16:04 | 2015-07-05 17:06 |  |  |  | 0 | 0.043056 | 0 | 0 |  |  |  | OMSU | CB A/trip only at Sikandara-UP end. No flag/facia reported. Line remain charged from Auraiya end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.043056 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
11 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
12 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 35.353 | 4631.243 | 4631.243 | 100
13 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 20.109 | 2634.279 | 2634.279 | 100
14 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 20.109 | 2634.279 | 2634.279 | 100
15 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 22.478 | 2944.618 | 2944.618 | 100
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 109 | 234.59 | 25570.31 | 25570.31 | 100
17 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR1 | -- | 2015-07-03 12:50 | 2015-07-03 14:34 | -- | -- | -- | 0 | 0.072222 | 0 | 0 | -- | -- | -- | OMSU | Tripped on R-N fault by pilot rope during OPGW work under ULDC scheme. FLR:Pithoragh=59.7km.
[5 empty] | -- | 2015-07-12 07:45 | 2015-07-12 07:50 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | -- | -- | -- | GOVC | Tripped on O/Voltage protection at Dhauliganga>240kv. DT received at Pthrgrh.
[5 empty] | -- | 2015-07-12 07:50 | 2015-07-12 16:40 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | -- | -- | -- | LVRD | Line kept open for Voltage regulation. Dganga>235kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.072222 | 0.0034722 | 0.36806 | -- | -- | -- |  |  |  | 743.9167 | 156 | 59.01 | 9205.56 | 9205.56 | 100
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR1 | -- | 2015-07-11 12:26 | 2015-07-11 17:55 | -- | -- |  | 0.22847 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for remote operation checking of TBC at Fatehpur.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.22847 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 687.1024 | 99.263
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
21 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR1 | -- | 2015-07-08 10:22 | 2015-07-08 12:55 |  |  |  | 0 | 0 | 0 | 0.10625 |  |  |  | OSPD | S/D by UPPCL for replacement of jumper at Naubasta end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.10625 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
22 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 15.69 | 2055.39 | 2055.39 | 100
23 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 15.69 | 2055.39 | 2055.39 | 100
24 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 | -- | 2015-07-01 16:48 | 2015-07-01 17:51 | -- | -- |  | 0 | 0 | 0 | 0.04375 | -- | -- | -- | OSFD | S/D by NTPC to attend Hot Spot at FGPP S/yard.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.04375 | -- | -- | -- |  |  |  | 744 | 131 | 17.691 | 2317.521 | 2317.521 | 100
25 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | -- | 2015-07-02 11:06 | 2015-07-02 15:51 |  |  |  | 0 | 0 | 0 | 0.19792 |  |  |  | OSFD | S/D by NTPC to attend Hot Spot in R-Ph CT at FGPP end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.19792 | -- | -- | -- |  |  |  | 744 | 131 | 17.691 | 2317.521 | 2317.521 | 100
26 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | -- | [15 empty] | 744 | 131 | 24.875 | 3258.625 | 3258.625 | 100
27 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | -- | [15 empty] | 744 | 131 | 12 | 1572 | 1572 | 100
28 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR1 | -- | 2015-07-16 11:38 | 2015-07-16 20:20 | -- | -- | -- | 0 | 0 | 0 | 0.3625 | -- | -- | -- | OSPD | S/D by UPPCL for maintenance work in their line portion.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.3625 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
29 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
30 | NR122018 | 220KV KNP-PANKI-I | 10.4 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
31 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
32 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
33 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
34 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
35 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
36 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 28.02 | 3698.64 | 3698.64 | 100
37 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- | 2015-07-08 10:34 | 2015-07-08 16:33 | -- | -- | -- | 0 | 0 | 0 | 0.24931 | -- | -- | -- | OSFD | S/D by UPPCL for attending hot spot at Mpurm end.
[6 empty] | 2015-07-15 14:46 | 2015-07-15 15:42 |  |  |  | 0 | 0 | 0 | 0.038889 |  |  |  | LPRD | Line hand tripped for Power regulation
[6 empty] | 2015-07-15 19:36 | 2015-07-15 20:18 |  |  |  | 0 | 0 | 0 | 0.029167 |  |  |  | LPRD | Line hand tripped for Power regulation
[6 empty] | 2015-07-20 21:41 | 2015-07-20 23:15 |  |  |  | 0 | 0 | 0 | 0.065278 |  |  |  | LPRD | Line hand tripped for Power regulation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.38264 | -- | -- | -- |  |  |  | 744 | 132 | 2.316 | 305.712 | 305.712 | 100
38 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- | 2015-07-15 14:48 | 2015-07-15 15:42 | -- | -- | -- | 0 | 0 | 0 | 0.0375 | -- | -- | -- | LPRD | Line hand tripped for Power regulation
[6 empty] | 2015-07-15 19:36 | 2015-07-15 20:18 |  |  |  | 0 | 0 | 0 | 0.029167 |  |  |  | LPRD | Line hand tripped for Power regulation
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.066667 | -- | -- | -- |  |  |  | 744 | 132 | 9.254 | 1221.528 | 1221.528 | 100
39 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- | 2015-07-02 12:31 | 2015-07-02 16:05 | -- | -- | -- | 0 | 0 | 0 | 0.14861 | -- | -- | -- | OSFD | S/D by UPPCL for maintenance at their end.
[6 empty] | 2015-07-09 14:11 | 2015-07-09 19:14 |  |  |  | 0 | 0 | 0 | 0.21042 |  |  |  | OSPD | S/D by UPPCL for maintenance work at Nara end.
[6 empty] | 2015-07-11 18:20 | 2015-07-11 20:40 |  |  |  | 0 | 0 | 0 | 0.097222 |  |  |  | OSPD | S/D by UPPCL to attend broken E/wire in their portion.
[6 empty] | 2015-07-31 15:00 | 2015-07-31 18:36 |  |  |  | 0 | 0 | 0 | 0.15 |  |  |  | OSPD | S/D by UPPCL for maintenance work at Nara end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.60625 | -- | -- | -- |  |  |  | 744 | 132 | 2.316 | 305.712 | 305.712 | 100
40 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 8.234 | 1086.888 | 1086.888 | 100
41 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 | -- | 2015-07-09 14:53 | 2015-07-09 18:03 | -- | -- |  | 0 | 0.13194 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on B-N fault in UPPCL portion. MRT-16.8Km.
[5 empty] | -- | 2015-07-25 17:04 | 2015-07-25 18:57 | -- | -- |  | 0 | 0 | 0 | 0.078472 | -- | -- | -- | OSFD | S/D by UPPCL to attend hot spot at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.13194 | 0 | 0.078472 | -- | -- | -- |  |  |  | 744 | 132 | 9.254 | 1221.528 | 1221.528 | 100
42 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 156 | 177.88 | 27749.28 | 27749.28 | 100
43 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
44 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR1 | -- | 2015-07-15 11:23 | 2015-07-16 00:27 |  |  |  | 0 | 0 | 0 | 0.54444 |  |  |  | OSPD | S/D by UPPCL for stringing of their 765KV Anpara-Unnao line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.54444 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
45 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 128.833 | 16877.123 | 16877.123 | 100
46 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 128.833 | 16877.123 | 16877.123 | 100
47 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 0.175 | 22.925 | 22.925 | 100
48 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 230.297 | 30168.907 | 30168.907 | 100
49 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 106.243 | 14024.076 | 14024.076 | 100
50 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 2.83 | 373.56 | 373.56 | 100
51 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 2.83 | 373.56 | 373.56 | 100
52 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
53 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
54 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR1 | -- | 2015-07-03 08:56 | 2015-07-03 09:51 | -- | -- | -- | 0 | 0.038194 | 0 | 0 | -- | -- | -- | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
[5 empty] | -- | 2015-07-03 10:47 | 2015-07-03 11:17 | -- | -- | -- | 0 | 0.020833 | 0 | 0 | -- | -- | -- | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
[5 empty] | -- | 2015-07-12 05:29 | 2015-07-12 06:29 | -- | -- | -- | 0 | 0.041667 | 0 | 0 | -- | -- | -- | OMSU | Tripped at CB ganj(UP) end only due to CB problem during R-N transient fault. Strganj=3.6km.
[5 empty] | -- | 2015-07-12 07:00 | 2015-07-12 17:09 | -- | -- | -- | 0.42292 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for jumper tightening and other maintenance work.
[6 empty] | 2015-07-13 11:33 | 2015-07-13 15:14 |  |  |  | 0 | 0.15347 | 0 | 0 |  |  |  | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.42292 | 0.25417 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 105.72 | 13955.04 | 13764.6587 | 98.6358
55 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR1 | -- | 2015-07-03 08:56 | 2015-07-03 09:50 |  |  |  | 0 | 0.0375 | 0 | 0 |  |  |  | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
[5 empty] | -- | 2015-07-03 10:47 | 2015-07-03 11:14 |  |  |  | 0 | 0.01875 | 0 | 0 |  |  |  | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
[5 empty] | -- | 2015-07-13 11:33 | 2015-07-13 15:06 |  |  |  | 0 | 0.14792 | 0 | 0 |  |  |  | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.20417 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 106 | 13992 | 13992 | 100
56 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR1 | -- | 2015-07-03 08:56 | 2015-07-03 09:51 |  |  |  | 0 | 0.038194 | 0 | 0 |  |  |  | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
[5 empty] | -- | 2015-07-03 10:47 | 2015-07-03 11:17 |  |  |  | 0 | 0.020833 | 0 | 0 |  |  |  | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
[5 empty] | -- | 2015-07-12 13:27 | 2015-07-12 17:24 |  |  |  | 0.16458 | 0 | 0 | 0 |  |  |  | OSPT | S/D due to heavy induction in jumper tightening work of CB ganj-Sitarganj line.
[5 empty] | -- | 2015-07-13 11:33 | 2015-07-13 15:21 |  |  |  | 0 | 0.15833 | 0 | 0 |  |  |  | OMSU | No power flow following disturbance at CB Ganj-UP s/s due to tripping of 400/220kv interconnector- Fault in Dohna line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.16458 | 0.21736 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 42.55 | 5616.6 | 5586.7807 | 99.4691
57 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR1 | -- | 2015-07-15 11:17 | 2015-07-16 01:03 | -- | -- |  | 0 | 0 | 0 | 0.57361 | -- | -- | -- | OSPD | S/D by UPPCL for stringing of their 765KV Anpara-Unnao line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.57361 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
58 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR1 | -- | 2015-07-15 10:12 | 2015-07-16 00:27 | -- | -- |  | 0 | 0 | 0 | 0.59375 | -- | -- | -- | OSPD | S/D by UPPCL for stringing of their 765KV Anpara-Unnao line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.59375 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
59 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR1 | -- | 2015-07-08 12:28 | 2015-07-08 13:24 | -- | -- |  | 0 | 0.038889 | 0 | 0 | -- | -- | -- | OMSU | Fault during lifting of material for tower erection work of 765kV Anpara-Unnao line by UPTCL erection gang.
[5 empty] | -- | 2015-07-18 10:11 | 2015-07-19 01:06 | -- | -- |  | 0 | 0 | 0 | 0.62153 | -- | -- | -- | OSPD | S/D by UPPCL for stringing of their 765KV Anpara-Unnao line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.038889 | 0 | 0.62153 | -- | -- | -- |  |  |  | 744 | 132 | 42.5 | 5610 | 5610 | 100
[5 empty] | -- | [17 empty] | 3441.839
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR1 | -- | [15 empty] | 744 | 50 | 58 | 2900 | 2900 | 100
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-12 04:10 | 1900-01-04 06:40 | 0.12361 | 1900-11-05 02:08 | [8 empty] | 21694.832 | 10512484.841 | 10484633.0276 | 99.7351 | %
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.7686 | % (AC) | 99.5621 | [6 empty] | %'(HVDC)
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 400/765KV ICT-I AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
7 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
9 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
10 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
13 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
14 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | -- | [15 empty] | 744 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR1 | -- | 2015-07-24 20:59 | 2015-07-28 00:01 | -- | -- |  | 1900-01-02 03:02 | 0 | 0 | 0 | -- | -- | -- | SICT | 765 kV ICT-1 tripped on Differential, PRD and Bucholz Opearted in Y-phase unit. Replaced.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 1900-01-02 03:02 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1348.7231 | 89.9149
F |  | 400/220 KV ICT'S |  | NR1 | --
1 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
2 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR1 | [16 empty] | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
5 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
6 | NR1ICT68 | 500MVA ICT-III BASSI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
7 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
8 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | -- | 2015-07-28 04:40 | 2015-07-28 07:43 |  |  |  | 0 | 0 | 0.12708 | 0 |  |  |  | GOFC | Tripped on O/Flux protn due to load crash and high voltage in Rajasthan followed by continuous rains. Bhinmal>248kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.12708 | 0 | -- | -- | -- |  |  |  | 740.95 | 315 |  | 315 | 315 | 100
9 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | -- | 2015-07-28 04:22 | 2015-07-28 07:43 |  |  |  | 0 | 0 | 0.13958 | 0 |  |  |  | GOFC | Tripped on O/Flux protn due to load crash and high voltage in Rajasthan followed by continuous rains. Bhinmal>248kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.13958 | 0 | -- | -- | -- |  |  |  | 740.65 | 315 |  | 315 | 315 | 100
10 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
13 | NR1ICT10 | 315MVA ICT-I BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
14 | NR1ICT11 | 315MVA ICT-II BLBGARH | 315 | NR1 | -- | 2015-07-14 10:30 | 2015-07-14 14:45 |  |  |  | 0.17708 | 0 | 0 | 0 |  |  |  | OSPT | S/D by BLB for tie isolator jumpering after retrofitment.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.17708 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 313.2006 | 99.4288
15 | NR1ICT12 | 315MVA ICT-III BLBGARH | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
16 | NR1ICT13 | 315MVA ICT-IV BLBGARH | 315 | NR1 | -- | 2015-07-04 10:15 | 2015-07-04 13:14 | -- | -- | -- | 0.12431 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for tie isolator Jumper replacement-retrofitment work.
[5 empty] | -- | 2015-07-15 08:21 | 2015-07-15 12:04 | -- | -- | -- | 0.15486 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for Tie bay isolator jumpering at BLB after retrofitment.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.27917 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 312.1633 | 99.0995
17 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
18 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
19 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
20 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
21 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
22 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
23 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
24 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
25 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
26 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
27 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
28 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
29 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
30 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
31 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
32 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
33 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
34 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
35 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
36 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 | -- | 2015-07-20 05:39 | 2015-07-20 09:50 |  |  |  | 0.17431 | 0 | 0 | 0 |  |  |  | SICT | ICT tripped on OTI alarm due to relay problem.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.17431 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 313.2288 | 99.4377
37 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
38 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
39 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
40 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
41 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
42 | NR1ICT28 | 315MVA ICT-I MANDOLA | 315 | NR1 | -- | 2015-07-24 12:48 | 2015-07-24 17:24 |  |  |  | 0 | 0 | 0 | 0.19167 |  |  |  | OSFD | S/D to attend jumper Hot Spot in ICT-V 220kv DTL S/Yard, connected in parallel under special approval for DTL supply.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.19167 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
43 | NR1ICT29 | 315MVA ICT-II MANDOLA | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
44 | NR1ICT30 | 315MVA ICT-III MANDOLA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
45 | NR1ICT31 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
46 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
47 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
48 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 316 |  | 316 | 316 | 100
49 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
50 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
51 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | [17 empty] | 744 | 500 |  | 500 | 500 | 100
52 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
53 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | -- | [15 empty] | 744 | 500 |  | 500 | 500 | 100
54 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
55 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
56 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
57 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR1 | [16 empty] | 744 | 500 |  | 500 | 500 | 100
58 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR1 | [16 empty] | 744 | 500 |  | 500 | 500 | 100
59 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
60 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
61 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
62 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | -- | [15 empty] | 744 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR1 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR1 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
--
83 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 1900-01-06 12:20 | 0 | 0.53333 | 0.38333 | [7 empty] | 44951 |  | 44951 | 44793.3159 | 99.6492 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR1 | -- | 2015-07-04 07:35 | 2015-07-04 13:46 |  |  |  | 0.25764 | 0 | 0 | 0 |  |  |  | OSPT | S/D to replace faulty Thyristor in valve hall at Rh/HVDC.
[6 empty] | 2015-07-27 08:29 | 2015-07-27 16:38 |  |  |  | 0.33958 | 0 | 0 | 0 |  |  |  | OSPT | S/D to replace faulty Thyristor in valve hall at Rh/HVDC.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.59722 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 599474.1263 | 98.0735
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR1 | -- | 2015-07-05 06:54 | 2015-07-05 07:21 |  |  |  | 0.01875 | 0 | 0 | 0 |  |  |  | OMST | Pole blocked on External protn trip at Balia.
[6 empty] | 2015-07-06 08:11 | 2015-07-06 18:53 |  |  |  | 0 | 0 | 0 | 0.44583 |  |  |  | LCSD | S/D for stringing work of 765 KV KNP-Jhatikra line.
[6 empty] | 2015-07-07 09:19 | 2015-07-07 23:04 |  |  |  | 0 | 0 | 0 | 0.57292 |  |  |  | LCSD | S/D for stringing work of 765 KV KNP-Jhatikra line
[6 empty] | 2015-07-11 11:24 | 2015-07-11 11:38 |  |  |  | 0.0097222 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to Valve cooling problem at Balia.
[6 empty] | 2015-07-16 04:25 | 2015-07-16 07:08 |  |  |  | 0.11319 | 0 | 0 | 0 |  |  |  | OMST | Pole tripped due to problem in auxillary supply at Ballia.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.14167 | 0 | 0 | 1899-12-31 00:27 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 982720.9536 | 99.543
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR1 | -- | 2015-07-05 06:54 | 2015-07-05 07:21 |  |  |  | 0.01875 | 0 | 0 | 0 |  |  |  | OMST | Pole blocked on External protn trip at Balia.
[6 empty] | 2015-07-06 08:11 | 2015-07-06 18:53 |  |  |  | 0 | 0 | 0 | 0.44583 |  |  |  | LCSD | S/D for stringing work of 765 KV KNP-Jhatikra line.
[6 empty] | 2015-07-07 09:19 | 2015-07-07 20:29 |  |  |  | 0 | 0 | 0 | 0.46528 |  |  |  | LCSD | S/D for stringing work of 765 KV KNP-Jhatikra line
[6 empty] | 2015-07-16 04:25 | 2015-07-16 07:31 |  |  |  | 0.12917 | 0 | 0 | 0 |  |  |  | OMST | Pole tripped due to problem in auxillary supply at Ballia.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.14792 | 0 | 0 | 0.91111 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 982521.9148 | 99.5228
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0.88681 | 0 | 0 | 1899-12-31 22:19 | [8 empty] | 3209.572 | 3196965 | 3175966.9948 | 99.3432 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | +/-250MW HVDC B/B BLOCK-I | 250 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 500 | 500 | 100 | %
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 280 | 280 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-II AGRA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-III AGRA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR1 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 50MVAR B/Reactor-I BAREILLY | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
16 | NR1BRT04 | 50MVAR B/Reactor BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
17 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
18 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
19 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
20 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
21 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
22 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
23 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR1 | -- | 2015-07-23 09:35 | 2015-07-31 16:46 |  |  |  | 0 | 0 | 0 | 1900-01-07 07:11 |  |  |  | SVRD | H/ tripped for voltage regulation<654kv. (Standing Instrn)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-07 07:11 | -- | -- | -- |  |  |  | 744 | 330 |  | 330 | 330 | 100
24 | NR1BRT39 | 125MVAR B/Reactor GORAKHPUR | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
25 | NR1BRT37 | 125MVAR B/Reactor-1 JAIPUR(S) | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
26 | NR1BRT31 | 240MVAR B/Reactor JHATIKALA-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
27 | NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
28 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- | 2015-07-06 09:42 | 2015-07-08 10:26 |  |  |  | 0 | 0 | 0 | 1900-01-01 00:44 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 00:44 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
29 | NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
30 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
31 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
32 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
33 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
34 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
35 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 | -- | 2015-07-29 12:42 | 2015-07-29 17:45 | -- | -- | -- | 0 | 0 | 0 | 0.21042 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.21042 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
36 | NR1BRT30 | 125MVAR B/Reactor MANESAR | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
37 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
38 | NR1BRT12 | 50MVAR B/Reactor MURADNGR |  | NR1 | -- | 2015-07-01 | 2015-08-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-30 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
39 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- | [15 empty] | 744 | 80 |  | 80 | 80 | 100
40 | NR1BRT40 | 125MVAR B/Reactor Roorki | 125 | NR1 | -- | 2015-07-01 | 2015-07-06 06:30 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 06:30 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2015-07-06 12:09 | 2015-07-08 10:26 |  |  |  | 0 | 0 | 0 | 1899-12-31 22:17 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<391kv. (Standing Instrn)
[6 empty] | 2015-07-11 08:40 | 2015-07-12 06:06 |  |  |  | 0 | 0 | 0 | 0.89306 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
[6 empty] | 2015-07-13 08:41 | 2015-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-17 15:19 | -- | -- | -- | SVRD | H/ tripped for voltage regulation<395kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-25 17:32 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
41 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
42 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR1 | -- | [15 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
43 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR1 | -- | [15 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
44 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
45 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR1 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
46 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
47 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
48 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
49 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
50 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
51 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
52 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
53 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
54 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
55 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR1 | -- | [15 empty] | 744 | 330 |  | 330 | 330 | 100
56 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
57 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
58 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
59 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
60 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
61 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
62 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR1 | -- | [15 empty] | 744 | 63 |  | 63 | 63 | 100
63 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
64 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
65 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
66 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR1 | -- | [15 empty] | 744 | 240 |  | 240 | 240 | 100
67 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
68 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | -- | [15 empty] | 744 | 50 |  | 50 | 50 | 100
69 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 1900-05-15 13:00 | [9 empty] | 8248.4 | 8248.4 | 100 | %
|  | TOTAL | [8 empty] | 1900-01-20 13:47 | 1900-01-04 06:40 | 0.65694 | 1901-03-23 22:39
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L15:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M15:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N15:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O15:[Deemed Available, row above])
Note on C118: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C395: DOC-11-02-15
Note on C513: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14
Note on C698: DOC-15/06/14
Note on C699: DOC-26/09/14