## SOP DATA NR1 AUGUST 19
Standard of Performance data for the month of August - 2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD.,Northern Region-I | [19 empty] | ANNEXURE-A
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | NSC | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 23 | 24 | 25 | 26 | 27 | 22
|  | 765 KV TRANS LINES | [5 empty] | -- | -- | -- | [16 empty] | 0
1 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 267.628 | 1070.512 | 1070.512 | 100 | 744
2 | NR176516 | 765KV AJMER-CHITTOR-I | 211.01 | NR1 |  | 2019-08-01 18:23 | 2019-08-05 11:59 |  |  |  | 0 | 0 | 0 | 1900-01-02 17:36 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Chittorgarh- 803KV.
[6 empty] | 2019-08-15 09:49 | 2019-08-16 22:34 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:45 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Chitorgarh- 802 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 06:21 | [5 empty] | NRPC | 744 | 6 | 211.01 | 1266.06 | 1266.06 | 100
3 | NR176517 | 765KV AJMER-CHITTOR-II | 211.01 | NR1 | -- | 2019-08-01 10:08 | 2019-08-01 10:08 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully A/R on B-N Fault, FLR:Ajmer-39.32KM/4.14KA, Chittorgarh-179.3KM/1.94KA.
[6 empty] | 2019-08-11 17:18 | 2019-08-12 09:30 |  |  |  | 0 | 0 | 0 | 0.675 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Chitorgarh- 808KV.
[6 empty] | 2019-08-16 23:07 | 2019-08-19 19:51 |  |  |  | 0 | 0 | 0 | 1900-01-01 20:44 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Chitorgarh- 788 KV.
[6 empty] | 2019-08-31 13:44 | 2019-08-31 15:54 |  |  |  | 0.090278 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for attending problem in Main-2 protection relay installed at Ajmer end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.090278 | 0 | 0 | 1900-01-02 12:56 | [5 empty] | NRPC | 744 | 6 | 211.01 | 1266.06 | 1262.373 | 99.7088
4 | NR176509 | 765KV BHIWANI-PHAGI(JPR)-I | 271.571 | NR1 | -- | 2019-08-17 04:31 | 2019-08-17 11:54 |  |  |  | 0 | 0 | 0 | 0.30764 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwani-800 KV.
[6 empty] | 2019-08-18 02:37 | 2019-08-18 19:23 |  |  |  | 0 | 0 | 0 | 0.69861 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwani-428 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 00:09 | [5 empty] | NRPC | 744 | 4 | 271.571 | 1086.284 | 1086.284 | 100
5 | NR176515 | 765KV BHIWANI-PHAGI(JPR)-II | 279.583 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 279.583 | 1118.332 | 1118.332 | 100
6 | NR276502 | 765KV JHATIKALA-BHIWANI | 85.188 | NR1 | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 85.188 | 340.752 | 340.752 | 100
7 | NR276503 | 765KV MEERUT-BHIWANI | 173 | NR1 | -- | 2019-08-17 17:13 | 2019-08-18 20:08 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:55 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwani-805 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 02:55 | [5 empty] | NRPC | 744 | 4 | 173 | 692 | 692 | 100
8 | NR176511 | 765KV MEERUT-GR.NOIDA | 119.159 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 119.159 | 476.636 | 476.636 | 100
9 | NR276501 | 765KV MOGA-BHIWANI | 273 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 273 | 1092 | 1092 | 100
10 | NR176519 | 765KV AJMER-BIKANER-I | 263 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 6 | 263 | 1578 | 1578 | 100
11 | NR176518 | 765KV AJMER-BIKANER-II | 263 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 6 | 263 | 1578 | 1578 | 100
400 KV TRANS LINES
12 | NR140116 | 400KV AGRA-JAIPUR(S)-I | 253.823 | NR1 | -- | 2019-08-03 04:11 | 2019-08-04 20:53 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:42 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Agra- 429 KV.
[6 empty] | 2019-08-07 01:36 | 2019-08-10 20:10 |  |  |  | 0 | 0 | 0 | 1900-01-02 18:34 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Agra- 428 KV.
[6 empty] | 2019-08-13 08:03 | 2019-08-15 20:55 |  |  |  | 0 | 0 | 0 | 1900-01-01 12:52 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 430 KV.
[6 empty] | 2019-08-20 02:26 | 2019-08-23 21:29 |  |  |  | 0 | 0 | 0 | 1900-01-02 19:03 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 427 KV.
[6 empty] | 2019-08-29 08:08 | 2019-08-30 14:31 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:23 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 429 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-12 01:34 | [5 empty] | NRPC | 744 | 2 | 253.823 | 507.646 | 507.646 | 100
13 | NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2019-08-15 03:20 | 2019-08-19 19:32 |  |  |  | 0 | 0 | 0 | 1900-01-03 16:12 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 430 KV.
| NR140126 | 400KV AGRA-JAIPUR(S)-II | 253.823 | NR1 | -- | 2019-08-24 06:06 | 2019-08-26 20:25 |  |  |  | 0 | 0 | 0 | 1900-01-01 14:19 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 431 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 06:31 | [5 empty] | NRPC | 744 | 2 | 253.823 | 507.646 | 507.646 | 100
14 | NR140144 | 400KV AGRA-SIKAR-I | 393.9 | NR1 | -- | 2019-08-03 04:12 | 2019-08-03 10:20 |  |  |  | 0 | 0 | 0 | 0.25556 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Agra- 429 KV.
[6 empty] | 2019-08-14 07:49 | 2019-08-18 20:49 |  |  |  | 0 | 0 | 0 | 1900-01-03 13:00 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 431 KV.
[6 empty] | 2019-08-20 04:22 | 2019-08-23 21:27 |  |  |  | 0 | 0 | 0 | 1900-01-02 17:05 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 427 KV.
[6 empty] | 2019-08-24 16:12 | 2019-08-24 22:30 |  |  |  | 0 | 0 | 0 | 0.2625 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 430 KV.
[6 empty] | 2019-08-26 04:05 | 2019-08-26 10:00 |  |  |  | 0 | 0 | 0 | 0.24653 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 430 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 00:26 | [5 empty] | NRPC | 744 | 4 | 393.9 | 1575.6 | 1575.6 | 100
15 | NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2019-08-03 06:08 | 2019-08-10 22:06 |  |  |  | 0 | 0 | 0 | 1900-01-06 15:58 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Agra- 429 KV.
[6 empty] | 2019-08-18 02:59 | 2019-08-19 19:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:45 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 430 KV.
| NR140145 | 400KV AGRA-SIKAR-II | 393.9 | NR1 | -- | 2019-08-24 04:04 | 2019-08-28 09:43 |  |  |  | 0 | 0 | 0 | 1900-01-03 05:39 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Agra- 430 KV. Charging done at 20:20hrs on 24.08.19 but could not hold due to over voltage protection operation at Agra twice, (Open end volatge reaching > 453KV). Line continued to keep open for v/ regulation as per NRLDC code (1607).
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-12 14:22 | [5 empty] | NRPC | 744 | 4 | 393.9 | 1575.6 | 1575.6 | 100
16 | NR140179 | 400KV AJMER-AJMER(RRVPNL)-I | 65.615 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 65.615 | 262.46 | 262.46 | 100
17 | NR140180 | 400KV AJMER-AJMER(RRVPNL)-II | 65.615 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 65.615 | 262.46 | 262.46 | 100
18 | NR140174 | 400KV BAGHPAT-DEHRADUN | 165 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 165 | 660 | 660 | 100
19 | NR140173 | 400KV BAGPAT-SAHARANPUR | 121 | NR1 |  | 2019-08-11 10:05 | 2019-08-11 10:05 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on R-N fault. FLR: BGPT-114.7 km/3.9KA, Saharnpur-48.5km/4.8KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 121 | 484 | 484 | 100
20 | NR240006 | 400KV BAHADURGRH-BAWANA | 48.981 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 48.981 | 97.962 | 97.962 | 100
21 | NR240102 | 400KV BAHADURGRH-KABULPR | 38.58 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 38.58 | 77.16 | 77.16 | 100
22 | NR240038 | 400KV BAHADURGRH-SONIPAT-I | 53.4 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 3 | 53.4 | 160.2 | 160.2 | 100
23 | NR240039 | 400KV BAHADURGRH-SONIPAT-II | 53.4 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 3 | 53.4 | 160.2 | 160.2 | 100
24 | NR140187 | 400KV BAMNOLI-TUGHLKBD-I | 27.88 | NR1 |  | 2019-08-04 08:50 | 2019-08-07 20:48 |  |  |  | 0 | 0 | 0 | 1900-01-02 11:58 |  |  |  | OSPD | S/D by DTL for shifting of line from ERS to main tower at Bamnauli end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 11:58 | [5 empty] | NRPC | 744 | 4 | 27.88 | 111.52 | 111.52 | 100
25 | NR140188 | 400KV BAMNOLI-TUGHLKBD-II | 27.88 | NR1 |  | 2019-08-01 | 2019-08-03 17:33 |  |  |  | 0 | 0 | 0 | 1900-01-01 17:33 |  |  |  | OSPD | S/D by DTL for shifting of line from ERS to main tower at Bamnauli end. Out since 31/07/2019 08:53:00
[6 empty] | 2019-08-07 12:39 | 2019-08-07 13:49 |  |  |  | 0 | 0 | 0 | 0.048611 |  |  |  | OSFD | S/D by DTL for safety reason in removing of back stay on Tower no-174.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 18:43 | [5 empty] | NRPC | 744 | 4 | 27.88 | 111.52 | 111.52 | 100
26 | NR140028 | 400KV BASSI-BHIWADI-I | 235 | NR1 | -- | 2019-08-09 19:40 | 2019-08-09 19:40 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully A/R on B-N fault. FLR:Bassi-34.3KM/13.3KA, Bhiwadi-204.6KM/2.0KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 235 | 470 | 470 | 100
27 | NR140030 | 400KV BASSI-HIRAPURA-I | 47.762 | NR1 |  | 2019-08-05 09:30 | 2019-08-06 13:21 |  |  |  | 1899-12-31 03:51 | 0 | 0 | 0 |  |  |  | OSPT | S/D for replacement of old CVTs at both ends.
[6 empty] | 2019-08-24 18:29 | 2019-08-24 21:03 |  |  |  | 0 | 0 | 0 | 0.10694 |  |  |  | LCSD | S/D for installation of OPGW pilot wire broken at loc-649-650 during on line stringing work under new ULDC scheme.
[6 empty] | 2019-08-25 11:25 | 2019-08-25 14:43 |  |  |  | 0 | 0 | 0 | 0.1375 |  |  |  | LCSD | S/D for installation of OPGW pilot wire broken at loc-649-650 during on line stringing work under new ULDC scheme.
|  | SUB TOTAL | [8 empty] | 1899-12-31 03:51 | 0 | 0 | 0.24444 | [5 empty] | NRPC | 744 | 2 | 47.762 | 95.524 | 91.9483 | 96.2567
28 | NR140031 | 400KV BASSI-HIRAPURA-II | 48.99 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 48.99 | 97.98 | 97.98 | 100
29 | NR140117 | 400KV BASSI-JAIPUR(S)-I | 37.164 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 37.164 | 74.328 | 74.328 | 100
30 | NR140127 | 400KV BASSI-JAIPUR(S)-II | 37.164 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 37.164 | 74.328 | 74.328 | 100
31 | NR140148 | 400KV BASSI-KOTPUTLI | 106.153 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 106.153 | 212.306 | 212.306 | 100
32 | NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
| NR140146 | 400KV BASSI-PHAGI-I (Kalisindh) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 48.432 | 193.728 | 193.728 | 100
33 | NR140147 | 400KV BASSI-PHAGI-II (Kawai) | 48.432 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 48.432 | 193.728 | 193.728 | 100
34 | NR140171 | 400KV BASSI-SIKAR-I | 169.8 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 169.8 | 339.6 | 339.6 | 100
35 | NR140172 | 400KV BASSI-SIKAR-II | 169.8 | NR1 | -- | 2019-08-17 17:30 | 2019-08-19 15:41 |  |  |  | 0 | 0 | 0 | 1899-12-31 22:11 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bassi-426 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 22:11 | [5 empty] | NRPC | 744 | 2 | 169.8 | 339.6 | 339.6 | 100
36 | NR140032 | 400KV BHIWADI-GURGAON | 82.8 | NR1 | -- | 2019-08-21 10:17 | 2019-08-21 18:53 |  |  |  | 0.35833 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & NTAMC signal/operation testing after SCADA upgradation work at Gurgaon.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.35833 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 82.8 | 165.6 | 163.6858 | 98.8441
37 | NR140033 | 400KV BHIWADI-HISAR-I | 211.547 | NR1 |  | 2019-08-15 04:47 | 2019-08-19 19:38 |  |  |  | 0 | 0 | 0 | 1900-01-03 14:51 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwadi- 425 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 14:51 | [5 empty] | NRPC | 744 | 2 | 211.547 | 423.094 | 423.094 | 100
38 | NR240087 | 400KV BHIWADI-HISAR-II | 144 | NR1 |  | 2019-08-08 16:50 | 2019-08-08 19:26 |  |  |  | 0.10833 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to arching found in CT wiring of Main-II relay at Bhiwadi end.
[6 empty] | 2019-08-09 14:01 | 2019-08-09 21:36 |  |  |  | 0.31597 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for rectification of Auto-recloser problem in main bay of the line at bhiwadi end.
[6 empty] | 2019-08-22 07:10 | 2019-08-23 21:15 |  |  |  | 0 | 0 | 0 | 1899-12-31 14:05 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwadi- 425 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.42431 | 0 | 0 | 1899-12-31 14:05 | [5 empty] | NRPC | 744 | 2 | 144 | 288 | 284.0581 | 98.6313
39 | NR240088 | 400KV BHIWADI-HISAR-III | 144 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 144 | 288 | 288 | 100
40 | NR140149 | 400KV BHIWADI-KOTPUTLI | 132.428 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 132.428 | 264.856 | 264.856 | 100
41 | NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 | NR1 | -- | 2019-08-15 04:46 | 2019-08-16 21:42 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:56 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwadi- 425 KV.
[6 empty] | 2019-08-17 03:50 | 2019-08-19 19:34 |  |  |  | 0 | 0 | 0 | 1900-01-01 15:44 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Nimrana- 427 KV.
| NR140106 | 400KV BHIWADI-NIMRANA-I | 48.428 |  | -- | 2019-08-25 16:09 | 2019-08-26 09:52 |  |  |  | 0 | 0 | 0 | 0.73819 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Nmrn-421 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 02:23 | [5 empty] | NRPC | 744 | 2 | 48.428 | 96.856 | 96.856 | 100
42 | NR140107 | 400KV BHIWADI-NIMRANA-II | 48.428 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 48.428 | 96.856 | 96.856 | 100
43 | NR240061 | 400KV BHIWANI-BAWANA | 97.415 | NR1 |  | 2019-08-22 15:41 | 2019-08-22 19:55 |  |  |  | 0.17639 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for replacement of B-phase CVT at Bhiwani(PG) end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.17639 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 97.415 | 194.83 | 193.7214 | 99.431
44 | NR240059 | 400KV BHIWANI-BHIWANI(BBMB) | 33.962 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 33.962 | 67.924 | 67.924 | 100
45 | NR240068 | 400KV BHIWANI-JIND-I | 82.23 | NR1 |  | 2019-08-18 00:51 | 2019-08-19 15:35 |  |  |  | 0 | 0 | 0 | 1899-12-31 14:44 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwani-428 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 14:44 | [5 empty] | NRPC | 744 | 2 | 82.23 | 164.46 | 164.46 | 100
46 | NR240069 | 400KV BHIWANI-JIND-II | 82.23 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 82.23 | 164.46 | 164.46 | 100
47 | NR240103 | 400KV BHIWANI-KABULPR | 26.64 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 26.64 | 53.28 | 53.28 | 100
48 | NR140035 | 400KV BLBGRH-GURGAON | 42.7 | NR1 |  | 2019-08-20 10:44 | 2019-08-20 18:52 |  |  |  | 0.33889 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & NTAMC signal/operation testing after SCADA upgradation work at Gurgaon end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.33889 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 42.7 | 85.4 | 84.4664 | 98.9068
49 | NR140036 | 400KV BLBGRH-MAHRANIBG | 60.68 | NR1 |  | 2019-08-11 13:56 | 2019-08-11 17:46 |  |  |  | 0.15972 | 0 | 0 | 0 |  |  |  | OSFT | S/D for dismaltling of OPGW at tension tower-135. Line SD to avoid tripping as OPGW is just above the conductor.
[6 empty] | 2019-08-14 01:48 | 2019-08-14 01:48 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Auto-reclose on B-N fault.FLR: Mahranibagh-39.14km/7.95 kA,Ballabhgarh-21.55km/14.02 kA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.15972 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 60.68 | 242.72 | 241.4694 | 99.4848
50 | NR140138 | 400KV BLBGRH-NAVADA | 12.55 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 12.55 | 50.2 | 50.2 | 100
51 | NR140189 | 400KV BLBGRH-TUGHLKBD-I | 27.88 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 27.88 | 111.52 | 111.52 | 100
52 | NR140190 | 400KV BLBGRH-TUGHLKBD-II | 27.88 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 27.88 | 111.52 | 111.52 | 100
53 | NR140181 | 400KV CHITTOR-CHITTOR(RVPNL)-I | 48.78 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 48.78 | 195.12 | 195.12 | 100
54 | NR140182 | 400KV CHITTOR-CHITTOR(RVPNL)-II | 48.78 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 48.78 | 195.12 | 195.12 | 100
55 | NR140039 | 400KV DAD-GR.NOIDA | 13.256 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 13.256 | 53.024 | 53.024 | 100
56 | NR140040 | 400KV DAD-MAHRANIBG | 54.36 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 54.36 | 217.44 | 217.44 | 100
57 | NR140041 | 400KV DAD-MANDOLA-I | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 46.3 | 185.2 | 185.2 | 100
58 | NR140042 | 400KV DAD-MANDOLA-II | 46.3 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 46.3 | 185.2 | 185.2 | 100
59 | NR140043 | 400KV DAD-MURADNGR | 33.098 | NR1 | -- | 2019-08-08 11:35 | 2019-08-08 12:52 |  |  |  | 0 | 0 | 0 | 0.053472 |  |  |  | LCSD | S/D for CT core wiring/ PMU installation at NTPC Dadri under NRLDC URTDSM scheme.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.053472 | [5 empty] | NRPC | 744 | 2 | 33.098 | 66.196 | 66.196 | 100
60 | NR140044 | 400KV DAD-PANIPAT-I | 112.322 | NR1 |  | 2019-08-08 15:41 | 2019-08-08 17:00 |  |  |  | 0 | 0 | 0 | 0.054861 |  |  |  | LCSD | S/D for CT core wiring/ PMU installation at NTPC Dadri under NRLDC URTDSM scheme.
[6 empty] | 2019-08-19 01:09 | 2019-08-19 01:44 |  |  |  | 0 | 0.024306 | 0 | 0 |  |  |  | OMSU | A/R at Dadri but tripped from Panipat BBMB end. FLR: Panipat- 12.3Km/7.75KA, Dadri-88.9Km.
[6 empty] | 2019-08-23 13:11 | 2019-08-23 13:11 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R succesfully on R-N fault.FLR-Dadri-71.45km, Zone-1, Panipat- B-N fault,31.38km,IF-5.75KA.
[6 empty] | 2019-08-29 09:26 | 2019-08-29 18:41 |  |  |  | 0.38542 | 0 | 0 | 0 |  |  |  | OSPT | S/D for replacement of polluted insulator at loc.145,146 & 148 by PG NR-1.
[6 empty] | 2019-08-29 18:41 | 2019-08-30 00:58 |  |  |  | 0 | 0 | 0 | 0.26181 |  |  |  | OSFD | Forced S/D by BBMB after return of PTW by PG, due to operational problem of their s/yard (Charging delayed by BBMB due to their ICTs Overloading at Panipat).
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.38542 | 0.024306 | 0 | 0.31667 | [5 empty] | NRPC | 744 | 2 | 112.322 | 224.644 | 221.851 | 98.7567
61 | NR140045 | 400KV DAD-PANIPAT-II | 117 | NR1 |  | 2019-08-09 11:02 | 2019-08-09 12:20 |  |  |  | 0 | 0 | 0 | 0.054167 |  |  |  | LCSD | S/D for CT core wiring/ PMU installation at NTPC Dadri under NRLDC URTDSM scheme.
[6 empty] | 2019-08-28 09:44 | 2019-08-28 19:10 |  |  |  | 0.39306 | 0 | 0 | 0 |  |  |  | OSPT | S/D for line maintenance work.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.39306 | 0 | 0 | 0.054167 | [5 empty] | NRPC | 744 | 2 | 117 | 234 | 231.0331 | 98.7321
62 | NR140185 | 400KV DEHRADUN-ABDULAPUR-I | 89.43 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 260.051 | 1040.204 | 1040.204 | 100
63 | NR140186 | 400KV DEHRADUN-ABDULAPUR-II | 89.43 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
| NR140125 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 260.051 | 1040.204 | 1040.204 | 100
64 | NR240026 | 400KV FATEHABAD-HISAR | 88.558 | NR1 |  | 2019-08-17 17:26 | 2019-08-19 14:34 |  |  |  | 0 | 0 | 0 | 1899-12-31 21:08 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Fatehabad-427 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 21:08 | [5 empty] | NRPC | 744 | 2 | 88.558 | 177.116 | 177.116 | 100
65 | NR140128 | 400KV GURGAON-MANESAR-I | 23.462 | NR1 |  | 2019-08-22 10:04 | 2019-08-22 17:18 |  |  |  | 0.30139 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & NTAMC signal/operation testing after SCADA upgradation work at Gurgaon.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.30139 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 23.462 | 93.848 | 92.9356 | 99.0278
66 | NR140129 | 400KV GURGAON-MANESAR-II | 23.462 | NR1 |  | 2019-08-23 10:14 | 2019-08-23 18:35 |  |  |  | 0.34792 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & NTAMC signal/operation testing after SCADA upgradation work at Gurgaon.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.34792 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 23.462 | 93.848 | 92.7947 | 98.8777
67 | NR240060 | 400KV HISAR-BHIWANI-I | 64.461 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 64.461 | 128.922 | 128.922 | 100
68 | NR240093 | 400KV HISAR-BHIWANI-II | 56.669 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 56.669 | 113.338 | 113.338 | 100
69 | NR240094 | 400KV HISAR-BHIWANI-III | 56.669 | NR1 |  | 2019-08-18 02:36 | 2019-08-19 15:32 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:56 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Bhiwani-428 KV.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:56 | [5 empty] | NRPC | 744 | 2 | 56.669 | 113.338 | 113.338 | 100
70 | NR240015 | 400KV HISAR-BHIWANI(BBMB) | 34.52 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 34.52 | 69.04 | 69.04 | 100
71 | NR240016 | 400KV HISAR-KAITHAL-I | 113.12 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 3 | 113.12 | 339.36 | 339.36 | 100
72 | NR240044 | 400KV HISAR-KAITHAL-II | 113.12 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 3 | 113.12 | 339.36 | 339.36 | 100
73 | NR140192 | 400KV JAIPUR(S)-RAPPD | 228.18 | NR1 | -- | 2019-08-07 10:22 | 2019-08-07 11:16 |  |  |  | 0 | 0 | 0 | 0.0375 |  |  |  | OSPD | S/D by RAPP for taking their L/R in service after conductivity testing at RAPP end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.0375 | [5 empty] | NRPC | 744 | 2 | 228.18 | 456.36 | 456.36 | 100
74 | NR140132 | 400KV JHATIKALA-BAMNOLI-I | 6.106 | NR1 | -- | 2019-08-14 12:46 | 2019-08-14 13:14 |  |  |  | 0 | 0.019444 | 0 | 0 |  |  |  | OMSU | Tripped only from Bamnoli due to fault in Bamnoli(DTL) S/Yard. Line remain charged from Jhatikala end. FLR: Jhatikr-11Km/2.3KA, Bamnoli-0Km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.019444 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 6.106 | 24.424 | 24.424 | 100
75 | NR140133 | 400KV JHATIKALA-BAMNOLI-II | 6.106 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 6.106 | 24.424 | 24.424 | 100
76 | NR140134 | 400KV JHATIKALA-MUNDKA-I | 6.782 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 6.782 | 27.128 | 27.128 | 100
77 | NR140135 | 400KV JHATIKALA-MUNDKA-II | 6.782 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 6.782 | 27.128 | 27.128 | 100
78 | NR140048 | 400KV KANKROLI-BHINMAL | 201.2 | NR1 |  | 2019-08-02 05:44 | 2019-08-02 12:37 |  |  |  | 0.28681 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on R-N Fault after two minuts of successful A/Reclose. FLR:Bhinmal-157.7KM, 2.2KA, Knk-48.1KM/5.5KA
[6 empty] | 2019-08-09 14:50 | 2019-08-09 14:50 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully A/R on B-N fault. FLR:Kankroli-110.65KM/ 3.2KA, Bhinmal-66.25KM/3.92KA.
[6 empty] | 2019-08-10 10:23 | 2019-08-10 15:59 |  |  |  | 0.23333 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to sparking in CT Circuit in control relay panel at Bhinmal end.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.52014 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 201.2 | 402.4 | 395.6483 | 98.3221
79 | NR140169 | 400KV KANKROLI-CHITTOR(RJ)-I | 71.03 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 71.03 | 142.06 | 142.06 | 100
80 | NR140049 | 400KV KANKROLI-JODHPUR | 187.965 | NR1 |  | 2019-08-11 05:19 | 2019-08-11 05:19 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on Y-N fault. FLR: Kankroli-25.2KM/ 7.19KA, Jodhpur-24.1KM/7.91KA.
[6 empty] | 2019-08-17 02:20 | 2019-08-17 02:29 |  |  |  | 0 | 0 | 0 | 0.00625 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Jodhpur-435 KV.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0.00625 | [5 empty] | NRPC | 744 | 2 | 187.965 | 375.93 | 375.93 | 100
81 | NR140051 | 400KV KANKROLI-RAPPC-II | 198.54 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 198.54 | 397.08 | 397.08 | 100
82 | NR140102 | 400KV KOTA-BEAWAR | 179.711 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 179.711 | 359.422 | 359.422 | 100
83 | NR140191 | 400KV KOTA-JAIPUR(S) | 180.11 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 180.11 | 360.22 | 360.22 | 100
84 | NR140060 | 400KV KOTA-MERTA-I | 255.56 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 255.56 | 511.12 | 511.12 | 100
85 | NR140062 | 400KV KOTA-RAPPC | 50.5 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 50.5 | 101 | 101 | 100
86 | NR140178 | 400KV KOTA-RAPPD | 55.103 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 55.103 | 110.206 | 110.206 | 100
87 | NR140063 | 400KV KOTESHWR-KHEP-I | 2.7 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 2.7 | 5.4 | 5.4 | 100
88 | NR140064 | 400KV KOTESHWR-KHEP-II | 2.7 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 2.7 | 5.4 | 5.4 | 100
89 | NR140065 | 400KV KOTESHWR-TEHRI-I | 14.463 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 14.463 | 57.852 | 57.852 | 100
90 | NR140098 | 400KV KOTESHWR-TEHRI-II | 16.49 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 16.49 | 65.96 | 65.96 | 100
91 | NR140165 | 400KV MEERUT-BAGPAT-I | 70.976 | NR1 | -- | 2019-08-13 10:18 | 2019-08-13 10:18 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Autoreclose on R-N fault.Meerut-35.92km, Bagpat-34.2km/8.69kA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 70.976 | 283.904 | 283.904 | 100
92 | NR140166 | 400KV MEERUT-BAGPAT-II | 70.976 | NR1 | -- | 2019-08-04 10:55 | 2019-08-04 12:51 |  |  |  | 0.080556 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for rectification of Bird guard of Y-ph wave trap, fell on ground at Baghpat end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.080556 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 70.976 | 283.904 | 283.1663 | 99.7401
93 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 66.009 | 132.018 | 132.018 | 100
94 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 66.009 | 132.018 | 132.018 | 100
95 | NR140077 | 400KV MEERUT-KOTESHWR-I | 178.69 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 178.69 | 714.76 | 714.76 | 100
96 | NR140099 | 400KV MEERUT-KOTESHWR-II | 175.63 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 175.63 | 702.52 | 702.52 | 100
97 | NR140078 | 400KV MEERUT-MND-I | 59.868 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 59.868 | 119.736 | 119.736 | 100
98 | NR140079 | 400KV MEERUT-MND-II | 59.868 | NR1 |  | 2019-08-31 14:58 | 2019-08-31 14:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Sucessfully A/R on B-N fault.FLR-Mrt-25.37km/12.71KA.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 59.868 | 119.736 | 119.736 | 100
99 | NR140143 | 400KV MEERUT-MND-III | 54.298 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 54.298 | 108.596 | 108.596 | 100
100 | NR140131 | 400KV MEERUT-MND-IV | 54.298 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 54.298 | 108.596 | 108.596 | 100
101 | NR140080 | 400KV MEERUT-MUZFRNGR | 37.38 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 37.38 | 74.76 | 74.76 | 100
102 | NR140103 | 400KV MERTA-BEAWAR | 76.018 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 76.018 | 152.036 | 152.036 | 100
103 | NR140176 | 400KV MORADABD-HAPUR(UP) | 106.85 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 106.85 | 213.7 | 213.7 | 100
104 | NR140177 | 400KV MURADNGR-HAPUR(UP) | 26.65 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 26.65 | 53.3 | 53.3 | 100
105 | NR140139 | 400KV NAVADA-GR.NOIDA | 30.15 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
| NR140139 | 400KV NAVADA-GR.NOIDA | 30.15 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 30.15 | 120.6 | 120.6 | 100
106 | NR140118 | 400KV NIMRANA-MANESAR-I | 67.041 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 67.041 | 134.082 | 134.082 | 100
107 | NR140119 | 400KV NIMRANA-MANESAR-II | 67.041 | NR1 |  | 2019-08-18 01:36 | 2019-08-18 14:19 |  |  |  | 0 | 0 | 0 | 0.52986 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Nimrana-430 KV.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0.52986 | [5 empty] | NRPC | 744 | 2 | 67.041 | 134.082 | 134.082 | 100
108 | NR140183 | 400KV NIMRANA-BABAI(RRVPNL) | 81 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 81 | 162 | 162 | 100
109 | NR140109 | 400KV NIMRANA-SIKAR-II | 175.859 | NR1 | -- | 2019-08-17 03:57 | 2019-08-19 19:38 |  |  |  | 0 | 0 | 0 | 1900-01-01 15:41 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Nimrana- 427 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 15:41 | [5 empty] | NRPC | 744 | 2 | 175.859 | 351.718 | 351.718 | 100
110 | NR140170 | 400KV RAPPC-CHITTOR(RJ)-I | 155.15 | NR1 |  | 2019-08-07 01:27 | 2019-08-07 01:27 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Autorecolse on R-N fault in UPPCL portion. FLR:Roorkee-64.33km/5.61kA.
[6 empty] | 2019-08-24 04:11 | 2019-08-24 04:11 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R succesfully on Y-N fault. FLR-Muzfngr-47.75km, Roorki-14.47km,IF-10.75KA. Fault in UPPCL section.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 155.15 | 310.3 | 310.3 | 100
111 | NR140175 | 400KV ROORKEE -DEHRADUN | 79.7 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 79.7 | 318.8 | 318.8 | 100
112 | NR140161 | 400KV ROORKI-KASHIPUR-I | 150.832 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 150.832 | 603.328 | 603.328 | 100
113 | NR140162 | 400KV ROORKI-KASHIPUR-II | 150.832 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 150.832 | 603.328 | 603.328 | 100
114 | NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | 2019-08-07 01:27 | 2019-08-07 01:27 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Autorecolse on R-N fault in UPPCL portion. FLR:Roorkee-64.33km/5.61kA.
| NR140086 | 400KV ROORKI-MUZFRNGR | 2.1 | NR1 | -- | 2019-08-24 04:11 | 2019-08-24 04:11 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R succesfully on Y-N fault. FLR-Muzfngr-47.75km, Roorki-14.47km,IF-10.75KA. Fault in UPPCL section.
|  | SUB TOTAL |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 2.1 | 4.2 | 4.2 | 100
115 | NR140087 | 400KV ROORKI-RISHIKESH | 2.1 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 2.1 | 4.2 | 4.2 | 100
116 | NR140167 | 400KV ROORKI-SAHARANPUR-I | 36.535 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 36.535 | 146.14 | 146.14 | 100
117 | NR140184 | 400KV SIKAR-BABAI(RRVPNL) | 94.43 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 2 | 94.43 | 188.86 | 188.86 | 100
118 | NR140155 | 400KV SIKAR-RATANGARH-I | 76.48 | NR1 | -- | 2019-08-09 04:26 | 2019-08-12 09:31 |  |  |  | 0 | 0 | 0 | 1900-01-02 05:05 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Sikar- 424KV.
[6 empty] | 2019-08-18 01:59 | 2019-08-18 07:15 |  |  |  | 0 | 0 | 0 | 0.21944 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Sikar-425 KV.
[6 empty] | 2019-08-20 01:55 | 2019-08-22 10:52 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:57 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Ratangarh - 422 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 19:18 | [5 empty] | NRPC | 744 | 2 | 76.48 | 152.96 | 152.96 | 100
119 | NR140156 | 400KV SIKAR-RATANGARH-II | 76.48 | NR1 | -- | 2019-08-01 16:15 | 2019-08-05 11:23 |  |  |  | 0 | 0 | 0 | 1900-01-02 19:08 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Sikar- 422KV.
[6 empty] | 2019-08-07 01:41 | 2019-08-08 10:50 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:09 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Sikar- 425KV.
[6 empty] | 2019-08-15 03:25 | 2019-08-19 19:31 |  |  |  | 0 | 0 | 0 | 1900-01-03 16:06 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Sikar- 420 KV.
[6 empty] | 2019-08-25 16:18 | 2019-08-26 22:41 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:23 |  |  |  | LVRD | Hand Tripped on Voltage Regulation, Sikar-421 KV.
[6 empty] | 2019-08-27 04:16 | 2019-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-03 19:44 |  |  |  | LVRD | Hand Tripped on Voltage Regulation,Sikar-421 KV.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 22:30 | [5 empty] | NRPC | 744 | 2 | 76.48 | 152.96 | 152.96 | 100
120 | NR140193 | 400KV BHADLA-BHADLA(RJ)-I | 26.542 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 26.542 | 106.168 | 106.168 | 100
121 | NR140194 | 400KV BHADLA-BHADLA(RJ)-II | 26.542 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 26.542 | 106.168 | 106.168 | 100
122 | NR140195 | 400KV BIKANER-BIKANER(RJ) | 9 | NR1 |  | 2019-08-20 12:29 | 2019-08-20 13:17 |  |  |  | 0.033333 | 0 | 0 | 0 |  |  |  | OSFT | Forced shutdown for isolation of Main Bay (40952) due to CB under lockout condition.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.033333 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 4 | 9 | 36 | 35.9613 | 99.8925
123 | NR140196 | 400KV BIKANER-BHADLA(RJ) | 9 | NR1 |  | 2019-08-26 19:18 | 2019-08-26 23:09 |  |  |  | 0 | 0 | 0 | 0.16042 |  |  |  | OSFD | Forced S/D by RRVPNL to attend hotspot at loc no-13 in their portion.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0.16042 | [5 empty] | NRPC | 744 | 4 | 9 | 36 | 36 | 100
|  | 220 KV TRANS LINES | [5 empty] | -- | -- | --
124 | NR122001 | 220KV ANTA-BHIL-I | 186.667 | NR1 | -- | 2019-08-19 20:00 | 2019-08-22 12:45 |  |  |  | 0 | 0 | 0 | 1900-01-01 16:45 |  |  |  | OSFD | CB H/ tripped by NTPC due to protection DC Earth fault problem at Anta. S/D continued by NTPC for rectification of problem. Line remain charged from Bhilwara end.
[6 empty] | 2019-08-27 00:22 | 2019-08-27 00:22 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed successfully on R-N fault. FLR-Bhilwara-176.6KM. Anta-46.68KM/2.723KA.
[6 empty] | 2019-08-28 18:19 | 2019-08-28 18:19 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on R-N fault, FLR, Anta-40KM/ Bhilwada-171.5km.
[6 empty] | 2019-08-28 19:54 | 2019-08-28 19:54 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on R-N fault, FLR, Anta-59.13KM/Bhilwada-156.53KM.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 16:45 | [5 empty] | NRPC | 744 | 1 | 186.667 | 186.667 | 186.667 | 100
125 | NR122002 | 220KV ANTA-BHIL-II | 186.667 | NR1 | -- | 2019-08-29 17:02 | 2019-08-29 18:03 |  |  |  | 0 | 0.042361 | 0 | 0 |  |  |  | OMSU | Line A/ reclosed at Bhilwara but tripped from Anta end due to Auto reclose problem at NTPC, during R-N fault. FLR: Anta-36.63km. Line remain charged from Bhilwara end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.042361 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 186.667 | 186.667 | 186.667 | 100
126 | NR122046 | 220KV ANTA-LALSOT | 180.287 | NR1 |  | 2019-08-20 10:22 | 2019-08-21 18:10 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:48 |  |  |  | OSFD | Hand tripped by NTPC during protection testing work at Anta end. S/D continued by them after charging attempt failed due to B-Phase CB not closed.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:48 | [5 empty] | NRPC | 744 | 1 | 180.287 | 180.287 | 180.287 | 100
127 | NR122004 | 220KV ANTA-RAPPC | 87.544 | NR1 | -- | 2019-08-30 23:32 | 2019-08-30 23:32 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Auto reclose on B-N fault.FLR:Anta-40.6km/2.88kA,RAPPC-41.41km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 87.544 | 87.544 | 87.544 | 100
128 | NR122005 | 220KV ANTA-S.MDHPR | 102.164 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 102.164 | 102.164 | 102.164 | 100
129 | NR122008 | 220KV BASSI-BAGRU | 35.353 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 35.353 | 35.353 | 35.353 | 100
130 | NR122009 | 220KV BASSI-DAUSA-I | 20.109 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 20.109 | 20.109 | 20.109 | 100
131 | NR122010 | 220KV BASSI-DAUSA-II | 20.109 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 20.109 | 20.109 | 20.109 | 100
132 | NR122011 | 220KV BASSI-IG NAGAR | 22.478 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 22.478 | 22.478 | 22.478 | 100
133 | BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
| BILHY2201 | 220KV FGPP-PALLA-I | 15.69 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 15.69 | 15.69 | 15.69 | 100
134 | BILHY2202 | 220KV FGPP-PALLA-II | 15.69 | NR1 |  | 2019-08-07 02:55 | 2019-08-07 04:52 |  |  |  | 0 | 0.08125 | 0 | 0 |  |  |  | OMSU | A/R at FGPP but tripped only from Palla(HVPNL) end due to Auto-reclose problem, during R-N fault. FLR:Palla-6.31km/3.90kA.
[6 empty] | 2019-08-27 09:24 | 2019-08-27 14:01 |  |  |  | 0 | 0 | 0 | 0.19236 |  |  |  | OSFD | Forced S/D by NTPC to attend hotspot on CT clamps at FGPP.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0.08125 | 0 | 0.19236 | [5 empty] | NRPC | 744 | 1 | 15.69 | 15.69 | 15.69 | 100
135 | BILHY2203 | 220KV FGPP-SPUR-I | 17.691 | NR1 |  | 2019-08-27 11:30 | 2019-08-27 13:17 |  |  |  | 0 | 0.074306 | 0 | 0 |  |  |  | OMSU | CB auto tripped only at FGPP end due to relay contact problem. Line remain charged from SPUR end.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0.074306 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 17.691 | 17.691 | 17.691 | 100
136 | BILHY2204 | 220KV FGPP-SPUR-II | 17.691 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 17.691 | 17.691 | 17.691 | 100
137 | NR122014 | 220KV HIRAPURA-IG NAGAR | 24.875 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 24.875 | 24.875 | 24.875 | 100
138 | NR122015 | 220KV HIRAPURA-SANGANER | 12 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 12 | 12 | 12 | 100
139 | NR222004 | 220KV HISAR-HISAR I/A-I | 13.77 | NR1 | -- | 2019-08-09 12:27 | 2019-08-09 19:20 |  |  |  | 0 | 0 | 0 | 0.28681 |  |  |  | OSFD | Forced S/D by HVPNL for attending hotspot in Y-phase CB at their end.
[6 empty] | 2019-08-29 11:39 | 2019-08-29 16:29 |  |  |  | 0 | 0 | 0 | 0.20139 |  |  |  | OSFD | Forced S/D by HVPNL to avoid overloading of line during Shutdown of Ckt-II.
[6 empty] | 2019-08-16 14:02 | 2019-08-16 19:38 |  |  |  | 0 | 0 | 0 | 0.23333 |  |  |  | OSFD | Forced S/D by HVPNL for attending hotspot on R-ph CT at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.72153 | [5 empty] | NRPC | 744 | 1 | 13.77 | 13.77 | 13.77 | 100
140 | NR222005 | 220KV HISAR-HISAR I/A-II | 13.77 | NR1 | -- | 2019-08-09 12:27 | 2019-08-09 19:20 |  |  |  | 0 | 0 | 0 | 0.28681 |  |  |  | OSFD | Forced S/D by HVPNL to avoid overloading, for attending hotspot in Y-phase CB of Ckt-I.
[6 empty] | 2019-08-16 14:03 | 2019-08-16 19:38 |  |  |  | 0 | 0 | 0 | 0.23264 |  |  |  | OSFD | Forced S/D by HVPNL to avoid overloading, for attending hotspot on R-ph CT of Ckt-I at their end.
32 | [5 empty] | 2019-08-29 11:39 | 2019-08-29 16:29 |  |  |  | 0 | 0 | 0 | 0.20139 |  |  |  | OSFD | Forced S/D by HVPNL for restoration of broken OPGW at their end connecting state telemetry/ SCADA data.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.72083 | [5 empty] | NRPC | 744 | 1 | 13.77 | 13.77 | 13.77 | 100
141 | NR122047 | 220KV LALSOT-DAUSA | 28.02 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 28.02 | 28.02 | 28.02 | 100
142 | BILUP2204 | 220KV MEERUT-MPURAM-I | 2.316 | NR1 | -- | 2019-08-08 15:56 | 2019-08-08 16:53 |  |  |  | 0 | 0.039583 | 0 | 0 |  |  |  | OMSU | Tripped on 220KV Bus-I LBB relay mal -operation of 220KV MEERUT-NEHTAUR (UPPCL) line.
[6 empty] | 2019-08-21 17:06 | 2019-08-21 19:47 |  |  |  | 0 | 0 | 0 | 0.11181 |  |  |  | OSFD | Forced S/D by UPPCL for replacement of red hot clamp of Y-phase CT at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.039583 | 0 | 0.11181 | [5 empty] | NRPC | 744 | 1 | 2.316 | 2.316 | 2.316 | 100
143 | BILUP2205 | 220KV MEERUT-MPURAM-II | 9.254 | NR1 | -- | 2019-08-03 00:20 | 2019-08-03 00:20 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed successfully on R-N fault,FLR-Meerut-4.00KM/18.71KA.
[6 empty] | 2019-08-03 15:10 | 2019-08-03 17:40 |  |  |  | 0.10417 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for replacement of flashover insulator at loc-15.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10417 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 9.254 | 9.254 | 9.2229 | 99.664
144 | BILUP2206 | 220KV MEERUT-NARA | 2.316 | NR1 | -- | 2019-08-08 13:46 | 2019-08-08 15:47 |  |  |  | 0 | 0.084028 | 0 | 0 |  |  |  | OMSU | Tripped on Y-N fault in UPPCL portion .FLR-Mrt-3.78km/ 15.69ka, Nara-29.13km,.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.084028 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 2.316 | 2.316 | 2.316 | 100
145 | BILUP2207 | 220KV MEERUT-SHTBDNGR | 8.234 | NR1 |  | 2019-08-01 11:23 | 2019-08-01 18:01 |  |  |  | 0 | 0 | 0 | 0.27639 |  |  |  | OSPD | S/D by UPPCL for lopping and chopping of trees in their line corridor
[6 empty] | 2019-08-03 10:07 | 2019-08-03 11:05 |  |  |  | 0 | 0.040278 | 0 | 0 |  |  |  | OMSU | A/Reclosed at Meerut but tripped from Shatabdingr end during B-N fault in UPPCL portion. FLR:Meerut-10.9km/11.4kA.
[6 empty] | 2019-08-03 20:00 | 2019-08-03 21:45 |  |  |  | 0 | 0.072917 | 0 | 0 |  |  |  | OMSU | A/Reclosed at Meerut but tripped from Shatabdingr end during B-N fault in UPPCL portion. FLR:Mrt-13.38km/9.92kA.
[6 empty] | 2019-08-05 08:22 | 2019-08-05 08:22 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Autorecolse on B-N fault in UPPCL portion. FLR:27.26km/7.26kA.
[6 empty] | 2019-08-05 12:55 | 2019-08-05 17:46 |  |  |  | 0 | 0 | 0 | 0.20208 |  |  |  | OSFD | Forced S/D by UPPCL to attend sparking in Y-phase CT clamp at Shatabdinagar(UPPCL) end .
[6 empty] | 2019-08-26 09:23 | 2019-08-26 10:10 |  |  |  | 0 | 0.032639 | 0 | 0 |  |  |  | OMSU | Tripped on B-N fault in UPPCL portion. FLR-Meerut-18.2KM/7.55KA. Shtbdngr-26.53KM/6.41KA.
[6 empty] | 2019-08-29 01:48 | 2019-08-29 02:39 |  |  |  | 0 | 0.035417 | 0 | 0 |  |  |  | SBBU | Tripped on Bus-Bar protection operated at Stbdngr due to blasting of B-ph CT of 160 MVA Trfrmr-I at Shatabdingr (UPPCL) S/S.
[6 empty] | 2019-08-31 04:34 | 2019-08-31 08:09 |  |  |  | 0 | 0.14931 | 0 | 0 |  |  |  | OMSU | Tripped on B-N fault in UPPCL portion. FLR-Meerut-14.89km/9.83kA. Satabdngr-27.3km/5.96KA.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0.33056 | 0 | 0.47847 | [5 empty] | NRPC | 744 | 1 | 8.234 | 8.234 | 8.234 | 100
146 | BILUP2208 | 220KV MEERUT-SIMBHOLI | 9.254 | NR1 |  | 2019-08-02 10:01 | 2019-08-02 12:22 |  |  |  | 0 | 0 | 0 | 0.097917 |  |  |  | OSFD | Forced shutdown by UPPCL due to sparking in their Y-Ph Bus Isolator at Simbholi. Line remain charged from Merrut.
[6 empty] | 2019-08-06 19:14 | 2019-08-06 19:14 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Autorecolse on R-N fault. FLR:18.7 km/8.1 kA. Fault in UPPCL portion.
[6 empty] | 2019-08-08 15:56 | 2019-08-08 16:54 |  |  |  | 0 | 0.040278 | 0 | 0 |  |  |  | OMSU | Tripped on 220KV Bus-I LBB relay mal -operation of 220KV MEERUT-NEHTAUR (UPPCL) line.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0.040278 | 0 | 0.097917 | [5 empty] | NRPC | 744 | 1 | 9.254 | 9.254 | 9.254 | 100
147 | NR122027 | 220KV RAPPB-CHITT-I | 128.833 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 128.833 | 128.833 | 128.833 | 100
148 | NR122028 | 220KV RAPPB-CHITT-II | 128.833 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 128.833 | 128.833 | 128.833 | 100
149 | NR122029 | 220KV RAPPB-RAPPC | 0.175 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 0.175 | 0.175 | 0.175 | 100
150 | NR122030 | 220KV RAPPB-UDAIPUR | 230.297 | NR1 |  | 2019-08-30 15:07 | 2019-08-30 15:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Successfully Auto reclose on B-N fault.FLR:RAPPB-58.64km,Udaipur-178.9km.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 230.297 | 230.297 | 230.297 | 100
151 | NR122031 | 220KV S.MDHPR-DAUSA-I | 106.243 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 106.243 | 106.243 | 106.243 | 100
152 | NR122042 | 220KV SIKAR-RATANGARH-I | 2.83 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 2.83 | 2.83 | 2.83 | 100
153 | NR122044 | 220KV SIKAR-RATANGARH-II | 2.83 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 2.83 | 2.83 | 2.83 | 100
154 | NR122043 | 220KV SIKAR-SIKAR(RJ)-I | 3 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 3 | 3 | 3 | 100
155 | NR122045 | 220KV SIKAR-SIKAR(RJ)-II | 3 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1 | 3 | 3 | 3 | 100
[8 empty] | -- | -- | --
| Lines | TOTAL FOR T/LS | [5 empty] | -- | -- | -- | 1900-01-03 20:59 | 0.73611 | 0 | 1900-04-19 13:40 | [5 empty] | NRPC |  |  | 13709.504 | 39076.3 | 39044.6036 | 99.9189 | %
|  | 765/400 KV ICT'S | [19 empty] | MVA |  | Weitage Factor
156 | NR1ICT86 | 765/400KV ICT-I AJMER | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
157 | NR1ICT87 | 765/400KV ICT-II AJMER | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
158 | NR1ICT88 | 765/400KV ICT-I CHITTORGRH | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
159 | NR1ICT89 | 765/400KV ICT-II CHITTORGRH | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
160 | NR1ICT709 | 765/400kv ICT-I JHATIKALA | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
7 | [7 empty] | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
161 | NR1ICT710 | 765/400kv ICT-II JHATIKALA | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
7 | [10 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
162 | NR1ICT711 | 765/400kv ICT-III JHATIKALA | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
163 | NR1ICT712 | 765/400kv ICT-IV JHATIKALA | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
164 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
| NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
165 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
166 | NR2ICT46 | 765/400KV ICT-I BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
167 | NR2ICT48 | 765/400KV ICT-II BHIWANI | 1500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
168 | NR1ICT715 | 765/400KV ICT-I BIKANER | 1500 | NR1 |  | 2019-08-01 05:30 | 2019-08-01 13:37 |  |  |  | 0.33819 | 0 | 0 | 0 |  |  |  | SICT | Tripped on R-ph OLTC PRD mal-operation due to moisture ingress during rain.
[6 empty] | 2019-08-01 13:37 | 2019-08-01 15:34 |  |  |  | 0 | 0 | 0 | 0.08125 |  |  |  | GOMD | Remain out in want of charging code from NRLDC, delayed after charging clearance/ code, requested by site.
[6 empty] | 2019-08-27 12:21 | 2019-08-27 19:36 |  |  |  | 0.30208 | 0 | 0 | 0 |  |  |  | OSPT | S/D for CSD tunning and CT oil sampling.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.64028 | 0 | 0 | 0.08125 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1469.0188 | 97.9346
169 | NR1ICT716 | 765/400KV ICT-II BIKANER | 1500 | NR1 |  | 2019-08-28 10:58 | 2019-08-28 20:13 |  |  |  | 0.38542 | 0 | 0 | 0 |  |  |  | OSPT | S/D for CSD tunning and CT oil sampling.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.38542 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1481.3508 | 98.7567
|  | 400/220 KV ICT'S | [5 empty] | -- | -- | --
170 | NR1ICT03 | 315MVA ICT-I BASSI | 315 | NR1 |  | 2019-08-17 04:10 | 2019-08-17 05:19 |  |  |  | 0 | 0 | 0.047917 | 0 |  |  |  | GOFC | Tripped due to over flux protection operated during high system voltage/ frequency in the grid following sudden load reduction in the grid. Bassi-425/239kV.
[6 empty] | 2019-08-18 03:09 | 2019-08-18 03:56 |  |  |  | 0 | 0 | 0.032639 | 0 |  |  |  | GOFC | Tripped due to over flux protection operated during high system voltage/ frequency in the grid following sudden load reduction in the grid. Bassi-425/239kV.
[6 empty] | 2019-08-18 05:18 | 2019-08-18 06:13 |  |  |  | 0 | 0 | 0.038194 | 0 |  |  |  | GOFC | Tripped due to over flux protection operated during high system voltage/ frequency in the grid following sudden load reduction in the grid. Bassi-425/239kV.
2 | [5 empty] | 2019-08-21 12:30 | 2019-08-21 13:10 |  |  |  | 0 | 0 | 0 | 0.027778 |  |  |  | SPRD | Hand tripped for Voltage regulation (Tap changed from 13 to 11)
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0.11875 | 0.027778 | [5 empty] | NRPC | 741.15 | 315 |  | 315 | 315 | 100
171 | NR1ICT04 | 315MVA ICT-II BASSI | 315 | NR1 |  | 2019-08-17 04:10 | 2019-08-17 05:21 |  |  |  | 0 | 0 | 0.049306 | 0 |  |  |  | GOFC | Tripped due to over flux protection operated during high system voltage/ frequency in the grid following sudden load reduction in the grid. Bassi-425/239kV.
[6 empty] | 2019-08-18 03:09 | 2019-08-18 03:56 |  |  |  | 0 | 0 | 0.032639 | 0 |  |  |  | GOFC | Tripped due to over flux protection operated during high system voltage/ frequency in the grid following sudden load reduction in the grid. Bassi-425/239kV.
[6 empty] | 2019-08-18 05:19 | 2019-08-18 07:11 |  |  |  | 0 | 0 | 0.077778 | 0 |  |  |  | GOFC | Tripped due to over flux protection operated during high system voltage/ frequency in the grid following sudden load reduction in the grid. Bassi-425/239kV.
[6 empty] | 2019-08-21 13:20 | 2019-08-21 13:45 |  |  |  | 0 | 0 | 0 | 0.017361 |  |  |  | SPRD | Hand tripped for Voltage regulation (Tap changed from 13 to 11)
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0.15972 | 0.017361 | [5 empty] | NRPC | 740.1667 | 315 |  | 315 | 315 | 100
172 | NR1ICT68 | 500MVA ICT-III BASSI | 500 | NR1 |  | 2019-08-21 14:12 | 2019-08-21 14:38 |  |  |  | 0 | 0 | 0 | 0.018056 |  |  |  | SPRD | Hand tripped for Voltage regulation (Tap changed from 13 to 11)
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0.018056 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
173 | NR1ICT75 | 500MVA ICT-I BAGPAT | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
174 | NR1ICT78 | 500MVA ICT-II BAGPAT | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
175 | NR2ICT08 | 315MVA ICT-I BAHADURGARH | 315 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
176 | NR2ICT42 | 500MVA ICT-II BAHADURGARH | 500 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
177 | NR1ICT05 | 315MVA ICT-III BAWANA | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
178 | NR1ICT06 | 315MVA ICT-I BHINMAL | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
179 | NR1ICT07 | 315MVA ICT-II BHINMAL | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
180 | NR1ICT08 | 315MVA ICT-I BHIWADI | 315 | NR1 |  | 2019-08-13 16:07 | 2019-08-13 18:21 |  |  |  | 0.093056 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for replacement of broken BPI.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.093056 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 314.0544 | 99.6998
181 | NR1ICT09 | 315MVA ICT-II BHIWADI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
182 | NR1ICT54 | 315MVA ICT-III BHIWADI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
183 | NR2ICT49 | 315MVA ICT-I BHIWANI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
184 | NR2ICT50 | 315MVA ICT-II BHIWANI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
185 | NR1ICT71 | 500MVA ICT-I BLBGARH | 500 | NR1 |  | 2019-08-30 10:03 | 2019-08-30 19:13 |  |  |  | 0.38194 | 0 | 0 | 0 |  |  |  | OSPT | S/D for retrofitment of relays, protection testing & AMP work.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.38194 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 493.8396 | 98.7679
186 | NR1ICT79 | 500MVA ICT-II BLBGARH | 500 | NR1 | -- | 2019-08-31 09:53 | 2019-08-31 17:34 |  |  |  | 0.32014 | 0 | 0 | 0 |  |  |  | OSPT | S/D for retrofitment of relays, protection testing & AMP work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.32014 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 494.8365 | 98.9673
187 | NR1ICT83 | 500MVA ICT-III BLBGARH | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
188 | NR1ICT84 | 500MVA ICT-IV BLBGARH | 500 | NR1 |  | 2019-08-01 09:42 | 2019-08-01 20:37 |  |  |  | 0.45486 | 0 | 0 | 0 |  |  |  | OSPT | S/D for replacement of disc insulator with polymer string in Ballabgarh switchyard.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.45486 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 492.6635 | 98.5327
189 | NR1ICT81 | 315MVA ICT-I DEHRADUN | 315 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
16 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
190 | NR1ICT82 | 315MVA ICT-II DEHRADUN | 315 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
191 | NR1ICT42 | 315MVA ICT-I GURGAON | 315 | NR1 |  | 2019-08-30 15:58 | 2019-08-30 20:01 |  |  |  | 0.16875 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to sparking in relay panel of ICT-I.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.16875 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 313.2853 | 99.4556
192 | NR1ICT51 | 315MVA ICT-II GURGAON | 315 | NR1 |  | 2019-08-30 09:38 | 2019-08-30 19:58 |  |  |  | 0.43056 | 0 | 0 | 0 |  |  |  | OSPT | S/D for NTAMC signal & operation testing after SCADA upgradation.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.43056 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 310.625 | 98.6111
193 | NR1ICT85 | 500MVA ICT-III GURGAON | 500 | NR1 |  | 2019-08-29 15:29 | 2019-08-29 18:22 |  |  |  | 0.12014 | 0 | 0 | 0 |  |  |  | OSPT | S/D for NTAMC signal & operation testing after SCADA upgradation.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.12014 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 498.0623 | 99.6125
194 | NR1ICT90 | 500MVA ICT-IV GURGAON | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
195 | NR2ICT09 | 315MVA ICT-I HISAR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
196 | NR2ICT10 | 315MVA ICT-II HISAR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
197 | NR2ICT34 | 315MVA ICT-III HISAR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
198 | NR1ICT57 | 500MVA ICT-I JAIPUR(S) | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
199 | NR1ICT62 | 500MVA ICT-II JAIPUR(S) | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
200 | NR2ICT53 | 500MVA ICT-I JIND | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
201 | NR2ICT54 | 500MVA ICT-II JIND | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
202 | NR1ICT16 | 315MVA ICT-I KANKROLI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
203 | NR1ICT17 | 315MVA ICT-II KANKROLI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
204 | NR1ICT18 | 315MVA ICT-III KANKROLI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
205 | NR1ICT21 | 315MVA ICT-I KOTA | 315 | NR1 |  | 2019-08-17 11:47 | 2019-08-17 17:44 |  |  |  | 0.24792 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to sparking in 220 KV side isolator at Kota.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.24792 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 312.4808 | 99.2003
206 | NR1ICT22 | 315MVA ICT-II KOTA | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
207 | NR1ICT63 | 315MVA ICT-I KOTPUTLI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
208 | NR1ICT64 | 315MVA ICT-II KOTPUTLI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
209 | NR1ICT24 | 315MVA ICT-I MAHRANIBAG | 315 | NR1 |  | 2019-08-23 12:38 | 2019-08-23 13:31 |  |  |  | 0.036806 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to smoke observed in CRP pannel of ICT-I.
33 |  |  |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.036806 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 314.626 | 99.8813
210 | NR1ICT25 | 315MVA ICT-II MAHRANIBAG | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
34 | [7 empty] | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
211 | NR1ICT45 | 500MVA ICT-III MAHRANIBAG | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
212 | NR1ICT46 | 500MVA ICT-IV MAHRANIBAG | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
213 | NR1ICT72 | 500MVA ICT-I MANDOLA | 500 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
40 |  |  |  | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
214 | NR1ICT80 | 500MVA ICT-II MANDOLA | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
215 | NR1ICT73 | 500MVA ICT-III MANDOLA | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
216 | NR1ICT74 | 500MVA ICT-IV MANDOLA | 500 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
| NR1ICT28 | 315MVA ICT-IV MANDOLA | 315 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
217 | NR1ICT58 | 500MVA ICT-I MANESAR | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
218 | NR1ICT61 | 500MVA ICT-II MANESAR | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
219 | NR1ICT32 | 315MVA ICT-I MEERUT | 315 | NR1 | -- | 2019-08-08 15:56 | 2019-08-08 16:51 |  |  |  | 0 | 0.038194 | 0 | 0 |  |  |  | OMSU | Tripped on 220KV Bus-I LBB relay mal -operation of 220KV MEERUT-NEHTAUR (UPPCL) line.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.038194 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
220 | NR1ICT33 | 315MVA ICT-II MEERUT | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
221 | NR1ICT34 | 315MVA ICT-III MEERUT | 315 | NR1 |  | 2019-08-08 15:56 | 2019-08-08 16:51 |  |  |  | 0 | 0.038194 | 0 | 0 |  |  |  | OMSU | Tripped on 220KV Bus-I LBB relay mal -operation of 220KV MEERUT-NEHTAUR (UPPCL) line.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0.038194 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
222 | NR1ICT69 | 500MVA ICT-IV MEERUT | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
223 | NR1ICT35 | 315MVA ICT-I MUZFRNGR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
224 | NR1ICT55 | 500MVA ICT-I NIMRANA | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
225 | NR1ICT50 | 315MVA ICT-II NIMRANA | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
226 | NR1ICT36 | 315MVA ICT-I ROORKI | 315 | NR1 |  | 2019-08-07 13:26 | 2019-08-08 02:41 |  |  |  | 0.55208 | 0 | 0 | 0 |  |  |  | SICT | Tripped on differential protection in Y-Phase during tripping of Roorkee-Ramnagar line on Z1 Y-ph fault.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.55208 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 309.3901 | 98.2191
227 | NR1ICT37 | 315MVA ICT-II ROORKI | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
228 | NR1ICT56 | 315MVA ICT-I SIKAR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
55 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
229 | NR1ICT52 | 315MVA ICT-II SIKAR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
230 | NR1ICT91 | 315MVA ICT-III SIKAR | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
231 | NR1ICT76 | 315MVA ICT-I SAHARANPUR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
| NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
232 | NR1ICT77 | 315MVA ICT-II SAHARANPUR | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
4 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
233 | NR2ICT36 | 315MVA ICT-I SONIPAT | 315 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
234 | NR2ICT35 | 315MVA ICT-II SONIPAT | 315 | NR1 | [6 empty] | 0 | 0 | 0 | 0
| NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
235 | NR1ICT92 | 500MVA ICT-I TUGHLKBD | 500 | NR1 |  | 2019-08-23 09:05 | 2019-08-25 13:14 |  |  |  | 1900-01-01 04:09 | 0 | 0 | 0 |  |  |  | OSPT | S/D for checking/ replacement of faulty socket bolt in 220kv side(LV) circuit breaker.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 1900-01-01 04:09 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 464.953 | 92.9906
236 | NR1ICT93 | 500MVA ICT-II TUGHLKBD | 500 | NR1 |  | 2019-08-26 08:48 | 2019-08-28 14:31 |  |  |  | 1900-01-01 05:43 | 0 | 0 | 0 |  |  |  | OSPT | S/D for checking/ replacement of faulty socket bolt in 220kv side(LV) circuit breaker.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 1900-01-01 05:43 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 463.9001 | 92.78
237 | NR1ICT95 | 500MVA ICT-III TUGHLKBD | 500 | NR1 |  | 2019-08-29 08:30 | 2019-08-31 15:02 |  |  |  | 1900-01-01 06:32 | 0 | 0 | 0 |  |  |  | OSPT | S/D for checking of socket bolt length 220kv side(LV) circuit breaker.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 1900-01-01 06:32 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 463.3513 | 92.6703
238 | NR1ICT94 | 500MVA ICT-IV TUGHLKBD | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
239 | NR1ICT96 | 500MVA ICT-II BHADLA | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
240 | NR1ICT97 | 500MVA ICT-III BHADLA | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
241 | NR1ICT98 | 500MVA ICT-I BHADLA | 500 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
|  | TOTAL FOR ICTs | [8 empty] | 1900-01-09 12:22 | 0.076389 | 0.27847 | 0.14444 | [5 empty] | NRPC |  | 46100 |  | 46100 | 46014.2332 | 99.814 | %
|  | SVC, | [5 empty] | -- | -- | -- | [11 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
242 | NR1SVC-01 | +400/-300MVAR SVC KANKROLI | 700 | NR1 |  | 2019-08-10 11:22 | 2019-08-10 17:09 |  |  |  | 0.24097 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D for attending hotspot in SVC TCR1 Bay.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.24097 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 700 |  | 700 | 694.5587 | 99.2227
|  | TOTAL FOR SVC |  | NR1 |  |  |  | -- | -- | -- | 0.24097 | 0 | 0 | 0 | [5 empty] | NRPC |  |  |  | 700 | 694.5587 | 99.2227 | %
|  | Bus & Switch Line Reactor |  | NR1 |  |  |  | -- | -- | -- | [11 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
243 | NR1BRT67 | 240MVAR B/Reactor AJMER-765 | 240 |  |  | 2019-08-03 21:04 | 2019-08-06 03:59 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:55 |  |  |  | SVRD | Hand tripped for Voltage regulation. Ajmer =754KV
[6 empty] | 2019-08-21 10:29 | 2019-08-21 14:59 |  |  |  | 0.1875 | 0 | 0 | 0 |  |  |  | OSPT | S/D for spare unit swapping and NTAMC operation checking work.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.1875 | 0 | 0 | 1900-01-01 06:55 | [5 empty] | NRPC | 744 | 240 |  | 240 | 238.5484 | 99.3952
244 | NR1BRT66 | 125MVAR B/Reactor AJMER | 125 | NR1 |  | 2019-08-30 10:12 | 2019-08-30 15:47 |  |  |  | 0.23264 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP & NTAMC operation checking work.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.23264 | 0 | 0 | [6 empty] | NRPC | 744 | 125 |  | 125 | 124.0619 | 99.2496
245 | NR1BRT57 | 125MVAR B/Reactor-I BAGPAT | 50 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
246 | NR1BRT04 | 50MVAR B/Reactor-I BASSI | 50 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
| NR1BRT04 | 50MVAR B/Reactor BASSI | 50 |  | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
247 | NR1BRT53 | 50MVAR B/Reactor-II BASSI | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | 50MVAR B/Reactor BASSI | 50 |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
248 | NR1BRT54 | 50MVAR B/Reactor-III BASSI | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | 50MVAR B/Reactor BASSI | 50 |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
249 | NR1BRT60 | 125MVAR B/Reactor-IV BASSI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | 50MVAR B/Reactor BASSI | 50 |  | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
250 | NR1BRT05 | 80MVAR B/Reactor BHINMAL | 80 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
251 | NR1BRT15 | 80MVAR B/Reactor BHIWADI | 80 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
252 | NR2BRT27 | 240MVAR B/Reactor-I BHIWANI | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
253 | NR2BRT28 | 240MVAR B/Reactor-II BHIWANI | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
254 | NR1BRT07 | 80MVAR B/Reactor BLBGARH | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
255 | NR1BRT68 | 125MVAR B/Reactor CHITTORGRH | 125 | NR1 |  | 2019-08-18 00:37 | 2019-08-18 05:09 |  |  |  | 0.18889 | 0 | 0 | 0 |  |  |  | OMST | Tripped on SPRD mal-operation due to moisture ingress.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.18889 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 124.2384 | 99.3907
256 | NR1BRT69 | 240MVAR B/Reactor CHITTORGRH-765 | 240 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1BRT23 | [9 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
257 | NR1BRT63 | 80MVAR B/Reactor-I DEHRADUN | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
258 | NR2BRT03 | 50MVAR B/Reactor-I HISAR | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
259 | NR2BRT22 | 125MVAR B/Reactor-II HISAR | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
260 | NR1BRT37 | 125MVAR B/Reactor-I JAIPUR(S) | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
261 | NR1BRT62 | 125MVAR B/Reactor-II JAIPUR(S) | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
262 | NR1BRT31 | 240MVAR B/Reactor-I JHATIKALA-765 | 240 | NR1 |  | 2019-08-01 | 2019-08-03 06:35 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:35 |  |  |  | SVRD | Hand tripped for Voltage regulation. Jhatikara=754KV. Out since 29/07/2019 14:59:00
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 06:35 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
263 | NR1BRT52 | 240MVAR B/Reactor-II JHATIKALA-765 | 240 | NR1 |  | 2019-08-05 14:58 | 2019-08-06 07:40 |  |  |  | 0 | 0 | 0 | 0.69583 |  |  |  | SVRD | Hand tripped for Voltage regulation.Jhatikara =757KV
[6 empty] | 2019-08-11 22:23 | 2019-08-13 17:19 |  |  |  | 0 | 0 | 0 | 1899-12-31 18:56 |  |  |  | SVRD | Hand Tripped on Voltage regulation.JHTKRA-753KV
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 11:38 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
264 | NR2BRT35 | 125MVAR Bus/Reactor JIND | 125 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
265 | NR1BRT08 | 50MVAR B/Reactor-I KANKROLI | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1BRT08 | 50MVAR B/Reactor KANKROLI | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
266 | NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1BRT34 | 125MVAR B/Reactor-II KANKROLI | 125 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
267 | NR1BRT09 | 80MVAR B/Reactor-II KOTA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1BRT09 | 80MVAR B/Reactor KOTA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
268 | NR1BRT55 | 50MVAR B/Reactor-II KOTA | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
269 | NR1BRT47 | 80MVAR B/Reactor-I KOTPUTLI | 80 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
270 | NR1BRT64 | 125MVAR B/Reactor Koteshwr HEP | 125 | NR1 | [6 empty] | 0 | 0 | 0 | 0
32 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
271 | NR1BRT11 | 50MVAR B/Reactor MANDOLA | 50 | NR1 |  | 2019-08-26 15:00 | 2019-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-04 09:00 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Mandola-395 KV
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 09:00 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
272 | NR1BRT30 | 125MVAR B/Reactor-I MANESAR | 125 | NR1 |  | 2019-08-26 14:56 | 2019-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-04 09:04 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Manesar-395 KV
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 09:04 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
273 | NR1BRT65 | 125MVAR B/Reactor-II MANESAR | 125 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
274 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
275 | NR1BRT12 | 50MVAR B/Reactor MURADNGR | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
276 | NR1BRT24 | 80MVAR B/Reactor NIMRANA | 80 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
277 | NR1BRT51 | 240MVAR B/Reactor-I PHAGI(JPR)-765 | 240 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
278 | NR1BRT48 | 125MVAR B/Reactor-I RATANGARH(RJ) | 125 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
279 | NR1BRT40 | 125MVAR B/Reactor ROORKI | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
| NR1BRT40 | 125MVAR B/Reactor Roorki | 125 | NR1 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
280 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
281 | NR2BRT13 | 125MVAR B/Reactor-I SONIPAT | 125 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
282 | NR1BRT61 | 125MVAR B/Reactor-II SONIPAT | 125 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
283 | NR1BRT58 | 50MVAR B/Reactor-I SAHARANPUR | 125 | NR1 |  | 2019-08-01 | 2019-08-02 05:38 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:38 |  |  |  | SVRD | Hand tripped for Voltage regulation.Sahranpur=389KV. Out since 29/07/2019 15:02:00
[6 empty] | 2019-08-10 23:13 | 2019-08-12 06:06 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:53 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Saharanpur-390KV
[6 empty] | 2019-08-12 21:44 | 2019-08-13 17:39 |  |  |  | 0 | 0 | 0 | 0.82986 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Saharnpur-388KV
[6 empty] | 2019-08-14 13:34 | 2019-08-15 17:29 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:55 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Saharnpur-392KV
[6 empty] | 2019-08-20 14:24 | 2019-08-21 05:23 |  |  |  | 0 | 0 | 0 | 0.62431 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Saharanpur -392 KV
[6 empty] | 2019-08-23 19:30 | 2019-08-24 16:27 |  |  |  | 0 | 0 | 0 | 0.87292 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Shrnpur-388KV
[6 empty] | 2019-08-28 09:32 | 2019-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-02 14:28 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Vol-392 KV
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 14:45 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
284 | NR1BRT59 | 50MVAR B/Reactor-II SAHARANPUR | 125 | NR1 |  | 2019-08-01 | 2019-08-02 05:38 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:38 |  |  |  | SVRD | Hand tripped for Voltage regulation.Sahranpur=389 KV. Out since 29/07/2019 15:02:00
[6 empty] | 2019-08-10 23:13 | 2019-08-12 06:06 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:53 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Saharanpur-390KV
[6 empty] | 2019-08-12 21:44 | 2019-08-13 17:39 |  |  |  | 0 | 0 | 0 | 0.82986 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Saharnpur-388KV
[6 empty] | 2019-08-14 13:34 | 2019-08-15 17:29 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:55 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Saharnpur-392KV
[6 empty] | 2019-08-20 14:24 | 2019-08-21 05:23 |  |  |  | 0 | 0 | 0 | 0.62431 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Saharanpur -392 KV
[6 empty] | 2019-08-23 19:30 | 2019-08-24 16:27 |  |  |  | 0 | 0 | 0 | 0.87292 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Shrnpur-388KV
[6 empty] | 2019-08-28 09:32 | 2019-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-02 14:28 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Vol-392 KV
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 14:45 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
285 | NR1BRT70 | 125MVAR B/Reactor TUGHLKBD | 125 | NR1 |  | 2019-08-05 14:53 | 2019-08-06 08:45 |  |  |  | 0 | 0 | 0 | 0.74444 |  |  |  | SVRD | Hand tripped for Voltage regulation. Tughlakabad =391 KV
| NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 |  | 2019-08-26 15:00 | 2019-09-01 |  |  |  | 0 | 0 | 0 | 1900-01-04 09:00 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Tuglaqabad-395 KV
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 02:52 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
286 | NR1BRT71 | 125MVAR B/Reactor BHADLA | 125 | NR1 |  | 2019-08-15 10:34 | 2019-08-15 17:24 |  |  |  | 0 | 0 | 0 | 0.28472 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Bhadla-378KV
| NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 |  | 2019-08-30 11:15 | 2019-09-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:45 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Bhadla-388 KV
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 19:35 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
287 | NR1BRT72 | 330MVAR B/Reactor-I BIKANER-765 | 330 | NR1 |  | 2019-08-11 22:34 | 2019-08-12 17:18 |  |  |  | 0 | 0 | 0 | 0.78056 |  |  |  | SVRD | Hand Tripped on Voltage regulation. Bikaner-744KV.
[6 empty] | 2019-08-26 11:37 | 2019-08-26 20:26 |  |  |  | 0 | 0 | 0 | 0.36736 |  |  |  | SVRD | Hand Tripped on Voltage regulation.Bikaner-756KV
| NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 |  | 2019-08-29 11:15 | 2019-08-29 16:34 |  |  |  | 0.22153 | 0 | 0 | 0 |  |  |  | OSPT | S/D for CSD commissioning and CT oil sampling.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.22153 | 0 | 0 | 1899-12-31 03:33 | [5 empty] | NRPC | 744 | 330 |  | 330 | 327.6418 | 99.2854
288 | NR1BRT73 | 125MVAR B/Reactor-II BIKANER | 125 | NR1 |  | 2019-08-30 10:42 | 2019-08-30 15:18 |  |  |  | 0.19167 | 0 | 0 | 0 |  |  |  | OSPT | S/D for CSD tuning and CT oil sampling.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.19167 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 124.2272 | 99.3817
289 | NR2BRT29 | BHIWANI 240MVAR S/R MEERUT line | 240 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
| NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 50 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
290 | NR1SRT06 | BHINML 50MVAR S/R KANKROLI | 50 | NR1 |  | 2019-08-05 10:40 | 2019-08-05 17:06 |  |  |  | 0.26806 | 0 | 0 | 0 |  |  |  | OSPT | S/D for rectification of problem in Vizimax make CSD of L/R at Bhinmal.
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0.26806 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 49.5677 | 99.1353
291 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
292 | NR1SRT33 | 330MVAR S/R ALIGARH Line at JHATIKALA | 330 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 330 |  | 330 | 330 | 100
293 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I | 50 | NR1 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
63 | NR1SRT09 | MEERUT 50MVAR S/R Kotesh Ckt-I | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
294 | NR1SRT10 | MEERUT 50MVAR S/R Kotesh Ckt-II | 50 | NR1 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
295 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | [7 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
296 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
297 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
298 | NR1SRT27 | PHAGI(JPR)240MVAR S/R BHIWANI-I | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
299 | NR1SRT28 | PHAGI(JPR)240MVAR S/R BHIWANI-II | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
300 | NR1SRT29 | AJMER 240MVAR S/R BIKANER-I Line | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
301 | NR1SRT30 | AJMER 240MVAR S/R BIKANER-II Line | 240 | NR1 |  | 2019-08-14 07:55 | 2019-08-14 13:25 |  |  |  | 0.22917 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to sparking in B-Ph L/Reactor isolator.
|  | SUB TOTAL | [8 empty] | 0.22917 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 238.2258 | 99.2608
302 | NR1SRT31 | 240MVAR S/R AJMER-I Line at CHITTOR | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
303 | NR1SRT32 | 240MVAR S/R AJMER-II Line at CHITTOR | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
304 | NR1SRT34 | AJMER 240MVAR S/R CHITTOR-I Line | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
305 | NR1SRT35 | AJMER 240MVAR S/R CHITTOR-II Line | 240 | NR1 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
306 | NR1SRT36 | BIKANER 330MVAR S/R AJMER-I Line | 330 | NR1 |  | 2019-08-23 10:25 | 2019-08-23 14:03 |  |  |  | 0.15139 | 0 | 0 | 0 |  |  |  | OSPT | S/D for CSD Tunning/ CT oil sampling.
|  | SUB TOTAL | [8 empty] | 0.15139 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 238.828 | 99.5116
307 | NR1SRT37 | BIKANER 330MVAR S/R AJMER-II Line | 330 | NR1 |  | 2019-08-24 09:48 | 2019-08-24 12:36 |  |  |  | 0.11667 | 0 | 0 | 0 |  |  |  | OSPT | S/D for CSD Tunning/ CT oil sampling.
|  | SUB TOTAL | [8 empty] | 0.11667 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 239.0968 | 99.6237
|  | TOTAL FOR BUS REACTORS | [8 empty] | 1899-12-31 18:54 | 0 | 0 | 1900-02-14 02:42 | [9 empty] | 7140 | 7133.2853 | 99.906 | %
|  | TOTAL | [8 empty] | 1900-01-16 10:02 | 0.8125 | 0.27847 | 1900-06-04 19:50
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L16:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M16:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N16:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O16:[Deemed Available, row above])
Note on C434: LILO of Anta-Dausa at LALKOT by RRVPNL DOC-01-02-14