## Nr2 Oct
Standard of Performance data for month of OCTOBER-2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
Annexure-A
| S.No | ELEMENT CODE | ELEMENT NAME | DESCRIPTION (Length/Nos/MVA/MVAr/etc) | Region | Type of Failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration time more than Specified (Y/N) | Difference between Actual and specified | NRLDC Code | Category Code | REASON OF OUTAGE | Outage certifying Agency and reference documents (NRPC) | % Availability as certified by certifying agency
[7 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | POWERGRID | OTHERS | System constraints / Natural calamity/ Militancy | Deemed Available
[12 empty] | @ (T) | # (U) | & ( C ) | * (D)
[12 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
1 | 1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | NRPC
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 |  | 2017-10-10 05:02 | 2017-10-10 06:04 | -- | -- | -- | 0 | 0.043056 | 0 | 0 | N/A | N/A | N/A | NR/10/527 | OMSU | LINE TRIPPED FROM JESSORE END ONLY. CB REMAIN CLOSED FROM BERASUIL AND SYNCHRONISED FROM JESSORE.
[7 empty] | 2017-10-26 10:10 | 2017-10-28 17:52 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 07:42 | N/A | N/A | N/A | NR/10/1758 | OSPD | SD TAKEN BY HPSEB, JESSORE FOR CB MAINTENANCE WORKS AT THEIR END.
[12 empty] | 0 | 0.043056 | 0 | 1900-01-01 07:42 | [7 empty] | 100
1 | 7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 |  | 2017-10-10 05:02 | 2017-10-10 07:41 | -- | -- | -- | 0.11042 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/529 | OSFT | LINE TRIPPED ON TRANSIENT FAULT.
[7 empty] | 2017-10-31 09:04 | 2017-10-31 17:33 | -- | -- | -- | 0 | 0 | 0 | 0.35347 | N/A | N/A | N/A | NR/10/2173 | OSPD | SD TAKEN BY NHPC, BAIRASUIL FOR AMP WORKS AT THEIR END.
[12 empty] | 0.11042 | 0 | 0 | 0.35347 | [7 empty] | 99.64
1 | 8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 |  | 2017-10-10 05:02 | 2017-10-10 06:49 | -- | -- | -- | 0 | 0.074306 | 0 | 0 | N/A | N/A | N/A | NR/10/530 | OMSU | LINE TRIPPED FROM JESSORE END ONLY. CB REMAIN CLOSED FROM PONG AND SYNCHRONISED FROM JESSORE.
[7 empty] | 2017-10-26 11:12 | 2017-10-26 19:24 | -- | -- | -- | 0 | 0 | 0 | 0.34167 | N/A | N/A | N/A | NR/10/1773 | OSPD | SD TAKEN BY HPSEB, JESSORE FOR CB MAINTENANCE WORKS AT THEIR END.
[7 empty] | 2017-10-28 13:12 | 2017-10-28 18:32 | -- | -- | -- | 0 | 0 | 0 | 0.22222 | N/A | N/A | N/A | NR/10/1942 | OSPD | SD TAKEN BY HPSEB, JESSORE FOR CB MAINTENANCE WORKS AT THEIR END.
[12 empty] | 0 | 0.074306 | 0 | 0.56389 | [7 empty] | 100
1 | 12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 |  | 2017-10-22 07:04 | 2017-10-22 15:45 | -- | -- | -- | 0 | 0 | 0 | 0.36181 | N/A | N/A | N/A | NR/10/1396 | OSPD | SD TAKEN BY JKPDD, JAMMU FOR MAINTENANCE WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.36181 | [7 empty] | 100
1 | 17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 |  | 2017-10-22 07:04 | 2017-10-22 17:27 | -- | -- | -- | 0 | 0 | 0 | 0.43264 | N/A | N/A | N/A | NR/10/1396 | OSPD | SD TAKEN BY JKPDD, JAMMU FOR MAINTENANCE WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.43264 | [7 empty] | 100
1 | 18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 |  | 2017-10-12 10:23 | 2017-10-18 13:49 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 03:26 | N/A | N/A | N/A | NR/10/746 | OSPD | SD TAKEN BY NHPC, SALAL FOR FOUNDATION WORK FOR INSTALLATION OF ISOLATOR OF CAPTIVE BAY AT THEIR END.
[7 empty] | 2017-10-22 13:00 | 2017-10-22 16:50 | -- | -- | -- | 0 | 0 | 0 | 0.15972 | N/A | N/A | N/A | NR/10/1418 | OSFD | LINE MANUALLY OPEN BY NHPC, SALAL DUE TO SPARKING ON LINE ISOLATOR AT THEIR END.
[12 empty] | 0 | 0 | 0 | 1900-01-05 07:16 | [7 empty] | 100
1 | 21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 |  | 2017-10-28 12:51 | 2017-10-28 16:10 | -- | -- | -- | 0 | 0 | 0 | 0.13819 | N/A | N/A | N/A | NR/10/1943 | OSPD | SD TAKEN BY JKPDD, PAMPORE FOR ATTENDING HOTSPOT ON CT AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.13819 | [7 empty] | 100
1 | 26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 28 | NR222028 | 220KV Jallandhar-Hamirpur(PG) -I | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 29 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 30 | NR222030 | 220KV Jallandhar-Hamirpur(PG) -II | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 31 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 32 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 |  | 2017-10-22 07:04 | 2017-10-22 15:15 | -- | -- | -- | 0 | 0 | 0 | 0.34097 | N/A | N/A | N/A | NR/10/1396 | OSPD | SD TAKEN BY JKPDD, JAMMU FOR MAINTENANCE WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.34097 | [7 empty] | 100
1 | 33 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 34 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 |  | 2017-10-14 10:19 | 2017-10-14 13:05 | -- | -- | -- | 0 | 0.11528 | 0 | 0 | N/A | N/A | N/A | NR/10/938 | OMSU | LINE TRIPPED ON Z-2, R-N FAULT DUE TO PROBLEM IN GENERATOR OF DTL, BAWANA CAUSED MULTIPLE TRIPPING. FLR ABDP : Z-2, 1.792KA , 177Km.
[12 empty] | 0 | 0.11528 | 0 | 0 | [7 empty] | 100
1 | 35 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 |  | 2017-10-24 02:58 | 2017-10-24 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.15694 | N/A | N/A | N/A | NR/10/1529 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION.AMRITSAR V=428V.
[12 empty] | 0 | 0 | 0 | 0.15694 | [7 empty] | 100
1 | 36 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 37 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 38 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 |  | 2017-10-12 05:40 | 2017-10-12 05:40 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R ON R-N FAULT. FLR JALANDHAR :15KM.
[7 empty] | 2017-10-20 00:28 | 2017-10-20 10:17 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | NR/10/1298 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=429KV.
[12 empty] | 0 | 0 | 0 | 0.40903 | [7 empty] | 100
1 | 39 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 |  | 2017-10-18 00:40 | 2017-10-18 04:47 | -- | -- | -- | 0 | 0 | 0 | 0.17153 | N/A | N/A | N/A | NR/10/1193 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=429KV.
[7 empty] | 2017-10-18 23:32 | 2017-10-19 18:38 | -- | -- | -- | 0 | 0 | 0 | 0.79583 | N/A | N/A | N/A | NR/10/1250 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=427KV.
[7 empty] | 2017-10-20 22:04 | 2017-10-21 18:41 | -- | -- | -- | 0 | 0 | 0 | 0.85903 | N/A | N/A | N/A | NR/10/1333 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=427KV.
[7 empty] | 2017-10-21 22:33 | 2017-10-22 11:13 | -- | -- | -- | 0 | 0 | 0 | 0.52778 | N/A | N/A | N/A | NR/10/1383 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=425KV.
[7 empty] | 2017-10-24 03:12 | 2017-10-24 15:33 | -- | -- | -- | 0 | 0 | 0 | 0.51458 | N/A | N/A | N/A | NR/10/1529 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=423KV.
[7 empty] | 2017-10-24 21:52 | 2017-10-25 09:22 | -- | -- | -- | 0 | 0 | 0 | 0.47917 | N/A | N/A | N/A | NR/10/1623 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-25 22:05 | 2017-10-26 08:30 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/10/1719 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-26 21:47 | 2017-10-27 14:21 | -- | -- | -- | 0 | 0 | 0 | 0.69028 | N/A | N/A | N/A | NR/10/1814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-27 22:03 | 2017-10-28 07:27 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-28 21:49 | 2017-10-29 07:56 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/10/1975 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-29 21:11 | 2017-10-30 06:58 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/10/2047 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 426KV
[7 empty] | 2017-10-30 21:43 | 2017-10-31 08:11 | -- | -- | -- | 0 | 0 | 0 | 0.43611 | N/A | N/A | N/A | NR/10/2142 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-31 20:56 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.12778 | N/A | N/A | N/A | NR/10/2209 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-05 06:10 | [7 empty] | 100
1 | 40 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 41 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 |  | 2017-10-18 23:48 | 2017-10-20 10:52 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:04 | N/A | N/A | N/A | NR/10/1251 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=427KV.
[12 empty] | 0 | 0 | 0 | 1899-12-31 11:04 | [7 empty] | 100
1 | 42 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 43 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 44 | NR240024 | 400KV Moga-Hissar | 209.39 | NR2 |  | 2017-10-13 10:05 | 2017-10-13 18:29 | -- | -- | -- | 0.35 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/835 | OSPT | SD TAKEN FOR AMP WORKS.
[7 empty] | 2017-10-25 21:51 | 2017-10-26 08:56 | -- | -- | -- | 0 | 0 | 0 | 0.46181 | N/A | N/A | N/A | NR/10/1717 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 426KV.
[12 empty] | 0.35 | 0 | 0 | 0.46181 | [7 empty] | 98.87
1 | 45 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 |  | 2017-10-20 21:15 | 2017-10-22 09:23 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:08 | N/A | N/A | N/A | NR/10/1331 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. FATEHABAD V=430KV.
[12 empty] | 0 | 0 | 0 | 1899-12-31 12:08 | [7 empty] | 100
1 | 46 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 |  | 2017-10-23 02:44 | 2017-10-23 02:44 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R ON R-N FAULT.FLR-PATIALA : 50.78KM, NALAGARH :35 KM.
[7 empty] | 2017-10-24 12:40 | 2017-10-24 14:27 | -- | -- | -- | 0.074306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1572 | OSPT | SD TAKEN FOR RECTIFICATION OF JUMPER AT LOC. NO.135.
[7 empty] | 2017-10-24 23:55 | 2017-10-25 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.22014 | N/A | N/A | N/A | NR/10/1626 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION AS PER NRLDC.
[7 empty] | 2017-10-26 01:24 | 2017-10-26 05:02 | -- | -- | -- | 0 | 0 | 0 | 0.15139 | N/A | N/A | N/A | NR/10/1723 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV.
[12 empty] | 0.074306 | 0 | 0 | 0.37153 | [7 empty] | 99.76
1 | 47 | NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 |  | 2017-10-26 09:10 | 2017-10-26 20:35 | -- | -- | -- | 0 | 0 | 0 | 0.47569 | N/A | N/A | N/A | NR/10/1742 | OSPD | SD TAKEN BY NHPC, URI-I FOR RELAY TESTING WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.47569 | [7 empty] | 100
1 | 48 | NR240031 | 400KV URI-WAGOORA-II | 94.99 | NR2 |  | 2017-10-27 09:18 | 2017-10-27 19:00 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/10/1833 | OSPD | SD TAKEN BY NHPC, URI-I FOR RELAY TESTING WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.40417 | [7 empty] | 100
1 | 49 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 50 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 51 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 52 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 53 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 54 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 55 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 56 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 57 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 58 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 |  | 2017-10-28 09:04 | 2017-10-28 19:28 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/10/1929 | OSPD | SD TAKEN BY NHPC, URI-I FOR RELAY TESTING WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.43333 | [7 empty] | 100
1 | 59 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 |  | 2017-10-11 10:01 | 2017-10-11 18:30 | -- | -- | -- | 0 | 0 | 0 | 0.35347 | N/A | N/A | N/A | NR/10/632 | LCSD | SD TAKEN FOR 400 KV BB EXTENSION FOR CONSTRUCTION OF NEW BAYS FOR ICT-1 & 2 AT BANALA.
[7 empty] | 2017-10-13 12:28 | 2017-10-13 19:43 | -- | -- | -- | 0 | 0 | 0 | 0.30208 | N/A | N/A | N/A | NR/10/833 | LCSD | SD TAKEN FOR 400 KV BB EXTENSION FOR CONSTRUCTION OF NEW BAYS FOR ICT-1 & 2 AT BANALA.
[7 empty] | 2017-10-16 01:07 | 2017-10-17 08:22 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:15 | N/A | N/A | N/A | NR/10/1049 | LVRD | LINE HAND TRIPPED ON VOLTAGE REGULATION. NALAGARH V=422KV.
[7 empty] | 2017-10-19 01:00 | 2017-10-20 12:21 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:21 | N/A | N/A | N/A | NR/10/1254 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH V=426KV.
[7 empty] | 2017-10-22 21:05 | 2017-10-23 08:22 | -- | -- | -- | 0 | 0 | 0 | 0.47014 | N/A | N/A | N/A | NR/10/1430 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION.NALAGARH V=419KV.
[7 empty] | 2017-10-24 00:25 | 2017-10-24 12:11 | -- | -- | -- | 0 | 0 | 0 | 0.49028 | N/A | N/A | N/A | NR/10/1526 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION.NALAGARH V=427V.
[7 empty] | 2017-10-24 22:03 | 2017-10-25 10:00 | -- | -- | -- | 0 | 0 | 0 | 0.49792 | N/A | N/A | N/A | NR/10/1625 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-10-25 21:44 | 2017-10-26 08:29 | -- | -- | -- | 0 | 0 | 0 | 0.44792 | N/A | N/A | N/A | NR/10/1717 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-10-26 22:59 | 2017-10-27 09:06 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/10/1818 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-10-27 21:53 | 2017-10-28 07:24 | -- | -- | -- | 0 | 0 | 0 | 0.39653 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-10-28 21:51 | 2017-10-29 08:34 | -- | -- | -- | 0 | 0 | 0 | 0.44653 | N/A | N/A | N/A | NR/10/1975 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-10-29 21:49 | 2017-10-30 10:10 | -- | -- | -- | 0 | 0 | 0 | 0.51458 | N/A | N/A | N/A | NR/10/2054 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-10-31 01:44 | 2017-10-31 08:25 | -- | -- | -- | 0 | 0 | 0 | 0.27847 | N/A | N/A | N/A | NR/10/2149 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 432KV
[7 empty] | 2017-10-31 21:48 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.091667 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[12 empty] | 0 | 0 | 0 | 1900-01-06 11:40 | [7 empty] | 100
1 | 60 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 61 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 |  | 2017-10-22 21:55 | 2017-10-23 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | N/A | N/A | N/A | NR/10/1434 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR V=422KV.
[7 empty] | 2017-10-23 08:02 | 2017-10-23 19:02 | -- | -- | -- | 0 | 0 | 0 | 0.45833 | N/A | N/A | N/A | NR/10/1454 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-23 21:10 | 2017-10-24 08:19 | -- | -- | -- | 0 | 0 | 0 | 0.46458 | N/A | N/A | N/A | NR/10/1517 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABD V=422KV.
[7 empty] | 2017-10-25 08:26 | 2017-10-25 19:37 | -- | -- | -- | 0 | 0 | 0 | 0.46597 | N/A | N/A | N/A | NR/10/1643 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-27 07:53 | 2017-10-27 19:53 | -- | -- | -- | 0 | 0 | 0 | 0.5 | N/A | N/A | N/A | NR/10/1828 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-28 22:34 | 2017-10-29 08:15 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/10/1977 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 423KV
[7 empty] | 2017-10-29 08:15 | 2017-10-29 14:13 | -- | -- | -- | 0 | 0 | 0 | 0.24861 | N/A | N/A | N/A | NR/10/1995 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-31 21:49 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.090972 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 427KV
[12 empty] | 0 | 0 | 0 | 1900-01-01 23:36 | [7 empty] | 100
1 | 62 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 |  | 2017-10-24 08:24 | 2017-10-24 19:10 | -- | -- | -- | 0 | 0 | 0 | 0.44861 | N/A | N/A | N/A | NR/10/1543 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-24 22:11 | 2017-10-25 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.325 | N/A | N/A | N/A | NR/10/1625 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 426KV
[7 empty] | 2017-10-25 21:48 | 2017-10-26 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/10/1717 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 426KV
[7 empty] | 2017-10-26 08:13 | 2017-10-26 19:12 | -- | -- | -- | 0 | 0 | 0 | 0.45764 | N/A | N/A | N/A | NR/10/1738 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-26 22:54 | 2017-10-27 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.28472 | N/A | N/A | N/A | NR/10/1818 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 424KV
[7 empty] | 2017-10-27 21:56 | 2017-10-28 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.41944 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 428KV
[7 empty] | 2017-10-28 08:00 | 2017-10-28 18:15 | -- | -- | -- | 0 | 0 | 0 | 0.42708 | N/A | N/A | N/A | NR/10/1921 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-31 08:03 | 2017-10-31 18:07 | -- | -- | -- | 0 | 0 | 0 | 0.41944 | N/A | N/A | N/A | NR/10/2168 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[12 empty] | 0 | 0 | 0 | 1900-01-02 03:36 | [7 empty] | 100
1 | 63 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 |  | 2017-10-26 23:03 | 2017-10-27 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.27014 | N/A | N/A | N/A | NR/10/1818 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 425KV
[7 empty] | 2017-10-29 23:46 | 2017-10-30 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.27569 | N/A | N/A | N/A | NR/10/2057 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 4224V
[7 empty] | 2017-10-30 08:01 | 2017-10-30 18:42 | -- | -- | -- | 0 | 0 | 0 | 0.44514 | N/A | N/A | N/A | NR/10/1828 | LCSD | SD TAKEN FOR REPLACMENT OF DISC INSULATOR WITH POLYMER INSULATOR.
[7 empty] | 2017-10-31 22:37 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.057639 | N/A | N/A | N/A | NR/10/2215 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 423KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 01:10 | [7 empty] | 100
1 | 64 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 |  | 2017-10-23 15:03 | 2017-10-23 15:33 | -- | -- | -- | 0.020833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1493 | LEFT | LINE TRIPPED ON Y-N FAULT. FLR PANCHKULA :5.97kA, 36.6KM & FLR NAPTHA-JHAKRI :-2.784kA, 133.8KM.
[7 empty] | 2017-10-24 23:59 | 2017-10-25 05:17 | -- | -- | -- | 0 | 0 | 0 | 0.22083 | N/A | N/A | N/A | NR/10/1626 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 423KV
[7 empty] | 2017-10-26 00:30 | 2017-10-26 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.20694 | N/A | N/A | N/A | NR/10/1721 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 425KV.
[7 empty] | 2017-10-27 22:12 | 2017-10-28 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.30625 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 424KV
[7 empty] | 2017-10-28 22:36 | 2017-10-29 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.31944 | N/A | N/A | N/A | NR/10/1977 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 423KV
[7 empty] | 2017-10-30 23:23 | 2017-10-31 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.24653 | N/A | N/A | N/A | NR/10/2146 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI = 428KV
[12 empty] | 0.020833 | 0 | 0 | 1899-12-31 07:12 | [7 empty] | 99.93
1 | 65 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 66 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 |  | 2017-10-14 10:19 | 2017-10-14 12:05 | -- | -- | -- | 0 | 0.073611 | 0 | 0 | N/A | N/A | N/A | NR/10/949 | OMSU | LINE TRIPPED ON Z-2, R-N FAULT DUE TO PROBLEM IN GENERATOR OF DTL, BAWANA CAUSED MULTIPLE TRIPPING. FLR DPLR : Z-2, R-N, IR=7.5KA and 25.1Km.
[12 empty] | 0 | 0.073611 | 0 | 0 | [7 empty] | 100
1 | 67 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 |  | 2017-10-12 02:42 | 2017-10-12 17:34 | -- | -- | -- | 0 | 0 | 0 | 0.61944 | N/A | N/A | N/A | NR/10/716 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=427KV.
[7 empty] | 2017-10-15 01:29 | 2017-10-15 19:09 | -- | -- | -- | 0 | 0 | 0 | 0.73611 | N/A | N/A | N/A | NR/10/1000 | LVRD | LINE HAND TRIPPED ON VOLTAGE REGULATION. VOLTAGE AT JALANDHAR V=427KV.
[7 empty] | 2017-10-16 00:40 | 2017-10-16 09:54 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | NR/10/1048 | LVRD | LINE HAND TRIPPED ON VOLTAGE REGULATION. JALANDHAR V=427KV.
[7 empty] | 2017-10-17 02:25 | 2017-10-17 02:29 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-10-17 02:29 | 2017-10-17 07:42 | -- | -- | -- | 0 | 0 | 0 | 0.21736 | N/A | N/A | N/A | NR/10/1128 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-18 00:45 | 2017-10-19 18:30 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 17:45 | N/A | N/A | N/A | NR/10/1193 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=429KV.
[7 empty] | 2017-10-20 03:58 | 2017-10-20 04:02 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 439KV
[7 empty] | 2017-10-20 04:02 | 2017-10-20 11:02 | -- | -- | -- | 0 | 0 | 0 | 0.29167 | N/A | N/A | N/A | NR/10/1301 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-20 21:34 | 2017-10-21 18:35 | -- | -- | -- | 0 | 0 | 0 | 0.87569 | N/A | N/A | N/A | NR/10/1332 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=427KV.
[7 empty] | 2017-10-21 22:31 | 2017-10-22 11:06 | -- | -- | -- | 0 | 0 | 0 | 0.52431 | N/A | N/A | N/A | NR/10/1383 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=425KV.
[7 empty] | 2017-10-22 22:18 | 2017-10-23 10:06 | -- | -- | -- | 0 | 0 | 0 | 0.49167 | N/A | N/A | N/A | NR/10/1436 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=427KV.
[7 empty] | 2017-10-24 00:23 | 2017-10-24 09:48 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/10/1526 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=431KV.
[7 empty] | 2017-10-24 21:49 | 2017-10-25 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/10/1623 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-25 21:43 | 2017-10-26 08:29 | -- | -- | -- | 0 | 0 | 0 | 0.44861 | N/A | N/A | N/A | NR/10/1717 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 427KV
[7 empty] | 2017-10-26 21:45 | 2017-10-27 08:49 | -- | -- | -- | 0 | 0 | 0 | 0.46111 | N/A | N/A | N/A | NR/10/1814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-27 22:00 | 2017-10-28 09:48 | -- | -- | -- | 0 | 0 | 0 | 0.49167 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-28 21:47 | 2017-10-29 07:47 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/10/1975 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-29 16:16 | 2017-10-30 06:59 | -- | -- | -- | 0 | 0 | 0 | 0.61319 | N/A | N/A | N/A | NR/10/2021 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 431KV
[7 empty] | 2017-10-30 21:36 | 2017-10-31 08:04 | -- | -- | -- | 0 | 0 | 0 | 0.43611 | N/A | N/A | N/A | NR/10/2142 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-31 20:56 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.12778 | N/A | N/A | N/A | NR/10/2209 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 425KV
[12 empty] | 0 | 0 | 0.0055556 | 1900-01-08 15:28 | [7 empty] | 100
1 | 68 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 |  | 2017-10-09 03:39 | 2017-10-09 03:43 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR : 437KV
[7 empty] | 2017-10-09 03:43 | 2017-10-09 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.11181 | N/A | N/A | N/A | NR/10/427 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-13 00:28 | 2017-10-13 06:41 | -- | -- | -- | 0 | 0 | 0 | 0.25903 | N/A | N/A | N/A | NR/10/812 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=424KV.
[7 empty] | 2017-10-16 01:40 | 2017-10-16 01:45 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 437KV.
[7 empty] | 2017-10-16 01:45 | 2017-10-16 09:51 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/10/1056 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-16 23:45 | 2017-10-17 09:32 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/10/1126 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=424KV.
[7 empty] | 2017-10-18 03:24 | 2017-10-18 03:28 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 437KV
[7 empty] | 2017-10-18 03:28 | 2017-10-18 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.13125 | N/A | N/A | N/A | NR/10/1197 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-19 02:49 | 2017-10-19 02:51 | -- | -- | -- | 0 | 0 | 0.0013889 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-10-19 02:51 | 2017-10-19 09:45 | -- | -- | -- | 0 | 0 | 0 | 0.2875 | N/A | N/A | N/A | NR/10/1256 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-20 00:29 | 2017-10-20 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.25486 | N/A | N/A | N/A | NR/10/1298 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=429KV.
[7 empty] | 2017-10-21 00:50 | 2017-10-21 00:55 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-10-21 00:55 | 2017-10-21 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.23056 | N/A | N/A | N/A | NR/10/1338 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-22 01:56 | 2017-10-22 02:02 | -- | -- | -- | 0 | 0 | 0.0041667 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-10-22 02:02 | 2017-10-22 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.18472 | N/A | N/A | N/A | --- | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-22 21:02 | 2017-10-23 07:31 | -- | -- | -- | 0 | 0 | 0 | 0.43681 | N/A | N/A | N/A | NR/10/1430 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=424KV.
[7 empty] | 2017-10-24 00:16 | 2017-10-24 00:22 | -- | -- | -- | 0 | 0 | 0.0041667 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-10-24 00:22 | 2017-10-24 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.26042 | N/A | N/A | N/A | NR/10/1526 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-25 22:06 | 2017-10-26 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.34097 | N/A | N/A | N/A | NR/10/1719 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-27 01:26 | 2017-10-27 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.21667 | N/A | N/A | N/A | NR/10/1820 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 428KV
[7 empty] | 2017-10-28 01:58 | 2017-10-28 02:03 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | N/A | N/A | N/A | NR/10/1908 | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-10-28 02:03 | 2017-10-28 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.16528 | N/A | N/A | N/A | NR/10/1908 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-29 00:18 | 2017-10-29 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.3125 | N/A | N/A | N/A | NR/10/1984 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 426KV
[7 empty] | 2017-10-29 21:22 | 2017-10-30 10:04 | -- | -- | -- | 0 | 0 | 0 | 0.52917 | N/A | N/A | N/A | NR/10/2051 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 426KV
[7 empty] | 2017-10-30 13:01 | 2017-10-30 13:06 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 437KV
[7 empty] | 2017-10-30 13:06 | 2017-10-31 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.72083 | N/A | N/A | N/A | NR/10/2105 | LVRD | LINE KEPT OPEN FOR SYSTEM VOLTAGE REGULATION.
[7 empty] | 2017-10-31 21:48 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.091667 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[12 empty] | 0 | 0 | 0.029167 | 1900-01-04 06:42 | [7 empty] | 100
1 | 69 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 70 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 71 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 |  | 2017-10-16 10:45 | 2017-10-16 10:45 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R ON B-N FAULT. FLR AMRITSAR : 173.9 KM AND BANALA : 87.3 KM
[6 empty] | Insulator failure | 2017-10-17 09:23 | 2017-10-17 16:24 | -- | -- | -- | 0.29236 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1142 | OSPT | SD TAKEN FOR RESTORATION OF B-PH DE-CAPPED INSULATOR STRING AT TOWER NO. 182.
[7 empty] | 2017-10-31 01:43 | 2017-10-31 08:35 | -- | -- | -- | 0 | 0 | 0 | 0.28611 | N/A | N/A | N/A | NR/10/2149 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 427KV
[7 empty] | 2017-10-31 21:46 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.093056 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 427KV
[12 empty] | 0.29236 | 0 | 0 | 0.37917 | [7 empty] | 99.06
1 | 72 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 73 | NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 74 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 75 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 76 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 |  | 2017-10-06 08:50 | 2017-10-06 19:00 | -- | -- | -- | 0 | 0 | 0 | 0.42361 | N/A | N/A | N/A | NR/10/253 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-07 08:28 | 2017-10-07 19:04 | -- | -- | -- | 0 | 0 | 0 | 0.44167 | N/A | N/A | N/A | NR/10/321 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-08 08:26 | 2017-10-08 19:03 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/10/378 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-09 08:04 | 2017-10-09 19:00 | -- | -- | -- | 0 | 0 | 0 | 0.45556 | N/A | N/A | N/A | NR/10/436 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-10 08:47 | 2017-10-10 19:09 | -- | -- | -- | 0 | 0 | 0 | 0.43194 | N/A | N/A | N/A | NR/10/537 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-11 08:24 | 2017-10-11 19:44 | -- | -- | -- | 0 | 0 | 0 | 0.47222 | N/A | N/A | N/A | NR/10/616 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-12 08:59 | 2017-10-12 19:15 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | N/A | N/A | N/A | NR/10/723 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-13 08:32 | 2017-10-13 19:01 | -- | -- | -- | 0 | 0 | 0 | 0.43681 | N/A | N/A | N/A | NR/10/826 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-14 08:51 | 2017-10-14 19:01 | -- | -- | -- | 0 | 0 | 0 | 0.42361 | N/A | N/A | N/A | NR/10/937 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[7 empty] | 2017-10-15 08:33 | 2017-10-15 19:33 | -- | -- | -- | 0 | 0 | 0 | 0.45833 | N/A | N/A | N/A | NR/10/1006 | LCSD | SD TAKEN FOR TOWER ERECTION WORK OF LILO OF 400KV KISHENPUR- NEW WANPOH-2 LINE AT BAGLIHAR.
[12 empty] | 0 | 0 | 0 | 1900-01-03 09:56 | [7 empty] | 100
1 | 77 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 78 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 79 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 |  | 2017-10-26 01:20 | 2017-10-26 04:59 | -- | -- | -- | 0 | 0 | 0 | 0.15208 | N/A | N/A | N/A | NR/10/1723 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV.
[7 empty] | 2017-10-28 00:16 | 2017-10-28 04:38 | -- | -- | -- | 0 | 0 | 0 | 0.18194 | N/A | N/A | N/A | NR/10/1907 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-10-31 23:32 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.019444 | N/A | N/A | N/A | NR/10/2216 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[12 empty] | 0 | 0 | 0 | 0.35347 | [7 empty] | 100
1 | 80 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 81 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 82 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 |  | 2017-10-24 23:53 | 2017-10-25 05:08 | -- | -- | -- | 0 | 0 | 0 | 0.21875 | N/A | N/A | N/A | NR/10/1626 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION AS PER NRLDC.
[7 empty] | 2017-10-27 01:24 | 2017-10-27 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.18333 | N/A | N/A | N/A | NR/10/1820 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION AS PER NRLDC. NALAGARH = 425KV
[7 empty] | 2017-10-30 23:34 | 2017-10-31 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.25556 | N/A | N/A | N/A | NR/10/2146 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[12 empty] | 0 | 0 | 0 | 0.65764 | [7 empty] | 100
1 | 83 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 84 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 85 | NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 86 | NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 87 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 |  | 2017-10-22 02:48 | 2017-10-22 09:03 | -- | -- | -- | 0 | 0 | 0 | 0.26042 | N/A | N/A | N/A | NR/10/1388 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. kURUKSHETRA V=428KV.
[7 empty] | 2017-10-22 21:52 | 2017-10-23 10:13 | -- | -- | -- | 0 | 0 | 0 | 0.51458 | N/A | N/A | N/A | NR/10/1434 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=430KV.
[7 empty] | 2017-10-23 21:14 | 2017-10-25 07:00 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:46 | N/A | N/A | N/A | NR/10/1517 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=431KV.
[12 empty] | 0 | 0 | 0 | 1900-01-01 04:22 | [7 empty] | 100
1 | 88 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 |  | 2017-10-26 22:03 | 2017-10-27 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.31875 | N/A | N/A | N/A | NR/10/1814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA = 429KV
[7 empty] | 2017-10-27 21:55 | 2017-10-28 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA = 431KV
[7 empty] | 2017-10-28 22:19 | 2017-10-29 03:45 | -- | -- | -- | 0 | 0 | 0 | 0.22639 | N/A | N/A | N/A | NR/10/1977 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 425KV
[7 empty] | 2017-10-29 20:27 | 2017-10-30 06:59 | -- | -- | -- | 0 | 0 | 0 | 0.43889 | N/A | N/A | N/A | NR/10/2039 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 08:17 | [7 empty] | 100
1 | 89 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 |  | 2017-10-15 11:10 | 2017-10-15 11:36 | -- | -- | -- | 0 | 0.018056 | 0 | 0 | N/A | N/A | N/A | NR/10/1015 | OMSU | LINE TRIPPED DUE TO DT RECEIVED AT KURUKSHETRA DUE TO OVER VOLTAGE DEVELOPED AT SONEPAT BECAUSE OF FAULT AND TRIPPING OF 220KV SONEPAT-MOHANA-II LINE OF HVPNL.
[7 empty] | 2017-10-21 01:21 | 2017-10-21 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.26875 | N/A | N/A | N/A | NR/10/1339 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=430KV.
[7 empty] | 2017-10-22 02:56 | 2017-10-22 09:04 | -- | -- | -- | 0 | 0 | 0 | 0.25556 | N/A | N/A | N/A | NR/10/1388 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. kURUKSHETRA V=428KV.
[7 empty] | 2017-10-22 23:25 | 2017-10-23 07:34 | -- | -- | -- | 0 | 0 | 0 | 0.33958 | N/A | N/A | N/A | NR/10/1438 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=430 KV.
[7 empty] | 2017-10-31 01:33 | 2017-10-31 07:23 | -- | -- | -- | 0 | 0 | 0 | 0.24306 | N/A | N/A | N/A | NR/10/2148 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 432KV
[7 empty] | 2017-10-31 21:08 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.11944 | N/A | N/A | N/A | NR/10/2212 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[12 empty] | 0 | 0.018056 | 0 | 1899-12-31 05:26 | [7 empty] | 100
1 | 90 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 |  | 2017-10-23 22:50 | 2017-10-25 09:25 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:35 | N/A | N/A | N/A | NR/10/1524 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=430KV.
[7 empty] | 2017-10-26 22:17 | 2017-10-27 09:59 | -- | -- | -- | 0 | 0 | 0 | 0.4875 | N/A | N/A | N/A | NR/10/1814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA = 429KV
[7 empty] | 2017-10-27 21:53 | 2017-10-28 07:27 | -- | -- | -- | 0 | 0 | 0 | 0.39861 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA = 431KV
[7 empty] | 2017-10-28 22:18 | 2017-10-29 07:50 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/10/1977 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-01 17:23 | [7 empty] | 100
1 | 91 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 |  | 2017-10-01 09:18 | 2017-10-01 18:08 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/10/09 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-02 08:56 | 2017-10-02 18:44 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/10/45 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-08 08:49 | 2017-10-08 19:52 | -- | -- | -- | 0 | 0 | 0 | 0.46042 | N/A | N/A | N/A | NR/10/45 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-09 10:42 | 2017-10-09 19:50 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/10/457 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-17 03:14 | 2017-10-18 10:16 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:02 | N/A | N/A | N/A | NR/10/1128 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=434KV.
[7 empty] | 2017-10-20 10:26 | 2017-10-20 19:45 | -- | -- | -- | 0 | 0 | 0 | 0.38819 | N/A | N/A | N/A | NR/10/1310 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-21 09:12 | 2017-10-21 19:14 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/10/1356 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-22 03:11 | 2017-10-22 04:08 | -- | -- | -- | 0 | 0.039583 | 0 | 0 | N/A | N/A | N/A | NR/10/1390 | OMSU | LINE TRIPPED ON R-N FAULT DUE TO PILOT WIRE HANGING WHILE LAYING OPGW UNDER ULDC SCHEME. RELAY AT KURUKSHATRA :FL=1.438kM .
[7 empty] | 2017-10-22 04:31 | 2017-10-22 10:42 | -- | -- | -- | 0 | 0.25764 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | LINE TRIPPED ON R-N FAULT DUE TO PILOT WIRE HANGING WHILE LAYING OPGW UNDER ULDC SCHEME. FLR KURUKSHATRA :1.6kM.
[7 empty] | 2017-10-22 10:42 | 2017-10-22 18:14 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/10/1408 | LCSD | SD TAKEN FOR RECTIFICATION OF PILOT WIRE FOR OPGW WOREKAT LOC NO. 3,4,5,6 (MULTI CKT. TOWER).
[7 empty] | 2017-10-23 00:39 | 2017-10-23 09:56 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/10/1440 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=431KV.
[7 empty] | 2017-10-23 21:12 | 2017-10-24 09:50 | -- | -- | -- | 0 | 0 | 0 | 0.52639 | N/A | N/A | N/A | NR/10/1517 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=431KV.
[7 empty] | 2017-10-24 22:03 | 2017-10-25 09:20 | -- | -- | -- | 0 | 0 | 0 | 0.47014 | N/A | N/A | N/A | NR/10/1625 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA = 429KV
[7 empty] | 2017-10-26 00:27 | 2017-10-27 10:10 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:43 | N/A | N/A | N/A | NR/10/1721 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-28 02:44 | 2017-10-28 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.19514 | N/A | N/A | N/A | NR/10/1909 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 431KV
[7 empty] | 2017-10-28 13:40 | 2017-10-29 11:22 | -- | -- | -- | 0 | 0 | 0 | 0.90417 | N/A | N/A | N/A | NR/10/1945 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 439KV
[7 empty] | 2017-10-29 21:38 | 2017-10-30 09:24 | -- | -- | -- | 0 | 0 | 0 | 0.49028 | N/A | N/A | N/A | NR/10/2053 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-30 15:31 | 2017-10-31 08:09 | -- | -- | -- | 0 | 0 | 0 | 0.69306 | N/A | N/A | N/A | NR/10/2110 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[7 empty] | 2017-10-31 21:10 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.11806 | N/A | N/A | N/A | NR/10/2212 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[12 empty] | 0 | 0.29722 | 0 | 1900-01-08 05:16 | [7 empty] | 100
1 | 92 | NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 93 | NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 |  | 2017-10-04 08:54 | 2017-10-04 18:55 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/10/124 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-05 08:54 | 2017-10-05 18:21 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/10/187 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-10 08:49 | 2017-10-10 19:03 | -- | -- | -- | 0 | 0 | 0 | 0.42639 | N/A | N/A | N/A | NR/10/538 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-11 08:25 | 2017-10-11 19:03 | -- | -- | -- | 0 | 0 | 0 | 0.44306 | N/A | N/A | N/A | NR/10/622 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-18 00:46 | 2017-10-20 10:33 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:47 | N/A | N/A | N/A | NR/10/1195 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA=428KV.
[7 empty] | 2017-10-20 10:33 | 2017-10-20 19:36 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/10/1310 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-20 21:37 | 2017-10-22 09:00 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:23 | N/A | N/A | N/A | NR/10/1332 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=427KV.
[7 empty] | 2017-10-22 21:58 | 2017-10-23 10:37 | -- | -- | -- | 0 | 0 | 0 | 0.52708 | N/A | N/A | N/A | NR/10/1434 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=430KV.
[7 empty] | 2017-10-23 11:01 | 2017-10-23 18:16 | -- | -- | -- | 0 | 0 | 0 | 0.30208 | N/A | N/A | N/A | NR/10/1477 | LCSD | SD TAKEN FOR CONDUCTOR STRINGING ON MULTICIRCUIT TOWERS FOR 400KV D/C KURUKSHETRA - JIND LINE UNDER CONSTRUCTION.
[7 empty] | 2017-10-23 22:45 | 2017-10-25 09:10 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:25 | N/A | N/A | N/A | NR/10/1524 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA V=430KV.
[7 empty] | 2017-10-26 00:23 | 2017-10-26 09:28 | -- | -- | -- | 0 | 0 | 0 | 0.37847 | N/A | N/A | N/A | NR/10/1721 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA = 429KV
[7 empty] | 2017-10-26 22:55 | 2017-10-29 09:33 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 10:38 | N/A | N/A | N/A | NR/10/1818 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA = 429KV
[7 empty] | 2017-10-29 20:32 | 2017-10-30 08:07 | -- | -- | -- | 0 | 0 | 0 | 0.48264 | N/A | N/A | N/A | NR/10/2042 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[7 empty] | 2017-10-30 21:36 | 2017-10-31 08:14 | -- | -- | -- | 0 | 0 | 0 | 0.44306 | N/A | N/A | N/A | NR/10/2142 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 431KV
[7 empty] | 2017-10-31 21:46 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.093056 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 431KV
[12 empty] | 0 | 0 | 0 | 1900-01-11 01:02 | [7 empty] | 100
1 | 94 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 |  | 2017-10-24 22:01 | 2017-10-25 09:05 | -- | -- | -- | 0 | 0 | 0 | 0.46111 | N/A | N/A | N/A | NR/10/1625 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. KAITHAL = 426KV
[12 empty] | 0 | 0 | 0 | 0.46111 | [7 empty] | 100
1 | 95 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 |  | 2017-10-24 02:08 | 2017-10-24 02:08 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R ON Y-N FAULT.FLR KAITHAL : 118.78 KM
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 96 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 97 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 98 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 99 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 100 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 |  | 2017-10-23 00:39 | 2017-10-23 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.22569 | N/A | N/A | N/A | NR/10/1440 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL V=421KV.
[12 empty] | 0 | 0 | 0 | 0.22569 | [7 empty] | 100
1 | 101 | NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 102 | NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 103 | NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 104 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 |  | 2017-10-25 01:00 | 2017-10-25 07:00 | -- | -- | -- | 0 | 0 | 0 | 0.25 | N/A | N/A | N/A | NR/10/1627 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 428KV
[7 empty] | 2017-10-26 00:29 | 2017-10-26 00:30 | -- | -- | -- | 0 | 0 | 0 | 0.00069444 | N/A | N/A | N/A | NR/10/1721 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-26 21:50 | 2017-10-27 14:25 | -- | -- | -- | 0 | 0 | 0 | 0.69097 | N/A | N/A | N/A | NR/10/1814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-27 21:56 | 2017-10-28 09:43 | -- | -- | -- | 0 | 0 | 0 | 0.49097 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 10:23 | [7 empty] | 100
1 | 105 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 |  | 2017-10-20 02:22 | 2017-10-20 12:07 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/10/1300 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=432KV.
[7 empty] | 2017-10-20 23:21 | 2017-10-21 07:55 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/10/1334 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=427KV.
[7 empty] | 2017-10-22 02:25 | 2017-10-22 08:14 | -- | -- | -- | 0 | 0 | 0 | 0.24236 | N/A | N/A | N/A | NR/10/1387 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR V=429KV.
[7 empty] | 2017-10-25 01:01 | 2017-10-25 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.24583 | N/A | N/A | N/A | NR/10/1627 | LVRD | LINE HANDTRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 428KV
[7 empty] | 2017-10-25 22:07 | 2017-10-26 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | N/A | N/A | N/A | NR/10/1719 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-26 21:48 | 2017-10-27 08:54 | -- | -- | -- | 0 | 0 | 0 | 0.4625 | N/A | N/A | N/A | NR/10/1814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-27 21:56 | 2017-10-28 09:45 | -- | -- | -- | 0 | 0 | 0 | 0.49236 | N/A | N/A | N/A | NR/10/1906 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-28 21:50 | 2017-10-29 07:50 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/10/1975 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-29 21:46 | 2017-10-30 09:18 | -- | -- | -- | 0 | 0 | 0 | 0.48056 | N/A | N/A | N/A | NR/10/2054 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-30 21:41 | 2017-10-31 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/10/2142 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 430KV
[7 empty] | 2017-10-31 21:50 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.090278 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[12 empty] | 0 | 0 | 0 | 1900-01-02 21:32 | [7 empty] | 100
1 | 106 | NR240116 | 400KV Dadri-Kaithal | 213 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 107 | NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 108 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 |  | 2017-10-11 09:57 | 2017-10-14 15:38 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 05:41 | N/A | N/A | N/A | NR/10/631 | LCSD | SD TAKEN FOR 400 KV BB EXTENSION FOR CONSTRUCTION OF NEW BAYS FOR ICT-1 & 2 AT BANALA.
[12 empty] | 0 | 0 | 0 | 1900-01-02 05:41 | [7 empty] | 100
1 | 109 | NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 |  | 2017-10-31 01:44 | 2017-10-31 03:05 | -- | -- | -- | 0 | 0 | 0.05625 | 0 | N/A | N/A | N/A | NR/10/2152 | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE.
[12 empty] | 0 | 0 | 0.05625 | 0 | [7 empty] | 100
1 | 110 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 111 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 |  | 2017-10-05 16:11 | 2017-10-05 17:19 | -- | -- | -- | 0 | 0.047222 | 0 | 0 | N/A | N/A | N/A | NR/10/221 | OMSU | LINE TRIPPED ON B-N FAULT DUE TO PILOT WIRE HANGING WHILE LAYING OPGW UNDER ULDC SCHEME. FLR KISHENPUR : 92KM & NEW WANPOH : 25KM.
[12 empty] | 0 | 0.047222 | 0 | 0 | [7 empty] | 100
1 | 112 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 |  | 2017-10-16 05:22 | 2017-10-16 09:51 | -- | -- | -- | 0 | 0 | 0 | 0.18681 | N/A | N/A | N/A | NR/10/1052 | LVRD | LINE HAND TRIPPED ON VOLTAGE REGULATION. VOLTAGE AT MOGA =797KV.
[7 empty] | 2017-10-17 03:17 | 2017-10-17 10:04 | -- | -- | -- | 0 | 0 | 0 | 0.28264 | N/A | N/A | N/A | NR/10/1129, NL/10/569 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=801KV.
[7 empty] | 2017-10-18 00:54 | 2017-10-18 09:28 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/10/1194, NL/10/617 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=793KV.
[7 empty] | 2017-10-19 01:18 | 2017-10-19 10:32 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | NR/10/1155, NL/10/643 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=795KV.
[7 empty] | 2017-10-19 14:38 | 2017-10-21 12:38 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 22:00 | N/A | N/A | N/A | NR/10/1279, NL/10/651 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=798KV.
[7 empty] | 2017-10-21 20:55 | 2017-10-22 09:24 | -- | -- | -- | 0 | 0 | 0 | 0.52014 | N/A | N/A | N/A | NR/10/1380, NL/10/706 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=795KV.
[7 empty] | 2017-10-22 21:03 | 2017-10-23 08:15 | -- | -- | -- | 0 | 0 | 0 | 0.46667 | N/A | N/A | N/A | NR/10/1431 NL/10/731 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=796KV.
[7 empty] | 2017-10-23 21:23 | 2017-10-24 07:55 | -- | -- | -- | 0 | 0 | 0 | 0.43889 | N/A | N/A | N/A | NR/10/1516 NL/10/771 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=801KV.
[7 empty] | 2017-10-24 21:38 | 2017-10-25 09:31 | -- | -- | -- | 0 | 0 | 0 | 0.49514 | N/A | N/A | N/A | NR/10/1622 NL/10/813 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA V=801KV.
[7 empty] | 2017-10-25 21:32 | 2017-10-26 09:09 | -- | -- | -- | 0 | 0 | 0 | 0.48403 | N/A | N/A | N/A | NR/10/1716 NL/10/856 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 802KV.
[7 empty] | 2017-10-26 20:51 | 2017-10-27 09:43 | -- | -- | -- | 0 | 0 | 0 | 0.53611 | N/A | N/A | N/A | NR/10/1813 NL/10/896 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 803KV.
[7 empty] | 2017-10-28 21:00 | 2017-10-29 11:45 | -- | -- | -- | 0 | 0 | 0 | 0.61458 | N/A | N/A | N/A | NR/10/1970 NL/10/981 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 802KV.
[7 empty] | 2017-10-29 20:00 | 2017-10-30 07:50 | -- | -- | -- | 0 | 0 | 0 | 0.49306 | N/A | N/A | N/A | NR/10/2036 NL/10/1015 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 803KV.
[7 empty] | 2017-10-30 20:28 | 2017-10-31 08:16 | -- | -- | -- | 0 | 0 | 0 | 0.49167 | N/A | N/A | N/A | NR/10/2136 NLDC-1056 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 803KV.
[7 empty] | 2017-10-31 20:27 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.14792 | N/A | N/A | N/A | NR/10/2206 NLDC-1084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 802KV.
[12 empty] | 0 | 0 | 0 | 1900-01-06 19:35 | [7 empty] | 100
1 | 113 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 114 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 115 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 |  | 2017-10-06 10:08 | 2017-10-07 02:42 | -- | -- | -- | 0 | 0 | 0 | 0.69028 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. KISHENPUR = 395 KV.
[12 empty] | 0 | 0 | 0 | 0.69028 | [7 empty] | 100
1 | 116 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 117 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 118 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 119 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 |  | 2017-10-01 | 2017-10-16 02:38 | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 02:38 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 395KV.
[7 empty] | 2017-10-16 06:08 | 2017-10-21 10:46 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 04:38 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 395KV.
[7 empty] | 2017-10-21 14:14 | 2017-10-28 13:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 22:46 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 390KV.
[7 empty] | 2017-10-28 16:14 | 2017-10-31 01:35 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:21 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 395KV.
[7 empty] | 2017-10-31 05:28 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.77222 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 394KV.
[12 empty] | 0 | 0 | 0 | 1900-01-29 09:55 | [7 empty] | 100
1 | 120 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 121 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 122 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 123 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 124 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 125 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 126 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 127 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 128 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 129 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 130 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 131 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 132 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 133 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 |  | 2017-10-06 10:08 | 2017-10-07 02:42 | -- | -- | -- | 0 | 0 | 0 | 0.69028 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. KISHENPUR =395 KV.
[12 empty] | 0 | 0 | 0 | 0.69028 | [7 empty] | 100
1 | 134 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 |  | 2017-10-14 16:26 | 2017-10-14 17:16 | -- | -- | -- | 0.034722 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/973 NL/476 | SEMT | B/R TRIPPED BY INADVERTANT TRIPPING EXTENDED DURING REPLACMENT OF FAULTY CORE OF CABLE.
[12 empty] | 0.034722 | 0 | 0 | 0 | [7 empty] | 99.89
1 | 135 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 136 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 137 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 138 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 139 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 140 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 141 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 142 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 143 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 |  | 2017-10-01 | 2017-10-16 02:54 | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 02:54 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH=386KV.
[7 empty] | 2017-10-16 08:51 | 2017-10-21 10:59 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 02:08 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH = 394KV.
[7 empty] | 2017-10-21 14:16 | 2017-10-28 13:09 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 22:53 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH = 394KV.
[7 empty] | 2017-10-28 17:30 | 2017-10-31 04:09 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 10:39 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH = 394KV.
[7 empty] | 2017-10-31 06:09 | 2017-11-01 | -- | -- | -- | 0 | 0 | 0 | 0.74375 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WANPOH = 395KV.
[12 empty] | 0 | 0 | 0 | 1900-01-29 08:25 | [7 empty] | 100
1 | 144 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 145 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 146 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 147 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 148 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 |  | 2017-10-11 10:53 | 2017-10-11 19:50 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/10/641 | SCSD | SD TAKEN FOR COMMSSIONING ACTIVITIES OF 63 MVAR BUS REACTOR-II AT BBMB, DEHAR AS BOTH ARE ON SAME BAY.
[7 empty] | 2017-10-16 17:13 | 2017-10-16 17:16 | -- | -- | -- | 0.0020833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1099 | OSPT | SD TAKEN FOR TRIGGERING OF CB CLOSING CHANNEL.
[7 empty] | 2017-10-17 16:45 | 2017-10-17 17:16 | -- | -- | -- | 0.021528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1174 | OSPT | SD TAKEN FOR TRIGGERING OF CB CLOSING CHANNEL..
[12 empty] | 0.023611 | 0 | 0 | 0.37292 | [7 empty] | 99.92
1 | 149 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 |  | 2017-10-16 17:13 | 2017-10-16 17:16 | -- | -- | -- | 0.0020833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1099 | OSPT | SD TAKEN FOR TRIGGERING OF CB CLOSING CHANNEL.
[7 empty] | 2017-10-17 16:45 | 2017-10-17 17:16 | -- | -- | -- | 0.021528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1174 | OSPT | SD TAKEN FOR TRIGGERING OF CB CLOSING CHANNEL.
[12 empty] | 0.023611 | 0 | 0 | 0 | [7 empty] | 99.92
1 | 150 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 |  | 2017-10-13 09:05 | 2017-10-13 18:36 | -- | -- | -- | 0.39653 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/830 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.39653 | 0 | 0 | 0 | [7 empty] | 98.72
1 | 151 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 152 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 153 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 154 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 155 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 |  | 2017-10-13 09:48 | 2017-10-13 18:22 | -- | -- | -- | 0.35694 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/834 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.35694 | 0 | 0 | 0 | [7 empty] | 98.85
1 | 156 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 157 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 158 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 159 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 160 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 161 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 162 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 163 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 164 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 165 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 166 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 167 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 168 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 169 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 170 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 171 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 172 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 173 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 174 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 175 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 |  | 2017-10-03 12:28 | 2017-10-03 12:49 | -- | -- | -- | 0.014583 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/94 | OSPT | SD TAKEN FOR SWITCHING IN SPARE UNIT WITH R-PH UNIT FOR OVERHAULING OF R-PH UNIT.
[12 empty] | 0.014583 | 0 | 0 | 0 | [7 empty] | 99.95
1 | 176 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 177 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 178 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 179 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 180 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 181 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 182 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 183 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 |  | 2017-10-26 09:53 | 2017-10-26 17:50 | -- | -- | -- | 0.33125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1761 | OSPT | SD TAKEN FOR AMP WORKS
[12 empty] | 0.33125 | 0 | 0 | 0 | [7 empty] | 98.53
1 | 184 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 |  | 2017-10-27 10:13 | 2017-10-27 17:38 | -- | -- | -- | 0.30903 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1849 | OSPT | SD TAKEN FOR AMP WORKS
[12 empty] | 0.30903 | 0 | 0 | 0 | [7 empty] | 99
1 | 185 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 186 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 187 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 |  | 2017-10-18 03:22 | 2017-10-18 04:45 | -- | -- | -- | 0.057639 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1198 , NL/618 | SICT | ICT TRIPPED ON DIFERENTIAL PROTECTION DUE TO R-PH CURRENT MEASUREMENT CARD FAILURE.
[12 empty] | 0.057639 | 0 | 0 | 0 | [7 empty] | 99.81
1 | 188 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 189 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 190 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 191 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 192 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 193 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 |  | 2017-10-16 08:54 | 2017-10-16 17:50 | -- | -- | -- | 0.37222 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1061 | OSPT | SD TAKEN FOR AMP WORKS
[12 empty] | 0.37222 | 0 | 0 | 0 | [7 empty] | 98.8
1 | 194 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 195 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 196 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 197 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 198 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 199 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 200 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 201 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 202 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 |  | 2017-10-28 10:07 | 2017-10-28 18:01 | -- | -- | -- | 0.32917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1937 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.32917 | 0 | 0 | 0 | [7 empty] | 98.94
1 | 203 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 204 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 205 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 |  | 2017-10-04 15:59 | 2017-10-04 16:16 | -- | -- | -- | 0.011806 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/75 | OMST | POLE BLOCKED DUE TO EXTERNAL VESDA PROTECTION OPERATED.
[7 empty] | 2017-10-04 17:50 | 2017-10-04 18:29 | -- | -- | -- | 0.027083 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/82 | OMST | POLE BLOCKED DUE TO MAL OPERATION OF CONTROL SYSTEM AT KURUKSHETRA.
[7 empty] | 2017-10-15 18:14 | 2017-10-16 23:25 | -- | -- | -- | 1899-12-31 05:11 | 0 | 0 | 0 | N/A | N/A | N/A | --- | OMST | POLE-I BLOCKED DUE TO DC DIFFERENTIAL PROTECTION OPERATED AT KURUKSHETRA.
[7 empty] | 2017-10-16 23:25 | 2017-10-22 22:29 | -- | -- | -- | 1900-01-04 23:04 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/567 NR/10/1125 WR/10/1598 | OSPT | SD TAKEN FOR REPLACEMENT OF HVDC BUSHING OF CONVERTER TRANSFORMER AT KURUKSHETRA END.
[7 empty] | 2017-10-22 22:44 | 2017-10-22 23:46 | -- | -- | -- | 0.043056 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/734, NR/10/1437 WR/10/1954 | OSPT | SD TAKEN TO CHECK THE STUCKED TAP POSITION OF CONVERTER TRANSFORMER.
[7 empty] | 2017-10-23 21:21 | 2017-10-23 22:33 | -- | -- | -- | 0.05 | 0 | 0 | 0 | N/A | N/A | N/A | --- | OMST | POLE BLOCKED DUE TO EXTERNAL BLOCK PROTN OPTD IN VOLTAGE DIVIDER IN HV LINE (LOW SF-6 PRESSURE) AT KURUKSHETRA.
[12 empty] | 1900-01-06 07:25 | 0 | 0 | 0 | [7 empty] | 76.42
1 | 206 | NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 |  | 2017-10-04 15:31 | 2017-10-04 18:50 | -- | -- | -- | 0.13819 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/83 | OMST | POLE BLOCKED DUE TO EXTERNAL VESDA PROTECTION OPERATED.
[7 empty] | 2017-10-19 15:40 | 2017-10-19 16:13 | -- | -- | -- | 0.022917 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/653 | OMST | POLE BLOCKED DUE TO DMR CNAP PROTECTION OPERATED AT CHAMPA.
[7 empty] | 2017-10-21 14:45 | 2017-10-21 14:59 | -- | -- | -- | 0.0097222 | 0 | 0 | 0 | N/A | N/A | N/A | NR/10/1368, NL/700 | OMST | POLE BLOCKED DUE TO ABNORMAL FIRING ANGLE, DURING POWER RAMP DOWN AT KURUKSHETRA.
[7 empty] | 2017-10-21 21:34 | 2017-10-21 22:39 | -- | -- | -- | 0.045139 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/708 | OMST | POLE BLOCKED DUE TO CONTROL MAL-OPERATION IN VOLTAGE DIVIDER IN HV LINE (LOW SF-6 PRESSURE) AT KURUKSHETRA.
[7 empty] | 2017-10-22 00:25 | 2017-10-22 02:07 | -- | -- | -- | 0.070833 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/710 | OMST | POLE BLOCKED DUE TO CONTROL MAL-OPERATION AT KURUKSHETRA.
[7 empty] | 2017-10-22 02:23 | 2017-10-22 04:50 | -- | -- | -- | 0.10208 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/712 | OMST | POLE BLOCKED DUE TO MAL-OPERATION DURING POWER RAMP-UP FROM 150MW TO 600MW AT KURUKSHETRA.
[7 empty] | 2017-10-23 21:21 | 2017-10-23 22:54 | -- | -- | -- | 0.064583 | 0 | 0 | 0 | N/A | N/A | N/A | --- | OMST | POLE BLOCKED DUE TO COMMUTATION FAILURE AT KURUKSHETRA.
[7 empty] | 2017-10-25 16:26 | 2017-10-25 19:05 | -- | -- | -- | 0.11042 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/835 | OSPT | SD TAKEN TO CHECK SMOKE ALARM WHICH IS BEING OBSERVED AT KURUKSHETRA.
[7 empty] | 2017-10-25 19:11 | 2017-10-25 19:24 | -- | -- | -- | 0.0090278 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/852 | OMST | POLE BLOCKED DUE TO SETTING/ REBOOT PROBLEM AT CHAMPA.
[7 empty] | 2017-10-29 11:08 | 2017-10-29 11:56 | -- | -- | -- | 0.033333 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/1001 | OMST | POLE BLOCKED DUE TO LVDC FILTER OVER LOAD PROTECTION OPTD AT CHAMPA.
[7 empty] | 2017-10-29 12:02 | 2017-10-29 14:21 | -- | -- | -- | 0.096528 | 0 | 0 | 0 | N/A | N/A | N/A | NL/10/1005 | OMST | POLE BLOCKED DUE TO LVDC FILTER OVER LOAD PROTECTION OPTD AT CHAMPA.
[12 empty] | 0.70278 | 0 | 0 | 0 | [7 empty] | 97.73
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM([DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM([OTHERS, row above])
Hrs:Min = IF(RIGHT([Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM([Hrs:Min, row above])
Deemed Available = IF(RIGHT([Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM([Deemed Available, row above])

## NR2 Nov
Standard of Performance data for month of NOVEMBER-2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
Annexure-A
| S.No | ELEMENT CODE | ELEMENT NAME | DESCRIPTION (Length/Nos/MVA/MVAr/etc) | Region | Type of Failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration time more than Specified (Y/N) | Difference between Actual and specified | NRLDC Code | Category Code | REASON OF OUTAGE | Outage certifying Agency and reference documents (NRPC) | % Availability as certified by certifying agency
[7 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | POWERGRID | OTHERS | System constraints / Natural calamity/ Militancy | Deemed Available
[12 empty] | @ (T) | # (U) | & ( C ) | * (D)
[12 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
1 | 1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 |  | 2017-11-03 10:21 | 2017-11-03 10:30 | -- | -- | -- | 0 | 0 | 0 | 0.00625 | N/A | N/A | N/A | NR/11/192 | OSPD | LINE SD TAKEN BY NHPC, SEWA-II FOR BLACK START OPERATION.
[12 empty] | 0 | 0 | 0 | 0.00625 | [7 empty] | 100
1 | 3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 |  | 2017-11-15 01:00 | 2017-11-15 02:31 | -- | -- | -- | 0 | 0.063194 | 0 | 0 | N/A | N/A | N/A | NR/11/1546 | OMSU | LINE TRIPPED FROM BERASUIL ON OVER VOLATGE , VOLTAGE=243 KV AT BERASUIL.
[12 empty] | 0 | 0.063194 | 0 | 0 | [7 empty] | 100
1 | 8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 |  | 2017-11-17 12:17 | 2017-11-17 13:52 | -- | -- | -- | 0.065972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1864 | LPPT | LINE TRIPPED ON Y-B FAULT FROM SALAL ONLY. FLR SALAL - Iy=5.648kA, Ib=5.33kA & Jammu - IB=2.55 kA, FL=36.77KM.
[12 empty] | 0.065972 | 0 | 0 | 0 | [7 empty] | 99.79
1 | 17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 |  | 2017-11-23 01:53 | 2017-11-23 12:36 | -- | -- | -- | 0.44653 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2562 | LEFT | LINE TRIPPED ON R-N FAULT, FLR SARNA:12.83 KM, 8.4 KA.
[12 empty] | 0.44653 | 0 | 0 | 0 | [7 empty] | 98.56
1 | 23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 |  | 2017-11-24 10:42 | 2017-11-24 15:55 | -- | -- | -- | 0 | 0 | 0 | 0.21736 | N/A | N/A | N/A | NR/11/2668 | OSPD | SD TAKEN BY PSTCL, SARNA FOR ATTENDING HOT SPOT AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.21736 | [7 empty] | 100
1 | 24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 |  | 2017-11-01 15:34 | 2017-11-01 18:12 | -- | -- | -- | 0 | 0.10972 | 0 | 0 | N/A | N/A | N/A | NR/11/49 | OMSU | LINE TRIPPED DUE TO R-PH JUMPER OPEN IN JKPDD PAMPORE SWITCHYARD.
[12 empty] | 0 | 0.10972 | 0 | 0 | [7 empty] | 100
1 | 25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 |  | 2017-11-01 11:40 | 2017-11-01 19:30 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/11/33 | OSPD | SD TAKEN BY JKPDD, PAMPORE FOR RECTIFICATION OF CT CLAMP HOT SPOT AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.32639 | [7 empty] | 100
1 | 26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 28 | NR222028 | 220KV Jallandhar-Hamirpur(PG) -I | 128.3 | NR2 |  | 2017-11-09 01:20 | 2017-11-09 01:20 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | - | LART | LINE A/R ON Y-N FAULT. FLR JALANDHAR - 23.676KM, 6.9 KA.
[7 empty] | 2017-11-09 03:49 | 2017-11-09 03:49 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | - | LART | LINE A/R ON Y-N FAULT. FLR JALANDHAR - 23.205KM 6.8KA.
[7 empty] | 2017-11-11 11:00 | 2017-11-11 14:47 | -- | -- | -- | 0.15764 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1128 | OSPT | SD TAKEN FOR REPLACEMENT OF FLASHED OVER POLYMER INSULATOR AT LOC. NO. 61.
[12 empty] | 0.15764 | 0 | 0 | 0 | [7 empty] | 99.49
1 | 29 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 30 | NR222030 | 220KV Jallandhar-Hamirpur(PG) -II | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 31 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 32 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 33 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 34 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 |  | 2017-11-09 08:53 | 2017-11-09 18:33 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/11/844 | LCSD | SD TAKEN FOR REMOVAL OF AVIATION GLOBES FROM EARTHWIRE FOR LAYING OPGW UNDER ULDC SCHEME.
[7 empty] | 2017-11-10 08:34 | 2017-11-10 19:07 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/11/978 | LCSD | SD TAKEN FOR REMOVAL OF AVIATION GLOBES FROM EARTHWIRE FOR LAYING OPGW UNDER ULDC SCHEME.
[7 empty] | 2017-11-11 08:32 | 2017-11-11 19:11 | -- | -- | -- | 0 | 0 | 0 | 0.44375 | N/A | N/A | N/A | NR/11/1107 | LCSD | SD TAKEN FOR REMOVAL OF AVIATION GLOBES FROM EARTHWIRE FOR LAYING OPGW UNDER ULDC SCHEME.
[7 empty] | 2017-11-12 08:05 | 2017-11-12 18:00 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/11/1208 | LCSD | SD TAKEN FOR REMOVAL OF AVIATION GLOBES FROM EARTHWIRE FOR LAYING OPGW UNDER ULDC SCHEME.
[12 empty] | 0 | 0 | 0 | 1899-12-31 16:47 | [7 empty] | 100
1 | 35 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 36 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 37 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 38 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 |  | 2017-11-26 14:44 | 2017-11-28 06:02 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:18 | N/A | N/A | N/A | NR/11/2888 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 15:18 | [7 empty] | 100
1 | 39 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 |  | 2017-11-01 | 2017-11-01 06:49 | -- | -- | -- | 0 | 0 | 0 | 0.28403 | N/A | N/A | N/A | NR/10/2209 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 425KV
[7 empty] | 2017-11-01 13:38 | 2017-11-02 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.67917 | N/A | N/A | N/A | NR/11/40 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-11-02 22:05 | 2017-11-03 09:48 | -- | -- | -- | 0 | 0 | 0 | 0.48819 | N/A | N/A | N/A | NR/11/162 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-03 20:49 | 2017-11-04 09:20 | -- | -- | -- | 0 | 0 | 0 | 0.52153 | N/A | N/A | N/A | NR/11/236 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-04 20:17 | 2017-11-06 06:09 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:52 | N/A | N/A | N/A | NR/11/318 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-06 21:24 | 2017-11-07 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.375 | N/A | N/A | N/A | NR/11/487 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-07 21:06 | 2017-11-08 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.37361 | N/A | N/A | N/A | NR/11/600 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-08 20:27 | 2017-11-09 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.37083 | N/A | N/A | N/A | NR/11/811 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-09 21:34 | 2017-11-10 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.32986 | N/A | N/A | N/A | NR/11/942 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-10 13:19 | 2017-11-11 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.69444 | N/A | N/A | N/A | NR/11/1017 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-11 20:00 | 2017-11-12 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.43819 | N/A | N/A | N/A | NR/11/1180 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 427KV
[7 empty] | 2017-11-12 20:26 | 2017-11-13 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.41389 | N/A | N/A | N/A | NR/11/1261 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 427KV
[7 empty] | 2017-11-13 21:20 | 2017-11-14 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/11/1396 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-11-14 21:39 | 2017-11-15 08:31 | -- | -- | -- | 0 | 0 | 0 | 0.45278 | N/A | N/A | N/A | NR/11/1527 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 432KV
[7 empty] | 2017-11-15 21:04 | 2017-11-16 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/11/1660 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 425KV
[7 empty] | 2017-11-16 20:13 | 2017-11-17 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/11/1786 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 423KV
[7 empty] | 2017-11-17 21:59 | 2017-11-18 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/11/1914 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 424KV
[7 empty] | 2017-11-18 20:38 | 2017-11-19 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.39306 | N/A | N/A | N/A | NR/11/2032 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-19 13:16 | 2017-11-20 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.725 | N/A | N/A | N/A | NR/11/2086 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-20 13:10 | 2017-11-21 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.70069 | N/A | N/A | N/A | NR/11/2192 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 434KV
[7 empty] | 2017-11-21 22:38 | 2017-11-22 07:11 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/11/2366 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 429KV
[7 empty] | 2017-11-22 22:03 | 2017-11-23 06:49 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/11/2503 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-11-23 20:26 | 2017-11-24 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.4125 | N/A | N/A | N/A | NR/11/2614 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-11-24 20:36 | 2017-11-25 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.40069 | N/A | N/A | N/A | NR/11/2732 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-11-25 19:51 | 2017-11-26 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.44792 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-11-28 20:14 | 2017-11-29 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/11/3188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-11-29 20:26 | 2017-11-30 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.41389 | N/A | N/A | N/A | NR/11/3327 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[7 empty] | 2017-11-30 22:09 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.077083 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[12 empty] | 0 | 0 | 0 | 1900-01-11 22:58 | [7 empty] | 100
1 | 40 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 |  | 2017-11-18 19:40 | 2017-11-18 19:40 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | - | LART | LINE A/R ON R-N FAULT, FLR KISHENPUR - 52.96 KM, 5.68 KA.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 41 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 42 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 |  | 2017-11-09 00:22 | 2017-11-10 11:55 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:33 | N/A | N/A | N/A | NR/11/826 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 427KV
[7 empty] | 2017-11-20 00:34 | 2017-11-20 09:22 | -- | -- | -- | 0 | 0 | 0 | 0.36667 | N/A | N/A | N/A | NR/11/2129 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 20:21 | [7 empty] | 100
1 | 43 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 44 | NR240024 | 400KV Moga-Hissar | 209.39 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 45 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 46 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 |  | 2017-11-01 21:54 | 2017-11-02 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.32361 | N/A | N/A | N/A | NR/11/74 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-03 21:22 | 2017-11-04 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | N/A | N/A | N/A | NR/11/240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-05 02:08 | 2017-11-05 04:27 | -- | -- | -- | 0 | 0 | 0 | 0.096528 | N/A | N/A | N/A | NR/11/335 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-08 21:16 | 2017-11-09 07:54 | -- | -- | -- | 0 | 0 | 0 | 0.44306 | N/A | N/A | N/A | NR/11/817 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-09 21:40 | 2017-11-10 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.33611 | N/A | N/A | N/A | NR/11/942 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 428KV
[7 empty] | 2017-11-10 22:05 | 2017-11-11 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.31319 | N/A | N/A | N/A | NR/11/1078 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-11 21:05 | 2017-11-13 07:56 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:51 | N/A | N/A | N/A | NR/11/1185 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-13 21:32 | 2017-11-14 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/11/1397 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-15 21:05 | 2017-11-16 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/11/1660 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-11-16 21:10 | 2017-11-17 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.34167 | N/A | N/A | N/A | NR/11/1787 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[7 empty] | 2017-11-17 22:05 | 2017-11-18 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.30625 | N/A | N/A | N/A | NR/11/1914 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-19 14:15 | 2017-11-20 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.67222 | N/A | N/A | N/A | NR/11/2088 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 432KV
[7 empty] | 2017-11-20 21:40 | 2017-11-21 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/11/2240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-21 21:44 | 2017-11-22 07:08 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/11/2364 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-26 22:22 | 2017-11-27 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.31042 | N/A | N/A | N/A | NR/11/2925 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-27 20:16 | 2017-11-28 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/11/3056 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 422KV
[7 empty] | 2017-11-28 20:07 | 2017-11-29 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.40139 | N/A | N/A | N/A | NR/11/3188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 421KV
[12 empty] | 0 | 0 | 0 | 1900-01-06 06:14 | [7 empty] | 100
1 | 47 | NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 48 | NR240031 | 400KV URI-WAGOORA-II | 94.99 | NR2 |  | 2017-11-15 01:10 | 2017-11-15 02:07 | -- | -- | -- | 0 | 0.039583 | 0 | 0 | N/A | N/A | N/A | NR/11/1544 | OMSU | LINE TRIPPED FROM URI-1 END ONLY ON OVER VOLATGE , VOLTAGE=429 KV AT URI1 END.
[12 empty] | 0 | 0.039583 | 0 | 0 | [7 empty] | 100
1 | 49 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 |  | 2017-11-14 09:06 | 2017-11-14 20:01 | -- | -- | -- | 0 | 0 | 0 | 0.45486 | N/A | N/A | N/A | NR/11/1428 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-15 01:13 | 2017-11-15 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.20347 | N/A | N/A | N/A | NR/11/1541 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KISHENPUR= 433KV
[7 empty] | 2017-11-23 12:29 | 2017-11-23 16:09 | -- | -- | -- | 0 | 0 | 0 | 0.15278 | N/A | N/A | N/A | NR/11/2561 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[12 empty] | 0 | 0 | 0 | 0.81111 | [7 empty] | 100
1 | 50 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 |  | 2017-11-16 10:33 | 2017-11-16 19:34 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/11/1726 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[12 empty] | 0 | 0 | 0 | 0.37569 | [7 empty] | 100
1 | 51 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 52 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 53 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 |  | 2017-11-02 22:00 | 2017-11-03 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.30972 | N/A | N/A | N/A | NR/11/163 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-08 04:01 | 2017-11-08 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.11736 | N/A | N/A | N/A | NR/11/610 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 431KV
[7 empty] | 2017-11-14 21:21 | 2017-11-15 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/11/1522 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-18 20:36 | 2017-11-19 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/11/2032 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 424KV
[7 empty] | 2017-11-22 22:05 | 2017-11-23 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/11/2503 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 431KV
[7 empty] | 2017-11-23 20:20 | 2017-11-24 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.37847 | N/A | N/A | N/A | NR/11/2614 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-24 20:32 | 2017-11-25 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/11/2732 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-25 20:51 | 2017-11-26 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.36042 | N/A | N/A | N/A | NR/11/2832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-29 20:23 | 2017-11-30 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/11/3327 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[12 empty] | 0 | 0 | 0 | 1900-01-02 02:25 | [7 empty] | 100
1 | 54 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 55 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 56 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 57 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 58 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 |  | 2017-11-17 15:50 | 2017-11-18 14:08 | -- | -- | -- | 0 | 0 | 0 | 0.92917 | N/A | N/A | N/A | NR/11/1869 | OSPD | SD TAKEN BY NHPC URI-2 FOR INSPECTION & RECTIFICATION OF GIS COMPARTMENT AT THERE END
[12 empty] | 0 | 0 | 0 | 0.92917 | [7 empty] | 100
1 | 59 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 |  | 2017-11-01 | 2017-11-01 08:37 | -- | -- | -- | 0 | 0 | 0 | 0.35903 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-11-01 21:52 | 2017-11-02 07:00 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/11/74 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-02 22:02 | 2017-11-03 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.32986 | N/A | N/A | N/A | NR/11/163 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-03 20:35 | 2017-11-04 09:21 | -- | -- | -- | 0 | 0 | 0 | 0.53194 | N/A | N/A | N/A | NR/11/235 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-04 21:34 | 2017-11-05 10:53 | -- | -- | -- | 0 | 0 | 0 | 0.55486 | N/A | N/A | N/A | NR/11/325 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-05 21:34 | 2017-11-06 08:42 | -- | -- | -- | 0 | 0 | 0 | 0.46389 | N/A | N/A | N/A | NR/11/390 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-06 21:20 | 2017-11-07 08:39 | -- | -- | -- | 0 | 0 | 0 | 0.47153 | N/A | N/A | N/A | NR/11/487 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-11-07 21:08 | 2017-11-08 09:39 | -- | -- | -- | 0 | 0 | 0 | 0.52153 | N/A | N/A | N/A | NR/11/600 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 424KV
[7 empty] | 2017-11-08 21:16 | 2017-11-09 09:09 | -- | -- | -- | 0 | 0 | 0 | 0.49514 | N/A | N/A | N/A | NR/11/817 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-09 20:53 | 2017-11-10 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | NR/11/941 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-10 19:55 | 2017-11-11 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.44583 | N/A | N/A | N/A | NR/11/1069 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 424KV
[7 empty] | 2017-11-11 19:57 | 2017-11-14 07:34 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 11:37 | N/A | N/A | N/A | NR/11/1180 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[7 empty] | 2017-11-14 21:21 | 2017-11-15 08:39 | -- | -- | -- | 0 | 0 | 0 | 0.47083 | N/A | N/A | N/A | NR/11/1522 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-15 20:42 | 2017-11-16 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.4 | N/A | N/A | N/A | NR/11/1658 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 428KV
[7 empty] | 2017-11-16 20:15 | 2017-11-17 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.38125 | N/A | N/A | N/A | NR/11/1786 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[7 empty] | 2017-11-17 22:00 | 2017-11-18 17:50 | -- | -- | -- | 0 | 0 | 0 | 0.82639 | N/A | N/A | N/A | NR/11/1914 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-18 20:35 | 2017-11-19 06:54 | -- | -- | -- | 0 | 0 | 0 | 0.42986 | N/A | N/A | N/A | NR/11/2032 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 424KV
[7 empty] | 2017-11-19 14:15 | 2017-11-20 07:33 | -- | -- | -- | 0 | 0 | 0 | 0.72083 | N/A | N/A | N/A | NR/11/2088 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 432KV
[7 empty] | 2017-11-20 13:08 | 2017-11-21 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.77778 | N/A | N/A | N/A | NR/11/2192 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 433KV
[7 empty] | 2017-11-21 21:49 | 2017-11-22 06:57 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/11/2364 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-22 22:09 | 2017-11-23 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/11/2503 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 431KV
[7 empty] | 2017-11-23 20:19 | 2017-11-24 09:36 | -- | -- | -- | 0 | 0 | 0 | 0.55347 | N/A | N/A | N/A | NR/11/2614 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-24 20:31 | 2017-11-25 07:01 | -- | -- | -- | 0 | 0 | 0 | 0.4375 | N/A | N/A | N/A | NR/11/2732 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-25 19:50 | 2017-11-26 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.48264 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 424KV
[7 empty] | 2017-11-26 20:27 | 2017-11-27 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.38889 | N/A | N/A | N/A | NR/11/2918 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-11-27 13:07 | 2017-11-28 08:38 | -- | -- | -- | 0 | 0 | 0 | 0.81319 | N/A | N/A | N/A | NR/11/2996 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 431KV
[7 empty] | 2017-11-28 20:06 | 2017-11-29 06:57 | -- | -- | -- | 0 | 0 | 0 | 0.45208 | N/A | N/A | N/A | NR/11/3188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 421KV
[7 empty] | 2017-11-29 13:06 | 2017-11-29 18:14 | -- | -- | -- | 0 | 0 | 0 | 0.21389 | N/A | N/A | N/A | NR/11/3266 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-11-29 20:24 | 2017-11-30 07:42 | -- | -- | -- | 0 | 0 | 0 | 0.47083 | N/A | N/A | N/A | NR/11/3327 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-11-30 13:03 | 2017-11-30 14:59 | -- | -- | -- | 0 | 0 | 0 | 0.080556 | N/A | N/A | N/A | NR/11/3395 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-11-30 22:10 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.076389 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 431KV
[12 empty] | 0 | 0 | 0 | 1900-01-15 04:04 | [7 empty] | 100
1 | 60 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 61 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 |  | 2017-11-01 | 2017-11-01 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.26597 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 427KV
[7 empty] | 2017-11-04 21:13 | 2017-11-05 04:41 | -- | -- | -- | 0 | 0 | 0 | 0.31111 | N/A | N/A | N/A | NR/11/324 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-11-11 21:05 | 2017-11-13 08:06 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:01 | N/A | N/A | N/A | NR/11/1185 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-11-19 21:22 | 2017-11-20 08:05 | -- | -- | -- | 0 | 0 | 0 | 0.44653 | N/A | N/A | N/A | NR/11/2122 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 427KV
[7 empty] | 2017-11-26 20:30 | 2017-11-27 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.375 | N/A | N/A | N/A | NR/11/2918 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 428KV
[7 empty] | 2017-11-28 23:35 | 2017-11-29 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.27569 | N/A | N/A | N/A | NR/11/3195 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 428KV
[12 empty] | 0 | 0 | 0 | 1900-01-02 03:12 | [7 empty] | 100
1 | 62 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 |  | 2017-11-03 21:36 | 2017-11-04 07:29 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/11/242 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PABDULLAPUR= 426KV
[7 empty] | 2017-11-08 04:05 | 2017-11-08 11:03 | -- | -- | -- | 0 | 0 | 0 | 0.29028 | N/A | N/A | N/A | NR/11/610 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. A'PUR = 429KV
[7 empty] | 2017-11-08 20:38 | 2017-11-09 11:21 | -- | -- | -- | 0 | 0 | 0 | 0.61319 | N/A | N/A | N/A | NR/11/814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 429KV
[7 empty] | 2017-11-13 22:28 | 2017-11-14 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.34375 | N/A | N/A | N/A | NR/11/1399 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 427KV
[7 empty] | 2017-11-15 21:41 | 2017-11-17 06:16 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:35 | N/A | N/A | N/A | NR/11/1661 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 427KV
[7 empty] | 2017-11-20 21:37 | 2017-11-21 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/11/2240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 428KV
[7 empty] | 2017-11-21 22:39 | 2017-11-22 07:15 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/11/2366 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 426KV
[7 empty] | 2017-11-24 20:35 | 2017-11-25 08:37 | -- | -- | -- | 0 | 0 | 0 | 0.50139 | N/A | N/A | N/A | NR/11/2732 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 422KV
[7 empty] | 2017-11-30 23:57 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.0020833 | N/A | N/A | N/A | NR/11/3463 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 421KV
[12 empty] | 0 | 0 | 0 | 1900-01-03 06:01 | [7 empty] | 100
1 | 63 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 |  | 2017-11-01 | 2017-11-01 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.25972 | N/A | N/A | N/A | NR/10/2215 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 423KV
[7 empty] | 2017-11-01 07:51 | 2017-11-01 17:47 | -- | -- | -- | 0 | 0 | 0 | 0.41389 | N/A | N/A | N/A | NR/11/14 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-02 22:08 | 2017-11-03 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.30139 | N/A | N/A | N/A | NR/11/163 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-03 08:04 | 2017-11-03 18:24 | -- | -- | -- | 0 | 0 | 0 | 0.43056 | N/A | N/A | N/A | NR/11/175 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-04 21:14 | 2017-11-05 04:51 | -- | -- | -- | 0 | 0 | 0 | 0.31736 | N/A | N/A | N/A | NR/11/324 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-11-05 14:34 | 2017-11-05 17:15 | -- | -- | -- | 0 | 0 | 0 | 0.11181 | N/A | N/A | N/A | NR/11/363 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-11-05 21:40 | 2017-11-06 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/11/389 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-11-07 21:23 | 2017-11-08 04:59 | -- | -- | -- | 0 | 0 | 0 | 0.31667 | N/A | N/A | N/A | NR/11/601 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULAR=425KV.
[7 empty] | 2017-11-09 20:25 | 2017-11-10 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/11/934 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-11-12 20:31 | 2017-11-13 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/11/1261 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NATHPAJHAKRI= 422KV
[7 empty] | 2017-11-15 19:59 | 2017-11-16 05:05 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | N/A | N/A | N/A | NR/11/1653 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 424KV
[7 empty] | 2017-11-16 20:18 | 2017-11-17 05:03 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/11/1786 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 424KV
[7 empty] | 2017-11-18 19:18 | 2017-11-19 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/11/2028 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-11-21 20:18 | 2017-11-22 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/11/2358 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 423KV
[7 empty] | 2017-11-25 20:12 | 2017-11-26 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 426KV
[7 empty] | 2017-11-26 14:50 | 2017-11-26 17:25 | -- | -- | -- | 0 | 0 | 0 | 0.10764 | N/A | N/A | N/A | NR/11/2888 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-11-26 20:07 | 2017-11-27 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/11/2916 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 428KV
[7 empty] | 2017-11-28 20:16 | 2017-11-29 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/11/3188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-11-29 20:13 | 2017-11-30 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | N/A | N/A | N/A | NR/11/3322 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-11-30 20:09 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.16042 | N/A | N/A | N/A | NR/11/3441 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[12 empty] | 0 | 0 | 0 | 1900-01-05 16:31 | [7 empty] | 100
1 | 64 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 |  | 2017-11-01 21:02 | 2017-11-02 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/11/69 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-02 08:31 | 2017-11-02 18:29 | -- | -- | -- | 0 | 0 | 0 | 0.41528 | N/A | N/A | N/A | NR/11/89 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-03 21:43 | 2017-11-04 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.33125 | N/A | N/A | N/A | NR/11/242 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-11-04 07:58 | 2017-11-04 19:14 | -- | -- | -- | 0 | 0 | 0 | 0.46944 | N/A | N/A | N/A | NR/11/257 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-06 21:00 | 2017-11-07 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | NR/11/486 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-08 20:43 | 2017-11-09 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/11/814 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 424KV
[7 empty] | 2017-11-10 20:54 | 2017-11-11 05:09 | -- | -- | -- | 0 | 0 | 0 | 0.34375 | N/A | N/A | N/A | NR/11/1073 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 427KV
[7 empty] | 2017-11-11 20:30 | 2017-11-12 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.37778 | N/A | N/A | N/A | NR/11/1183 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-11-13 20:28 | 2017-11-14 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/11/1389 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NATHPAJHAKRI= 424KV
[7 empty] | 2017-11-14 20:30 | 2017-11-15 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/11/1520 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-16 01:19 | 2017-11-16 04:18 | -- | -- | -- | 0 | 0 | 0 | 0.12431 | N/A | N/A | N/A | NR/11/1671 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-17 00:49 | 2017-11-17 04:58 | -- | -- | -- | 0 | 0 | 0 | 0.17292 | N/A | N/A | N/A | NR/11/1793 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-17 20:14 | 2017-11-18 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.375 | N/A | N/A | N/A | NR/11/1909 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-11-19 20:11 | 2017-11-20 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/11/2112 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-11-20 20:24 | 2017-11-21 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/11/2235 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 423KV
[7 empty] | 2017-11-22 20:05 | 2017-11-23 04:52 | -- | -- | -- | 0 | 0 | 0 | 0.36597 | N/A | N/A | N/A | NR/11/2493 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 424KV
[7 empty] | 2017-11-23 20:06 | 2017-11-24 05:07 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/11/2612 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 422KV
[7 empty] | 2017-11-24 20:06 | 2017-11-25 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/11/2727 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 423KV
[7 empty] | 2017-11-27 20:05 | 2017-11-28 05:16 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/11/3050 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 422KV.
[7 empty] | 2017-11-30 13:00 | 2017-11-30 16:32 | -- | -- | -- | 0 | 0 | 0 | 0.14722 | N/A | N/A | N/A | NR/11/3393 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 423KV.
[12 empty] | 0 | 0 | 0 | 1900-01-05 20:33 | [7 empty] | 100
1 | 65 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 66 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 67 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 |  | 2017-11-01 | 2017-11-01 06:41 | -- | -- | -- | 0 | 0 | 0 | 0.27847 | N/A | N/A | N/A | NR/10/2209 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 425KV
[7 empty] | 2017-11-02 01:31 | 2017-11-02 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.18333 | N/A | N/A | N/A | NR/11/76 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-03 03:02 | 2017-11-03 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.11875 | N/A | N/A | N/A | NR/11/166 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-03 20:50 | 2017-11-04 09:02 | -- | -- | -- | 0 | 0 | 0 | 0.50833 | N/A | N/A | N/A | NR/11/236 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-04 20:06 | 2017-11-06 05:57 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:51 | N/A | N/A | N/A | NR/11/317 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-06 22:52 | 2017-11-07 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.31111 | N/A | N/A | N/A | NR/11/491 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 427KV
[7 empty] | 2017-11-07 21:07 | 2017-11-08 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/11/600 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-08 20:26 | 2017-11-09 07:39 | -- | -- | -- | 0 | 0 | 0 | 0.46736 | N/A | N/A | N/A | NR/11/811 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-11 19:58 | 2017-11-13 06:26 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:28 | N/A | N/A | N/A | NR/11/1180 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 427KV
[7 empty] | 2017-11-14 02:48 | 2017-11-14 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.12986 | N/A | N/A | N/A | NR/11/1403 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 431KV
[7 empty] | 2017-11-15 00:10 | 2017-11-15 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.25347 | N/A | N/A | N/A | NR/11/1539 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 432KV
[7 empty] | 2017-11-15 21:02 | 2017-11-16 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/11/1660 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 425KV
[7 empty] | 2017-11-16 20:14 | 2017-11-17 07:41 | -- | -- | -- | 0 | 0 | 0 | 0.47708 | N/A | N/A | N/A | NR/11/1786 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 423KV
[7 empty] | 2017-11-18 20:39 | 2017-11-19 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.38403 | N/A | N/A | N/A | NR/11/2032 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-19 13:09 | 2017-11-20 09:24 | -- | -- | -- | 0 | 0 | 0 | 0.84375 | N/A | N/A | N/A | NR/11/2083 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-20 13:01 | 2017-11-20 13:05 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-11-20 13:05 | 2017-11-21 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.71736 | N/A | N/A | N/A | NR/11/2194 | LVRD | LINE KEPT OPEN FOR VOLTAGE REGULATIPON.
[7 empty] | 2017-11-21 22:34 | 2017-11-22 06:53 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/11/2366 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 429KV
[7 empty] | 2017-11-23 00:01 | 2017-11-23 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.27917 | N/A | N/A | N/A | NR/11/2508 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-11-23 21:17 | 2017-11-25 06:27 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:10 | N/A | N/A | N/A | NR/11/2620 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-11-25 08:48 | 2017-11-25 18:57 | -- | -- | -- | 0 | 0 | 0 | 0.42292 | N/A | N/A | N/A | NR/11/2769 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-26 20:30 | 2017-11-27 09:39 | -- | -- | -- | 0 | 0 | 0 | 0.54792 | N/A | N/A | N/A | NR/11/2918 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-11-27 09:39 | 2017-11-27 19:41 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/11/2958 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-28 00:56 | 2017-11-28 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.21528 | N/A | N/A | N/A | NR/11/3066 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-11-28 20:08 | 2017-11-29 09:15 | -- | -- | -- | 0 | 0 | 0 | 0.54653 | N/A | N/A | N/A | NR/11/3188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-11-29 09:15 | 2017-11-29 19:32 | -- | -- | -- | 0 | 0 | 0 | 0.42847 | N/A | N/A | N/A | NR/11/3237 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-29 20:24 | 2017-11-30 07:54 | -- | -- | -- | 0 | 0 | 0 | 0.47917 | N/A | N/A | N/A | NR/11/3327 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[7 empty] | 2017-11-30 21:59 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.084028 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[12 empty] | 0 | 0 | 0.0027778 | 1900-01-12 09:26 | [7 empty] | 100
1 | 68 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 |  | 2017-11-01 | 2017-11-01 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.25972 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[7 empty] | 2017-11-01 12:59 | 2017-11-01 13:03 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM OVER VOLTAGE. JALANDHAR = 438KV
[7 empty] | 2017-11-01 13:03 | 2017-11-03 09:50 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 20:47 | N/A | N/A | N/A | NR/11/38 | LVRD | LINE KEPT OPEN FOR VOLTAGE REGULATIPON.
[7 empty] | 2017-11-03 21:24 | 2017-11-04 09:20 | -- | -- | -- | 0 | 0 | 0 | 0.49722 | N/A | N/A | N/A | NR/11/240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-05 01:57 | 2017-11-05 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.14444 | N/A | N/A | N/A | NR/11/333 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-05 21:33 | 2017-11-08 09:54 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 12:21 | N/A | N/A | N/A | NR/11/390 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-08 21:18 | 2017-11-10 06:33 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:15 | N/A | N/A | N/A | NR/11/817 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 426KV
[7 empty] | 2017-11-10 13:22 | 2017-11-11 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.73125 | N/A | N/A | N/A | NR/11/1017 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-13 00:20 | 2017-11-16 06:40 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 06:20 | N/A | N/A | N/A | NR/11/1278 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 432KV
[7 empty] | 2017-11-16 21:14 | 2017-11-18 06:51 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:37 | N/A | N/A | N/A | NR/11/1787 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 424KV
[7 empty] | 2017-11-19 14:13 | 2017-11-24 05:54 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 15:41 | N/A | N/A | N/A | NR/11/2088 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-24 21:20 | 2017-11-25 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.37431 | N/A | N/A | N/A | NR/11/2735 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-11-25 19:48 | 2017-11-26 09:20 | -- | -- | -- | 0 | 0 | 0 | 0.56389 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-11-26 09:20 | 2017-11-26 18:55 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/11/2870 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-27 20:15 | 2017-11-28 09:00 | -- | -- | -- | 0 | 0 | 0 | 0.53125 | N/A | N/A | N/A | NR/11/3056 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-11-28 09:00 | 2017-11-28 18:30 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NR/11/3095 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-29 00:30 | 2017-11-29 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.23056 | N/A | N/A | N/A | NR/11/3201 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-11-30 00:08 | 2017-11-30 09:10 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/11/3337 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 429KV
[7 empty] | 2017-11-30 09:10 | 2017-11-30 18:22 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | N/A | N/A | N/A | NR/11/3369 | LCSD | SD TAKEN FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSUALTORS.
[7 empty] | 2017-11-30 21:59 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.084028 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[12 empty] | 0 | 0 | 0.0027778 | 1900-01-19 01:20 | [7 empty] | 100
1 | 69 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 |  | 2017-11-11 12:06 | 2017-11-11 16:06 | -- | -- | -- | 0.16667 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1130 | OSPT | SD TAKEN FOR ATTENDING HOT SPOT AT LOC. NO. 72.
[7 empty] | 2017-11-15 01:02 | 2017-11-15 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.22361 | N/A | N/A | N/A | NR/11/1540 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KISHENPUR= 433KV
[12 empty] | 0.16667 | 0 | 0 | 0.22361 | [7 empty] | 99.46
1 | 70 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 71 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 |  | 2017-11-01 | 2017-11-01 08:35 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 427KV
[7 empty] | 2017-11-01 21:54 | 2017-11-02 10:12 | -- | -- | -- | 0 | 0 | 0 | 0.5125 | N/A | N/A | N/A | NR/11/73 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-11-02 22:03 | 2017-11-03 10:31 | -- | -- | -- | 0 | 0 | 0 | 0.51944 | N/A | N/A | N/A | NR/11/162 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-11-03 21:23 | 2017-11-04 09:19 | -- | -- | -- | 0 | 0 | 0 | 0.49722 | N/A | N/A | N/A | NR/11/240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-11-05 02:22 | 2017-11-05 08:44 | -- | -- | -- | 0 | 0 | 0 | 0.26528 | N/A | N/A | N/A | NR/11/335 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-11-06 21:22 | 2017-11-07 11:11 | -- | -- | -- | 0 | 0 | 0 | 0.57569 | N/A | N/A | N/A | NR/11/487 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-11-07 21:09 | 2017-11-08 09:38 | -- | -- | -- | 0 | 0 | 0 | 0.52014 | N/A | N/A | N/A | NR/11/600 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 425KV
[7 empty] | 2017-11-08 21:14 | 2017-11-09 09:38 | -- | -- | -- | 0 | 0 | 0 | 0.51667 | N/A | N/A | N/A | NR/11/817 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 423KV
[7 empty] | 2017-11-10 19:54 | 2017-11-14 07:33 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 11:39 | N/A | N/A | N/A | NR/11/1069 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 423KV
[7 empty] | 2017-11-14 07:47 | 2017-11-14 07:47 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | - | LART | LINE A/R ON RN FAULT. FLR AMRITSAR -155 KM, 3.08 KA.
[7 empty] | 2017-11-15 00:12 | 2017-11-15 08:38 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | N/A | N/A | N/A | NR/11/1539 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 429KV
[7 empty] | 2017-11-15 21:07 | 2017-11-16 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.38125 | N/A | N/A | N/A | NR/11/1660 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-11-16 20:15 | 2017-11-18 16:50 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 20:35 | N/A | N/A | N/A | NR/11/1786 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 418KV
[7 empty] | 2017-11-18 20:33 | 2017-11-20 07:32 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:59 | N/A | N/A | N/A | NR/11/2032 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 423KV
[7 empty] | 2017-11-20 13:10 | 2017-11-23 09:55 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 20:45 | N/A | N/A | N/A | NR/11/2192 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 432KV
[7 empty] | 2017-11-23 20:20 | 2017-11-24 09:35 | -- | -- | -- | 0 | 0 | 0 | 0.55208 | N/A | N/A | N/A | NR/11/2614 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 423KV
[7 empty] | 2017-11-24 20:33 | 2017-11-25 18:05 | -- | -- | -- | 0 | 0 | 0 | 0.89722 | N/A | N/A | N/A | NR/11/2732 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 422KV
[7 empty] | 2017-11-25 19:49 | 2017-11-26 07:57 | -- | -- | -- | 0 | 0 | 0 | 0.50556 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 422KV
[7 empty] | 2017-11-26 20:26 | 2017-11-27 07:21 | -- | -- | -- | 0 | 0 | 0 | 0.45486 | N/A | N/A | N/A | NR/11/2918 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 428KV
[7 empty] | 2017-11-27 13:08 | 2017-11-28 08:37 | -- | -- | -- | 0 | 0 | 0 | 0.81181 | N/A | N/A | N/A | NR/11/2996 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 428KV
[7 empty] | 2017-11-28 20:04 | 2017-11-29 09:57 | -- | -- | -- | 0 | 0 | 0 | 0.57847 | N/A | N/A | N/A | NR/11/3188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-11-29 13:07 | 2017-11-30 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.72361 | N/A | N/A | N/A | NR/11/3266 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-11-30 13:04 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.45556 | N/A | N/A | N/A | NR/11/3395 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 423KV
[12 empty] | 0 | 0 | 0 | 1900-01-18 03:24 | [7 empty] | 100
1 | 72 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 |  | 2017-11-29 10:45 | 2017-11-29 15:18 | -- | -- | -- | 0.18958 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/3251 | OSPT | SD TAKEN FOR CARRYING OUT RECTIFICATION WORK IN B PH CVT AT BANALA END.
[12 empty] | 0.18958 | 0 | 0 | 0 | [7 empty] | 99.39
1 | 73 | NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 74 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 |  | 2017-11-25 21:47 | 2017-11-25 22:11 | -- | -- | -- | 0.016667 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2841 | LEFT | LINE TRIPPED ON R-N FAULT. FLR WAGOORA: 53.91 KM, 4.35 KA & WANPOH: 5.7 KMS, 7.1 KA.
[12 empty] | 0.016667 | 0 | 0 | 0 | [7 empty] | 99.95
1 | 75 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 |  | 2017-11-15 01:32 | 2017-11-15 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.18819 | N/A | N/A | N/A | NR/11/1542 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KISHENPUR= 433KV
[12 empty] | 0 | 0 | 0 | 0.18819 | [7 empty] | 100
1 | 76 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 77 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 78 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 |  | 2017-11-08 08:19 | 2017-11-08 17:17 | -- | -- | -- | 0 | 0 | 0 | 0.37361 | N/A | N/A | N/A | NR/11/628 | OSPD | SD TAKEN BY SJVNL FOR AMP OF GIS LINE BAY AT JAKHRI & REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTOR AT RAMPUR.
[7 empty] | 2017-11-10 08:19 | 2017-11-10 17:36 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/11/973 | OSPD | SD TAKEN BY SJVNL FOR AMP OF GIS LINE BAY AT JAKHRI & REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTOR AT RAMPUR.
[7 empty] | 2017-11-19 21:49 | 2017-11-20 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.35 | N/A | N/A | N/A | NR/11/2122 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NJPC = 425KV
[7 empty] | 2017-11-22 20:12 | 2017-11-23 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/11/2493 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. RAMPUR= 422KV
[7 empty] | 2017-11-24 21:31 | 2017-11-25 05:05 | -- | -- | -- | 0 | 0 | 0 | 0.31528 | N/A | N/A | N/A | NR/11/2735 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 422KV
[7 empty] | 2017-11-30 21:04 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.12222 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL FOR MAINTENANCE & TESTING OF BB2 AT RAMPUR HEP.
[12 empty] | 0 | 0 | 0 | 1899-12-31 22:16 | [7 empty] | 100
1 | 79 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 |  | 2017-11-01 | 2017-11-01 05:02 | -- | -- | -- | 0 | 0 | 0 | 0.20972 | N/A | N/A | N/A | NR/10/2216 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[7 empty] | 2017-11-01 22:41 | 2017-11-02 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.27639 | N/A | N/A | N/A | NR/11/75 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-04 02:36 | 2017-11-04 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.13056 | N/A | N/A | N/A | NR/11/246 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-05 23:13 | 2017-11-06 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.26597 | N/A | N/A | N/A | NR/11/394 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-06 22:46 | 2017-11-07 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.28056 | N/A | N/A | N/A | NR/11/491 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[7 empty] | 2017-11-08 00:17 | 2017-11-08 05:10 | -- | -- | -- | 0 | 0 | 0 | 0.20347 | N/A | N/A | N/A | NR/11/604 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-11-09 00:25 | 2017-11-09 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.20347 | N/A | N/A | N/A | NR/11/826 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-10 22:04 | 2017-11-11 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.30972 | N/A | N/A | N/A | NR/11/1078 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-12 22:22 | 2017-11-13 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/11/1274 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-14 21:23 | 2017-11-15 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/11/1522 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-15 09:12 | 2017-11-15 17:15 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/11/1577 | OSPD | SD TAKEN BY RAMPUR SJVNL FOR REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTORS ON BB2 SIDE.
[7 empty] | 2017-11-16 09:56 | 2017-11-16 17:17 | -- | -- | -- | 0 | 0 | 0 | 0.30625 | N/A | N/A | N/A | NR/11/1722 | OSPD | SD TAKEN BY RAMPUR SJVNL FOR REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTORS ON BB2 SIDE.
[7 empty] | 2017-11-16 21:17 | 2017-11-17 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/11/1787 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[7 empty] | 2017-11-17 22:07 | 2017-11-18 05:08 | -- | -- | -- | 0 | 0 | 0 | 0.29236 | N/A | N/A | N/A | NR/11/1914 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-18 20:41 | 2017-11-19 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.38889 | N/A | N/A | N/A | NR/11/2032 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 424KV
[7 empty] | 2017-11-19 21:26 | 2017-11-20 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.32986 | N/A | N/A | N/A | NR/11/2122 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 428KV
[7 empty] | 2017-11-21 21:43 | 2017-11-22 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.32708 | N/A | N/A | N/A | NR/11/2364 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-23 21:25 | 2017-11-24 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | N/A | N/A | N/A | NR/11/2620 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 429KV
[7 empty] | 2017-11-24 21:19 | 2017-11-25 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.34444 | N/A | N/A | N/A | NR/11/2735 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 421KV
[7 empty] | 2017-11-25 20:49 | 2017-11-26 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/11/2832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-28 22:52 | 2017-11-29 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.27639 | N/A | N/A | N/A | NR/11/3194 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-29 20:22 | 2017-11-30 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/11/3327 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-11-30 20:58 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.12639 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL FOR MAINTENANCE & TESTING OF BB2 AT RAMPUR HEP.
[12 empty] | 0 | 0 | 0 | 1900-01-05 18:05 | [7 empty] | 100
1 | 80 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 81 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 |  | 2017-11-13 08:11 | 2017-11-13 17:35 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/11/1308 | OSPD | SD TAKEN BY SJVNL FOR AMP OF GIS LINE BAY AT JAKHRI & REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTOR AT RAMPUR.
[7 empty] | 2017-11-14 08:37 | 2017-11-14 16:51 | -- | -- | -- | 0 | 0 | 0 | 0.34306 | N/A | N/A | N/A | NR/11/1424 | OSPD | SD TAKEN BY SJVNL FOR AMP OF GIS LINE BAY AT JAKHRI & REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTOR AT RAMPUR.
[7 empty] | 2017-11-20 20:24 | 2017-11-21 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.375 | N/A | N/A | N/A | NR/11/2235 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 423KV
[7 empty] | 2017-11-21 20:22 | 2017-11-22 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/11/2358 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 423KV
[7 empty] | 2017-11-23 20:11 | 2017-11-24 04:22 | -- | -- | -- | 0 | 0 | 0 | 0.34097 | N/A | N/A | N/A | NR/11/2612 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JHAKRI= 422KV
[7 empty] | 2017-11-30 21:04 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.12222 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL FOR MAINTENANCE & TESTING OF BB2 AT RAMPUR HEP.
[12 empty] | 0 | 0 | 0 | 1899-12-31 22:55 | [7 empty] | 100
1 | 82 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 |  | 2017-11-03 00:08 | 2017-11-03 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.21736 | N/A | N/A | N/A | NR/11/165 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-04 22:28 | 2017-11-05 04:30 | -- | -- | -- | 0 | 0 | 0 | 0.25139 | N/A | N/A | N/A | NR/11/327 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-11-09 21:37 | 2017-11-10 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.33264 | N/A | N/A | N/A | NR/11/942 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 428KV
[7 empty] | 2017-11-11 21:44 | 2017-11-12 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.325 | N/A | N/A | N/A | NR/11/1188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 423KV
[7 empty] | 2017-11-13 21:30 | 2017-11-14 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.33333 | N/A | N/A | N/A | NR/11/1397 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 425KV
[7 empty] | 2017-11-15 20:41 | 2017-11-16 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.35903 | N/A | N/A | N/A | NR/11/1658 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 428KV
[7 empty] | 2017-11-17 09:15 | 2017-11-17 17:20 | -- | -- | -- | 0 | 0 | 0 | 0.33681 | N/A | N/A | N/A | NR/11/1833 | OSPD | SD TAKEN BY RAMPUR SJVNL FOR REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTORS ON BB2 SIDE.
[7 empty] | 2017-11-18 09:23 | 2017-11-18 16:39 | -- | -- | -- | 0 | 0 | 0 | 0.30278 | N/A | N/A | N/A | NR/11/1951 | OSPD | SD TAKEN BY RAMPUR SJVNL FOR REPLACEMENT OF INSULATED DRIVING RODS IN GIS DIS-CONNECTORS ON BB2 SIDE.
[7 empty] | 2017-11-20 21:38 | 2017-11-21 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.32083 | N/A | N/A | N/A | NR/11/2240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-23 00:04 | 2017-11-23 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.28194 | N/A | N/A | N/A | NR/11/2508 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 431KV
[7 empty] | 2017-11-26 22:09 | 2017-11-27 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.31667 | N/A | N/A | N/A | NR/11/2925 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 426KV
[7 empty] | 2017-11-27 22:23 | 2017-11-28 05:17 | -- | -- | -- | 0 | 0 | 0 | 0.2875 | N/A | N/A | N/A | NR/11/3062 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH = 427KV
[7 empty] | 2017-11-30 20:59 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.12569 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL FOR MAINTENANCE & TESTING OF BB2 AT RAMPUR HEP.
[12 empty] | 0 | 0 | 0 | 1900-01-02 18:59 | [7 empty] | 100
1 | 83 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 |  | 2017-11-08 10:12 | 2017-11-08 19:44 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/11/721 | OSPD | SD TAKEN BY BBMB FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSULATORS.
[7 empty] | 2017-11-09 08:01 | 2017-11-09 19:50 | -- | -- | -- | 0 | 0 | 0 | 0.49236 | N/A | N/A | N/A | NR/11/842 | OSPD | SD TAKEN BY BBMB FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSULATORS.
[7 empty] | 2017-11-10 08:05 | 2017-11-10 19:45 | -- | -- | -- | 0 | 0 | 0 | 0.48611 | N/A | N/A | N/A | NR/11/968 | OSPD | SD TAKEN BY BBMB FOR REPLACEMENT OF PORCELAIN INSULATOR WITH POLYMER INSULATORS.
[12 empty] | 0 | 0 | 0 | 1899-12-31 09:01 | [7 empty] | 100
1 | 84 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 |  | 2017-11-16 00:56 | 2017-11-17 07:59 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:03 | N/A | N/A | N/A | NR/11/1670 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-22 01:22 | 2017-11-22 07:02 | -- | -- | -- | 0 | 0 | 0 | 0.23611 | N/A | N/A | N/A | NR/11/2371 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 428KV
[7 empty] | 2017-11-23 00:15 | 2017-11-23 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.25347 | N/A | N/A | N/A | NR/11/2509 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 430KV
[7 empty] | 2017-11-24 00:22 | 2017-11-24 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.26458 | N/A | N/A | N/A | NR/11/2626 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 426KV
[7 empty] | 2017-11-24 23:01 | 2017-11-25 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/11/2740 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-11-25 23:40 | 2017-11-28 08:54 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:14 | N/A | N/A | N/A | NR/11/2845 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV.
[7 empty] | 2017-11-28 09:18 | 2017-11-28 11:59 | -- | -- | -- | 0.11181 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/3101 | OSPT | SD TAKEN TO ATTEND THE SPARKING ON LINE ISOLATOR AT PANCHKULA.
[7 empty] | 2017-11-29 00:05 | 2017-11-29 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.25208 | N/A | N/A | N/A | NR/11/3197 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 421KV
[7 empty] | 2017-11-30 00:25 | 2017-11-30 06:53 | -- | -- | -- | 0 | 0 | 0 | 0.26944 | N/A | N/A | N/A | NR/11/3337 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 420KV
[12 empty] | 0.11181 | 0 | 0 | 1900-01-07 00:46 | [7 empty] | 99.64
1 | 85 | NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 |  | 2017-11-27 09:14 | 2017-11-27 21:00 | -- | -- | -- | 0.49028 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2962 | OSPT | SD TAKEN FOR AMP WORK AND CSD RELAY COMMISSIONING WORK AT MOGA S/S END.
[12 empty] | 0.49028 | 0 | 0 | 0 | [7 empty] | 98.42
1 | 86 | NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 87 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 |  | 2017-11-02 22:02 | 2017-11-03 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.32778 | N/A | N/A | N/A | NR/11/162 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-11-03 21:28 | 2017-11-04 11:22 | -- | -- | -- | 0 | 0 | 0 | 0.57917 | N/A | N/A | N/A | NR/11/240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-11-06 21:46 | 2017-11-08 09:41 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:55 | N/A | N/A | N/A | NR/11/487 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-11-10 03:26 | 2017-11-10 03:57 | -- | -- | -- | 0 | 0 | 0.021528 | 0 | N/A | N/A | N/A | NR/11/952 | GOVC | LINE TRIPPED DUE TO OVER VOLTAGE STAGE-1 OPERATED AT KURUKSHETRA END.KURUKSHETRA VOLTAGE= 439KV
[7 empty] | 2017-11-10 13:21 | 2017-11-10 21:12 | -- | -- | -- | 0 | 0 | 0 | 0.32708 | N/A | N/A | N/A | NR/11/1017 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 433KV
[7 empty] | 2017-11-17 22:05 | 2017-11-18 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/11/1914 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 428KV
[7 empty] | 2017-11-18 23:36 | 2017-11-19 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.2625 | N/A | N/A | N/A | NR/11/2038 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR = 431KV
[12 empty] | 0 | 0 | 0.021528 | 1900-01-02 07:43 | [7 empty] | 100
1 | 88 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 |  | 2017-11-04 20:14 | 2017-11-06 19:46 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 23:32 | N/A | N/A | N/A | NR/11/317 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 431KV
[7 empty] | 2017-11-08 20:05 | 2017-11-10 08:42 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:37 | N/A | N/A | N/A | NR/11/804 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-11-22 08:26 | 2017-11-28 15:50 | -- | -- | -- | 1900-01-05 07:24 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2393 | OSPT | SD TAKEN FOR BB-3 EXTENSION WORKS FOR JIND D/C UNDER CONSTRUCTION AND AS TIE CB WAS UNDER FORCED OUTAGE.
[12 empty] | 1900-01-05 07:24 | 0 | 0 | 1900-01-02 12:09 | [7 empty] | 79.65
1 | 89 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 |  | 2017-11-01 | 2017-11-01 08:45 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/10/2212 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[7 empty] | 2017-11-03 00:05 | 2017-11-03 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.24722 | N/A | N/A | N/A | NR/11/165 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 428KV
[7 empty] | 2017-11-04 20:22 | 2017-11-05 08:40 | -- | -- | -- | 0 | 0 | 0 | 0.5125 | N/A | N/A | N/A | NR/11/318 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 433KV
[7 empty] | 2017-11-06 21:36 | 2017-11-14 09:40 | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 12:04 | N/A | N/A | N/A | NR/11/487 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-11-14 21:28 | 2017-11-16 07:10 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:42 | N/A | N/A | N/A | NR/11/1522 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 429KV
[7 empty] | 2017-11-16 22:13 | 2017-11-20 10:03 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 11:50 | N/A | N/A | N/A | NR/11/1791 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 429KV
[7 empty] | 2017-11-21 20:51 | 2017-11-22 07:54 | -- | -- | -- | 0 | 0 | 0 | 0.46042 | N/A | N/A | N/A | NR/11/2359 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 427KV
[7 empty] | 2017-11-30 00:11 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.99236 | N/A | N/A | N/A | NR/11/3337 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[12 empty] | 0 | 0 | 0 | 1900-01-13 23:27 | [7 empty] | 100
1 | 90 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 |  | 2017-11-01 21:53 | 2017-11-02 06:34 | -- | -- | -- | 0 | 0 | 0 | 0.36181 | N/A | N/A | N/A | NR/11/74 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-11-10 03:26 | 2017-11-10 03:56 | -- | -- | -- | 0 | 0 | 0.020833 | 0 | N/A | N/A | N/A | NR/11/952 | GOVC | LINE TRIPPED DUE TO OVER VOLTAGE STAGE-1 OPERATED AT KURUKSHETRA END.KURUKSHETRA VOLTAGE= 442KV
[7 empty] | 2017-11-20 22:00 | 2017-11-21 06:57 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/11/2240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 435KV
[7 empty] | 2017-11-22 20:05 | 2017-11-24 06:50 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:45 | N/A | N/A | N/A | NR/11/2491 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-11-25 23:09 | 2017-11-26 07:55 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/11/2841 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-11-27 22:26 | 2017-11-29 06:59 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:33 | N/A | N/A | N/A | NR/11/3062 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[12 empty] | 0 | 0 | 0.020833 | 1900-01-02 21:42 | [7 empty] | 100
1 | 91 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 |  | 2017-11-01 | 2017-11-01 08:47 | -- | -- | -- | 0 | 0 | 0 | 0.36597 | N/A | N/A | N/A | NR/10/2212 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[7 empty] | 2017-11-01 13:18 | 2017-11-02 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.70625 | N/A | N/A | N/A | NR/11/40 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-11-02 20:15 | 2017-11-04 11:17 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:02 | N/A | N/A | N/A | NR/11/152 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[7 empty] | 2017-11-04 20:10 | 2017-11-07 18:57 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 22:47 | N/A | N/A | N/A | NR/11/317 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-07 20:03 | 2017-11-10 12:08 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 16:05 | N/A | N/A | N/A | NR/11/593 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[7 empty] | 2017-11-10 19:57 | 2017-11-13 16:08 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 20:11 | N/A | N/A | N/A | NR/11/1069 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 433KV
[7 empty] | 2017-11-13 20:47 | 2017-11-23 07:09 | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 10:22 | N/A | N/A | N/A | NR/11/1392 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 428KV
[7 empty] | 2017-11-23 21:41 | 2017-11-25 09:26 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:45 | N/A | N/A | N/A | NR/11/2622 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-11-25 20:01 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 03:59 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[12 empty] | 0 | 0 | 0 | 1900-01-26 05:55 | [7 empty] | 100
1 | 92 | NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 93 | NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 |  | 2017-11-01 | 2017-11-02 07:11 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:11 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 431KV
[7 empty] | 2017-11-02 20:20 | 2017-11-03 09:21 | -- | -- | -- | 0 | 0 | 0 | 0.54236 | N/A | N/A | N/A | NR/11/152 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 430KV
[7 empty] | 2017-11-03 21:35 | 2017-11-06 10:26 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 12:51 | N/A | N/A | N/A | NR/11/240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-11-06 21:23 | 2017-11-10 10:47 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 13:24 | N/A | N/A | N/A | NR/11/487 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-11-10 13:45 | 2017-11-13 16:08 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 02:23 | N/A | N/A | N/A | NR/11/1017 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 433KV
[7 empty] | 2017-11-13 20:49 | 2017-11-17 08:13 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 11:24 | N/A | N/A | N/A | NR/11/1392 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 428KV
[7 empty] | 2017-11-17 20:37 | 2017-11-22 18:53 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 22:16 | N/A | N/A | N/A | NR/11/1912 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUSHETRA= 431KV
[7 empty] | 2017-11-22 21:12 | 2017-11-30 14:53 | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 17:41 | N/A | N/A | N/A | NR/11/2499 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-11-30 22:01 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.082639 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[12 empty] | 0 | 0 | 0 | 1900-01-26 06:10 | [7 empty] | 100
1 | 94 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 95 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 96 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 |  | 2017-11-16 00:53 | 2017-11-16 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.23264 | N/A | N/A | N/A | NR/11/1670 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[7 empty] | 2017-11-16 21:13 | 2017-11-17 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/11/1787 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 421KV
[7 empty] | 2017-11-25 19:53 | 2017-11-26 06:48 | -- | -- | -- | 0 | 0 | 0 | 0.45486 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA = 421KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 01:55 | [7 empty] | 100
1 | 97 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 |  | 2017-11-05 02:19 | 2017-11-05 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.12569 | N/A | N/A | N/A | NR/11/335 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 426KV
[7 empty] | 2017-11-19 21:32 | 2017-11-20 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.37083 | N/A | N/A | N/A | NR/11/2122 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 426KV
[7 empty] | 2017-11-20 21:34 | 2017-11-21 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.36736 | N/A | N/A | N/A | NR/11/2240 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 426KV
[7 empty] | 2017-11-22 00:22 | 2017-11-22 07:08 | -- | -- | -- | 0 | 0 | 0 | 0.28194 | N/A | N/A | N/A | NR/11/2370 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 428KV
[7 empty] | 2017-11-23 00:10 | 2017-11-23 07:42 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/11/2508 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 430KV
[7 empty] | 2017-11-23 21:26 | 2017-11-24 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.34583 | N/A | N/A | N/A | NR/11/2620 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 426KV
[7 empty] | 2017-11-24 21:26 | 2017-11-25 07:42 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | N/A | N/A | N/A | NR/11/2735 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA = 422KV
[7 empty] | 2017-11-26 20:29 | 2017-11-28 05:57 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:28 | N/A | N/A | N/A | NR/11/2918 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 428KV
[7 empty] | 2017-11-28 22:56 | 2017-11-29 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.27222 | N/A | N/A | N/A | NR/11/3194 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 428KV
[7 empty] | 2017-11-30 00:11 | 2017-11-30 07:35 | -- | -- | -- | 0 | 0 | 0 | 0.30833 | N/A | N/A | N/A | NR/11/3337 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 420KV
[7 empty] | 2017-11-30 22:03 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.08125 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 420KV
[12 empty] | 0 | 0 | 0 | 1900-01-03 06:57 | [7 empty] | 100
1 | 98 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 |  | 2017-11-05 02:14 | 2017-11-05 09:00 | -- | -- | -- | 0 | 0 | 0 | 0.28194 | N/A | N/A | N/A | NR/11/333 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[7 empty] | 2017-11-13 00:43 | 2017-11-14 07:32 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:49 | N/A | N/A | N/A | NR/11/1279 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 430KV
[7 empty] | 2017-11-16 00:24 | 2017-11-16 07:14 | -- | -- | -- | 0 | 0 | 0 | 0.28472 | N/A | N/A | N/A | NR/11/1666 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[7 empty] | 2017-11-16 21:23 | 2017-11-17 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.37014 | N/A | N/A | N/A | NR/11/1787 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 421KV
[7 empty] | 2017-11-23 21:19 | 2017-11-24 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | N/A | N/A | N/A | NR/11/2620 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA = 424KV
[7 empty] | 2017-11-24 21:31 | 2017-11-25 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/11/2735 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA = 421KV
[7 empty] | 2017-11-28 09:15 | 2017-11-28 17:50 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/11/3099 | OSPD | SD TAKEN BY PATRAN STATION FOR MAINTENANCE AND INSULATORS REPLACEMENT WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 1900-01-02 07:05 | [7 empty] | 100
1 | 99 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 |  | 2017-11-20 00:46 | 2017-11-20 08:07 | -- | -- | -- | 0 | 0 | 0 | 0.30625 | N/A | N/A | N/A | NR/11/2129 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 429KV
[7 empty] | 2017-11-30 00:23 | 2017-11-30 07:41 | -- | -- | -- | 0 | 0 | 0 | 0.30417 | N/A | N/A | N/A | NR/11/3337 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[12 empty] | 0 | 0 | 0 | 0.61042 | [7 empty] | 100
1 | 100 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 |  | 2017-11-29 09:09 | 2017-11-29 17:41 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/11/3238 | OSPD | SD TAKEN BY PATRAN STATION FOR MAINTENANCE AND INSULATORS REPLACEMENT WORK AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.35556 | [7 empty] | 100
1 | 101 | NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 |  | 2017-11-20 00:48 | 2017-11-20 08:03 | -- | -- | -- | 0 | 0 | 0 | 0.30208 | N/A | N/A | N/A | NR/11/2129 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 426KV
[12 empty] | 0 | 0 | 0 | 0.30208 | [7 empty] | 100
1 | 102 | NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 103 | NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2017-11-07 08:01 | 2017-11-07 08:01 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | - | LART | LINE A/R ON R-N FAULT. FLR BHIWANI : 142KM.
[7 empty] | 2017-11-07 08:22 | 2017-11-07 14:47 | -- | -- | -- | 0 | 0.26736 | 0 | 0 | N/A | N/A | N/A | NR/11/554 | OMSU | LINE TRIPPED ON R-N FAULT. FLR BHIWANI : 142KM. (TOTAL LINE LENGTH: 212 KM, POWERGRID PORTION : 14.4 KM FROM RAJPURA)
[12 empty] | 0 | 0.26736 | 0 | 0 | [7 empty] | 100
1 | 104 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 |  | 2017-11-01 21:57 | 2017-11-02 11:23 | -- | -- | -- | 0 | 0 | 0 | 0.55972 | N/A | N/A | N/A | NR/11/73 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-11-02 21:59 | 2017-11-03 09:29 | -- | -- | -- | 0 | 0 | 0 | 0.47917 | N/A | N/A | N/A | NR/11/163 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-11-04 21:36 | 2017-11-05 08:43 | -- | -- | -- | 0 | 0 | 0 | 0.46319 | N/A | N/A | N/A | NR/11/325 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-11-10 00:15 | 2017-11-10 11:30 | -- | -- | -- | 0 | 0 | 0 | 0.46875 | N/A | N/A | N/A | NR/11/948 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-10 21:55 | 2017-11-11 07:34 | -- | -- | -- | 0 | 0 | 0 | 0.40208 | N/A | N/A | N/A | NR/11/1078 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-13 01:23 | 2017-11-13 08:11 | -- | -- | -- | 0 | 0 | 0 | 0.28333 | N/A | N/A | N/A | NR/11/1281 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 432KV
[7 empty] | 2017-11-16 00:21 | 2017-11-17 08:26 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:05 | N/A | N/A | N/A | NR/11/1666 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-11-19 21:28 | 2017-11-20 08:01 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/11/2122 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 425KV
[7 empty] | 2017-11-24 21:55 | 2017-11-25 08:41 | -- | -- | -- | 0 | 0 | 0 | 0.44861 | N/A | N/A | N/A | NR/11/2736 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR = 422KV
[7 empty] | 2017-11-26 00:40 | 2017-11-27 06:22 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 05:42 | N/A | N/A | N/A | NR/11/2848 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 434KV
[12 empty] | 0 | 0 | 0 | 1900-01-05 02:51 | [7 empty] | 100
1 | 105 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 |  | 2017-11-01 | 2017-11-01 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.26736 | N/A | N/A | N/A | NR/10/2214 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[7 empty] | 2017-11-01 21:52 | 2017-11-02 06:54 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/11/73 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-02 21:58 | 2017-11-03 09:35 | -- | -- | -- | 0 | 0 | 0 | 0.48403 | N/A | N/A | N/A | NR/11/163 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 430KV
[7 empty] | 2017-11-03 20:51 | 2017-11-04 09:09 | -- | -- | -- | 0 | 0 | 0 | 0.5125 | N/A | N/A | N/A | NR/11/236 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-04 20:12 | 2017-11-04 20:12 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | LINE A/R ON Y-N FAULT. FLR HAMIRPUR - 56.988 KM, 5.37KA.
[7 empty] | 2017-11-04 21:35 | 2017-11-05 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/11/325 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-05 21:33 | 2017-11-06 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.35069 | N/A | N/A | N/A | NR/11/390 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-06 21:20 | 2017-11-07 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/11/487 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-09 21:40 | 2017-11-10 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/11/942 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-10 21:55 | 2017-11-11 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.36736 | N/A | N/A | N/A | NR/11/1078 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-11 21:42 | 2017-11-13 07:50 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:08 | N/A | N/A | N/A | NR/11/1188 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 429KV
[7 empty] | 2017-11-13 21:20 | 2017-11-14 07:28 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/11/1396 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-11-14 21:33 | 2017-11-17 08:29 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 10:56 | N/A | N/A | N/A | NR/11/1527 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 432KV
[7 empty] | 2017-11-17 22:02 | 2017-11-18 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/11/1914 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 424KV
[7 empty] | 2017-11-18 20:37 | 2017-11-19 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/11/2032 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-19 21:30 | 2017-11-20 09:36 | -- | -- | -- | 0 | 0 | 0 | 0.50417 | N/A | N/A | N/A | NR/11/2122 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-21 00:26 | 2017-11-21 10:52 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | NR/11/2247 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALLANDHAR= 428KV
[7 empty] | 2017-11-23 20:23 | 2017-11-25 07:32 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:09 | N/A | N/A | N/A | NR/11/2614 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-11-26 00:39 | 2017-11-27 05:51 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 05:12 | N/A | N/A | N/A | NR/11/2848 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 434KV
[7 empty] | 2017-11-27 22:27 | 2017-11-29 06:57 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:30 | N/A | N/A | N/A | NR/11/3062 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-11-29 20:21 | 2017-11-30 08:05 | -- | -- | -- | 0 | 0 | 0 | 0.48889 | N/A | N/A | N/A | NR/11/3327 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR = 429KV
[7 empty] | 2017-11-30 23:52 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.0055556 | N/A | N/A | N/A | NR/11/3463 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-12 22:41 | [7 empty] | 100
1 | 106 | NR240116 | 400KV Dadri-Kaithal | 213 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 107 | NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 |  | 2017-11-23 12:31 | 2017-11-23 15:36 | -- | -- | -- | 0.12847 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2571 | LEFT | LINE TRIPPED ON B-N FAULT. FLR KAITHAL -204 KMS 1.6 KA, DADRI: 5.9 KMS.
[12 empty] | 0.12847 | 0 | 0 | 0 | [7 empty] | 99.59
1 | 108 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 |  | 2017-11-13 10:54 | 2017-11-13 17:43 | -- | -- | -- | 0 | 0 | 0 | 0.28403 | N/A | N/A | N/A | NR/11/1334 | OSPD | SD TAKEN BY NHPC PARBATI-2 FOR ATTENDING GAS LEAKAGE IN GIS AT THEIR END.
[12 empty] | 0 | 0 | 0 | 0.28403 | [7 empty] | 100
1 | 109 | NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 110 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 111 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 112 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 |  | 2017-11-01 | 2017-11-01 09:06 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | N/A | N/A | N/A | NR/10/2206 NLDC-1084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA = 802KV.
[7 empty] | 2017-11-01 21:49 | 2017-11-02 09:36 | -- | -- | -- | 0 | 0 | 0 | 0.49097 | N/A | N/A | N/A | NR/11/72 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 802KV
[7 empty] | 2017-11-02 21:13 | 2017-11-03 09:18 | -- | -- | -- | 0 | 0 | 0 | 0.50347 | N/A | N/A | N/A | NR/11/156 NLDC/83 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 798KV
[7 empty] | 2017-11-03 20:09 | 2017-11-04 10:06 | -- | -- | -- | 0 | 0 | 0 | 0.58125 | N/A | N/A | N/A | NR/11/232 NLDC/126 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 801KV
[7 empty] | 2017-11-04 20:05 | 2017-11-05 06:46 | -- | -- | -- | 0 | 0 | 0 | 0.44514 | N/A | N/A | N/A | NR/11/315 NLDC/161 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 801KV
[7 empty] | 2017-11-05 19:58 | 2017-11-06 12:45 | -- | -- | -- | 0 | 0 | 0 | 0.69931 | N/A | N/A | N/A | NR/11/386 NLDC/200 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 802KV
[7 empty] | 2017-11-06 20:06 | 2017-11-07 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/11/482 NLDC/257 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 801KV
[7 empty] | 2017-11-07 19:54 | 2017-11-08 09:46 | -- | -- | -- | 0 | 0 | 0 | 0.57778 | N/A | N/A | N/A | NR/11/589 NLDC/319 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 802KV
[7 empty] | 2017-11-08 20:15 | 2017-11-09 11:22 | -- | -- | -- | 0 | 0 | 0 | 0.62986 | N/A | N/A | N/A | NR/11/806 NLDC/388 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 805KV
[7 empty] | 2017-11-09 19:46 | 2017-11-10 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.47222 | N/A | N/A | N/A | NR/11/929 NLDC/453 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 795KV
[7 empty] | 2017-11-10 22:17 | 2017-11-11 09:54 | -- | -- | -- | 0 | 0 | 0 | 0.48403 | N/A | N/A | N/A | NR/11/1082 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 797KV
[7 empty] | 2017-11-11 19:58 | 2017-11-13 09:38 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 13:40 | N/A | N/A | N/A | NR/11/1176 & NL/11/572 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 803KV
[7 empty] | 2017-11-13 16:46 | 2017-11-15 09:15 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 16:29 | N/A | N/A | N/A | NR/11/1357 & NL/11/652 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 793KV
[7 empty] | 2017-11-15 19:35 | 2017-11-16 09:04 | -- | -- | -- | 0 | 0 | 0 | 0.56181 | N/A | N/A | N/A | NR/11/1650 & NLDC- 794 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 793KV
[7 empty] | 2017-11-16 16:34 | 2017-11-17 09:44 | -- | -- | -- | 0 | 0 | 0 | 0.71528 | N/A | N/A | N/A | NR/11/1755& NLDC- 833 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 795KV
[7 empty] | 2017-11-17 19:44 | 2017-11-18 07:15 | -- | -- | -- | 0 | 0 | 0 | 0.47986 | N/A | N/A | N/A | NR/11/1904& NLDC- 926 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 803KV
[7 empty] | 2017-11-18 20:12 | 2017-11-19 09:38 | -- | -- | -- | 0 | 0 | 0 | 0.55972 | N/A | N/A | N/A | NR/11/2030 & NLDC- 993 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 803KV
[7 empty] | 2017-11-19 19:38 | 2017-11-20 07:38 | -- | -- | -- | 0 | 0 | 0 | 0.5 | N/A | N/A | N/A | NR/11/2111 & NLDC- 1036 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 796KV
[7 empty] | 2017-11-20 19:49 | 2017-11-21 07:22 | -- | -- | -- | 0 | 0 | 0 | 0.48125 | N/A | N/A | N/A | NR/11/2227& NLDC- 1094 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 782KV
[7 empty] | 2017-11-21 19:53 | 2017-11-22 07:40 | -- | -- | -- | 0 | 0 | 0 | 0.49097 | N/A | N/A | N/A | NR/11/2357 NLDC-1211 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 797KV
[7 empty] | 2017-11-22 19:58 | 2017-11-23 07:13 | -- | -- | -- | 0 | 0 | 0 | 0.46875 | N/A | N/A | N/A | NR/11/2492 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 804KV
[7 empty] | 2017-11-23 19:16 | 2017-11-24 07:29 | -- | -- | -- | 0 | 0 | 0 | 0.50903 | N/A | N/A | N/A | NR/11/2606 NLDC/1347 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 792KV
[7 empty] | 2017-11-24 19:20 | 2017-11-25 07:39 | -- | -- | -- | 0 | 0 | 0 | 0.51319 | N/A | N/A | N/A | NR/11/2719 NLDC/1421 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 793KV
[7 empty] | 2017-11-25 19:22 | 2017-11-26 11:21 | -- | -- | -- | 0 | 0 | 0 | 0.66597 | N/A | N/A | N/A | NR/11/2824 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 795KV
[7 empty] | 2017-11-26 20:22 | 2017-11-27 09:35 | -- | -- | -- | 0 | 0 | 0 | 0.55069 | N/A | N/A | N/A | NR/11/2917 & NL/1532 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 805KV
[7 empty] | 2017-11-27 20:04 | 2017-11-28 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.47778 | N/A | N/A | N/A | NR/11/3051& NLDC- 1599 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 801KV
[7 empty] | 2017-11-28 19:27 | 2017-11-29 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.47083 | N/A | N/A | N/A | NR/11/3185& NLDC- 1655 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 796KV
[7 empty] | 2017-11-29 20:33 | 2017-11-30 07:36 | -- | -- | -- | 0 | 0 | 0 | 0.46042 | N/A | N/A | N/A | NR/11/3326 & NLDC- 1719 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 799KV.
[7 empty] | 2017-11-30 19:38 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 0.18194 | N/A | N/A | N/A | NR/11/3439 & NLDC- 1719 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 799KV.
[12 empty] | 0 | 0 | 0 | 1900-01-16 00:24 | [7 empty] | 100
1 | 113 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 114 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 115 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 116 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 117 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 118 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 119 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 |  | 2017-11-01 | 2017-11-01 02:07 | -- | -- | -- | 0 | 0 | 0 | 0.088194 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 394KV.
[7 empty] | 2017-11-01 05:52 | 2017-11-01 15:07 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 395KV.
[7 empty] | 2017-11-01 20:09 | 2017-11-08 09:35 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 13:26 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 384KV.
[7 empty] | 2017-11-08 14:09 | 2017-11-15 00:40 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 10:31 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 393KV.
[7 empty] | 2017-11-15 11:15 | 2017-11-19 02:35 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 15:20 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 395KV.
[7 empty] | 2017-11-19 06:37 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 17:23 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 395KV.
[12 empty] | 0 | 0 | 0 | 1900-01-27 20:02 | [7 empty] | 100
1 | 120 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 121 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 122 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 123 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 124 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 125 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 126 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 127 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 128 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 129 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 130 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 131 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 132 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 133 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 134 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 |  | 2017-11-12 13:44 | 2017-11-12 15:59 | -- | -- | -- | 0.09375 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1230 & NL/11/599 | OSPT | SD TAKEN FOR ATTENDING HOT SPOT ON B-PHASE ISOLATOR OF BUS- REACCTOR-I
[12 empty] | 0.09375 | 0 | 0 | 0 | [7 empty] | 99.7
1 | 135 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 136 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 137 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 138 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 139 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 140 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 141 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 142 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 143 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 |  | 2017-11-01 | 2017-11-01 15:13 | -- | -- | -- | 0 | 0 | 0 | 0.63403 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WANPOH = 395KV.
[7 empty] | 2017-11-04 08:44 | 2017-11-08 09:38 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 00:54 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WANPOH = 387KV.
[7 empty] | 2017-11-09 17:12 | 2017-11-15 00:50 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 07:38 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WANPOH = 395KV.
[7 empty] | 2017-11-15 11:35 | 2017-12-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 12:25 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH = 395KV.
[12 empty] | 0 | 0 | 0 | 1900-01-24 12:10 | [7 empty] | 100
1 | 144 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 145 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 |  | 2017-11-23 17:26 | 2017-11-23 18:07 | -- | -- | -- | 0.028472 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2585 | OSPT | SD TAKEN FOR SF6 GAS FILLING IN MAIN BAY GIS CHAMBER.
[12 empty] | 0.028472 | 0 | 0 | 0 | [7 empty] | 99.91
1 | 146 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 |  | 2017-11-02 21:31 | 2017-11-02 23:20 | -- | -- | -- | 0.075694 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/164 | SRET | B/R TRIPPED ON DIFFERENTIAL DUE TO FAILURE OF B-PH CT OF TIE BAY 408 AT PANCHKULA.
[12 empty] | 0.075694 | 0 | 0 | 0 | [7 empty] | 99.76
1 | 147 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 148 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 |  | 2017-11-15 15:45 | 2017-11-16 12:06 | -- | -- | -- | 0 | 0 | 0 | 0.84792 | N/A | N/A | N/A | -- | OSPD | B/R HAND TRIPPED BY BBMB DEHAR FOR TESTING OF MACHINE NO. 6 ON LEADING POWER FACTOR.
[12 empty] | 0 | 0 | 0 | 0.84792 | [7 empty] | 100
1 | 149 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 |  | 2017-11-15 15:45 | 2017-11-16 12:06 | -- | -- | -- | 0 | 0 | 0 | 0.84792 | N/A | N/A | N/A | -- | OSPD | B/R HAND TRIPPED BY BBMB DEHAR FOR TESTING OF MACHINE NO. 6 ON LEADING POWER FACTOR.
[12 empty] | 0 | 0 | 0 | 0.84792 | [7 empty] | 100
1 | 150 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 151 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 152 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 153 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 154 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 155 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 |  | 2017-11-18 11:22 | 2017-11-18 14:35 | -- | -- | -- | 0.13403 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1965 | OSPT | SD TO ATTEND HOTSPOT AT T-ISOLATOR.
[12 empty] | 0.13403 | 0 | 0 | 0 | [7 empty] | 99.57
1 | 156 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 |  | 2017-11-29 13:25 | 2017-11-29 14:52 | -- | -- | -- | 0.060417 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/3263 | OSPT | SD TAKEN FOR OLTC GEAR ASSEMBLY REPLACEMENT.
[12 empty] | 0.060417 | 0 | 0 | 0 | [7 empty] | 99.81
1 | 157 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 158 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 159 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 160 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 161 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 162 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 163 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 164 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 165 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 166 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 167 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 168 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 169 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 170 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 171 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 172 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 173 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 174 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 |  | 2017-11-01 15:34 | 2017-11-01 15:55 | -- | -- | -- | 0 | 0.014583 | 0 | 0 | N/A | N/A | N/A | NR/11/49 | OMSU | ICT TRIPPED DUE TO HEAVY CURRENT DUE TO JUMPER SNAPPING ON PAMPORE CKT-1 AT JKPDD END.
[12 empty] | 0 | 0.014583 | 0 | 0 | [7 empty] | 100
1 | 175 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 |  | 2017-11-01 14:25 | 2017-11-01 14:58 | -- | -- | -- | 0.022917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/43 | OSPT | SD TAKEN FOR TAKING Y-PH UNIT OUT OF SERVICE FOR AMP WORKS & TAKING IN SPARE UNIT.
[12 empty] | 0.022917 | 0.029167 | 0 | 0 | [7 empty] | 99.93
1 | 176 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 |  | 2017-11-01 15:34 | 2017-11-01 15:57 | -- | -- | -- | 0 | 0.015972 | 0 | 0 | N/A | N/A | N/A | NR/11/49 | OMSU | ICT TRIPPED DUE TO HEAVY CURRENT DUE TO JUMPER SNAPPING ON PAMPORE CKT-1 AT JKPDD END.
[7 empty] | 2017-11-08 10:19 | 2017-11-08 17:38 | -- | -- | -- | 0.30486 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/725 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.30486 | 0.015972 | 0 | 0 | [7 empty] | 99.02
1 | 177 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 178 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 179 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 180 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 181 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 182 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 |  | 2017-11-04 19:05 | 2017-11-10 22:35 | -- | -- | -- | 1900-01-05 03:30 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/309 | OSPT | SD TAKEN TO CHECK BUCHHOLZ ALARM AND
[12 empty] | 1900-01-05 03:30 | 0 | 0 | 0 | [7 empty] | 80.17
1 | 183 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 |  | 2017-11-24 08:21 | 2017-11-24 09:39 | -- | -- | -- | 0.054167 | 0 | 0 | 0 | N/A | N/A | N/A | --- | SICT | ICT TRRIPPED DUE TO BUCHHOLZ PRTN OPERATION.
[7 empty] | 2017-11-24 09:39 | 2017-11-24 12:59 | -- | -- | -- | 0.13889 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2665 | OSPT | SD TAKEN FOR RECTIFICATION WORK AFTER TRIPPING ON BUCHHOLZ.
[12 empty] | 0.19306 | 0 | 0 | 0 | [7 empty] | 99.38
1 | 184 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 185 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 |  | 2017-11-22 09:29 | 2017-11-22 18:31 | -- | -- | -- | 0.37639 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2412 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.37639 | 0 | 0 | 0 | [7 empty] | 98.79
1 | 186 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 187 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 |  | 2017-11-07 03:48 | 2017-11-07 05:00 | -- | -- | -- | 0.05 | 0 | 0 | 0 | N/A | N/A | N/A | - | SICT | ICT TRIPPED ON Y-PH OIL SURGE RELAY OPERATION.
[7 empty] | 2017-11-07 05:00 | 2017-11-07 15:22 | -- | -- | -- | 0.43194 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/502 NLDC/269 | OSPT | SD TAKEN TO CHECK & TEST ICT AFTER TRIPPING ON Y-PH OSR PRTN.
[12 empty] | 0.48194 | 0 | 0 | 0 | [7 empty] | 98.45
1 | 188 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 189 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 190 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 191 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 192 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 193 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 194 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 195 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 196 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 197 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 198 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 199 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 200 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 201 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 202 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 203 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 |  | 2017-11-22 10:22 | 2017-11-22 19:38 | -- | -- | -- | 0.38611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2408 | OSPT | SD TAKEN FOR CARRYING OUT COMPLETE TESTING OF TRANSFORMER.
[7 empty] | 2017-11-23 09:20 | 2017-11-23 17:57 | -- | -- | -- | 0.35903 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/2539 | OSPT | SD TAKEN FOR CARRYING OUT COMPLETE TESTING OF TRANSFORMER.
[12 empty] | 0.74514 | 0 | 0 | 0 | [7 empty] | 97.6
1 | 204 | NR2ICT73 | KAITHAL ICT -III | [5 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0
1 | 205 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 |  | 2017-11-01 11:25 | 2017-11-01 12:20 | -- | -- | -- | 0 | 0.038194 | 0 | 0 | N/A | N/A | N/A | NR/11/35 | OMSU | SVC TRIPPED ON Y-PHASE TRANSFORMER E/F CREATED BY MONKEY ON 36 KV BUSHING.
[12 empty] | 0 | 0.038194 | 0 | 0 | [7 empty] | 100
1 | 206 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 |  | 2017-11-10 03:26 | 2017-11-10 04:58 | -- | -- | -- | 0 | 0 | 0 | 0.063889 | N/A | N/A | N/A | NR/11/954 | GOMD | POLE BLOCKED DUE TO LOSS OF AC POWER TRANSFER CAUSED BY TRIPPING OF ALL CONNECTED AC LINES ON OVER VOLTAGE.
[7 empty] | 2017-11-17 01:42 | 2017-11-18 15:53 | -- | -- | -- | 1899-12-31 14:11 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1933 | OMST | POLE BLOCKED DURING CHANGEOVER FOR VOLTAGE REGULATION BY NLDC.
[7 empty] | 2017-11-21 21:16 | 2017-11-21 21:40 | -- | -- | -- | 0.016667 | 0 | 0 | 0 | N/A | N/A | N/A | NL/11/1216 | OMST | POLE BLOCKED DUE TO UNAVAILABILITY OF MINIMUM FILTERS AT HVDC KURUKSHETRA END.
[7 empty] | 2017-11-24 11:13 | 2017-11-24 11:43 | -- | -- | -- | 0.020833 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/1391 | OMST | POLE BLOCKED DUE TO CONTROL MAL OPERATION AT KURUKSHETRA.
[7 empty] | 2017-11-25 01:23 | 2017-11-25 01:30 | -- | -- | -- | 0.0048611 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/1436 | OMST | POLE BLOCKED DURING RAMP DOWN THE POWER AT KURUKSHETRA.
[12 empty] | 1899-12-31 15:12 | 0 | 0 | 0.063889 | [7 empty] | 94.72
1 | 207 | NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 |  | 2017-11-10 03:26 | 2017-11-10 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.091667 | N/A | N/A | N/A | NR/11/956 | GOMD | POLE BLOCKED DUE TO LOSS OF AC POWER TRANSFER CAUSED BY TRIPPING OF ALL CONNECTED AC LINES ON OVER VOLTAGE.
[7 empty] | 2017-11-11 15:55 | 2017-11-11 17:17 | -- | -- | -- | 0.056944 | 0 | 0 | 0 | N/A | N/A | N/A | - | OMST | POLE BLOCKED DUE TO DC UNDER CURRENT PROTECTION OPTD IN LINE
[7 empty] | 2017-11-17 00:06 | 2017-11-17 04:23 | -- | -- | -- | 0 | 0 | 0 | 0.17847 | N/A | N/A | N/A | NL/11/812 | LVRD | POLE BLOCKED FOR VOLTAGE REGULATION BY NLDC
[7 empty] | 2017-11-17 10:52 | 2017-11-17 11:07 | -- | -- | -- | 0.010417 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC-891,NRLDC-1853 | OMST | POLE BLOCKED DUE TO CONTROL MAL-OPERATION.
[7 empty] | 2017-11-17 12:23 | 2017-11-17 12:59 | -- | -- | -- | 0.025 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1842, NLDC-896, WRLDC-2234 | OMST | POLE BLOCKED DUE TO COMMUTATION FAILURE AT KURUKSHETRA END.
[7 empty] | 2017-11-17 13:01 | 2017-11-17 13:24 | -- | -- | -- | 0.015972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/11/1860, NLDC-897, WRLDC-2236 | OMST | POLE BLOCKED DUE TO TOVC PROTN. OPTD. AT KURUKSHETRA END.
[7 empty] | 2017-11-17 21:56 | 2017-11-17 23:09 | -- | -- | -- | 0.050694 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/932 | OMST | POLE BLOCKED DUE TO TOV (TEMPORARY OVER VOLTAGE) OPERATED AT HVDC KURUKSHETRA END.
[7 empty] | 2017-11-21 21:16 | 2017-11-21 21:40 | -- | -- | -- | 0.016667 | 0 | 0 | 0 | N/A | N/A | N/A | NL/11/1216 | OMST | POLE BLOCKED DUE TO UNAVAILABILITY OF MINIMUM FILTERS AT HVDC KURUKSHETRA END.
[7 empty] | 2017-11-24 08:38 | 2017-11-25 22:03 | -- | -- | -- | 1899-12-31 13:25 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/1369 | OMST | SD TAKEN TO ATTEND THE FAULT OCCURRED VBO FIRING IN VALVE 6 AND THRYSTER FAILED IN VALVE 12.
[12 empty] | 1899-12-31 17:38 | 0 | 0 | 0.27014 | [7 empty] | 94.39
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM([DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM([OTHERS, row above])
Hrs:Min = IF(RIGHT([Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM([Hrs:Min, row above])
Deemed Available = IF(RIGHT([Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM([Deemed Available, row above])

## NR2 Dec
Standard of Performance data for month of DECEMBER 2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
Annexure-A
| S.No | ELEMENT CODE | ELEMENT NAME | DESCRIPTION (Length/Nos/MVA/MVAr/etc) | Region | Type of Failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration time more than Specified (Y/N) | Difference between Actual and specified | NRLDC Code | Category Code | REASON OF OUTAGE | Outage certifying Agency and reference documents (NRPC) | % Availability as certified by certifying agency
[7 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | POWERGRID | OTHERS | System constraints / Natural calamity/ Militancy | Deemed Available
[12 empty] | @ (T) | # (U) | & ( C ) | * (D)
[12 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
1 | 1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 |  | 2017-12-03 08:02 | 2017-12-03 15:04 | -- | -- | -- | 0 | 0 | 0 | 0.29306 | N/A | N/A | N/A | NR/12/232 | OSPD | SD TAKEN BY JKPDD FOR AMP WORKS AT HIRANAGAR.
[7 empty] | 2017-12-17 08:17 | 2017-12-17 17:38 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/12/1769 | OSPD | SD TAKEN BY NHPC FOR MAINTENANCE WORKS AT SEWA-2.
[12 empty] | 0 | 0 | 0 | 0.68264 | [7 empty] | 100
1 | 2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 |  | 2017-12-17 08:17 | 2017-12-17 18:00 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/12/1769 | OSPD | SD TAKEN BY NHPC FOR MAINTENANCE WORKS AT SEWA-2.
[12 empty] | 0 | 0 | 0 | 0.40486 | [7 empty] | 100
1 | 3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 |  | 2017-12-03 08:02 | 2017-12-03 14:58 | -- | -- | -- | 0 | 0 | 0 | 0.28889 | N/A | N/A | N/A | NR/12/232 | OSPD | SD TAKEN BY JKPDD FOR APM WORKS AT HIRANAGAR.
[7 empty] | 2017-12-17 08:18 | 2017-12-17 17:40 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/12/1769 | OSPD | SD TAKEN BY NHPC FOR MAINTENANCE WORKS AT SEWA-2.
[12 empty] | 0 | 0 | 0 | 0.67917 | [7 empty] | 100
1 | 4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 |  | 2017-12-12 07:25 | 2017-12-12 08:08 | -- | -- | -- | 0.029861 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1155 | OSFT | LINE TRIPPED ON B-N FAULT FROM SEWA2 END ONLY. FLR SEWA :- 13.2KM.
[7 empty] | 2017-12-17 08:18 | 2017-12-17 17:41 | -- | -- | -- | 0 | 0 | 0 | 0.39097 | N/A | N/A | N/A | NR/12/1769 | OSPD | SD TAKEN BY NHPC FOR MAINTENANCE WORKS AT SEWA-2.
[12 empty] | 0.029861 | 0 | 0 | 0.39097 | [7 empty] | 99.9
1 | 6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 |  | 2017-12-03 08:24 | 2017-12-03 14:35 | -- | -- | -- | 0 | 0 | 0 | 0.25764 | N/A | N/A | N/A | NR/12/232 | OSPD | SD TAKEN BY JKPDD FOR AMP WORKS AT HIRANAGAR.
[12 empty] | 0 | 0 | 0 | 0.25764 | [7 empty] | 100
1 | 9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 |  | 2017-12-14 09:24 | 2017-12-14 15:49 | -- | -- | -- | 0 | 0 | 0 | 0.26736 | N/A | N/A | N/A | NR/12/1433 | OSPD | SD TAKEN BY PSTCL DASUA FOR MAINTENANCE WORKS.
[12 empty] | 0 | 0 | 0 | 0.26736 | [7 empty] | 100
1 | 10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 |  | 2017-12-15 11:35 | 2017-12-15 16:24 | -- | -- | -- | 0 | 0 | 0 | 0.20069 | N/A | N/A | N/A | NR/12/1567 | OSPD | SD TAKEN BY PSTCL DASUA FOR MAINTENANCE WORKS.
[12 empty] | 0 | 0 | 0 | 0.20069 | [7 empty] | 100
1 | 11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 |  | 2017-12-23 09:29 | 2017-12-23 19:34 | -- | -- | -- | 0 | 0 | 0 | 0.42014 | N/A | N/A | N/A | NR/12/2480 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-25 14:08 | 2017-12-25 17:35 | -- | -- | -- | 0 | 0 | 0 | 0.14375 | N/A | N/A | N/A | NR/12/2715 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[12 empty] | 0 | 0 | 0 | 0.56389 | [7 empty] | 100
1 | 13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 |  | 2017-12-15 10:54 | 2017-12-15 15:29 | -- | -- | -- | 0.19097 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1562 | OSPT | SD TAKEN TO ATTEND OIL LEAKAGE B-PHASE CVT AT KISHENPUR.
[7 empty] | 2017-12-24 08:52 | 2017-12-24 15:27 | -- | -- | -- | 0 | 0 | 0 | 0.27431 | N/A | N/A | N/A | NR/12/2596 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-26 07:52 | 2017-12-26 12:38 | -- | -- | -- | 0 | 0 | 0 | 0.19861 | N/A | N/A | N/A | NR/12/2772 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[12 empty] | 0.19097 | 0 | 0 | 0.47292 | [7 empty] | 99.38
1 | 14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 |  | 2017-12-21 10:54 | 2017-12-21 17:04 | -- | -- | -- | 0.25694 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/2242 | OSPT | SD TAKEN FOR REPLACEMENT OF R- PHASE LINE CT AT UDHAMPUR.
[12 empty] | 0.25694 | 0 | 0 | 0 | [7 empty] | 99.17
1 | 15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 |  | 2017-12-01 10:11 | 2017-12-01 18:18 | -- | -- | -- | 0.33819 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/48 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.33819 | 0 | 0 | 0 | [7 empty] | 98.91
1 | 20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 |  | 2017-12-01 10:23 | 2017-12-01 17:12 | -- | -- | -- | 0 | 0 | 0 | 0.28403 | N/A | N/A | N/A | NR/12/50 | OSPD | SD TAKEN BY PSTCL TO ATTEND HOTSPOT AT SARNA.
[7 empty] | 2017-12-14 10:15 | 2017-12-14 15:46 | -- | -- | -- | 0 | 0 | 0 | 0.22986 | N/A | N/A | N/A | NR/12/1433 | OSPD | SD TAKEN BY PSTCL DASUA FOR COMMISSIONING OF 220KV BUS BAR PROTECTION PANAL.
[12 empty] | 0 | 0 | 0 | 0.51389 | [7 empty] | 100
1 | 23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 |  | 2017-12-12 06:13 | 2017-12-12 07:02 | -- | -- | -- | 0.034028 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1140 | LEFT | LINE TRIPPED ON R-N FAULT. FLR SARNA : 2.5KM
[7 empty] | 2017-12-13 10:56 | 2017-12-13 17:11 | -- | -- | -- | 0 | 0 | 0 | 0.26042 | N/A | N/A | N/A | NR/12/1315 | OSPD | SD TAKEN BY PSTCL FOR ATTEND HOT SPOT AND MAINT. WORK AT DASUYA.
[12 empty] | 0.034028 | 0 | 0 | 0.26042 | [7 empty] | 99.89
1 | 24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 28 | NR222028 | 220KV Jallandhar-Hamirpur(PG) -I | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 29 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 30 | NR222030 | 220KV Jallandhar-Hamirpur(PG) -II | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 31 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 32 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 33 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 |  | 2017-12-03 08:10 | 2017-12-03 14:35 | -- | -- | -- | 0 | 0 | 0 | 0.26736 | N/A | N/A | N/A | NR/12/232 | OSPD | SD TAKEN BY JKPDD FOR APM WORKS AT HIRANAGAR.
[12 empty] | 0 | 0 | 0 | 0.26736 | [7 empty] | 100
1 | 34 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 |  | 2017-12-29 10:28 | 2017-12-29 20:15 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/12/3098 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-30 10:53 | 2017-12-30 19:42 | -- | -- | -- | 0 | 0 | 0 | 0.36736 | N/A | N/A | N/A | NR/12/4182 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[12 empty] | 0 | 0 | 0 | 0.775 | [7 empty] | 100
1 | 35 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 36 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 37 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 38 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 |  | 2017-12-05 08:22 | 2017-12-05 19:10 | -- | -- | -- | 0 | 0 | 0 | 0.45 | N/A | N/A | N/A | NR/12/403 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-06 19:47 | 2017-12-07 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.43264 | N/A | N/A | N/A | NR/12/582 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-07 08:30 | 2017-12-07 18:58 | -- | -- | -- | 0 | 0 | 0 | 0.43611 | N/A | N/A | N/A | NR/12/604 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-09 08:20 | 2017-12-09 18:51 | -- | -- | -- | 0 | 0 | 0 | 0.43819 | N/A | N/A | N/A | NR/12/842 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-13 08:56 | 2017-12-13 19:13 | -- | -- | -- | 0 | 0 | 0 | 0.42847 | N/A | N/A | N/A | NR/12/1300 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-16 08:35 | 2017-12-16 18:20 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/12/1656 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-18 08:58 | 2017-12-18 19:21 | -- | -- | -- | 0 | 0 | 0 | 0.43264 | N/A | N/A | N/A | NR/12/1866 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-19 21:51 | 2017-12-20 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.36667 | N/A | N/A | N/A | NR/12/2067 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-20 08:23 | 2017-12-20 16:15 | -- | -- | -- | 0 | 0 | 0 | 0.32778 | N/A | N/A | N/A | NR/12/2088 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[12 empty] | 0 | 0 | 0 | 1900-01-02 17:15 | [7 empty] | 100
1 | 39 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 |  | 2017-12-01 | 2017-12-01 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.2625 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[7 empty] | 2017-12-01 20:20 | 2017-12-02 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/12/127 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-02 21:16 | 2017-12-03 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.37431 | N/A | N/A | N/A | NR/12/213 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-03 20:09 | 2017-12-04 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/12/279 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-04 20:11 | 2017-12-05 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/12/378 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-05 19:58 | 2017-12-06 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/12/481 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-06 08:49 | 2017-12-06 18:35 | -- | -- | -- | 0 | 0 | 0 | 0.40694 | N/A | N/A | N/A | NR/12/516 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-07 19:48 | 2017-12-08 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.43819 | N/A | N/A | N/A | NR/12/702 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-08 08:27 | 2017-12-08 18:29 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/12/736 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-08 20:30 | 2017-12-09 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.47917 | N/A | N/A | N/A | NR/12/815 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[7 empty] | 2017-12-09 20:23 | 2017-12-10 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/12/911 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 423KV
[7 empty] | 2017-12-10 08:38 | 2017-12-10 17:55 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/12/942 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-10 21:09 | 2017-12-11 07:24 | -- | -- | -- | 0 | 0 | 0 | 0.42708 | N/A | N/A | N/A | NR/12/981 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-11 20:14 | 2017-12-12 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.42083 | N/A | N/A | N/A | NR/12/1073 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-12 20:18 | 2017-12-13 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.42431 | N/A | N/A | N/A | NR/12/1263 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-12-13 21:42 | 2017-12-14 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/12/1383 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-14 08:36 | 2017-12-14 18:25 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | NR/12/1430 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-14 21:35 | 2017-12-15 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/12/1515 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-15 20:09 | 2017-12-16 07:27 | -- | -- | -- | 0 | 0 | 0 | 0.47083 | N/A | N/A | N/A | NR/12/1630 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-16 20:19 | 2017-12-17 07:46 | -- | -- | -- | 0 | 0 | 0 | 0.47708 | N/A | N/A | N/A | NR/12/1739 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-17 08:52 | 2017-12-17 18:33 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/12/1777 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-17 20:14 | 2017-12-18 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/12/1829 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-18 19:56 | 2017-12-19 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.40139 | N/A | N/A | N/A | NR/12/1941 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-19 08:24 | 2017-12-19 18:39 | -- | -- | -- | 0 | 0 | 0 | 0.42708 | N/A | N/A | N/A | NR/12/1969 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-21 00:14 | 2017-12-21 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.26597 | N/A | N/A | N/A | NR/12/2193 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-21 08:53 | 2017-12-21 13:25 | -- | -- | -- | 0 | 0 | 0 | 0.18889 | N/A | N/A | N/A | NR/12/2220 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-21 20:11 | 2017-12-22 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/12/2307 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-22 19:57 | 2017-12-23 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/12/2430 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-23 20:12 | 2017-12-24 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/12/2563 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-24 20:55 | 2017-12-25 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.38403 | N/A | N/A | N/A | NR/12/2636 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-25 20:04 | 2017-12-26 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-26 20:05 | 2017-12-27 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NR/12/2850 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-12-27 21:48 | 2017-12-28 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/12/2978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-28 23:16 | 2017-12-29 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.27431 | N/A | N/A | N/A | NR/12/3084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-29 19:58 | 2017-12-30 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/12/4102 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-30 19:57 | 2017-12-31 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/12/4226 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-31 19:46 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.17639 | N/A | N/A | N/A | NR/12/4305 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[12 empty] | 0 | 0 | 0 | 1900-01-13 06:05 | [7 empty] | 100
1 | 40 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 41 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 42 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 43 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 44 | NR240024 | 400KV Moga-Hissar | 209.39 | NR2 |  | 2017-12-11 21:30 | 2017-12-11 21:52 | -- | -- | -- | 0.015278 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1087 | LEFT | LINE TRIPPED ON B-N FAULT. FLR MOGA : 103KM AND HISAR :107KM.
[7 empty] | 2017-12-11 23:55 | 2017-12-14 12:04 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 12:09 | N/A | N/A | N/A | NR/12/1097 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-14 20:53 | 2017-12-15 09:36 | -- | -- | -- | 0 | 0 | 0 | 0.52986 | N/A | N/A | N/A | NR/12/1513 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. HISSAR= 421KV
[12 empty] | 0.015278 | 0 | 0 | 1900-01-02 00:52 | [7 empty] | 99.95
1 | 45 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 |  | 2017-12-15 01:24 | 2017-12-15 03:03 | -- | -- | -- | 0.06875 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1519 | SRET | LINE TRIPPED DUE TO NGR BUCHOLTZ PROTECTION OF LINE REACTOR OPERATED AT FATEHABAD END.
[12 empty] | 0.06875 | 0 | 0 | 0 | [7 empty] | 99.78
1 | 46 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 |  | 2017-12-01 20:16 | 2017-12-02 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | N/A | N/A | N/A | NR/12/127 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-02 21:08 | 2017-12-03 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/12/213 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-03 20:16 | 2017-12-04 05:07 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | NR/12/281 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-04 20:08 | 2017-12-05 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/12/378 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-05 21:27 | 2017-12-06 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.32431 | N/A | N/A | N/A | NR/12/490 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-06 19:57 | 2017-12-07 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/12/582 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-08 20:28 | 2017-12-09 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/12/815 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-10 19:52 | 2017-12-11 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.45486 | N/A | N/A | N/A | NR/12/978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-11 21:39 | 2017-12-12 06:11 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/12/1084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 425KV
[7 empty] | 2017-12-12 21:38 | 2017-12-13 05:09 | -- | -- | -- | 0 | 0 | 0 | 0.31319 | N/A | N/A | N/A | NR/12/1267 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-13 21:39 | 2017-12-14 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.33056 | N/A | N/A | N/A | NR/12/1383 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-14 21:34 | 2017-12-15 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.31806 | N/A | N/A | N/A | NR/12/1515 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-15 20:17 | 2017-12-16 07:31 | -- | -- | -- | 0 | 0 | 0 | 0.46806 | N/A | N/A | N/A | NR/12/1630 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-17 20:08 | 2017-12-18 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | NR/12/1829 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 429KV
[7 empty] | 2017-12-18 20:04 | 2017-12-19 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/12/1941 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-19 21:49 | 2017-12-20 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/12/2067 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-21 00:20 | 2017-12-21 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.22222 | N/A | N/A | N/A | NR/12/2193 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-23 00:59 | 2017-12-23 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.19583 | N/A | N/A | N/A | NR/12/2455 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 429KV
[7 empty] | 2017-12-23 19:57 | 2017-12-24 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/12/2559 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-25 20:07 | 2017-12-26 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-26 21:04 | 2017-12-27 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/12/2859 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-27 19:55 | 2017-12-28 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/12/2969 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-28 23:21 | 2017-12-29 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.26319 | N/A | N/A | N/A | NR/12/3084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-29 20:00 | 2017-12-30 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.39514 | N/A | N/A | N/A | NR/12/4102 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-30 19:56 | 2017-12-31 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/12/4226 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[12 empty] | 0 | 0 | 0 | 1900-01-08 00:42 | [7 empty] | 100
1 | 47 | NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 48 | NR240031 | 400KV URI-WAGOORA-II | 94.99 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 49 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 |  | 2017-12-20 11:47 | 2017-12-20 14:47 | -- | -- | -- | 0.125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/2125 | OSPT | SD TAKEN TO ATTEND OIL LEAKAGE IN R-PH LINE CT.
[12 empty] | 0.125 | 0 | 0 | 0 | [7 empty] | 99.6
1 | 50 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 |  | 2017-12-12 00:51 | 2017-12-12 00:55 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM HIGH VOLTAGE. MOGA = 438KV
[7 empty] | 2017-12-12 00:55 | 2017-12-12 10:27 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/12/1105 | LVRD | LINE KEPT OPEN ON NRLDC FOR VOLTAGE REGULATION.
[12 empty] | 0 | 0 | 0.0027778 | 0.39722 | [7 empty] | 100
1 | 51 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 52 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 53 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 |  | 2017-12-07 19:53 | 2017-12-08 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.43819 | N/A | N/A | N/A | NR/12/702 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-09 20:16 | 2017-12-10 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/12/911 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-24 20:49 | 2017-12-25 08:03 | -- | -- | -- | 0 | 0 | 0 | 0.46806 | N/A | N/A | N/A | NR/12/2636 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 07:12 | [7 empty] | 100
1 | 54 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 55 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 |  | 2017-12-11 01:54 | 2017-12-12 06:36 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:42 | N/A | N/A | N/A | NR/12/989 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 425KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 04:42 | [7 empty] | 100
1 | 56 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 57 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 |  | 2017-12-26 08:36 | 2017-12-26 18:29 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/12/2776 | OSPD | SD TAKEN BY STERLITE FOR CROSSING OF 400KV D/C SAMBA-AMARGARH LINES.
[7 empty] | 2017-12-27 08:26 | 2017-12-27 17:41 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/12/2889 | OSPD | SD TAKEN BY STERLITE FOR CROSSING OF 400KV D/C SAMBA-AMARGARH LINES.
[12 empty] | 0 | 0 | 0 | 0.79722 | [7 empty] | 100
1 | 58 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 59 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 |  | 2017-12-01 | 2017-12-01 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.2625 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 431KV
[7 empty] | 2017-12-01 20:15 | 2017-12-02 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.4 | N/A | N/A | N/A | NR/12/127 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-02 21:08 | 2017-12-03 07:33 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/12/213 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-03 20:15 | 2017-12-04 07:02 | -- | -- | -- | 0 | 0 | 0 | 0.44931 | N/A | N/A | N/A | NR/12/281 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-04 20:07 | 2017-12-05 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | NR/12/378 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-05 19:56 | 2017-12-06 06:34 | -- | -- | -- | 0 | 0 | 0 | 0.44306 | N/A | N/A | N/A | NR/12/481 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 422KV
[7 empty] | 2017-12-06 19:58 | 2017-12-07 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.47222 | N/A | N/A | N/A | NR/12/582 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-07 19:52 | 2017-12-08 07:31 | -- | -- | -- | 0 | 0 | 0 | 0.48542 | N/A | N/A | N/A | NR/12/702 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-08 20:27 | 2017-12-09 08:17 | -- | -- | -- | 0 | 0 | 0 | 0.49306 | N/A | N/A | N/A | NR/12/815 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-09 20:16 | 2017-12-10 10:20 | -- | -- | -- | 0 | 0 | 0 | 0.58611 | N/A | N/A | N/A | NR/12/911 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-10 14:25 | 2017-12-11 10:46 | -- | -- | -- | 0 | 0 | 0 | 0.84792 | N/A | N/A | N/A | NR/12/966 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-11 19:54 | 2017-12-12 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.45208 | N/A | N/A | N/A | NR/12/1075 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-12 20:15 | 2017-12-13 06:41 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | NR/12/1263 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-13 11:00 | 2017-12-14 11:20 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 00:20 | N/A | N/A | N/A | NR/12/1319 | LCSD | SD TAKEN FOR BUS BAR EXTENSION WORK OF ICT-1 AND ICT-2 UNDER CONSTRUCTION AT GIS BANALA.
[7 empty] | 2017-12-15 21:36 | 2017-12-16 07:47 | -- | -- | -- | 0 | 0 | 0 | 0.42431 | N/A | N/A | N/A | NR/12/1632 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-16 09:59 | 2017-12-17 16:55 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:56 | N/A | N/A | N/A | NR/12/1671 | LCSD | SD TAKEN FOR BUS BAR EXTENSION WORK OF ICT-1 AND ICT-2 UNDER CONSTRUCTION AT GIS BANALA.
[7 empty] | 2017-12-17 21:59 | 2017-12-18 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.34444 | N/A | N/A | N/A | NR/12/1835 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-18 19:57 | 2017-12-19 06:34 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/12/1941 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-19 13:10 | 2017-12-20 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.73681 | N/A | N/A | N/A | NR/12/2009 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-20 20:08 | 2017-12-21 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.44028 | N/A | N/A | N/A | NR/12/2182 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 422KV
[7 empty] | 2017-12-21 20:30 | 2017-12-22 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/12/2307 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 422KV
[7 empty] | 2017-12-22 20:08 | 2017-12-23 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/12/2339 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-23 19:58 | 2017-12-24 07:19 | -- | -- | -- | 0 | 0 | 0 | 0.47292 | N/A | N/A | N/A | NR/12/2559 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-24 20:47 | 2017-12-25 09:43 | -- | -- | -- | 0 | 0 | 0 | 0.53889 | N/A | N/A | N/A | NR/12/2636 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-25 20:06 | 2017-12-26 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-26 21:03 | 2017-12-27 07:19 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | N/A | N/A | N/A | NR/12/2859 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-27 21:42 | 2017-12-28 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.35903 | N/A | N/A | N/A | NR/12/2978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-28 20:12 | 2017-12-29 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/12/3076 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-29 19:59 | 2017-12-30 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.41042 | N/A | N/A | N/A | NR/12/4102 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-30 19:54 | 2017-12-31 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/12/4226 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-31 21:23 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.10903 | N/A | N/A | N/A | NR/12/4314 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[12 empty] | 0 | 0 | 0 | 1900-01-14 06:55 | [7 empty] | 100
1 | 60 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 |  | 2017-12-12 09:30 | 2017-12-13 11:55 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 02:25 | N/A | N/A | N/A | NR/12/1169 | OSPD | SD TAKEN BY NTPC FOR GENERAL MAINT. WORK AT KOLDAM.
[12 empty] | 0 | 0 | 0 | 1899-12-31 02:25 | [7 empty] | 100
1 | 61 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 |  | 2017-12-03 01:09 | 2017-12-03 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.22014 | N/A | N/A | N/A | NR/12/218 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 424KV
[7 empty] | 2017-12-06 21:29 | 2017-12-07 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.34861 | N/A | N/A | N/A | NR/12/591 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 425KV
[7 empty] | 2017-12-08 00:04 | 2017-12-08 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.32222 | N/A | N/A | N/A | NR/12/717 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 430KV
[7 empty] | 2017-12-10 23:06 | 2017-12-11 07:19 | -- | -- | -- | 0 | 0 | 0 | 0.34236 | N/A | N/A | N/A | NR/12/984 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 430KV
[7 empty] | 2017-12-13 21:52 | 2017-12-14 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.34583 | N/A | N/A | N/A | NR/12/1384 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 424KV
[7 empty] | 2017-12-16 21:59 | 2017-12-17 07:51 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/12/1746 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 426KV
[7 empty] | 2017-12-21 21:38 | 2017-12-22 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/12/2310 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 424 KV
[7 empty] | 2017-12-23 22:30 | 2017-12-24 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.31875 | N/A | N/A | N/A | NR/12/2570 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 419KV
[7 empty] | 2017-12-29 20:56 | 2017-12-30 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/12/4110 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422 KV
[12 empty] | 0 | 0 | 0 | 1900-01-02 01:12 | [7 empty] | 100
1 | 62 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 |  | 2017-12-01 | 2017-12-01 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.24514 | N/A | N/A | N/A | NR/11/3463 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 421KV
[7 empty] | 2017-12-01 21:23 | 2017-12-02 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/12/131 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 420KV
[7 empty] | 2017-12-04 21:57 | 2017-12-05 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | N/A | N/A | N/A | NR/12/382 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 428KV
[7 empty] | 2017-12-05 23:30 | 2017-12-06 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.26389 | N/A | N/A | N/A | NR/12/493 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 427KV
[7 empty] | 2017-12-11 19:59 | 2017-12-12 12:09 | -- | -- | -- | 0 | 0 | 0 | 0.67361 | N/A | N/A | N/A | NR/12/1075 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 425KV
[7 empty] | 2017-12-12 21:33 | 2017-12-13 05:11 | -- | -- | -- | 0 | 0 | 0 | 0.31806 | N/A | N/A | N/A | NR/12/1267 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 430KV
[7 empty] | 2017-12-14 21:34 | 2017-12-15 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.35347 | N/A | N/A | N/A | NR/12/1515 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 430KV
[7 empty] | 2017-12-15 21:41 | 2017-12-16 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.41042 | N/A | N/A | N/A | NR/12/1632 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 424KV
[7 empty] | 2017-12-22 21:31 | 2017-12-23 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | N/A | N/A | N/A | NR/12/2448 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 427KV
[7 empty] | 2017-12-24 21:29 | 2017-12-25 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.36389 | N/A | N/A | N/A | NR/12/2640 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 426KV
[7 empty] | 2017-12-28 20:13 | 2017-12-29 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NR/12/3076 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. ABDULLAPUR= 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-03 00:25 | [7 empty] | 100
1 | 63 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 |  | 2017-12-01 | 2017-12-01 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.22292 | N/A | N/A | N/A | NR/11/3441 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-12-02 19:59 | 2017-12-03 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/12/202 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-12-04 20:07 | 2017-12-05 05:16 | -- | -- | -- | 0 | 0 | 0 | 0.38125 | N/A | N/A | N/A | NR/12/378 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 423KV
[7 empty] | 2017-12-09 19:48 | 2017-12-10 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/12/905 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422KV
[7 empty] | 2017-12-11 19:41 | 2017-12-12 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/12/1072 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 425KV
[7 empty] | 2017-12-13 19:46 | 2017-12-14 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/12/1375 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-12-16 20:06 | 2017-12-17 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.3875 | N/A | N/A | N/A | NR/12/1738 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-18 20:49 | 2017-12-19 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/12/1945 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 424KV
[7 empty] | 2017-12-20 19:56 | 2017-12-21 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NL/12/2177 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 423KV
[7 empty] | 2017-12-23 20:05 | 2017-12-24 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/12/2557 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422 KV
[7 empty] | 2017-12-25 19:59 | 2017-12-26 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/12/2741 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 421 KV
[7 empty] | 2017-12-27 19:53 | 2017-12-28 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/12/2969 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422 KV
[7 empty] | 2017-12-28 11:02 | 2017-12-28 14:11 | -- | -- | -- | 0.13125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/3025 | OSPT | SD TAKEN FOR ATTENDING HOT SPOT AT TOWER NO. 67.
[7 empty] | 2017-12-29 19:57 | 2017-12-30 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/12/4099 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422 KV
[7 empty] | 2017-12-31 19:48 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.175 | N/A | N/A | N/A | NR/12/4305 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 425 KV
[12 empty] | 0.13125 | 0 | 0 | 1900-01-04 03:25 | [7 empty] | 99.58
1 | 64 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 |  | 2017-12-01 20:05 | 2017-12-02 05:13 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/12/125 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-03 20:17 | 2017-12-04 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/12/279 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 421KV
[7 empty] | 2017-12-05 20:04 | 2017-12-06 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/12/482 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 423KV
[7 empty] | 2017-12-06 19:50 | 2017-12-07 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/12/582 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422KV
[7 empty] | 2017-12-07 19:48 | 2017-12-08 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/12/701 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422KV
[7 empty] | 2017-12-08 20:01 | 2017-12-09 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.39097 | N/A | N/A | N/A | NR/12/813 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-10 19:39 | 2017-12-11 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/12/977 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-12 19:53 | 2017-12-13 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | NR/12/1258 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 427KV
[7 empty] | 2017-12-14 19:48 | 2017-12-15 05:17 | -- | -- | -- | 0 | 0 | 0 | 0.39514 | N/A | N/A | N/A | NR/12/1509 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-15 19:27 | 2017-12-16 05:10 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/12/1621 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-17 20:10 | 2017-12-18 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/12/1826 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-12-19 20:34 | 2017-12-20 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/12/2063 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 423KV
[7 empty] | 2017-12-21 19:53 | 2017-12-22 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/12/2304 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 420 KV
[7 empty] | 2017-12-22 19:52 | 2017-12-23 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.40556 | N/A | N/A | N/A | NR/12/2430 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422 KV
[7 empty] | 2017-12-24 20:01 | 2017-12-25 05:27 | -- | -- | -- | 0 | 0 | 0 | 0.39306 | N/A | N/A | N/A | NR/12/2629 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 420 KV
[7 empty] | 2017-12-26 19:54 | 2017-12-27 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/12/2849 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422 KV
[7 empty] | 2017-12-28 19:56 | 2017-12-29 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/12/3073 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 422 KV
[7 empty] | 2017-12-30 19:58 | 2017-12-31 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NR/12/4225 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 421 KV
[12 empty] | 0 | 0 | 0 | 1900-01-06 03:30 | [7 empty] | 100
1 | 65 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 |  | 2017-12-11 23:55 | 2017-12-12 10:25 | -- | -- | -- | 0 | 0 | 0 | 0.4375 | N/A | N/A | N/A | NR/12/1098 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. DIPALPUR = 438KV
[7 empty] | 2017-12-20 08:50 | 2017-12-20 20:16 | -- | -- | -- | 0.47639 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/2091 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.47639 | 0 | 0 | 0.4375 | [7 empty] | 98.46
1 | 66 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 |  | 2017-12-08 10:02 | 2017-12-08 21:13 | -- | -- | -- | 0 | 0 | 0 | 0.46597 | N/A | N/A | N/A | NR/12/744 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATORS.
[7 empty] | 2017-12-11 23:55 | 2017-12-11 23:59 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM HIGH VOLTAGE. DIPALPUR = 438KV
[7 empty] | 2017-12-11 23:59 | 2017-12-12 08:22 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/12/1105 | LVRD | LINE KEPT OPEN FOR VOLTAGE REGULATION.
[12 empty] | 0 | 0 | 0.0027778 | 0.81528 | [7 empty] | 100
1 | 67 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 |  | 2017-12-01 | 2017-12-01 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.25 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[7 empty] | 2017-12-01 07:46 | 2017-12-01 19:26 | -- | -- | -- | 0 | 0 | 0 | 0.48611 | N/A | N/A | N/A | NR/12/20 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-01 21:14 | 2017-12-02 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.33194 | N/A | N/A | N/A | NR/12/131 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-12-02 21:10 | 2017-12-03 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.375 | N/A | N/A | N/A | NR/12/213 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-03 08:31 | 2017-12-03 16:11 | -- | -- | -- | 0 | 0 | 0 | 0.31944 | N/A | N/A | N/A | NR/12/240 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-03 20:08 | 2017-12-04 07:55 | -- | -- | -- | 0 | 0 | 0 | 0.49097 | N/A | N/A | N/A | NR/12/279 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-04 20:09 | 2017-12-05 08:17 | -- | -- | -- | 0 | 0 | 0 | 0.50556 | N/A | N/A | N/A | NR/12/378 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-05 19:57 | 2017-12-06 07:24 | -- | -- | -- | 0 | 0 | 0 | 0.47708 | N/A | N/A | N/A | NR/12/481 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-06 19:46 | 2017-12-07 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/12/582 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-07 19:46 | 2017-12-08 07:35 | -- | -- | -- | 0 | 0 | 0 | 0.49236 | N/A | N/A | N/A | NR/12/702 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-08 20:25 | 2017-12-09 07:59 | -- | -- | -- | 0 | 0 | 0 | 0.48194 | N/A | N/A | N/A | NR/12/815 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[7 empty] | 2017-12-09 20:17 | 2017-12-10 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.39653 | N/A | N/A | N/A | NR/12/911 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 423KV
[7 empty] | 2017-12-10 14:24 | 2017-12-12 04:17 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 13:53 | N/A | N/A | N/A | NR/12/966 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-13 21:37 | 2017-12-14 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/12/1383 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-14 21:33 | 2017-12-15 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.34792 | N/A | N/A | N/A | NR/12/1515 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-16 01:18 | 2017-12-16 07:23 | -- | -- | -- | 0 | 0 | 0 | 0.25347 | N/A | N/A | N/A | NR/12/1638 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-16 21:56 | 2017-12-17 07:36 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/12/1746 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-17 21:03 | 2017-12-18 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.35278 | N/A | N/A | N/A | NR/12/1832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-18 19:57 | 2017-12-19 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/12/1941 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-21 20:10 | 2017-12-22 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/12/2307 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-22 19:43 | 2017-12-23 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/12/2430 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-23 22:32 | 2017-12-24 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | N/A | N/A | N/A | NR/12/2570 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-24 20:50 | 2017-12-25 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.38403 | N/A | N/A | N/A | NR/12/2636 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-25 20:02 | 2017-12-26 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.39514 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-26 20:03 | 2017-12-27 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NR/12/2850 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-12-27 19:51 | 2017-12-28 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.42361 | N/A | N/A | N/A | NR/12/2969 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 423KV
[7 empty] | 2017-12-28 20:14 | 2017-12-29 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/12/3076 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 423KV
[7 empty] | 2017-12-29 19:58 | 2017-12-30 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/12/4102 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-30 19:52 | 2017-12-31 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/12/4226 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 422KV
[7 empty] | 2017-12-31 21:20 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.11111 | N/A | N/A | N/A | NR/12/4314 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[12 empty] | 0 | 0 | 0 | 1900-01-11 20:17 | [7 empty] | 100
1 | 68 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 |  | 2017-12-01 | 2017-12-01 07:17 | -- | -- | -- | 0 | 0 | 0 | 0.30347 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 433KV
[7 empty] | 2017-12-01 20:17 | 2017-12-02 08:40 | -- | -- | -- | 0 | 0 | 0 | 0.51597 | N/A | N/A | N/A | NR/12/127 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-02 08:40 | 2017-12-02 18:37 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/12/154 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-03 00:01 | 2017-12-03 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.25486 | N/A | N/A | N/A | NR/12/216 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-04 00:25 | 2017-12-04 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.22292 | N/A | N/A | N/A | NR/12/288 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 434KV
[7 empty] | 2017-12-04 08:02 | 2017-12-04 17:41 | -- | -- | -- | 0 | 0 | 0 | 0.40208 | N/A | N/A | N/A | NR/12/307 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[7 empty] | 2017-12-05 23:27 | 2017-12-06 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.29444 | N/A | N/A | N/A | NR/12/493 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-06 23:26 | 2017-12-07 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.275 | N/A | N/A | N/A | NR/12/593 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-10 21:08 | 2017-12-11 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/12/981 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-11 13:04 | 2017-12-11 16:11 | -- | -- | -- | 0 | 0 | 0 | 0.12986 | N/A | N/A | N/A | NR/12/1034 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-11 23:46 | 2017-12-16 09:40 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 09:54 | N/A | N/A | N/A | NR/12/1097 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-16 23:46 | 2017-12-18 10:25 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:39 | N/A | N/A | N/A | NR/12/1747 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-18 21:15 | 2017-12-21 10:38 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 13:23 | N/A | N/A | N/A | NR/12/1946 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-21 21:39 | 2017-12-22 07:52 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/12/2310 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-12-22 21:49 | 2017-12-23 07:16 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/12/2448 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-29 23:58 | 2017-12-30 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.22917 | N/A | N/A | N/A | NR/12/4122 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[12 empty] | 0 | 0 | 0 | 1900-01-11 16:05 | [7 empty] | 100
1 | 69 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 70 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 71 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 |  | 2017-12-01 | 2017-12-01 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.26181 | N/A | N/A | N/A | NR/11/3395 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 423KV
[7 empty] | 2017-12-01 21:12 | 2017-12-04 09:50 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 12:38 | N/A | N/A | N/A | NR/12/131 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 421KV
[7 empty] | 2017-12-05 19:55 | 2017-12-06 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.48403 | N/A | N/A | N/A | NR/12/481 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 421KV
[7 empty] | 2017-12-06 19:51 | 2017-12-07 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.47847 | N/A | N/A | N/A | NR/12/582 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-07 19:51 | 2017-12-08 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.48681 | N/A | N/A | N/A | NR/12/702 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-08 20:26 | 2017-12-09 08:16 | -- | -- | -- | 0 | 0 | 0 | 0.49306 | N/A | N/A | N/A | NR/12/815 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-12-09 20:19 | 2017-12-10 10:19 | -- | -- | -- | 0 | 0 | 0 | 0.58333 | N/A | N/A | N/A | NR/12/911 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 423KV
[7 empty] | 2017-12-10 19:50 | 2017-12-11 12:56 | -- | -- | -- | 0 | 0 | 0 | 0.7125 | N/A | N/A | N/A | NR/12/978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 421KV
[7 empty] | 2017-12-11 19:53 | 2017-12-12 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.45417 | N/A | N/A | N/A | NR/12/1075 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 423KV
[7 empty] | 2017-12-12 20:16 | 2017-12-13 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | N/A | N/A | N/A | NR/12/1263 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-12-14 19:45 | 2017-12-15 09:16 | -- | -- | -- | 0 | 0 | 0 | 0.56319 | N/A | N/A | N/A | NR/12/1509 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-15 21:35 | 2017-12-16 07:39 | -- | -- | -- | 0 | 0 | 0 | 0.41944 | N/A | N/A | N/A | NR/12/1632 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-16 20:21 | 2017-12-17 07:55 | -- | -- | -- | 0 | 0 | 0 | 0.48194 | N/A | N/A | N/A | NR/12/1739 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-17 20:10 | 2017-12-18 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.41875 | N/A | N/A | N/A | NR/12/1829 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 426KV
[7 empty] | 2017-12-18 19:56 | 2017-12-19 06:32 | -- | -- | -- | 0 | 0 | 0 | 0.44167 | N/A | N/A | N/A | NR/12/1941 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 425KV
[7 empty] | 2017-12-19 21:47 | 2017-12-20 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/12/2067 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-12-20 20:07 | 2017-12-21 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/12/2182 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-21 20:30 | 2017-12-22 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.39861 | N/A | N/A | N/A | NR/12/2307 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-22 20:07 | 2017-12-23 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/12/2339 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-12-23 19:59 | 2017-12-25 08:16 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:17 | N/A | N/A | N/A | NR/12/2559 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-12-25 20:10 | 2017-12-26 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.43611 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-26 21:00 | 2017-12-27 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/12/2859 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-27 21:43 | 2017-12-28 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.35972 | N/A | N/A | N/A | NR/12/2978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-28 20:16 | 2017-12-29 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/12/3076 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 420KV
[7 empty] | 2017-12-29 19:57 | 2017-12-30 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.47778 | N/A | N/A | N/A | NR/12/4102 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 422KV
[7 empty] | 2017-12-30 19:51 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:09 | N/A | N/A | N/A | NR/12/4226 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. AMRITSAR= 421KV
[12 empty] | 0 | 0 | 0 | 1900-01-14 16:16 | [7 empty] | 100
1 | 72 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 73 | NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 |  | 2017-12-12 12:28 | 2017-12-12 12:36 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1212 | LNCC | LINE TRIPPED ON R-N FAULT DUE TO HEAVY SNOWFALL IN KASHMIR VALLEY. FLR NEW WANPOH : 27KM & KISHENPUR : 108km.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 74 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 75 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 76 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 77 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 |  | 2017-12-13 11:08 | 2017-12-13 11:38 | -- | -- | -- | 0.020833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1327 | OSFT | LINE TRPPED DURING 220V DCDB SOURCE-I EXTENSION WORK FOR ICT-III UNDER CONSTRUCTION AT HAMIRPUR.
[7 empty] | 2017-12-15 15:49 | 2017-12-15 17:10 | -- | -- | -- | 0 | 0 | 0 | 0.05625 | N/A | N/A | N/A | NR/12/1590 | LCSD | SD TAKEN FOR REMOVAL OF OPGW ROPE WHICHV GOT STUCK AT MIDDLE CONDUCTOR WHILE LAYING OPGW UNDER ULDC SCHEME BETWEEN LOC NO 175 TO 176.
[7 empty] | 2017-12-24 17:21 | 2017-12-24 18:21 | -- | -- | -- | 0 | 0.041667 | 0 | 0 | N/A | N/A | N/A | NR/12/2622 | OMSU | LINE TRIPPED ON R-N FAULT DUE TO PILOT WIRE HANGING WHILE LAYING OPGW UNDER ULDC SCHEME. FLR BANALA : 3.71 KA , 66.8 KMS.
[12 empty] | 0.020833 | 0.041667 | 0 | 0.05625 | [7 empty] | 99.93
1 | 78 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 |  | 2017-12-01 | 2017-12-01 05:10 | -- | -- | -- | 0 | 0 | 0 | 0.21528 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-02 20:18 | 2017-12-03 05:01 | -- | -- | -- | 0 | 0 | 0 | 0.36319 | N/A | N/A | N/A | NR/12/206 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-16 08:18 | 2017-12-16 16:11 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/12/1649 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-18 09:07 | 2017-12-18 17:15 | -- | -- | -- | 0 | 0 | 0 | 0.33889 | N/A | N/A | N/A | NR/12/1863 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-19 08:25 | 2017-12-19 17:12 | -- | -- | -- | 0 | 0 | 0 | 0.36597 | N/A | N/A | N/A | NR/12/1965 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[12 empty] | 0 | 0 | 0 | 1899-12-31 14:41 | [7 empty] | 100
1 | 79 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 |  | 2017-12-01 | 2017-12-01 04:58 | -- | -- | -- | 0 | 0 | 0 | 0.20694 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-01 21:20 | 2017-12-02 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.33264 | N/A | N/A | N/A | NR/12/131 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-02 20:20 | 2017-12-03 04:44 | -- | -- | -- | 0 | 0 | 0 | 0.35 | N/A | N/A | N/A | NR/12/207 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-04 21:43 | 2017-12-05 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.32431 | N/A | N/A | N/A | NR/12/382 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-09 20:15 | 2017-12-10 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.39861 | N/A | N/A | N/A | NR/12/911 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-12 21:33 | 2017-12-13 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.33403 | N/A | N/A | N/A | NR/12/1267 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-16 22:00 | 2017-12-17 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.32778 | N/A | N/A | N/A | NR/12/1746 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-17 21:06 | 2017-12-18 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.34375 | N/A | N/A | N/A | NR/12/1832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-18 20:31 | 2017-12-19 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/12/1945 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-20 08:04 | 2017-12-20 17:03 | -- | -- | -- | 0 | 0 | 0 | 0.37431 | N/A | N/A | N/A | NR/12/2086 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-21 08:22 | 2017-12-21 17:08 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/12/2218 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-21 21:36 | 2017-12-22 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/12/2310 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-22 08:15 | 2017-12-22 17:01 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/12/2339 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-23 08:21 | 2017-12-23 17:17 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/12/2475 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-23 22:29 | 2017-12-24 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.29236 | N/A | N/A | N/A | NR/12/2570 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 421KV
[7 empty] | 2017-12-26 00:22 | 2017-12-26 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.22292 | N/A | N/A | N/A | NR/12/2753 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 422KV
[7 empty] | 2017-12-26 21:06 | 2017-12-27 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/12/2859 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-28 23:18 | 2017-12-29 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.26875 | N/A | N/A | N/A | NR/12/3084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-29 20:52 | 2017-12-30 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/12/4110 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 423KV
[7 empty] | 2017-12-31 21:30 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.10417 | N/A | N/A | N/A | NR/12/4314 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 430KV
[12 empty] | 0 | 0 | 0 | 1900-01-05 10:10 | [7 empty] | 100
1 | 80 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 |  | 2017-12-14 09:49 | 2017-12-15 18:40 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:51 | N/A | N/A | N/A | NR/12/1439 | OSPD | SD TAKEN BY NTPC, KOLDAM FOR AMP WORKS.
[12 empty] | 0 | 0 | 0 | 1899-12-31 08:51 | [7 empty] | 100
1 | 81 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 |  | 2017-12-01 | 2017-12-01 05:08 | -- | -- | -- | 0 | 0 | 0 | 0.21389 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-02 20:22 | 2017-12-03 05:04 | -- | -- | -- | 0 | 0 | 0 | 0.3625 | N/A | N/A | N/A | NR/12/206 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-11 08:33 | 2017-12-11 17:01 | -- | -- | -- | 0 | 0 | 0 | 0.35278 | N/A | N/A | N/A | NR/12/1009 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-12 08:35 | 2017-12-12 16:49 | -- | -- | -- | 0 | 0 | 0 | 0.34306 | N/A | N/A | N/A | NR/12/1164 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-13 08:17 | 2017-12-13 16:34 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | N/A | N/A | N/A | NR/12/1296 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-14 08:10 | 2017-12-14 16:02 | -- | -- | -- | 0 | 0 | 0 | 0.32778 | N/A | N/A | N/A | NR/12/1425 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-15 08:49 | 2017-12-15 16:22 | -- | -- | -- | 0 | 0 | 0 | 0.31458 | N/A | N/A | N/A | NR/12/1536 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[12 empty] | 0 | 0 | 0 | 1900-01-01 06:14 | [7 empty] | 100
1 | 82 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 |  | 2017-12-01 | 2017-12-01 05:13 | -- | -- | -- | 0 | 0 | 0 | 0.21736 | N/A | N/A | N/A | NR/11/3450 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-02 20:20 | 2017-12-03 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.375 | N/A | N/A | N/A | NR/12/207 | OSPD | SD TAKEN BY SJVNL RAMPUR FOR MAINTENANCE & GIS BB RECTIFICATION WORKS AT THEIR END.
[7 empty] | 2017-12-03 20:18 | 2017-12-04 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/12/281 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 427KV
[7 empty] | 2017-12-05 21:24 | 2017-12-06 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.33056 | N/A | N/A | N/A | NR/12/490 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-06 21:50 | 2017-12-07 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.31667 | N/A | N/A | N/A | NR/12/591 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-07 20:23 | 2017-12-08 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.38611 | N/A | N/A | N/A | NR/12/707 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-08 20:53 | 2017-12-09 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.38125 | N/A | N/A | N/A | NR/12/818 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-10 19:55 | 2017-12-11 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.39653 | N/A | N/A | N/A | NR/12/978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 424KV
[7 empty] | 2017-12-11 19:54 | 2017-12-12 05:10 | -- | -- | -- | 0 | 0 | 0 | 0.38611 | N/A | N/A | N/A | NR/12/1075 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-13 21:41 | 2017-12-14 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/12/1383 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-14 21:37 | 2017-12-15 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.32153 | N/A | N/A | N/A | NR/12/1515 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-15 20:16 | 2017-12-16 05:06 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/12/1630 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-19 20:23 | 2017-12-20 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/12/2063 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 425KV
[7 empty] | 2017-12-21 00:18 | 2017-12-21 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.21597 | N/A | N/A | N/A | NR/12/2193 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-22 21:32 | 2017-12-23 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.34167 | N/A | N/A | N/A | NR/12/2448 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[7 empty] | 2017-12-24 21:28 | 2017-12-25 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/12/2640 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 422KV
[7 empty] | 2017-12-27 08:04 | 2017-12-27 17:00 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/12/2888 | OSPD | SD TAKEN BY SJVNL, RAMPUR FOR GENERAL MAINTENANCE WORKS AT THEIR END.
[7 empty] | 2017-12-27 21:46 | 2017-12-28 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.31806 | N/A | N/A | N/A | NR/12/2978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 428KV
[7 empty] | 2017-12-28 09:25 | 2017-12-28 16:48 | -- | -- | -- | 0 | 0 | 0 | 0.30764 | N/A | N/A | N/A | NR/12/3012 | OSPD | SD TAKEN BY SJVNL, RAMPUR FOR GENERAL MAINTENANCE WORKS AT THEIR END.
[7 empty] | 2017-12-30 21:42 | 2017-12-31 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.32778 | N/A | N/A | N/A | NR/12/4236 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. NALAGARH= 426KV
[12 empty] | 0 | 0 | 0 | 1900-01-05 19:25 | [7 empty] | 100
1 | 83 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 |  | 2017-12-31 20:46 | 2017-12-31 23:20 | -- | -- | -- | 0 | 0.10694 | 0 | 0 | N/A | N/A | N/A | NR/12/4317 | OMSU | LINE TRIPPED DUE TO DT RECEIVED AT PANCHKULA FROM BBMB DEHAR.
[12 empty] | 0 | 0.10694 | 0 | 0 | [7 empty] | 100
1 | 84 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 |  | 2017-12-05 00:09 | 2017-12-05 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.225 | N/A | N/A | N/A | NR/12/387 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA=422KV.
[7 empty] | 2017-12-06 00:32 | 2017-12-06 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.225 | N/A | N/A | N/A | NR/12/494 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-12-10 23:14 | 2017-12-11 07:05 | -- | -- | -- | 0 | 0 | 0 | 0.32708 | N/A | N/A | N/A | NR/12/984 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-12-11 23:15 | 2017-12-12 07:21 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/12/1091 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA=424KV.
[7 empty] | 2017-12-12 11:35 | 2017-12-12 12:57 | -- | -- | -- | 0 | 0.056944 | 0 | 0 | N/A | N/A | N/A | NR/12/1210 | OMSU | LINE TRIPPED FROM BBMB DEHAR ONLY. TRIPPING EXTENDED FROM DEHAR END DURING TESTING OF 400KV BUS-BAR-1 WHICH IS UNDER SD AT DEHAR.
[7 empty] | 2017-12-16 01:21 | 2017-12-16 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.225 | N/A | N/A | N/A | NR/12/1638 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 427KV
[7 empty] | 2017-12-16 23:46 | 2017-12-17 06:54 | -- | -- | -- | 0 | 0 | 0 | 0.29722 | N/A | N/A | N/A | NR/12/1747 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-12-18 00:32 | 2017-12-18 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.23472 | N/A | N/A | N/A | NR/12/1836 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-26 08:31 | 2017-12-26 18:43 | -- | -- | -- | 0 | 0 | 0 | 0.425 | N/A | N/A | N/A | NR/12/2773 | OSPD | SD TAKEN BY BBMB FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[12 empty] | 0 | 0.056944 | 0 | 1900-01-01 07:07 | [7 empty] | 100
1 | 85 | NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 86 | NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 87 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 |  | 2017-12-11 21:26 | 2017-12-12 07:03 | -- | -- | -- | 0 | 0 | 0 | 0.40069 | N/A | N/A | N/A | NR/12/1084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-12-13 00:39 | 2017-12-13 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.25069 | N/A | N/A | N/A | NR/12/1270 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[12 empty] | 0 | 0 | 0 | 0.65139 | [7 empty] | 100
1 | 88 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 89 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 |  | 2017-12-01 | 2017-12-01 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.26944 | N/A | N/A | N/A | NR/11/3337 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-02 01:15 | 2017-12-02 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.20347 | N/A | N/A | N/A | NR/12/138 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-02 20:56 | 2017-12-04 06:48 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:52 | N/A | N/A | N/A | NR/12/211 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-04 21:55 | 2017-12-05 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/12/382 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-05 20:49 | 2017-12-06 06:46 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/12/485 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-06 09:36 | 2017-12-06 19:55 | -- | -- | -- | 0 | 0 | 0 | 0.42986 | N/A | N/A | N/A | NR/12/526 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATORS.
[7 empty] | 2017-12-06 21:30 | 2017-12-07 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/12/591 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 435KV
[7 empty] | 2017-12-07 22:03 | 2017-12-08 07:46 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/12/714 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-08 21:03 | 2017-12-09 07:55 | -- | -- | -- | 0 | 0 | 0 | 0.45278 | N/A | N/A | N/A | NR/12/819 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-09 23:59 | 2017-12-10 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.26458 | N/A | N/A | N/A | NR/12/926 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 431KV
[7 empty] | 2017-12-11 13:11 | 2017-12-12 07:13 | -- | -- | -- | 0 | 0 | 0 | 0.75139 | N/A | N/A | N/A | NR/12/1034 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 434KV
[7 empty] | 2017-12-12 20:03 | 2017-12-13 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.44444 | N/A | N/A | N/A | NR/12/1260 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 427KV
[7 empty] | 2017-12-13 19:55 | 2017-12-14 10:33 | -- | -- | -- | 0 | 0 | 0 | 0.60972 | N/A | N/A | N/A | NR/12/1377 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-14 19:51 | 2017-12-15 07:39 | -- | -- | -- | 0 | 0 | 0 | 0.49167 | N/A | N/A | N/A | NR/12/1509 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 425KV
[7 empty] | 2017-12-15 20:19 | 2017-12-16 07:39 | -- | -- | -- | 0 | 0 | 0 | 0.47222 | N/A | N/A | N/A | NR/12/1630 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-16 13:14 | 2017-12-17 08:01 | -- | -- | -- | 0 | 0 | 0 | 0.78264 | N/A | N/A | N/A | NR/12/1695 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-17 13:51 | 2017-12-18 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.65833 | N/A | N/A | N/A | NR/12/1796 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-18 21:27 | 2017-12-19 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.34167 | N/A | N/A | N/A | NR/12/1946 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-20 20:15 | 2017-12-21 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/12/2182 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-22 20:18 | 2017-12-23 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/12/2339 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-23 20:14 | 2017-12-24 07:21 | -- | -- | -- | 0 | 0 | 0 | 0.46319 | N/A | N/A | N/A | NR/12/2563 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-24 13:49 | 2017-12-26 05:33 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:44 | N/A | N/A | N/A | NR/12/2611 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 433KV
[7 empty] | 2017-12-26 21:37 | 2017-12-27 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | N/A | N/A | N/A | NR/12/2860 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 426KV
[7 empty] | 2017-12-28 10:11 | 2017-12-28 19:13 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/12/3016 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATORS.
[7 empty] | 2017-12-30 23:55 | 2017-12-31 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.2625 | N/A | N/A | N/A | NR/12/4238 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-31 20:01 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.16597 | N/A | N/A | N/A | NR/12/4307 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[12 empty] | 0 | 0 | 0 | 1900-01-12 04:57 | [7 empty] | 100
1 | 90 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 |  | 2017-12-02 07:17 | 2017-12-02 07:35 | -- | -- | -- | 0.0125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/150 | LEFT | LINE TRIPPED ON R-N FAULT. FLR KURUKSHETRA : 38.4KM & SONEPAT : 66.75KM.
[7 empty] | 2017-12-07 09:54 | 2017-12-07 20:58 | -- | -- | -- | 0 | 0 | 0 | 0.46111 | N/A | N/A | N/A | NR/12/622 | LCSD | SD TAKEN FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATORS.
[7 empty] | 2017-12-10 21:15 | 2017-12-11 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/12/981 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 425KV
[7 empty] | 2017-12-19 21:48 | 2017-12-20 07:01 | -- | -- | -- | 0 | 0 | 0 | 0.38403 | N/A | N/A | N/A | NR/12/2067 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 431KV
[7 empty] | 2017-12-27 21:54 | 2017-12-28 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/12/2978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[12 empty] | 0.0125 | 0 | 0 | 1899-12-31 14:29 | [7 empty] | 99.96
1 | 91 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 |  | 2017-12-01 | 2017-12-01 09:45 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/11/2828 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-01 20:54 | 2017-12-02 09:21 | -- | -- | -- | 0 | 0 | 0 | 0.51875 | N/A | N/A | N/A | NR/12/129 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-02 20:07 | 2017-12-04 06:53 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:46 | N/A | N/A | N/A | NR/12/205 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-04 20:12 | 2017-12-05 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.43889 | N/A | N/A | N/A | NR/12/378 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 435KV
[7 empty] | 2017-12-05 13:06 | 2017-12-06 07:45 | -- | -- | -- | 0 | 0 | 0 | 0.77708 | N/A | N/A | N/A | NR/12/442 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 431KV
[7 empty] | 2017-12-06 19:58 | 2017-12-07 07:38 | -- | -- | -- | 0 | 0 | 0 | 0.48611 | N/A | N/A | N/A | NR/12/582 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 425KV
[7 empty] | 2017-12-07 19:51 | 2017-12-08 07:43 | -- | -- | -- | 0 | 0 | 0 | 0.49444 | N/A | N/A | N/A | NR/12/702 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-08 21:05 | 2017-12-09 07:50 | -- | -- | -- | 0 | 0 | 0 | 0.44792 | N/A | N/A | N/A | NR/12/820 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-09 20:32 | 2017-12-13 07:20 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 10:48 | N/A | N/A | N/A | NR/12/920 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-13 13:18 | 2017-12-17 07:52 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 18:34 | N/A | N/A | N/A | NR/12/1336 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-17 13:41 | 2017-12-21 06:33 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 16:52 | N/A | N/A | N/A | NR/12/1796 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-21 21:42 | 2017-12-22 08:02 | -- | -- | -- | 0 | 0 | 0 | 0.43056 | N/A | N/A | N/A | NR/12/2310 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 427KV
[7 empty] | 2017-12-22 20:10 | 2017-12-24 07:26 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:16 | N/A | N/A | N/A | NR/12/2339 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-24 13:31 | 2017-12-25 07:46 | -- | -- | -- | 0 | 0 | 0 | 0.76042 | N/A | N/A | N/A | NR/12/2610 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 433KV
[7 empty] | 2017-12-25 20:11 | 2017-12-26 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.39653 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-26 20:10 | 2017-12-27 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/12/2850 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-27 19:49 | 2017-12-28 09:10 | -- | -- | -- | 0 | 0 | 0 | 0.55625 | N/A | N/A | N/A | NR/12/2969 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 427KV
[7 empty] | 2017-12-28 14:47 | 2017-12-28 15:16 | -- | -- | -- | 0.020139 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/3044 | OSFT | LINE TRIPPED DURING DC E/F DETECTION WORK AT JALANDHAR END.
[7 empty] | 2017-12-28 20:20 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 03:40 | N/A | N/A | N/A | NR/12/3076 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[12 empty] | 0.020139 | 0 | 0 | 1900-01-22 02:44 | [7 empty] | 99.94
1 | 92 | NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 93 | NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 |  | 2017-12-01 | 2017-12-04 06:44 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 06:44 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-04 20:08 | 2017-12-05 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/12/378 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 435KV
[7 empty] | 2017-12-05 20:52 | 2017-12-10 06:18 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 09:26 | N/A | N/A | N/A | NR/12/485 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-10 14:35 | 2017-12-16 09:33 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 18:58 | N/A | N/A | N/A | NR/12/966 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-16 21:56 | 2017-12-18 06:48 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:52 | N/A | N/A | N/A | NR/12/1746 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-18 21:23 | 2017-12-19 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.33889 | N/A | N/A | N/A | NR/12/1946 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-19 13:13 | 2017-12-20 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.72708 | N/A | N/A | N/A | NR/12/2009 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-20 20:07 | 2017-12-23 07:16 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 11:09 | N/A | N/A | N/A | NR/12/2182 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-23 20:13 | 2017-12-25 09:56 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 13:43 | N/A | N/A | N/A | NR/12/2563 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-25 20:13 | 2017-12-26 08:52 | -- | -- | -- | 0 | 0 | 0 | 0.52708 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-26 13:31 | 2017-12-27 09:57 | -- | -- | -- | 0 | 0 | 0 | 0.85139 | N/A | N/A | N/A | NR/12/2813 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-27 21:51 | 2017-12-28 09:06 | -- | -- | -- | 0 | 0 | 0 | 0.46875 | N/A | N/A | N/A | NR/12/2978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-28 20:14 | 2017-12-29 07:01 | -- | -- | -- | 0 | 0 | 0 | 0.44931 | N/A | N/A | N/A | NR/12/3076 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-30 22:02 | 2017-12-31 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.33611 | N/A | N/A | N/A | NR/12/4236 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-31 19:54 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.17083 | N/A | N/A | N/A | NR/12/4307 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[12 empty] | 0 | 0 | 0 | 1900-01-22 04:09 | [7 empty] | 100
1 | 94 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 |  | 2017-12-12 00:02 | 2017-12-12 10:32 | -- | -- | -- | 0 | 0 | 0 | 0.4375 | N/A | N/A | N/A | NR/12/1097 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 428KV
[7 empty] | 2017-12-13 00:37 | 2017-12-13 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.24306 | N/A | N/A | N/A | NR/12/1270 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 424KV
[12 empty] | 0 | 0 | 0 | 0.68056 | [7 empty] | 100
1 | 95 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 96 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 97 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 |  | 2017-12-01 | 2017-12-01 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.26597 | N/A | N/A | N/A | NR/11/3461 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 420KV
[7 empty] | 2017-12-01 21:22 | 2017-12-02 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/12/131 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 420KV
[7 empty] | 2017-12-02 21:15 | 2017-12-03 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/12/213 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-05 23:27 | 2017-12-06 07:36 | -- | -- | -- | 0 | 0 | 0 | 0.33958 | N/A | N/A | N/A | NR/12/493 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 426KV
[7 empty] | 2017-12-06 21:26 | 2017-12-07 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.32986 | N/A | N/A | N/A | NR/12/591 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 422KV
[7 empty] | 2017-12-11 01:13 | 2017-12-11 06:52 | -- | -- | -- | 0 | 0 | 0 | 0.23542 | N/A | N/A | N/A | NR/12/987 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 425KV
[7 empty] | 2017-12-11 19:56 | 2017-12-12 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.44514 | N/A | N/A | N/A | NR/12/1075 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 425KV
[7 empty] | 2017-12-13 21:36 | 2017-12-14 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/12/1383 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 425KV
[7 empty] | 2017-12-14 21:33 | 2017-12-15 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | N/A | N/A | N/A | NR/12/1515 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 425KV
[7 empty] | 2017-12-17 21:08 | 2017-12-18 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.34097 | N/A | N/A | N/A | NR/12/1832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-12-18 21:22 | 2017-12-19 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/12/1946 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULA= 423KV
[7 empty] | 2017-12-21 21:32 | 2017-12-22 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.34375 | N/A | N/A | N/A | NR/12/2310 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PANCHKULLA= 424 KV
[7 empty] | 2017-12-22 21:30 | 2017-12-23 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.33403 | N/A | N/A | N/A | NR/12/2448 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 426KV
[12 empty] | 0 | 0 | 0 | 1900-01-03 09:38 | [7 empty] | 100
1 | 98 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 |  | 2017-12-01 21:18 | 2017-12-02 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | NR/12/131 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 421KV
[7 empty] | 2017-12-04 22:03 | 2017-12-05 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.34375 | N/A | N/A | N/A | NR/12/382 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 428KV
[7 empty] | 2017-12-08 00:28 | 2017-12-08 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/12/718 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 427KV
[7 empty] | 2017-12-10 21:11 | 2017-12-11 10:48 | -- | -- | -- | 0 | 0 | 0 | 0.56736 | N/A | N/A | N/A | NR/12/981 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 422KV
[7 empty] | 2017-12-12 21:46 | 2017-12-13 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.36944 | N/A | N/A | N/A | NR/12/1267 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[7 empty] | 2017-12-16 22:08 | 2017-12-17 08:11 | -- | -- | -- | 0 | 0 | 0 | 0.41875 | N/A | N/A | N/A | NR/12/1746 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 422KV
[7 empty] | 2017-12-17 21:02 | 2017-12-18 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | N/A | N/A | N/A | NR/12/1832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 423KV
[7 empty] | 2017-12-21 00:16 | 2017-12-21 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.26944 | N/A | N/A | N/A | NR/12/2193 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[7 empty] | 2017-12-23 22:32 | 2017-12-24 07:21 | -- | -- | -- | 0 | 0 | 0 | 0.36736 | N/A | N/A | N/A | NR/12/2570 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 418KV
[7 empty] | 2017-12-31 21:32 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.10278 | N/A | N/A | N/A | NR/12/4314 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-02 11:21 | [7 empty] | 100
1 | 99 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 |  | 2017-12-01 00:02 | 2017-12-01 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.26875 | N/A | N/A | N/A | NR/11/3463 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[7 empty] | 2017-12-01 00:02 | 2017-12-01 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.26875 | N/A | N/A | N/A | NR/11/3463 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 424KV
[7 empty] | 2017-12-03 00:32 | 2017-12-04 06:54 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:22 | N/A | N/A | N/A | NR/12/288 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 428KV
[7 empty] | 2017-12-05 10:07 | 2017-12-05 17:58 | -- | -- | -- | 0.32708 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/423 | OSPT | SD TAKEN FOR AMP WORKS.
[7 empty] | 2017-12-11 21:25 | 2017-12-12 11:28 | -- | -- | -- | 0 | 0 | 0 | 0.58542 | N/A | N/A | N/A | NR/12/1084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 425KV
[7 empty] | 2017-12-15 21:44 | 2017-12-16 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/12/1632 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 421KV
[7 empty] | 2017-12-24 21:31 | 2017-12-25 08:17 | -- | -- | -- | 0 | 0 | 0 | 0.44861 | N/A | N/A | N/A | NR/12/2640 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. PATIALA= 421KV
[12 empty] | 0.32708 | 0 | 0 | 1900-01-02 05:53 | [7 empty] | 98.94
1 | 100 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 |  | 2017-12-12 21:48 | 2017-12-13 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.36736 | N/A | N/A | N/A | NR/12/1267 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 428KV
[7 empty] | 2017-12-16 22:07 | 2017-12-17 08:08 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/12/1746 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 422KV
[7 empty] | 2017-12-17 21:03 | 2017-12-18 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.35069 | N/A | N/A | N/A | NR/12/1832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 422KV
[7 empty] | 2017-12-23 22:33 | 2017-12-24 07:23 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/12/2570 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 417KV
[7 empty] | 2017-12-31 21:33 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.10208 | N/A | N/A | N/A | NR/12/4314 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 425KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 14:32 | [7 empty] | 100
1 | 101 | NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 |  | 2017-12-11 01:36 | 2017-12-11 10:50 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | NR/12/987 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 424KV
[7 empty] | 2017-12-11 21:24 | 2017-12-12 11:31 | -- | -- | -- | 0 | 0 | 0 | 0.58819 | N/A | N/A | N/A | NR/12/1084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 424KV
[7 empty] | 2017-12-15 21:45 | 2017-12-16 07:33 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/12/1632 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 423KV
[7 empty] | 2017-12-24 21:32 | 2017-12-25 08:29 | -- | -- | -- | 0 | 0 | 0 | 0.45625 | N/A | N/A | N/A | NR/12/2640 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KAITHAL= 421KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 20:06
1 | 102 | NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2017-12-12 11:35 | 2017-12-12 12:45 | -- | -- | -- | 0 | 0.048611 | 0 | 0 | N/A | N/A | N/A | NR/12/1210 | OMSU | LINE TRIPPED FROM BBMB DEHAR ONLY. TRIPPING EXTENDED FROM DEHAR END DURING TESTING OF 400KV BUS-BAR-1 WHICH IS UNDER SD AT DEHAR.
[7 empty] | 2017-12-19 08:50 | 2017-12-19 20:01 | -- | -- | -- | 0 | 0 | 0 | 0.46597 | N/A | N/A | N/A | NR/12/1967 | OSPD | SD TAKEN BY BBMB FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[12 empty] | 0 | 0.048611 | 0 | 0.46597 | [7 empty] | 100
1 | 103 | NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2017-12-30 08:24 | 2017-12-30 19:48 | -- | -- | -- | 0 | 0 | 0 | 0.475 | N/A | N/A | N/A | NR/12/4153 | OSPD | SD TAKEN BY BBMB FOR REPLACEMENT OF DISC INSULATORS WITH POLYMER INSULATOR.
[12 empty] | 0 | 0 | 0 | 0.475 | [7 empty] | 100
1 | 104 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 |  | 2017-12-03 20:43 | 2017-12-04 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/12/283 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 434KV
[7 empty] | 2017-12-04 21:23 | 2017-12-05 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.38889 | N/A | N/A | N/A | NR/12/382 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-08 00:18 | 2017-12-08 07:38 | -- | -- | -- | 0 | 0 | 0 | 0.30556 | N/A | N/A | N/A | NR/12/718 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 432KV
[7 empty] | 2017-12-08 21:12 | 2017-12-10 06:18 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:06 | N/A | N/A | N/A | NR/12/818 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 431KV
[7 empty] | 2017-12-10 21:06 | 2017-12-11 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.40069 | N/A | N/A | N/A | NR/12/981 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-11 21:40 | 2017-12-12 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.35972 | N/A | N/A | N/A | NR/12/1084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-14 00:35 | 2017-12-15 09:18 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:43 | N/A | N/A | N/A | NR/12/1392 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[7 empty] | 2017-12-16 01:20 | 2017-12-16 07:52 | -- | -- | -- | 0 | 0 | 0 | 0.27222 | N/A | N/A | N/A | NR/12/1638 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-16 23:45 | 2017-12-17 08:56 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/12/1747 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-17 21:01 | 2017-12-18 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.35972 | N/A | N/A | N/A | NR/12/1832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-18 21:19 | 2017-12-19 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/12/1946 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-19 21:46 | 2017-12-22 07:44 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 09:58 | N/A | N/A | N/A | NR/12/2067 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-24 21:33 | 2017-12-25 07:51 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/12/2640 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-31 21:22 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.10972 | N/A | N/A | N/A | NR/12/4314 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[12 empty] | 0 | 0 | 0 | 1900-01-07 22:31 | [7 empty] | 100
1 | 105 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 |  | 2017-12-01 | 2017-12-01 10:05 | -- | -- | -- | 0 | 0 | 0 | 0.42014 | N/A | N/A | N/A | NR/11/3463 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-12-03 20:42 | 2017-12-04 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.41528 | N/A | N/A | N/A | NR/12/283 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 434KV
[7 empty] | 2017-12-04 21:22 | 2017-12-05 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.38889 | N/A | N/A | N/A | NR/12/382 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-08 21:12 | 2017-12-09 08:05 | -- | -- | -- | 0 | 0 | 0 | 0.45347 | N/A | N/A | N/A | NR/12/818 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 431KV
[7 empty] | 2017-12-09 20:20 | 2017-12-10 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/12/911 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 423KV
[7 empty] | 2017-12-11 02:00 | 2017-12-11 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.19583 | N/A | N/A | N/A | NR/12/989 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 432KV
[7 empty] | 2017-12-11 13:06 | 2017-12-11 15:55 | -- | -- | -- | 0 | 0 | 0 | 0.11736 | N/A | N/A | N/A | NR/12/1034 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 430KV
[7 empty] | 2017-12-11 19:40 | 2017-12-15 07:30 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 11:50 | N/A | N/A | N/A | NR/12/1073 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-15 20:09 | 2017-12-16 07:22 | -- | -- | -- | 0 | 0 | 0 | 0.46736 | N/A | N/A | N/A | NR/12/1630 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-16 20:13 | 2017-12-17 10:04 | -- | -- | -- | 0 | 0 | 0 | 0.57708 | N/A | N/A | N/A | NR/12/1739 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-17 21:00 | 2017-12-18 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/12/1832 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-18 20:52 | 2017-12-19 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/12/1945 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 425KV
[7 empty] | 2017-12-19 21:45 | 2017-12-20 06:53 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/12/2067 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-21 00:19 | 2017-12-21 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.26806 | N/A | N/A | N/A | NR/12/2193 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-23 01:02 | 2017-12-23 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.21875 | N/A | N/A | N/A | NR/12/2455 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 429KV
[7 empty] | 2017-12-23 20:13 | 2017-12-24 07:22 | -- | -- | -- | 0 | 0 | 0 | 0.46458 | N/A | N/A | N/A | NR/12/2563 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 428KV
[7 empty] | 2017-12-25 20:04 | 2017-12-26 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/12/2744 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-26 21:00 | 2017-12-27 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/12/2859 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 421KV
[7 empty] | 2017-12-27 21:44 | 2017-12-28 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.34375 | N/A | N/A | N/A | NR/12/2978 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 427KV
[7 empty] | 2017-12-28 23:17 | 2017-12-29 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.26389 | N/A | N/A | N/A | NR/12/3084 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 424KV
[7 empty] | 2017-12-31 19:47 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.17569 | N/A | N/A | N/A | NR/12/4305 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. JALANDHAR= 426KV
[12 empty] | 0 | 0 | 0 | 1900-01-09 12:49 | [7 empty] | 100
1 | 106 | NR240116 | 400KV Dadri-Kaithal | 213 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 107 | NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 108 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 |  | 2017-12-13 10:57 | 2017-12-18 20:40 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 09:43 | N/A | N/A | N/A | NR/12/1320 | LCSD | SD TAKEN FOR BUS BAR EXTENSION WORK OF ICT-1 AND ICT-2 UNDER CONSTRUCTION AT GIS BANALA.
[12 empty] | 0 | 0 | 0 | 1900-01-04 09:43 | [7 empty] | 100
1 | 109 | NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 110 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 |  | 2017-12-11 23:31 | 2017-12-12 00:13 | -- | -- | -- | 0 | 0 | 0.029167 | 0 | N/A | N/A | N/A | NR/12/1099 | LNCC | LINE TRIPPED ON R-N FAULT DUE TO HEAVY SNOWFALL IN KASHMIR VALLEY. FLR NEW WANPOH : 19.2KM & KISHENPUR : 156.9KM.
[7 empty] | 2017-12-12 04:23 | 2017-12-12 04:39 | -- | -- | -- | 0 | 0 | 0.011111 | 0 | N/A | N/A | N/A | NR/12/1123 | LNCC | LINE TRIPPED ON R-N FAULT DUE TO HEAVY SNOWFALL IN KASHMIR VALLEY. FLR NEW WANPOH : 25.3KM.
[7 empty] | 2017-12-12 10:53 | 2017-12-12 18:10 | -- | -- | -- | 0 | 0 | 0.30347 | 0 | N/A | N/A | N/A | --- | LNCC | LINE TRIPPED ON R-N FAULT DUE TO HEAVY SNOWFALL IN KASHMIR VALLEY. FLR NEW WANPOH: 25KM & KISHENPUR: 108km.
[7 empty] | 2017-12-27 13:09 | 2017-12-27 13:12 | -- | -- | -- | 0 | 0 | 0 | 0.0020833 | N/A | N/A | N/A | NR/12/2923 | LCSD | SD TAKEN TO CHECK DYNAMIC BEHAVIOUR OF SVC UNDER CONSTRUCTION AT NEW WANPOH.
[12 empty] | 0 | 0 | 0.34375 | 0.0020833 | [7 empty] | 100
1 | 111 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 |  | 2017-12-12 00:51 | 2017-12-12 00:55 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | LNCC | LINE TRIPPED ON B-N FAULT DUE TO HEAVY SNOWFALL IN KASHMIR VALLEY. FLR NEW WANPOH: 19.2KM.
[7 empty] | 2017-12-12 00:55 | 2017-12-13 10:18 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:23 | N/A | N/A | N/A | NR/12/1105 | LVRD | LINE KEPT OPEN AFTER TRIPPING ON VOLTAGE REGULATION.
[12 empty] | 0 | 0 | 0.0027778 | 1899-12-31 09:23 | [7 empty] | 100
1 | 112 | NR240122 | 400KV Kurukshetra - Jind - I | 103.6 | NR2 |  | 2017-12-12 01:57 | 2017-12-12 02:03 | -- | -- | -- | 0 | 0 | 0.0041667 | 0 | N/A | N/A | N/A | --- | GOVC | LINE TRIPPED ON SYSTEM HIGH VOLTAGE. KURUKSHETRA= 439KV
[7 empty] | 2017-12-12 02:03 | 2017-12-12 08:53 | -- | -- | -- | 0 | 0 | 0 | 0.28472 | N/A | N/A | N/A | NR/12/1113 | LVRD | LINE KEPT OPEN ON VOLTAGE REGULATION.
[7 empty] | 2017-12-12 20:00 | 2017-12-14 11:08 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:08 | N/A | N/A | N/A | NR/12/1260 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 427KV
[7 empty] | 2017-12-15 20:30 | 2017-12-16 09:35 | -- | -- | -- | 0 | 0 | 0 | 0.54514 | N/A | N/A | N/A | NR/12/1630 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-17 13:49 | 2017-12-18 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.69236 | N/A | N/A | N/A | NR/12/1796 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[7 empty] | 2017-12-18 21:33 | 2017-12-19 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.34792 | N/A | N/A | N/A | NR/12/1946 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-20 00:13 | 2017-12-20 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.28681 | N/A | N/A | N/A | NR/12/2070 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 431KV
[7 empty] | 2017-12-21 00:40 | 2017-12-21 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.22431 | N/A | N/A | N/A | NR/12/2194 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 431KV
[7 empty] | 2017-12-22 00:42 | 2017-12-22 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.22639 | N/A | N/A | N/A | NR/12/2318 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 427KV
[7 empty] | 2017-12-23 20:16 | 2017-12-24 07:23 | -- | -- | -- | 0 | 0 | 0 | 0.46319 | N/A | N/A | N/A | NR/12/2563 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-24 13:50 | 2017-12-26 05:39 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:49 | N/A | N/A | N/A | NR/12/2611 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 433KV
[7 empty] | 2017-12-26 20:11 | 2017-12-27 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.40069 | N/A | N/A | N/A | NR/12/2850 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-28 01:51 | 2017-12-28 09:25 | -- | -- | -- | 0 | 0 | 0 | 0.31528 | N/A | N/A | N/A | NR/12/2984 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 428KV
[7 empty] | 2017-12-29 02:27 | 2017-12-29 07:07 | -- | -- | -- | 0 | 0 | 0 | 0.19444 | N/A | N/A | N/A | NR/12/3097 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-31 | 2017-12-31 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.26111 | N/A | N/A | N/A | NR/12/4238 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 430KV
[7 empty] | 2017-12-31 19:58 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.16806 | N/A | N/A | N/A | NR/12/4307 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[12 empty] | 0 | 0 | 0.0041667 | 1900-01-06 16:48 | [7 empty] | 100
1 | 113 | NR240123 | 400KV Kurukshetra - Jind - II | 103.6 | NR2 |  | 2017-12-13 01:34 | 2017-12-13 07:14 | -- | -- | -- | 0 | 0 | 0 | 0.23611 | N/A | N/A | N/A | NR/12/1273 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 429KV
[7 empty] | 2017-12-23 00:06 | 2017-12-23 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.26597 | N/A | N/A | N/A | NR/12/2452 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. KURUKSHETRA= 432KV
[12 empty] | 0 | 0 | 0 | 0.50208 | [7 empty] | 100
1 | 114 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 |  | 2017-12-01 | 2017-12-01 07:24 | -- | -- | -- | 0 | 0 | 0 | 0.30833 | N/A | N/A | N/A | NR/11/3439 & NLDC- 1719 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 799KV.
[7 empty] | 2017-12-01 13:46 | 2017-12-02 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.73194 | N/A | N/A | N/A | NR/12/77 NLDC/27 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=795KV.
[7 empty] | 2017-12-02 13:33 | 2017-12-03 07:29 | -- | -- | -- | 0 | 0 | 0 | 0.74722 | N/A | N/A | N/A | NR/12/176 NLDC/83 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 798KV
[7 empty] | 2017-12-03 13:06 | 2017-12-04 07:59 | -- | -- | -- | 0 | 0 | 0 | 0.78681 | N/A | N/A | N/A | NR/12/253 NLDC/132 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 801KV
[7 empty] | 2017-12-04 19:06 | 2017-12-05 08:46 | -- | -- | -- | 0 | 0 | 0 | 0.56944 | N/A | N/A | N/A | NR/12/374 NLDC/204 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 796KV
[7 empty] | 2017-12-05 13:06 | 2017-12-06 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.73056 | N/A | N/A | N/A | NR/12/441 NLDC/244 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 803 KV
[7 empty] | 2017-12-06 18:39 | 2017-12-07 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.49861 | N/A | N/A | N/A | NR/12/572 NLDC/312 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 796 KV
[7 empty] | 2017-12-07 13:25 | 2017-12-07 14:09 | -- | -- | -- | 0.030556 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/658 | LEFT | LINE TRIPPED ON R-N FAULT. FLR MOGA : 226KM, 2.417 KA.
[7 empty] | 2017-12-07 14:31 | 2017-12-07 19:32 | -- | -- | -- | 0.20903 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/697 | LEFT | LINE TRIPPED ON R-N FAULT. FLR MOGA : 226KM & MEERUT: 103KM.
[7 empty] | 2017-12-07 20:45 | 2017-12-08 08:15 | -- | -- | -- | 0 | 0 | 0 | 0.47917 | N/A | N/A | N/A | NR/12/709 NLDC/373 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=800KV
[7 empty] | 2017-12-08 19:31 | 2017-12-09 07:45 | -- | -- | -- | 0 | 0 | 0 | 0.50972 | N/A | N/A | N/A | NR/12/811 NLDC/441 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 799 KV
[7 empty] | 2017-12-09 13:12 | 2017-12-10 08:37 | -- | -- | -- | 0 | 0 | 0 | 0.80903 | N/A | N/A | N/A | NR/12/811 NLDC/441 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA= 794KV
[7 empty] | 2017-12-10 19:00 | 2017-12-11 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.53333 | N/A | N/A | N/A | NR/12/976 NLDC/518 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=800KV
[7 empty] | 2017-12-11 13:11 | 2017-12-13 11:39 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 22:28 | N/A | N/A | N/A | NR/12/1035 NLDC/551 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=805KV
[7 empty] | 2017-12-13 20:05 | 2017-12-14 09:14 | -- | -- | -- | 0 | 0 | 0 | 0.54792 | N/A | N/A | N/A | NR/12/1379 NLDC/693 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=795KV
[7 empty] | 2017-12-14 19:36 | 2017-12-15 09:10 | -- | -- | -- | 0 | 0 | 0 | 0.56528 | N/A | N/A | N/A | NR/12/1506 NLDC/762 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=795KV
[7 empty] | 2017-12-15 20:11 | 2017-12-16 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.44722 | N/A | N/A | N/A | NR/12/1631 NLDC/826 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=798KV
[7 empty] | 2017-12-16 13:05 | 2017-12-17 07:00 | -- | -- | -- | 0 | 0 | 0 | 0.74653 | N/A | N/A | N/A | NR/12/1693 NLDC/863 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=805KV
[7 empty] | 2017-12-17 13:48 | 2017-12-18 07:00 | -- | -- | -- | 0 | 0 | 0 | 0.71667 | N/A | N/A | N/A | NR/12/1794 NLDC/903 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=802KV
[7 empty] | 2017-12-18 20:22 | 2017-12-19 07:33 | -- | -- | -- | 0 | 0 | 0 | 0.46597 | N/A | N/A | N/A | NR/12/1944 NLDC/985 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=800KV
[7 empty] | 2017-12-19 13:28 | 2017-12-20 07:12 | -- | -- | -- | 0 | 0 | 0 | 0.73889 | N/A | N/A | N/A | NR/12/2011 NLDC/1027 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=800KV
[7 empty] | 2017-12-20 20:47 | 2017-12-21 08:39 | -- | -- | -- | 0 | 0 | 0 | 0.49444 | N/A | N/A | N/A | NR/12/2186 NLDC/1117 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=795KV
[7 empty] | 2017-12-21 19:37 | 2017-12-22 07:16 | -- | -- | -- | 0 | 0 | 0 | 0.48542 | N/A | N/A | N/A | NR/12/2301& NLDC/1181 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=796KV
[7 empty] | 2017-12-22 12:39 | 2017-12-22 13:57 | -- | -- | -- | 0.054167 | 0 | 0 | 0 | N/A | N/A | N/A | ------ | OMST | LINE TRIPPED DUE TO DT RECEIVED AT MOGA.
[7 empty] | 2017-12-22 19:53 | 2017-12-23 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.46736 | N/A | N/A | N/A | NR/12/2433& NLDC/1258 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=802KV
[7 empty] | 2017-12-23 20:01 | 2017-12-24 08:18 | -- | -- | -- | 0 | 0 | 0 | 0.51181 | N/A | N/A | N/A | NR/12/2560 NLDC/1326 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=802KV
[7 empty] | 2017-12-24 20:58 | 2017-12-25 08:22 | -- | -- | -- | 0 | 0 | 0 | 0.475 | N/A | N/A | N/A | NR/12/2637 NLDC/1375 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=796 KV
[7 empty] | 2017-12-25 19:58 | 2017-12-26 07:46 | -- | -- | -- | 0 | 0 | 0 | 0.49167 | N/A | N/A | N/A | NR/12/2743 NLDC/1431 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=801 KV
[7 empty] | 2017-12-26 20:50 | 2017-12-27 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | N/A | N/A | N/A | NR/12/2854 NLDC/1491 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=792 KV
[7 empty] | 2017-12-27 20:34 | 2017-12-28 07:08 | -- | -- | -- | 0 | 0 | 0 | 0.44028 | N/A | N/A | N/A | NR/12/2975 NLDC/1561 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=798 KV
[7 empty] | 2017-12-28 13:20 | 2017-12-29 08:23 | -- | -- | -- | 0 | 0 | 0 | 0.79375 | N/A | N/A | N/A | NR/12/3040 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=798 KV
[7 empty] | 2017-12-29 20:06 | 2017-12-30 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.46806 | N/A | N/A | N/A | NR/12/4103 NLDC/1687 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=798 KV
[7 empty] | 2017-12-30 20:05 | 2017-12-31 09:43 | -- | -- | -- | 0 | 0 | 0 | 0.56806 | N/A | N/A | N/A | NR/12/4229 NLDC/1739 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=793 KV
[7 empty] | 2017-12-31 19:41 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 0.17986 | N/A | N/A | N/A | NR/12/4306 NLDC/1779 | LVRD | LINE HAND TRIPPED FOR VOLTAGE REGULATION. MOGA=799 KV
[12 empty] | 0.29375 | 0 | 0 | 1900-01-17 16:08 | [7 empty] | 99.05
1 | 115 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 116 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 117 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 |  | 2017-12-12 14:35 | 2017-12-13 10:00 | -- | -- | -- | 0 | 0 | 0 | 0.80903 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. KISHENPUR = 395 KV.
[12 empty] | 0 | 0 | 0 | 0.80903 | [7 empty] | 100
1 | 118 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 119 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 120 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 121 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 |  | 2017-12-01 | 2017-12-05 16:01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 16:01 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA - 394KV.
[7 empty] | 2017-12-05 18:22 | 2017-12-11 04:08 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 09:46 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 393KV.
[7 empty] | 2017-12-11 11:11 | 2017-12-16 13:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 01:49 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 393KV.
[7 empty] | 2017-12-16 16:14 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 07:46 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. WAGOORA = 393KV.
[12 empty] | 0 | 0 | 0 | 1900-01-29 11:22 | [7 empty] | 100
1 | 122 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 123 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 124 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 125 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 126 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 127 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 128 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 129 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 130 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 131 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 132 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 133 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 134 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 135 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 |  | 2017-12-12 14:35 | 2017-12-13 10:00 | -- | -- | -- | 0 | 0 | 0 | 0.80903 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. KISHENPUR = 394KV.
[12 empty] | 0 | 0 | 0 | 0.80903 | [7 empty] | 100
1 | 136 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 137 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 138 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 139 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 140 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 141 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 142 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 143 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 144 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 145 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 |  | 2017-12-01 | 2017-12-11 04:24 | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 04:24 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH = 394KV.
[7 empty] | 2017-12-12 14:34 | 2017-12-16 13:37 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 23:03 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH = 391KV.
[7 empty] | 2017-12-16 18:40 | 2018-01-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 05:20 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R HAND TRIPPED FOR VOLTAGE REGULATION. NEW WANPOH = 395KV.
[12 empty] | 0 | 0 | 0 | 1900-01-28 08:47 | [7 empty] | 100
1 | 146 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 147 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 148 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 149 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 150 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 |  | 2017-12-16 13:36 | 2017-12-16 19:25 | -- | -- | -- | 0.24236 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1730 | OMST | REACTOR TRIPPED DUE TO PRD PRTN OPERATION OF REACTOR-II AS BOTH REACTORS ARE CHARGED THROUGH ONE BREAKER AT DEHAR.
[7 empty] | 2017-12-17 13:56 | 2017-12-17 15:31 | -- | -- | -- | 0.065972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1802 | OMST | REACTOR TRIPPED DUE TO PRD PRTN OPERATION OF REACTOR-II AS BOTH REACTORS ARE CHARGED THROUGH ONE BREAKER AT DEHAR.
[7 empty] | 2017-12-18 12:52 | 2017-12-18 12:59 | -- | -- | -- | 0.0048611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1892 | OSPT | TAKEN OUT FOR RECTIFICATION WORKS ON B/R-2 AS BOTH REACTORS ARE ON SAME CB AT DEHAR.
[7 empty] | 2017-12-18 14:38 | 2017-12-18 14:40 | -- | -- | -- | 0.0013889 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1901 | OSPT | TAKEN OUT FOR CHARGING OF REACTOR-2 AS BOTH REACTORS ARE ON SAME CB AT DEHAR.
[7 empty] | 2017-12-27 12:12 | 2017-12-27 18:04 | -- | -- | -- | 0.24444 | 0 | 0 | 0 | N/A | N/A | N/A | ------ | OMST | REACTOR TRIPPED DUE TO PRD PRTN OPERATION OF REACTOR-II AS BOTH REACTORS ARE CHARGED THROUGH ONE BREAKER AT DEHAR.
[12 empty] | 0.55903 | 0 | 0 | 0 | [7 empty] | 98.2
1 | 151 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 |  | 2017-12-16 13:36 | 2017-12-16 19:25 | -- | -- | -- | 0.24236 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1730 | SRET | REACTOR TRIPPED DUE TO PRD RELAY OPERATED.
[7 empty] | 2017-12-17 13:56 | 2017-12-17 14:30 | -- | -- | -- | 0.023611 | 0 | 0 | 0 | N/A | N/A | N/A | .--- | SRET | REACTOR TRIPPED DUE TO PRD RELAY OPERATED.
[7 empty] | 2017-12-17 14:30 | 2017-12-17 20:57 | -- | -- | -- | 0.26875 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1803 | OSPT | SD TAKEN FOR CHECKING & RECTIFICATION OF PRD.
[7 empty] | 2017-12-18 12:52 | 2017-12-18 14:40 | -- | -- | -- | 0.075 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1892 | OSPT | SD TAKEN FOR RECTIFICATION WORK FOR MALFUNCTION OF PRD.
[7 empty] | 2017-12-27 12:12 | 2017-12-27 18:04 | -- | -- | -- | 0.24444 | 0 | 0 | 0 | N/A | N/A | N/A | ------ | SRET | REACTOR TRIPPED DUE TO PRD RELAY OPERATED.
[12 empty] | 0.85417 | 0 | 0 | 0 | [7 empty] | 97.24
1 | 152 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0
1 | 153 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0
1 | 154 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 |  | 2017-12-28 09:29 | 2017-12-28 19:00 | -- | -- | -- | 0.39653 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/3008 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.39653 | 0 | 0 | 0 | [7 empty] | 98.72
1 | 155 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 156 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 157 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 158 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 159 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 |  | 2017-12-13 11:03 | 2017-12-13 16:55 | -- | -- | -- | 0.24444 | 0 | 0 | 0 | N/A | N/A | N/A | --- | SICT | ICT TRIPPED ON DIFF. AND REF PROTN OPERATION.
[7 empty] | 2017-12-13 16:55 | 2018-01-01 | -- | -- | -- | 1900-01-17 07:05 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1357 | OSPT | SD TAKEN FOR RECTIFICATION WORK AFTER ICT TRIPPED ON DIFF. AND REF PROTECTION.
[12 empty] | 1900-01-17 12:57 | 0 | 0 | 0 | [7 empty] | 99.21
1 | 160 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 161 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 162 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 163 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 |  | 2017-12-11 15:22 | 2017-12-11 16:02 | -- | -- | -- | 0.027778 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1042 | SICT | ICT TRIPPED ON OLTC BUCHHOLZ PRTN OPERATION DUE TO MOISTURE INGRESSING.
[12 empty] | 0.027778 | 0 | 0 | 0 | [7 empty] | 99.91
1 | 164 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 165 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 166 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 167 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 |  | 2017-12-01 09:17 | 2017-12-01 18:21 | -- | -- | -- | 0.37778 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/35 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.37778 | 0 | 0 | 0 | [7 empty] | 98.78
1 | 168 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 |  | 2017-12-02 09:17 | 2017-12-02 19:07 | -- | -- | -- | 0.40972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/165 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.40972 | 0 | 0 | 0 | [7 empty] | 98.68
1 | 169 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 |  | 2017-12-04 09:43 | 2017-12-04 17:46 | -- | -- | -- | 0.33542 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/334 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.33542 | 0 | 0 | 0 | [7 empty] | 98.92
1 | 170 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 |  | 2017-12-05 09:43 | 2017-12-05 17:27 | -- | -- | -- | 0.32222 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/419 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.32222 | 0 | 0 | 0 | [7 empty] | 98.96
1 | 171 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 |  | 2017-12-19 10:03 | 2017-12-19 18:45 | -- | -- | -- | 0.3625 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1985 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.3625 | 0 | 0 | 0 | [7 empty] | 98.83
1 | 172 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 |  | 2017-12-20 10:02 | 2017-12-20 17:06 | -- | -- | -- | 0.29444 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/2105 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.29444 | 0 | 0 | 0 | [7 empty] | 99.05
1 | 173 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 174 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 175 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 176 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 177 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 178 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 179 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 180 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 181 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 |  | 2017-12-07 09:05 | 2017-12-07 20:28 | -- | -- | -- | 0.47431 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/621 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.47431 | 0 | 0 | 0 | [7 empty] | 98.47
1 | 182 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 183 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 184 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 185 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 186 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 187 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 188 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 |  | 2017-12-19 09:49 | 2017-12-19 15:57 | -- | -- | -- | 0.25556 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1979 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.25556 | 0 | 0 | 0 | [7 empty] | 99.18
1 | 189 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 190 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 191 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 192 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 193 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 194 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 195 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 196 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 |  | 2017-12-21 09:47 | 2017-12-21 15:42 | -- | -- | -- | 0.24653 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/2238 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.24653 | 0 | 0 | 0 | [7 empty] | 99.2
1 | 197 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 |  | 2017-12-13 11:08 | 2017-12-13 11:18 | -- | -- | -- | 0.0069444 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1327 | OMST | ICT TRIPPED DURING 220V DCDB SOURCE-I EXTENSION WORK FOR ICT-III UNDER CONSTRUCTION AT HAMIRPUR.
[12 empty] | 0.0069444 | 0 | 0 | 0 | [7 empty] | 99.98
1 | 198 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 199 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 200 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 |  | 2017-12-26 09:22 | 2017-12-26 18:06 | -- | -- | -- | 0.36389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/2788 | OSPT | SD TAKEN FOR AMP WORKS.
[12 empty] | 0.36389 | 0 | 0 | 0 | [7 empty] | 98.83
1 | 201 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 202 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 203 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 204 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 205 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 206 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 207 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 |  | 2017-12-17 09:09 | 2017-12-17 11:18 | -- | -- | -- | 0.089583 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/900 | OMST | POLE BLOCKED DUE TO DC UNDER CURRENT RELY OPTD. AT CHAMPA.
[7 empty] | 2017-12-19 10:52 | 2017-12-19 11:34 | -- | -- | -- | 0.029167 | 0 | 0 | 0 | N/A | N/A | N/A | NL-1020 | OMST | POLE BLOCKED DUE TO FILTER TRIPPED AT CHAMPA END.
[7 empty] | 2017-12-20 07:56 | 2017-12-20 18:43 | -- | -- | -- | 0.44931 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/1113 | OMST | POLE BLOCKED DUE TO DC UNDER VOLTAGE PROTN. OPTD. AT CHAMPA END.
[7 empty] | 2017-12-22 12:11 | 2017-12-22 15:41 | -- | -- | -- | 0.14583 | 0 | 0 | 0 | N/A | N/A | N/A | NL/12/1224, NR/12/2375, WR/12/2483 | OSPT | SD TAKEN FOR REPLACEMENT OF CIB (Control Interface Board) OF BOTH LANE I & II AND UPLOADING OF FIRMWARE (MATCHING WITH EXISTING SOFTWARE VERSION V-1-.01) AT KURUKSHETRA END
[7 empty] | 2017-12-29 22:34 | 2017-12-30 14:39 | -- | -- | -- | 0.67014 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/4116 WRLDC/3305 NLDC/1561 | OSPT | SD TAKEN FOR REBOOTING SOFTWARE OF HVDC SYSTEM.
[12 empty] | 1899-12-31 09:13 | 0 | 0 | 0 | [7 empty] | 95.54
1 | 208 | NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 |  | 2017-12-13 03:12 | 2017-12-13 18:08 | -- | -- | -- | 0.62222 | 0 | 0 | 0 | N/A | N/A | N/A | --- | OMST | POLE BLOCKED DUE TO PROBLEM AT DC SWITCHYARD AT KURUKSHETRA END..
[7 empty] | 2017-12-14 16:43 | 2017-12-14 18:25 | -- | -- | -- | 0.070833 | 0 | 0 | 0 | N/A | N/A | N/A | NL/748 | OMST | POLE BLOCKED DUE TO DC LINE FAULT PROTECTION OPERATED AT KURUKSHETRA END.
[7 empty] | 2017-12-17 10:38 | 2017-12-17 10:59 | -- | -- | -- | 0.014583 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/899 | OMST | POLE BLOCKED DUE TO ABNORMAL FIRING ANGLE LATCH AT KURUKSHETRA.
[7 empty] | 2017-12-19 10:52 | 2017-12-19 13:26 | -- | -- | -- | 0.10694 | 0 | 0 | 0 | N/A | N/A | N/A | --- | OMST | POLE BLOCKED DUE TO FILTER TRIPPED AT CHAMPA END.
[7 empty] | 2017-12-20 10:20 | 2017-12-20 10:57 | -- | -- | -- | 0.025694 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/2014 NLDC/1089 | OMST | BLOCKED ON TAP LIMIT DUE TO UNAVAILABILITY OF TELECOM.
[7 empty] | 2017-12-20 17:26 | 2017-12-20 17:55 | -- | -- | -- | 0.020139 | 0 | 0 | 0 | N/A | N/A | N/A | NL/12/1105 | OMST | POLE BLOCKED DUE TO FILTER (21, 22, 31) BANK TRIPPING AT CHAMPA END
[7 empty] | 2017-12-22 12:10 | 2017-12-22 15:52 | -- | -- | -- | 0.15417 | 0 | 0 | 0 | N/A | N/A | N/A | NL/12/1224, NR/12/2375, WR/12/2484 | OSPT | SD TAKEN FOR REPLACEMENT OF CIB (Control Interface Board) OF BOTH LANE I & II AND UPLOADING OF FIRMWARE (MATCHING WITH EXISTING SOFTWARE VERSION V-1-.01) AT KURUKSHETRA END
[12 empty] | 1899-12-31 00:21 | 0 | 0 | 0 | [7 empty] | 96.73
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT(R386)="T",(+[Total outage in days (1)]-[no. of insulator failed]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM([DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT(R386)="U",(+[Total outage in days (1)]-[no. of insulator failed]),0)
OTHERS = SUM([OTHERS, row above])
Hrs:Min = IF(RIGHT(R386)="C",(+[Total outage in days (1)]-[no. of insulator failed]),0)
Hrs:Min = SUM([Hrs:Min, row above])
Deemed Available = IF(RIGHT(R386)="D",(+[Total outage in days (1)]-[no. of insulator failed]),0)
Deemed Available = SUM([Deemed Available, row above])

## NR2 jan
Standard of Performance data for month of JANUARY 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
Annexure-A
| S.No | ELEMENT CODE | ELEMENT NAME | DESCRIPTION (Length/Nos/MVA/MVAr/etc) | Region | Type of Failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration time more than Specified (Y/N) | Difference between Actual and specified | NRLDC Code | Category Code | REASON OF OUTAGE | Outage certifying Agency and reference documents (NRPC) | % Availability as certified by certifying agency
[7 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | POWERGRID | OTHERS | System constraints / Natural calamity/ Militancy | Deemed Available
[12 empty] | @ (T) | # (U) | & ( C ) | * (D)
[12 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
1 | 1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 |  | 2018-01-21 09:05 | 2018-01-21 18:19 | -- | -- | -- | 0.38472 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2021 | OSPT | SD taken for installation of additional jumpers in loc. 119-146.
[7 empty] | 2018-01-22 08:45 | 2018-01-22 18:06 | -- | -- | -- | 0.38958 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2082 | OSPT | SD taken for installation of additional jumpers in loc. 138-170.
[7 empty] | 2018-01-23 08:47 | 2018-01-23 14:03 | -- | -- | -- | 0.21944 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2177 | OSPT | SD taken for installation of additional jumpers in loc. 112-116 & 170-195.
[7 empty] | 2018-01-24 08:54 | 2018-01-24 18:10 | -- | -- | -- | 0.38611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2284 | OSPT | SD taken for installation of additional jumpers in loc. 112-116 & 170-195.
[7 empty] | 2018-01-25 09:03 | 2018-01-25 18:24 | -- | -- | -- | 0.38958 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2391 | OSPT | SD taken for installation of additional jumpers in location No. 200 to 218
[7 empty] | 2018-01-27 09:07 | 2018-01-27 18:13 | -- | -- | -- | 0.37917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2539 | OSPT | SD taken for installation of additional jumpers at various locations of the line.
[7 empty] | 2018-01-28 08:42 | 2018-01-28 18:07 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/01/2615 | OSPD | SD taken by JKPDD for carrying out preventive maintenance work at Hiranagar.
[7 empty] | 2018-01-29 09:36 | 2018-01-29 18:21 | -- | -- | -- | 0.36458 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2693 | OSPT | SD taken for installation of additional jumpers in location No. 92 to 104
[7 empty] | 2018-01-31 09:12 | 2018-01-31 18:30 | -- | -- | -- | 0.3875 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2851 | OSPT | SD taken for installation of additional jumpers in location No. 70 to 90
[12 empty] | 1900-01-01 21:37 | 0 | 0 | 0.39236 | [7 empty] | 99.64
1 | 2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 |  | 2018-01-28 08:51 | 2018-01-28 16:44 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/01/2645 | OSPD | During opening of 132kV Sewa2- Hiranagar-I &II at Sewa2, this line opened worngly by Sewa2 NHPC.
[12 empty] | 0 | 0 | 0 | 0.32847 | [7 empty] | 100
1 | 3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 |  | 2018-01-21 09:05 | 2018-01-21 18:16 | -- | -- | -- | 0.38264 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2021 | OSPT | SD taken for installation of additional jumpers in loc. 119-146.
[7 empty] | 2018-01-22 08:45 | 2018-01-22 18:06 | -- | -- | -- | 0.38958 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2082 | OSPT | SD taken for installation of additional jumpers in loc. 138-170.
[7 empty] | 2018-01-23 08:47 | 2018-01-23 14:03 | -- | -- | -- | 0.21944 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2177 | OSPT | SD taken for installation of additional jumpers in loc. 112-116 & 170-195.
[7 empty] | 2018-01-24 08:54 | 2018-01-24 18:15 | -- | -- | -- | 0.38958 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2284 | OSPT | SD taken for installation of additional jumpers in loc. 112-116 & 170-195.
[7 empty] | 2018-01-25 09:03 | 2018-01-25 18:24 | -- | -- | -- | 0.38958 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2391 | OSPT | SD taken for installation of additional jumpers in location No. 200 to 218
[7 empty] | 2018-01-27 09:07 | 2018-01-27 18:13 | -- | -- | -- | 0.37917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2539 | OSPT | SD taken for installation of additional jumpers.
[7 empty] | 2018-01-28 08:44 | 2018-01-28 18:07 | -- | -- | -- | 0 | 0 | 0 | 0.39097 | N/A | N/A | N/A | NR/01/2615 | OSPD | SD taken by JKPDD for carrying out preventive maintenance work at Hiranagar.
[7 empty] | 2018-01-29 09:36 | 2018-01-29 18:23 | -- | -- | -- | 0.36597 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2693 | OSPT | SD taken for installation of additional jumpers in location No. 92 to 104
[7 empty] | 2018-01-31 09:11 | 2018-02-01 | -- | -- | -- | 0.61736 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2851 | OSPT | SD taken for installation of additional jumpers in location No. 70 to 90
[12 empty] | 1900-01-02 03:12 | 0 | 0 | 0.39097 | [7 empty] | 89.89
1 | 4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 |  | 2018-01-28 08:51 | 2018-01-28 16:37 | -- | -- | -- | 0 | 0 | 0 | 0.32361 | N/A | N/A | N/A | NR/01/2645 | OSPD | During opening of 132kV Sewa2- Hiranagar-I &II at Sewa2, this line opened worngly by Sewa2 NHPC
[12 empty] | 0 | 0 | 0 | 0.32361 | [7 empty] | 100
1 | 6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 |  | 2018-01-15 11:32 | 2018-01-17 16:14 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 04:42 | N/A | N/A | N/A | NR/01/1480 | OSPD | SD taken by NHPC for replacement of CT at Berrasuil.
[7 empty] | 2018-01-23 02:11 | 2018-01-23 04:57 | -- | -- | -- | 0 | 0 | 0.11528 | 0 | N/A | N/A | N/A | NR/01/2162 | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Jessore.
[7 empty] | 2018-01-28 01:05 | 2018-01-28 01:15 | -- | -- | -- | 0 | 0 | 0.0069444 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Jessore.
[7 empty] | 2018-01-28 01:15 | 2018-01-28 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.17014 | N/A | N/A | N/A | NR/01/2593 | LVRD | Line kept open for voltage regulation.
[7 empty] | 2018-01-29 01:54 | 2018-01-29 02:07 | -- | -- | -- | 0 | 0 | 0.0090278 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Jessore.
[7 empty] | 2018-01-29 02:07 | 2018-01-29 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.18333 | N/A | N/A | N/A | NR/01/2674 | LVRD | Line kept open for voltage regulation.
[7 empty] | 2018-01-30 01:06 | 2018-01-30 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.23958 | N/A | N/A | N/A | NR/01/2760 | LVRD | Line hand tripped for voltage regulation. Berasuil = 242KV
[7 empty] | 2018-01-31 01:40 | 2018-01-31 02:04 | -- | -- | -- | 0 | 0 | 0.016667 | 0 | N/A | N/A | N/A | ---- | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Jessore.
[7 empty] | 2018-01-31 02:04 | 2018-01-31 09:25 | -- | -- | -- | 0 | 0 | 0 | 0.30625 | N/A | N/A | N/A | NR/01/2831 | LVRD | Line kept open for voltage regulation.
[12 empty] | 0 | 0 | 0.14792 | 1900-01-02 02:17 | [7 empty] | 100
1 | 7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 |  | 2018-01-10 09:28 | 2018-01-13 17:45 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 08:17 | N/A | N/A | N/A | NR/01/1011 | OSPD | SD taken by NHPC for CT replacement work at Berasuil.
[7 empty] | 2018-01-17 00:02 | 2018-01-17 05:28 | -- | -- | -- | 0 | 0 | 0.22639 | 0 | N/A | N/A | N/A | NR/01/1628 | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Pong.
[7 empty] | 2018-01-23 00:04 | 2018-01-23 05:57 | -- | -- | -- | 0 | 0 | 0.24514 | 0 | N/A | N/A | N/A | NR/01/2163 | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Pong.
[7 empty] | 2018-01-23 23:01 | 2018-01-24 06:18 | -- | -- | -- | 0 | 0 | 0.30347 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Pong.
[7 empty] | 2018-01-25 00:18 | 2018-01-25 06:29 | -- | -- | -- | 0 | 0 | 0.25764 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Berasuil only and remained charged from Pong.
[12 empty] | 0 | 0 | 1899-12-31 00:47 | 1900-01-02 08:17
1 | 8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 |  | 2018-01-28 08:48 | 2018-01-28 14:55 | -- | -- | -- | 0 | 0 | 0 | 0.25486 | N/A | N/A | N/A | NR/01/2618 | OSPD | SD taken by JKPDD for carrying out preventive maintenance work at Hiranagar.
[12 empty] | 0 | 0 | 0 | 0.25486 | [7 empty] | 100
1 | 9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 |  | 2018-01-03 11:29 | 2018-01-03 12:23 | -- | -- | -- | 0 | 0 | 0 | 0.0375 | N/A | N/A | N/A | NR/01/276 | OSPD | SD taken by PSTCL for maintenance work at Sarna.
[12 empty] | 0 | 0 | 0 | 0.0375 | [7 empty] | 100
1 | 13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 28 | NR222028 | 220KV Jallandhar-Hamirpur(PG) -I | 128.3 | NR2 |  | 2018-01-22 03:35 | 2018-01-22 03:35 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R on R-N fault. FLR Hamirpur - 68 km & Jal - 46.44 km.
[7 empty] | 2018-01-25 02:27 | 2018-01-25 02:27 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R on R-N fault. FLR Hamirpur : 79.213Kms & Jalandhar : 38.80Kms.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 29 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 30 | NR222030 | 220KV Jallandhar-Hamirpur(PG) -II | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 31 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 32 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 33 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 |  | 2018-01-28 08:40 | 2018-01-28 14:25 | -- | -- | -- | 0 | 0 | 0 | 0.23958 | N/A | N/A | N/A | NR/01/2618 | OSPD | SD taken by JKPDD for carrying out preventive maintenance work at Hiranagar.
[12 empty] | 0 | 0 | 0 | 0.23958 | [7 empty] | 100
1 | 34 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 |  | 2018-01-01 08:50 | 2018-01-01 14:40 | -- | -- | -- | 0.24306 | 0 | 0 | 0 | N/A | N/A | N/A | ---- | SRET | Line tripped on Y-N fault due to wave trap problem at Bawana.
[7 empty] | 2018-01-01 14:40 | 2018-01-01 17:51 | -- | -- | -- | 0 | 0 | 0 | 0.13264 | N/A | N/A | N/A | NR/01/67 | OSPD | SD taken for rectification of problem in wave trap at DTL, Bawana.
[7 empty] | 2018-01-06 08:27 | 2018-01-06 10:04 | -- | -- | -- | 0 | 0.067361 | 0 | 0 | N/A | N/A | N/A | NR/01/635 | OMSU | Line tripped due to BUS BAR tripping at DTL Bawana.
[12 empty] | 0.24306 | 0.067361 | 0 | 0.13264 | [7 empty] | 99.22
1 | 35 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 36 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 37 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 38 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 |  | 2018-01-05 19:33 | 2018-01-05 19:33 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ---- | LART | A/R on Y-N fault. FLR Jalandhar : 81.21Kms.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 39 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 |  | 2018-01-01 | 2018-01-01 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.25417 | N/A | N/A | N/A | NR/12/4305 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-01 19:37 | 2018-01-02 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.48819 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-02 19:27 | 2018-01-03 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/01/214 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-03 19:25 | 2018-01-04 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.43125 | N/A | N/A | N/A | NR/01/330 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-04 20:01 | 2018-01-05 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/01/457 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-05 20:17 | 2018-01-06 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.40139 | N/A | N/A | N/A | NR/01/595 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429kV
[7 empty] | 2018-01-06 19:41 | 2018-01-07 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/01/686 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-07 20:04 | 2018-01-08 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/01/761 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-01-08 20:12 | 2018-01-09 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.42708 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-09 20:25 | 2018-01-10 06:41 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | N/A | N/A | N/A | NR/01/977 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-10 20:05 | 2018-01-11 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/01/1087 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-11 20:03 | 2018-01-12 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/01/1192 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-12 20:07 | 2018-01-13 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.4125 | N/A | N/A | N/A | NR/01/1278 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-13 19:49 | 2018-01-14 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.41528 | N/A | N/A | N/A | NR/01/1365 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-14 21:22 | 2018-01-15 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/01/1444 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-15 19:47 | 2018-01-16 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/01/1523 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422kV
[7 empty] | 2018-01-16 21:38 | 2018-01-17 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | N/A | N/A | N/A | NR/01/1613 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-17 21:44 | 2018-01-18 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.34375 | N/A | N/A | N/A | NR/01/1704 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425kV
[7 empty] | 2018-01-18 19:59 | 2018-01-19 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/01/1813 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-19 20:09 | 2018-01-20 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/01/1898 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-20 19:47 | 2018-01-21 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.42083 | N/A | N/A | N/A | NR/01/1985 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-21 19:48 | 2018-01-22 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.41944 | N/A | N/A | N/A | NR/01/2055 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-22 20:20 | 2018-01-23 06:53 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/01/2147 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-23 12:04 | 2018-01-24 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.76319 | N/A | N/A | N/A | NR/01/2201 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 432kV
[7 empty] | 2018-01-24 21:36 | 2018-01-25 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.35069 | N/A | N/A | N/A | NR/01/2358 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-25 20:40 | 2018-01-26 17:59 | -- | -- | -- | 0 | 0 | 0 | 0.88819 | N/A | N/A | N/A | NR/01/2442 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-26 20:10 | 2018-01-27 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/01/2491 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422kV
[7 empty] | 2018-01-27 20:22 | 2018-01-28 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/01/2580 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-28 22:09 | 2018-01-29 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.35 | N/A | N/A | N/A | NR/01/2669 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-29 20:18 | 2018-01-30 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/01/2753 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-01-30 22:06 | 2018-01-31 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.30764 | N/A | N/A | N/A | NR/01/2829 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-01-31 21:23 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.10903 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[12 empty] | 0 | 0 | 0 | 1900-01-12 07:56 | [7 empty] | 100
1 | 40 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 41 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 42 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 43 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 44 | NR240024 | 400KV Moga-Hissar | 209.39 | NR2 |  | 2018-01-27 01:13 | 2018-01-27 07:36 | -- | -- | -- | 0 | 0 | 0 | 0.26597 | N/A | N/A | N/A | NR/01/2506 | LVRD | Line hand tripped for voltage regulation. Moga= 421kV
[12 empty] | 0 | 0 | 0 | 0.26597 | [7 empty] | 100
1 | 45 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 |  | 2018-01-04 19:51 | 2018-01-05 09:32 | -- | -- | -- | 0 | 0 | 0 | 0.57014 | N/A | N/A | N/A | NR/01/453 | LVRD | Line hand tripped for voltage regulation. Fatehabad= 430KV
[12 empty] | 0 | 0 | 0 | 0.57014 | [7 empty] | 100
1 | 46 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 |  | 2018-01-02 19:25 | 2018-01-03 04:51 | -- | -- | -- | 0 | 0 | 0 | 0.39306 | N/A | N/A | N/A | NR/01/214 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 420kV
[7 empty] | 2018-01-03 19:38 | 2018-01-04 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/01/330 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-04 21:38 | 2018-01-05 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.34583 | N/A | N/A | N/A | NR/01/467 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-05 20:21 | 2018-01-06 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | N/A | N/A | N/A | NR/01/595 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 428kV
[7 empty] | 2018-01-06 20:03 | 2018-01-07 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/01/687 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[7 empty] | 2018-01-07 20:03 | 2018-01-08 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.40694 | N/A | N/A | N/A | NR/01/761 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-09 21:40 | 2018-01-10 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.37847 | N/A | N/A | N/A | NR/01/980 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 420kV
[7 empty] | 2018-01-10 20:05 | 2018-01-11 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/01/1087 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-01-11 20:02 | 2018-01-12 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.42083 | N/A | N/A | N/A | NR/01/1192 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-12 21:41 | 2018-01-13 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | N/A | N/A | N/A | NR/01/1284 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-01-14 20:19 | 2018-01-15 07:57 | -- | -- | -- | 0 | 0 | 0 | 0.48472 | N/A | N/A | N/A | NR/01/1441 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-01-20 23:08 | 2018-01-21 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.30278 | N/A | N/A | N/A | NR/01/2001 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-21 22:22 | 2018-01-22 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.29167 | N/A | N/A | N/A | NR/01/2061 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-25 20:37 | 2018-01-26 18:02 | -- | -- | -- | 0 | 0 | 0 | 0.89236 | N/A | N/A | N/A | NR/01/2442 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-28 21:53 | 2018-01-29 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/01/2669 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[12 empty] | 0 | 0 | 0 | 1900-01-05 04:34 | [7 empty] | 100
1 | 47 | NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 |  | 2018-01-08 12:11 | 2018-01-08 19:41 | -- | -- | -- | 0 | 0 | 0 | 0.3125 | N/A | N/A | N/A | NR/01/829 | OSPD | SD taken by NHPC for maintenance works at URI-1.
[7 empty] | 2018-01-29 08:54 | 2018-01-29 18:43 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | NR/01/2695 | OSPD | Shutdown taken by NRSS 29 Transmission Co Ltd(Sterlite) for const. activity of Samba-Amargarh D/C under construction.
[7 empty] | 2018-01-30 08:46 | 2018-01-30 14:06 | -- | -- | -- | 0 | 0 | 0 | 0.22222 | N/A | N/A | N/A | NR/01/2779 | OSPD | Shutdown taken by NRSS 29 Transmission Co Ltd(Sterlite) for const. activity of Samba-Amargarh D/C under construction.
[7 empty] | 2018-01-31 09:20 | 2018-01-31 18:18 | -- | -- | -- | 0 | 0 | 0 | 0.37361 | N/A | N/A | N/A | NR/01/2855 | OSPD | Shutdown taken by NRSS 29 Transmission Co Ltd(Sterlite) for const. activity of Samba-Amargarh D/C under construction.
[12 empty] | 0 | 0 | 0 | 1899-12-31 07:37 | [7 empty] | 100
1 | 48 | NR240031 | 400KV URI-WAGOORA-II | 94.99 | NR2 |  | 2018-01-29 08:56 | 2018-01-29 18:53 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/01/2695 | OSPD | Shutdown taken by NRSS 29 Transmission Co Ltd(Sterlite) for const. activity of Samba-Amargarh D/C under construction.
[7 empty] | 2018-01-30 08:47 | 2018-01-30 14:08 | -- | -- | -- | 0 | 0 | 0 | 0.22292 | N/A | N/A | N/A | NR/01/2779 | OSPD | Shutdown taken by NRSS 29 Transmission Co Ltd(Sterlite) for const. activity of Samba-Amargarh D/C under construction.
[7 empty] | 2018-01-31 09:22 | 2018-01-31 18:19 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/01/2856 | OSPD | Shutdown taken by NRSS 29 Transmission Co Ltd(Sterlite) for const. activity of Samba-Amargarh D/C under construction.
[12 empty] | 0 | 0 | 0 | 1899-12-31 00:15 | [7 empty] | 100
1 | 49 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 |  | 2018-01-24 10:09 | 2018-01-24 18:29 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/01/2297 | LCSD | SD taken for line- crossing work of 765KV Bikaner- Moga DC under construction.
[12 empty] | 0 | 0 | 0 | 0.34722 | [7 empty] | 100
1 | 50 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 51 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 52 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 53 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 |  | 2018-01-01 21:38 | 2018-01-02 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/01/119 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-08 16:04 | 2018-01-08 16:04 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R on B-N fault. FLR Patiala : 82Kms & Nalagarh : 13.03Kms.
[7 empty] | 2018-01-08 20:09 | 2018-01-09 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-13 21:20 | 2018-01-14 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.34792 | N/A | N/A | N/A | NR/01/1372 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-15 19:47 | 2018-01-16 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/01/1525 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-01-19 23:43 | 2018-01-20 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.23472 | N/A | N/A | N/A | NR/01/1910 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425kV
[7 empty] | 2018-01-23 21:19 | 2018-01-24 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.33611 | N/A | N/A | N/A | NR/01/2252 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-01-24 21:37 | 2018-01-25 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/01/2358 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[7 empty] | 2018-01-26 20:08 | 2018-01-27 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/01/2491 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-27 20:24 | 2018-01-28 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.42014 | N/A | N/A | N/A | NR/01/2580 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-28 13:28 | 2018-01-28 18:25 | -- | -- | -- | 0 | 0 | 0 | 0.20625 | N/A | N/A | N/A | NR/01/2636 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 431kV
[7 empty] | 2018-01-29 20:15 | 2018-01-30 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/01/2753 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-30 22:05 | 2018-01-31 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.31875 | N/A | N/A | N/A | NR/01/2829 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[12 empty] | 0 | 0 | 0 | 1900-01-03 04:57 | [7 empty] | 100
1 | 54 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 55 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 56 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 57 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 58 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 59 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 |  | 2018-01-01 | 2018-01-01 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.28264 | N/A | N/A | N/A | NR/12/4314 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-01-01 19:38 | 2018-01-02 07:26 | -- | -- | -- | 0 | 0 | 0 | 0.49167 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-01-02 19:23 | 2018-01-03 05:07 | -- | -- | -- | 0 | 0 | 0 | 0.40556 | N/A | N/A | N/A | NR/01/214 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[7 empty] | 2018-01-03 19:30 | 2018-01-04 06:30 | -- | -- | -- | 0 | 0 | 0 | 0.45833 | N/A | N/A | N/A | NR/01/330 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[7 empty] | 2018-01-04 19:56 | 2018-01-05 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.45417 | N/A | N/A | N/A | NR/01/457 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425kV
[7 empty] | 2018-01-05 20:20 | 2018-01-06 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/01/595 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-06 19:38 | 2018-01-08 08:17 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:39 | N/A | N/A | N/A | NR/01/686 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[7 empty] | 2018-01-08 20:09 | 2018-01-09 07:44 | -- | -- | -- | 0 | 0 | 0 | 0.48264 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-01-09 20:22 | 2018-01-10 07:30 | -- | -- | -- | 0 | 0 | 0 | 0.46389 | N/A | N/A | N/A | NR/01/977 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-01-10 20:04 | 2018-01-11 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/01/1087 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-01-11 20:03 | 2018-01-12 07:08 | -- | -- | -- | 0 | 0 | 0 | 0.46181 | N/A | N/A | N/A | NR/01/1192 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-12 20:02 | 2018-01-13 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | N/A | N/A | N/A | NR/01/1278 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-01-13 19:44 | 2018-01-14 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.42708 | N/A | N/A | N/A | NR/01/1365 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-14 14:09 | 2018-01-15 06:34 | -- | -- | -- | 0 | 0 | 0 | 0.68403 | N/A | N/A | N/A | NR/01/1413 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-15 19:43 | 2018-01-16 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.44097 | N/A | N/A | N/A | NR/01/1523 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-01-16 21:34 | 2018-01-17 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/01/1613 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-17 21:40 | 2018-01-18 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.40139 | N/A | N/A | N/A | NR/01/1704 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425kV
[7 empty] | 2018-01-18 20:04 | 2018-01-19 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.43819 | N/A | N/A | N/A | NR/01/1813 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425kV
[7 empty] | 2018-01-19 20:06 | 2018-01-20 06:30 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/01/1898 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-01-20 19:40 | 2018-01-21 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/01/1985 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-21 19:46 | 2018-01-22 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/01/2055 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-22 20:17 | 2018-01-23 07:28 | -- | -- | -- | 0 | 0 | 0 | 0.46597 | N/A | N/A | N/A | NR/01/2147 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-23 12:02 | 2018-01-24 07:15 | -- | -- | -- | 0 | 0 | 0 | 0.80069 | N/A | N/A | N/A | NR/01/2201 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 431kV
[7 empty] | 2018-01-24 13:11 | 2018-01-25 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.73542 | N/A | N/A | N/A | NR/01/2319 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430kV
[7 empty] | 2018-01-25 20:39 | 2018-01-26 18:01 | -- | -- | -- | 0 | 0 | 0 | 0.89028 | N/A | N/A | N/A | NR/01/2442 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-26 20:08 | 2018-01-27 06:41 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/01/2491 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-27 20:24 | 2018-01-28 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/01/2580 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-28 13:29 | 2018-01-28 18:25 | -- | -- | -- | 0 | 0 | 0 | 0.20556 | N/A | N/A | N/A | NR/01/2636 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 431kV
[7 empty] | 2018-01-28 21:52 | 2018-01-29 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/01/2669 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425kV
[7 empty] | 2018-01-29 20:17 | 2018-01-30 07:49 | -- | -- | -- | 0 | 0 | 0 | 0.48056 | N/A | N/A | N/A | NR/01/2753 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-30 13:12 | 2018-01-31 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.71389 | N/A | N/A | N/A | NR/01/2799 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-31 21:25 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.10764 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[12 empty] | 0 | 0 | 0 | 1900-01-14 23:25 | [7 empty] | 100
1 | 60 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 61 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 62 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 |  | 2018-01-05 20:28 | 2018-01-06 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.38889 | N/A | N/A | N/A | NR/01/595 | LVRD | Line hand tripped for voltage regulation. Abdullapur= 426KV
[7 empty] | 2018-01-09 21:38 | 2018-01-10 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.35347 | N/A | N/A | N/A | NR/01/980 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 417KV
[12 empty] | 0 | 0 | 0 | 0.74236 | [7 empty] | 100
1 | 63 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 |  | 2018-01-01 | 2018-01-01 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.22847 | N/A | N/A | N/A | NR/12/4305 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 425KV
[7 empty] | 2018-01-01 19:43 | 2018-01-02 10:48 | -- | -- | -- | 0 | 0 | 0 | 0.62847 | N/A | N/A | N/A | NR/01/104 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 426KV
[7 empty] | 2018-01-04 19:48 | 2018-01-05 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/01/452 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 425KV
[7 empty] | 2018-01-06 19:55 | 2018-01-07 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/01/686 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 420KV
[7 empty] | 2018-01-08 19:57 | 2018-01-09 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/01/867 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 421KV
[7 empty] | 2018-01-09 19:46 | 2018-01-10 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/01/974 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 421KV
[7 empty] | 2018-01-11 19:47 | 2018-01-12 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.41597 | N/A | N/A | N/A | NR/01/1189 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422kV
[7 empty] | 2018-01-15 19:46 | 2018-01-16 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/01/1525 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422kV
[7 empty] | 2018-01-17 19:47 | 2018-01-18 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/01/1691 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422KV.
[7 empty] | 2018-01-19 19:49 | 2018-01-20 05:07 | -- | -- | -- | 0 | 0 | 0 | 0.3875 | N/A | N/A | N/A | NR/01/1895 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422KV.
[7 empty] | 2018-01-21 19:38 | 2018-01-22 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/01/2053 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 426KV.
[7 empty] | 2018-01-22 20:47 | 2018-01-23 02:46 | -- | -- | -- | 0 | 0 | 0 | 0.24931 | N/A | N/A | N/A | NR/01/2149 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-23 19:57 | 2018-01-24 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.3875 | N/A | N/A | N/A | NR/01/2247 | LVRD | Line hand tripped for voltage regulation. Naptha Jhakri= 420KV.
[7 empty] | 2018-01-25 09:17 | 2018-01-25 17:23 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/01/2394 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-25 19:57 | 2018-01-26 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/01/2437 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422kV
[7 empty] | 2018-01-27 08:54 | 2018-01-27 17:28 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/01/2538 | OSPD | SD taken by SJVNL, Jhakri for installation and commissioning of busbar interface equipments.
[7 empty] | 2018-01-30 09:34 | 2018-01-30 17:44 | -- | -- | -- | 0 | 0 | 0 | 0.34028 | N/A | N/A | N/A | NR/01/2783 | OSPD | SD taken by SJVNL, Jhakri for General maintenance, Retrofitting of CB poles & associated equipments.
[12 empty] | 0 | 0 | 0 | 1900-01-05 12:53 | [7 empty] | 100
1 | 64 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 |  | 2018-01-02 19:52 | 2018-01-03 04:55 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/01/216 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 420KV.
[7 empty] | 2018-01-03 20:19 | 2018-01-04 04:46 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/01/334 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422KV.
[7 empty] | 2018-01-05 19:56 | 2018-01-06 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.40208 | N/A | N/A | N/A | NR/01/590 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 426KV.
[7 empty] | 2018-01-07 20:16 | 2018-01-08 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/01/761 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422KV.
[7 empty] | 2018-01-10 20:04 | 2018-01-11 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.40208 | N/A | N/A | N/A | NR/01/1086 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422KV.
[7 empty] | 2018-01-12 19:58 | 2018-01-13 04:51 | -- | -- | -- | 0 | 0 | 0 | 0.37014 | N/A | N/A | N/A | NR/01/1273 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 421kV
[7 empty] | 2018-01-13 19:48 | 2018-01-14 05:03 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/01/1364 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 421kV
[7 empty] | 2018-01-14 19:44 | 2018-01-15 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/01/1437 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422kV
[7 empty] | 2018-01-16 19:41 | 2018-01-17 05:09 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/01/1606 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 423kV
[7 empty] | 2018-01-18 19:51 | 2018-01-19 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/01/1811 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422KV.
[7 empty] | 2018-01-20 19:39 | 2018-01-21 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/01/1984 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 421KV.
[7 empty] | 2018-01-22 19:49 | 2018-01-22 20:47 | -- | -- | -- | 0 | 0 | 0 | 0.040278 | N/A | N/A | N/A | NR/01/2143 | LVRD | Line hand tripped for voltage regulation. Naptha Jhakri= 420KV.
[7 empty] | 2018-01-22 20:47 | 2018-01-23 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/01/2149 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-24 19:54 | 2018-01-25 05:13 | -- | -- | -- | 0 | 0 | 0 | 0.38819 | N/A | N/A | N/A | NR/01/2348 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420kV
[7 empty] | 2018-01-25 09:20 | 2018-01-25 17:24 | -- | -- | -- | 0 | 0 | 0 | 0.33611 | N/A | N/A | N/A | NR/01/2394 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-26 08:48 | 2018-01-31 18:56 | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 10:08 | N/A | N/A | N/A | NR/01/2467 | OSPD | SD taken by SJVNL, Jhakri for General maintenance, Retrofitting of 3 nos CB poles & associated equipments in place of existing obsolete line CB type FB16D.
[7 empty] | 2018-01-31 20:10 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.15972 | N/A | N/A | N/A | NR/01/2906 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420kV
[12 empty] | 0 | 0 | 0 | 1900-01-09 23:16 | [7 empty] | 100
1 | 65 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 |  | 2018-01-06 03:01 | 2018-01-06 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.20764 | N/A | N/A | N/A | NR/01/609 | LVRD | Line hand tripped for voltage regulation. Abdullapur= 429kV
[7 empty] | 2018-01-07 02:41 | 2018-01-07 07:26 | -- | -- | -- | 0 | 0 | 0 | 0.19792 | N/A | N/A | N/A | NR/01/708 | LVRD | Line hand tripped for voltage regulation. Abdullapur= 430kV
[7 empty] | 2018-01-07 13:38 | 2018-01-08 07:13 | -- | -- | -- | 0 | 0 | 0 | 0.73264 | N/A | N/A | N/A | NR/01/736 | LVRD | Line hand tripped for voltage regulation. Abdullapur= 425kV
[7 empty] | 2018-01-27 03:14 | 2018-01-27 07:07 | -- | -- | -- | 0 | 0 | 0 | 0.16181 | N/A | N/A | N/A | NR/01/2515 | LVRD | Line hand tripped for voltage regulation. Abdullapur= 430kV
[12 empty] | 0 | 0 | 0 | 1899-12-31 07:12 | [7 empty] | 100
1 | 66 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 |  | 2018-01-06 08:27 | 2018-01-06 12:00 | -- | -- | -- | 0 | 0.14792 | 0 | 0 | N/A | N/A | N/A | ---- | OMSU | Line tripped due to BUS BAR tripping at DTL Bawana.
[7 empty] | 2018-01-06 12:00 | 2018-01-07 17:37 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 05:37 | N/A | N/A | N/A | NR/01/639 | OSPD | SD taken by DTL for replacement of damaged Y-PH wave trap at Bawana.
[7 empty] | 2018-01-08 02:09 | 2018-01-08 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.21458 | N/A | N/A | N/A | NR/01/777 | LVRD | Line hand tripped for voltage regulation.
[12 empty] | 0 | 0.14792 | 0 | 1899-12-31 10:46 | [7 empty] | 100
1 | 67 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 |  | 2018-01-01 | 2018-01-01 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.27569 | N/A | N/A | N/A | NR/12/4314 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-01-01 19:37 | 2018-01-02 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.48681 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-01-02 19:26 | 2018-01-03 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.425 | N/A | N/A | N/A | NR/01/214 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422KV
[7 empty] | 2018-01-03 19:26 | 2018-01-04 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.42847 | N/A | N/A | N/A | NR/01/330 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-04 19:59 | 2018-01-05 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/01/457 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-01-05 20:16 | 2018-01-06 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.4 | N/A | N/A | N/A | NR/01/595 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-01-06 19:39 | 2018-01-07 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | N/A | N/A | N/A | NR/01/686 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-01-07 20:02 | 2018-01-08 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.41389 | N/A | N/A | N/A | NR/01/761 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421KV
[7 empty] | 2018-01-08 20:12 | 2018-01-09 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-09 20:23 | 2018-01-10 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/01/977 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-10 20:04 | 2018-01-11 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.40139 | N/A | N/A | N/A | NR/01/1087 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-11 20:02 | 2018-01-12 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/01/1192 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-12 20:04 | 2018-01-13 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/01/1278 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-13 19:46 | 2018-01-14 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.42083 | N/A | N/A | N/A | NR/01/1365 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-14 14:10 | 2018-01-15 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.65764 | N/A | N/A | N/A | NR/01/1413 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-15 19:44 | 2018-01-16 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/01/1523 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422kV
[7 empty] | 2018-01-16 21:36 | 2018-01-17 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/01/1613 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-17 21:44 | 2018-01-18 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.34167 | N/A | N/A | N/A | NR/01/1704 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425kV
[7 empty] | 2018-01-18 19:58 | 2018-01-19 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/01/1813 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-19 20:07 | 2018-01-20 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/01/1898 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-20 19:40 | 2018-01-21 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/01/1985 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-21 19:47 | 2018-01-22 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/01/2055 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-22 20:18 | 2018-01-23 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/01/2147 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-23 12:00 | 2018-01-24 07:09 | -- | -- | -- | 0 | 0 | 0 | 0.79792 | N/A | N/A | N/A | NR/01/2201 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 432kV
[7 empty] | 2018-01-24 13:12 | 2018-01-25 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.73264 | N/A | N/A | N/A | NR/01/2319 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430kV
[7 empty] | 2018-01-25 20:38 | 2018-01-27 06:30 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:52 | N/A | N/A | N/A | NR/01/2442 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-27 20:22 | 2018-01-29 06:40 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:18 | N/A | N/A | N/A | NR/01/2580 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-29 20:16 | 2018-01-30 07:44 | -- | -- | -- | 0 | 0 | 0 | 0.47778 | N/A | N/A | N/A | NR/01/2753 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-01-30 22:04 | 2018-01-31 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.31458 | N/A | N/A | N/A | NR/01/2829 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-01-31 21:21 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.11042 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[12 empty] | 0 | 0 | 0 | 1900-01-13 20:07 | [7 empty] | 100
1 | 68 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 |  | 2018-01-07 23:54 | 2018-01-08 07:57 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/01/772 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-01-23 23:51 | 2018-01-24 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.27222 | N/A | N/A | N/A | NR/01/2255 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429kV
[7 empty] | 2018-01-25 02:18 | 2018-01-25 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.15 | N/A | N/A | N/A | NR/01/2369 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 433kV
[12 empty] | 0 | 0 | 0 | 0.75764 | [7 empty] | 100
1 | 69 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 |  | 2018-01-23 09:24 | 2018-01-23 16:35 | -- | -- | -- | 0.29931 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2185 | OSPT | SD for jumper tightening and maintenance works
[12 empty] | 0.29931 | 0 | 0 | 0 | [7 empty] | 99.03
1 | 70 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 71 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 |  | 2018-01-01 | 2018-01-01 06:46 | -- | -- | -- | 0 | 0 | 0 | 0.28194 | N/A | N/A | N/A | NR/12/4226 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-01-01 19:34 | 2018-01-02 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.49375 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Amritsar= 426KV
[7 empty] | 2018-01-02 19:24 | 2018-01-03 06:46 | -- | -- | -- | 0 | 0 | 0 | 0.47361 | N/A | N/A | N/A | NR/01/214 | LVRD | Line hand tripped for voltage regulation. Amritsar= 418KV
[7 empty] | 2018-01-03 19:31 | 2018-01-04 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.45694 | N/A | N/A | N/A | NR/01/330 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424KV
[7 empty] | 2018-01-04 19:54 | 2018-01-05 06:48 | -- | -- | -- | 0 | 0 | 0 | 0.45417 | N/A | N/A | N/A | NR/01/457 | LVRD | Line hand tripped for voltage regulation. Amritsar= 425KV
[7 empty] | 2018-01-05 20:34 | 2018-01-06 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/01/599 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-01-06 20:04 | 2018-01-08 08:16 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:12 | N/A | N/A | N/A | NR/01/687 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-01-08 20:17 | 2018-01-09 07:43 | -- | -- | -- | 0 | 0 | 0 | 0.47639 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Amritsar= 423KV
[7 empty] | 2018-01-09 20:30 | 2018-01-10 07:31 | -- | -- | -- | 0 | 0 | 0 | 0.45903 | N/A | N/A | N/A | NR/01/977 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-01-10 20:03 | 2018-01-11 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.47014 | N/A | N/A | N/A | NR/01/1087 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-01-11 20:04 | 2018-01-12 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.45972 | N/A | N/A | N/A | NR/01/1192 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420kV
[7 empty] | 2018-01-12 20:01 | 2018-01-13 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | N/A | N/A | N/A | NR/01/1278 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422kV
[7 empty] | 2018-01-13 19:43 | 2018-01-14 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.42708 | N/A | N/A | N/A | NR/01/1365 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422kV
[7 empty] | 2018-01-14 14:08 | 2018-01-15 06:32 | -- | -- | -- | 0 | 0 | 0 | 0.68333 | N/A | N/A | N/A | NR/01/1413 | LVRD | Line hand tripped for voltage regulation. Amritsar = 422kV
[7 empty] | 2018-01-15 19:42 | 2018-01-16 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.44097 | N/A | N/A | N/A | NR/01/1523 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420kV
[7 empty] | 2018-01-16 21:33 | 2018-01-17 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/01/1613 | LVRD | Line hand tripped for voltage regulation. Amritsar = 423kV
[7 empty] | 2018-01-17 21:41 | 2018-01-18 07:16 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/01/1704 | LVRD | Line hand tripped for voltage regulation. Amritsar = 421kV
[7 empty] | 2018-01-18 20:00 | 2018-01-19 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/01/1813 | LVRD | Line hand tripped for voltage regulation. Amritsar = 420kV
[7 empty] | 2018-01-19 20:05 | 2018-01-20 06:30 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/01/1898 | LVRD | Line hand tripped for voltage regulation. Amritsar = 420kV
[7 empty] | 2018-01-20 19:39 | 2018-01-21 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/01/1985 | LVRD | Line hand tripped for voltage regulation. Amritsar = 420kV
[7 empty] | 2018-01-21 10:28 | 2018-01-21 15:38 | -- | -- | -- | 0.21528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2028 | OSPT | SD taken for installation of insulator string after de-capping at Loc. No. 322.
[7 empty] | 2018-01-21 19:45 | 2018-01-22 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.425 | N/A | N/A | N/A | NR/01/2055 | LVRD | Line hand tripped for voltage regulation. Amritsar = 420kV
[7 empty] | 2018-01-22 20:16 | 2018-01-23 07:26 | -- | -- | -- | 0 | 0 | 0 | 0.46528 | N/A | N/A | N/A | NR/01/2147 | LVRD | Line hand tripped for voltage regulation. Amritsar = 420kV
[7 empty] | 2018-01-23 12:01 | 2018-01-24 07:15 | -- | -- | -- | 0 | 0 | 0 | 0.80139 | N/A | N/A | N/A | NR/01/2201 | LVRD | Line hand tripped for voltage regulation. Amritsar = 427kV
[7 empty] | 2018-01-24 13:10 | 2018-01-25 06:49 | -- | -- | -- | 0 | 0 | 0 | 0.73542 | N/A | N/A | N/A | NR/01/2319 | LVRD | Line hand tripped for voltage regulation. Amritsar = 426kV
[7 empty] | 2018-01-25 13:06 | 2018-01-26 18:00 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:54 | N/A | N/A | N/A | NR/01/2414 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425kV
[7 empty] | 2018-01-26 20:07 | 2018-01-27 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/01/2491 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420kV
[7 empty] | 2018-01-27 20:28 | 2018-01-28 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.43194 | N/A | N/A | N/A | NR/01/2580 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420kV
[7 empty] | 2018-01-28 21:54 | 2018-01-29 07:19 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/01/2669 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422kV
[7 empty] | 2018-01-29 20:16 | 2018-01-30 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.48056 | N/A | N/A | N/A | NR/01/2753 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420kV
[7 empty] | 2018-01-30 13:09 | 2018-01-31 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.71528 | N/A | N/A | N/A | NR/01/2799 | LVRD | Line hand tripped for voltage regulation. Amritsar= 426kV
[7 empty] | 2018-01-31 13:02 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.45694 | N/A | N/A | N/A | NR/01/2870 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421kV
[12 empty] | 0.21528 | 0 | 0 | 1900-01-15 13:16 | [7 empty] | 99.31
1 | 72 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 73 | NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 74 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 |  | 2018-01-02 13:21 | 2018-01-02 14:23 | -- | -- | -- | 0.043056 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/185 | OSFT | Line tripped due to CVT fuse failure at New Wanpoh.
[7 empty] | 2018-01-02 14:23 | 2018-01-02 14:32 | -- | -- | -- | 0.00625 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/187 | OSPT | SD taken for CVT fuse replacment.
[12 empty] | 0.049306 | 0 | 0 | 0 | [7 empty] | 99.84
1 | 75 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 76 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 77 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 |  | 2018-01-10 15:20 | 2018-01-10 16:30 | -- | -- | -- | 0 | 0.048611 | 0 | 0 | N/A | N/A | N/A | NR/01/1052 | OMSU | Line tripped on R-N fault due to Pilot wire hanging while laying OPGW under ULDC scheme. FLR Banala: FL=58.6 km & Hamirpur: 18.499 km.
[7 empty] | 2018-01-17 19:11 | 2018-01-17 22:19 | -- | -- | -- | 0 | 0.13056 | 0 | 0 | N/A | N/A | N/A | NR/01/1706 | OMSU | Line tripped on R-N fault due to Pilot wire hanging while laying OPGW under ULDC scheme. FLR Banala: FL=51 km & Hamirpur: 26.27 km.
[7 empty] | 2018-01-20 18:05 | 2018-01-20 18:40 | -- | -- | -- | 0 | 0.024306 | 0 | 0 | N/A | N/A | N/A | NR/01/1973 | OMSU | SD taken for removal of Traction Machine struck between Span Tower No. 132 -133 during OPGW laying work under ULDC scheme.
[7 empty] | 2018-01-22 12:15 | 2018-01-22 13:45 | -- | -- | -- | 0 | 0.0625 | 0 | 0 | N/A | N/A | N/A | NR/01/2116 | OMSU | Line tripped on R-N fault due to Pilot wire hanging while laying OPGW under ULDC scheme. FLR Banala: FL=52 .6 km & Hamirpur: 25.72 km.
[12 empty] | 0 | 0.26597 | 0 | 0 | [7 empty] | 100
1 | 78 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 |  | 2018-01-22 20:48 | 2018-01-23 02:21 | -- | -- | -- | 0 | 0 | 0 | 0.23125 | N/A | N/A | N/A | NR/01/2149 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-25 09:26 | 2018-01-25 17:19 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/01/2394 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-27 09:02 | 2018-01-27 17:05 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/01/2538 | OSPD | SD taken by SJVNL, Jhakri for installation and commissioning of busbar interface equipments.
[7 empty] | 2018-01-30 09:37 | 2018-01-30 18:00 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/01/2783 | OSPD | SD taken by SJVNL, Jhakri for General maintenance, Retrofitting of CB poles & associated equipments .
[12 empty] | 0 | 0 | 0 | 1899-12-31 05:52 | [7 empty] | 100
1 | 79 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 |  | 2018-01-01 | 2018-01-01 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.25 | N/A | N/A | N/A | NR/12/4314 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-01-01 21:37 | 2018-01-02 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/01/119 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427KV
[7 empty] | 2018-01-02 21:13 | 2018-01-03 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.33958 | N/A | N/A | N/A | NR/01/223 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-01-03 21:26 | 2018-01-04 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.34028 | N/A | N/A | N/A | NR/01/342 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-01-10 21:23 | 2018-01-11 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/01/1091 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-01-13 21:18 | 2018-01-14 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/01/1372 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-16 21:35 | 2018-01-17 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/01/1613 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-17 21:44 | 2018-01-18 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.33958 | N/A | N/A | N/A | NR/01/1704 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425kV
[7 empty] | 2018-01-18 21:13 | 2018-01-19 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.34236 | N/A | N/A | N/A | NR/01/1819 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-21 22:11 | 2018-01-22 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.3 | N/A | N/A | N/A | NR/01/2061 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-23 21:18 | 2018-01-24 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/01/2252 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-01-24 21:36 | 2018-01-25 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.32083 | N/A | N/A | N/A | NR/01/2358 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[7 empty] | 2018-01-27 00:24 | 2018-01-27 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.2375 | N/A | N/A | N/A | NR/01/2502 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-01-27 23:34 | 2018-01-28 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.2625 | N/A | N/A | N/A | NR/01/2589 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-01-29 21:48 | 2018-01-30 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/01/2758 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[12 empty] | 0 | 0 | 0 | 1900-01-03 19:30 | [7 empty] | 100
1 | 80 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 81 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 |  | 2018-01-22 20:49 | 2018-01-23 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.35417 | N/A | N/A | N/A | NR/01/2149 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-25 09:26 | 2018-01-25 17:22 | -- | -- | -- | 0 | 0 | 0 | 0.33056 | N/A | N/A | N/A | NR/01/2394 | OSPD | SD taken by SJVNL for installation & commg. of operating mechanism for common point earth switch of BR bay at Jhakri.
[7 empty] | 2018-01-27 09:03 | 2018-01-27 16:48 | -- | -- | -- | 0 | 0 | 0 | 0.32292 | N/A | N/A | N/A | NR/01/2538 | OSPD | SD taken by SJVNL, Jhakri for installation and commissioning of busbar interface equipments.
[7 empty] | 2018-01-30 09:37 | 2018-01-30 17:55 | -- | -- | -- | 0 | 0 | 0 | 0.34583 | N/A | N/A | N/A | NR/01/2783 | OSPD | SD taken by SJVNL, Jhakri for General maintenance, Retrofitting of CB poles & associated equipments .
[12 empty] | 0 | 0 | 0 | 1899-12-31 08:29 | [7 empty] | 100
1 | 82 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 |  | 2018-01-04 21:34 | 2018-01-05 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.34097 | N/A | N/A | N/A | NR/01/467 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-01-05 20:21 | 2018-01-06 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.38611 | N/A | N/A | N/A | NR/01/595 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 428KV
[7 empty] | 2018-01-06 22:03 | 2018-01-07 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.31667 | N/A | N/A | N/A | NR/01/705 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-01-07 21:22 | 2018-01-08 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.35069 | N/A | N/A | N/A | NR/01/768 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-01-08 20:08 | 2018-01-09 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426KV
[7 empty] | 2018-01-09 21:38 | 2018-01-10 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | N/A | N/A | N/A | NR/01/980 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 420KV
[7 empty] | 2018-01-11 21:17 | 2018-01-12 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/01/1193 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 420kV
[7 empty] | 2018-01-12 21:43 | 2018-01-13 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.33889 | N/A | N/A | N/A | NR/01/1284 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-01-14 21:20 | 2018-01-15 05:27 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | N/A | N/A | N/A | NR/01/1444 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-15 21:49 | 2018-01-16 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.31458 | N/A | N/A | N/A | NR/01/1531 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425kV
[7 empty] | 2018-01-19 21:07 | 2018-01-20 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.34236 | N/A | N/A | N/A | NR/01/1904 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-01-20 23:15 | 2018-01-21 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.25972 | N/A | N/A | N/A | NR/01/2001 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-25 21:45 | 2018-01-26 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.33403 | N/A | N/A | N/A | NR/01/2447 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-28 21:57 | 2018-01-29 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.32431 | N/A | N/A | N/A | NR/01/2669 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-01-30 22:07 | 2018-01-31 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.31458 | N/A | N/A | N/A | NR/01/2829 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-01-31 21:28 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.10556 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV
[12 empty] | 0 | 0 | 0 | 1900-01-04 04:13 | [7 empty] | 100
1 | 83 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 |  | 2018-01-01 01:47 | 2018-01-01 19:35 | -- | -- | -- | 0 | 0.74167 | 0 | 0 | N/A | N/A | N/A | ---- | OMSU | Line tripped on R-N fault. FLR Panchkulla : 133 Kms & BBMB Panipat : 21.25 Km. (Fault in BBMB Portion. POWERGRID Portion is only LILO with length: 9.0 km)
[7 empty] | 2018-01-04 00:56 | 2018-01-04 08:05 | -- | -- | -- | 0 | 0.29792 | 0 | 0 | N/A | N/A | N/A | ---- | OMSU | Line tripped on R-N fault. FLR Panchkulla : 154.6 Kms & BBMB Panipat : 1.5 Km. (Fault in BBMB portion. POWERGRID Portion is only LILO with length: 9.0 km)
[7 empty] | 2018-01-04 08:05 | 2018-01-04 17:51 | -- | -- | -- | 0 | 0 | 0 | 0.40694 | N/A | N/A | N/A | NR/01/363 | OSPD | SD taken by BBMB for rectification after tripping on R-N fault.
[7 empty] | 2018-01-05 03:12 | 2018-01-05 03:57 | -- | -- | -- | 0 | 0.03125 | 0 | 0 | N/A | N/A | N/A | NR/01/477 | OMSU | A/R on B-N fault from Panchkulla & tripped from BBMB, Panipat. FLR Panchkulla : 154Kms & Panipat : 11.6KA. ( Fault in BBMB portion. POWERGRID LILO length is 9 km only)
[7 empty] | 2018-01-05 04:16 | 2018-01-05 06:17 | -- | -- | -- | 0 | 0.084028 | 0 | 0 | N/A | N/A | N/A | ---- | OMSU | Line tripped on R-N fault. FLR Panchkulla : 164.6 Kms & panipat : 12.5 Km. (Fault in BBMB portion only. POWERGRID Portion is only LILO with length: 9.0 km)
[7 empty] | 2018-01-05 06:17 | 2018-01-05 17:06 | -- | -- | -- | 0 | 0 | 0 | 0.45069 | N/A | N/A | N/A | NR/01/485 | OSPD | SD taken by BBMB for rectification after tripping on B-N fault.
[7 empty] | 2018-01-07 09:13 | 2018-01-07 18:10 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/01/726 | OSPD | SD taken by BBMB for cleaning of Disc Insulator.
[7 empty] | 2018-01-08 07:54 | 2018-01-08 18:42 | -- | -- | -- | 0 | 0 | 0 | 0.45 | N/A | N/A | N/A | NR/01/798 | OSPD | SD taken by BBMB for cleaning of Disc Insulator.
[7 empty] | 2018-01-09 17:44 | 2018-01-09 20:10 | -- | -- | -- | 0 | 0 | 0 | 0.10139 | N/A | N/A | N/A | NR/01/951 | OSPD | SD Taken by BBMB for remove of hanging rope struck during OPGW laying.
[7 empty] | 2018-01-21 08:07 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 15:53 | N/A | N/A | N/A | NR/01/2018 | OSPD | SD taken by BBMB for TL maintenance works.
[12 empty] | 0 | 1899-12-31 03:43 | 0 | 1900-01-11 10:39 | [7 empty] | 100
1 | 84 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 |  | 2018-01-02 03:14 | 2018-01-02 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.10208 | N/A | N/A | N/A | NR/01/128 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 428KV
[7 empty] | 2018-01-10 01:15 | 2018-01-10 07:04 | -- | -- | -- | 0 | 0 | 0 | 0.24236 | N/A | N/A | N/A | NR/01/986 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 421KV
[7 empty] | 2018-01-15 05:55 | 2018-01-15 07:36 | -- | -- | -- | 0 | 0.070139 | 0 | 0 | N/A | N/A | N/A | ---- | OMSU | Line tripped from BBMB, Dehar only, Line remains charged from Panchkula end.
[7 empty] | 2018-01-17 03:16 | 2018-01-17 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.11736 | N/A | N/A | N/A | NR/01/1622 | LVRD | Line hand tripped for voltage regulation. Panchkula= 423kV
[7 empty] | 2018-01-20 08:08 | 2018-01-20 18:04 | -- | -- | -- | 0 | 0 | 0 | 0.41389 | N/A | N/A | N/A | NR/01/1929 | OSPD | SD taken by BBMB for TL maintenance works.
[7 empty] | 2018-01-22 05:53 | 2018-01-22 06:44 | -- | -- | -- | 0 | 0.035417 | 0 | 0 | N/A | N/A | N/A | NR/01/2076 | OMSU | Line tripped from BBMB, Dehar only, Line remains charged from Panchkula end.
[7 empty] | 2018-01-23 11:17 | 2018-01-24 14:55 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 03:38 | N/A | N/A | N/A | NR/01/2194 | OSPD | SD taken by BBMB for testing of line CVT at Dehar.
[7 empty] | 2018-01-31 06:06 | 2018-01-31 08:32 | -- | -- | -- | 0 | 0.10139 | 0 | 0 | N/A | N/A | N/A | NR/01/2844 | OMSU | Line tripped from BBMB, Dehar only, Line remains charged from Panchkula end.
[12 empty] | 0 | 0.20694 | 0 | 1900-01-01 00:39 | [7 empty] | 100
1 | 85 | NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 86 | NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 87 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 88 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 |  | 2018-01-04 10:59 | 2018-01-04 14:39 | -- | -- | -- | 0.15278 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/394 | OSPT | SD taken for replacment of Y-ph LA at Abdullapur.
[7 empty] | 2018-01-23 21:37 | 2018-01-23 21:37 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R on B-N fault. FLR Abdullapur : 36.2Kms & Kurukshetra : 10.8Kms.
[7 empty] | 2018-01-24 13:15 | 2018-01-24 14:58 | -- | -- | -- | 0 | 0 | 0 | 0.071528 | N/A | N/A | N/A | NR/01/2319 | LVRD | Line hand tripped for voltage regulation. Kurushetra=428 kV
[12 empty] | 0.15278 | 0 | 0 | 0.071528 | [7 empty] | 99.51
1 | 89 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 |  | 2018-01-01 | 2018-01-01 06:30 | -- | -- | -- | 0 | 0 | 0 | 0.27083 | N/A | N/A | N/A | NR/12/4307 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429KV
[7 empty] | 2018-01-01 19:39 | 2018-01-02 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.51458 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-01-02 21:23 | 2018-01-03 04:33 | -- | -- | -- | 0 | 0 | 0 | 0.29861 | N/A | N/A | N/A | NR/01/223 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 426KV
[7 empty] | 2018-01-03 21:36 | 2018-01-04 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.34167 | N/A | N/A | N/A | NR/01/342 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 420KV
[7 empty] | 2018-01-06 02:40 | 2018-01-06 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.16597 | N/A | N/A | N/A | NR/01/607 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 433KV
[7 empty] | 2018-01-08 00:45 | 2018-01-08 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.24514 | N/A | N/A | N/A | NR/01/775 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 431KV
[7 empty] | 2018-01-10 21:21 | 2018-01-11 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.36319 | N/A | N/A | N/A | NR/01/1091 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 426KV
[7 empty] | 2018-01-11 21:27 | 2018-01-12 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.36944 | N/A | N/A | N/A | NR/01/1193 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 422kV
[7 empty] | 2018-01-23 14:54 | 2018-01-24 07:19 | -- | -- | -- | 0 | 0 | 0 | 0.68403 | N/A | N/A | N/A | NR/01/2212 | LVRD | Line hand tripped for voltage regulation. Kurukshetra=434kV
[7 empty] | 2018-01-26 22:03 | 2018-01-27 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.33958 | N/A | N/A | N/A | NR/01/2498 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 421kV
[7 empty] | 2018-01-28 01:43 | 2018-01-28 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.2 | N/A | N/A | N/A | NR/01/2595 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 426kV
[7 empty] | 2018-01-31 12:51 | 2018-01-31 18:45 | -- | -- | -- | 0 | 0 | 0 | 0.24583 | N/A | N/A | N/A | NR/01/2870 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[12 empty] | 0 | 0 | 0 | 1900-01-03 00:56 | [7 empty] | 100
1 | 90 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 |  | 2018-01-12 21:45 | 2018-01-13 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.37153 | N/A | N/A | N/A | NR/01/1284 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 423kV
[12 empty] | 0 | 0 | 0 | 0.37153 | [7 empty] | 100
1 | 91 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 |  | 2018-01-01 | 2018-01-01 07:34 | -- | -- | -- | 0 | 0 | 0 | 0.31528 | N/A | N/A | N/A | NR/12/3076 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-01-01 19:37 | 2018-01-04 06:07 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 10:30 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-01-04 19:54 | 2018-01-05 11:55 | -- | -- | -- | 0 | 0 | 0 | 0.66736 | N/A | N/A | N/A | NR/01/457 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428KV
[7 empty] | 2018-01-05 21:19 | 2018-01-06 11:25 | -- | -- | -- | 0 | 0 | 0 | 0.5875 | N/A | N/A | N/A | NR/01/602 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 425KV
[7 empty] | 2018-01-06 19:56 | 2018-01-08 06:59 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:03 | N/A | N/A | N/A | NR/01/686 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-01-08 20:14 | 2018-01-09 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-09 20:31 | 2018-01-10 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/01/977 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-10 21:22 | 2018-01-11 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/01/1091 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-11 21:22 | 2018-01-12 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/01/1193 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 422kV
[7 empty] | 2018-01-12 21:43 | 2018-01-13 07:01 | -- | -- | -- | 0 | 0 | 0 | 0.3875 | N/A | N/A | N/A | NR/01/1284 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 423kV
[7 empty] | 2018-01-13 19:25 | 2018-01-14 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.44722 | N/A | N/A | N/A | NR/01/1361 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428kV
[7 empty] | 2018-01-14 14:14 | 2018-01-15 10:52 | -- | -- | -- | 0 | 0 | 0 | 0.85972 | N/A | N/A | N/A | NR/01/1413 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-15 21:51 | 2018-01-16 07:26 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/01/1531 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422kV
[7 empty] | 2018-01-18 20:02 | 2018-01-19 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/01/1813 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-19 20:08 | 2018-01-20 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/01/1898 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-21 02:53 | 2018-01-21 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.16111 | N/A | N/A | N/A | NR/01/2009 | LVRD | Line hand tripped for voltage regulation. Kurukshetra=429kV
[7 empty] | 2018-01-21 19:47 | 2018-01-22 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.41875 | N/A | N/A | N/A | NR/01/2055 | LVRD | Line hand tripped for voltage regulation. Kurukshetra=430kV
[7 empty] | 2018-01-22 20:17 | 2018-01-23 06:46 | -- | -- | -- | 0 | 0 | 0 | 0.43681 | N/A | N/A | N/A | NR/01/2147 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 420kV
[7 empty] | 2018-01-23 14:49 | 2018-01-24 06:34 | -- | -- | -- | 0 | 0 | 0 | 0.65625 | N/A | N/A | N/A | NR/01/2212 | LVRD | Line hand tripped for voltage regulation. Kurukshetra=434kV
[7 empty] | 2018-01-25 13:11 | 2018-01-27 05:30 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 16:19 | N/A | N/A | N/A | NR/01/2414 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425kV
[7 empty] | 2018-01-28 13:35 | 2018-01-29 07:40 | -- | -- | -- | 0 | 0 | 0 | 0.75347 | N/A | N/A | N/A | NR/01/2636 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[7 empty] | 2018-01-29 21:47 | 2018-01-30 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/01/2758 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 424kV
[7 empty] | 2018-01-30 12:57 | 2018-01-31 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.72292 | N/A | N/A | N/A | NR/01/2797 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428kV
[7 empty] | 2018-01-31 12:29 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.47986 | N/A | N/A | N/A | NR/01/2867 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[12 empty] | 0 | 0 | 0 | 1900-01-14 13:43 | [7 empty] | 100
1 | 92 | NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 93 | NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 |  | 2018-01-01 | 2018-01-01 12:20 | -- | -- | -- | 0 | 0 | 0 | 0.51389 | N/A | N/A | N/A | NR/12/4307 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429KV
[7 empty] | 2018-01-01 19:46 | 2018-01-03 10:28 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 14:42 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-01-03 19:26 | 2018-01-04 10:04 | -- | -- | -- | 0 | 0 | 0 | 0.60972 | N/A | N/A | N/A | NR/01/330 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428KV
[7 empty] | 2018-01-04 19:55 | 2018-01-05 09:40 | -- | -- | -- | 0 | 0 | 0 | 0.57292 | N/A | N/A | N/A | NR/01/457 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428KV
[7 empty] | 2018-01-05 21:22 | 2018-01-06 11:19 | -- | -- | -- | 0 | 0 | 0 | 0.58125 | N/A | N/A | N/A | NR/01/602 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428KV
[7 empty] | 2018-01-06 23:50 | 2018-01-06 23:50 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | A/R on B-N fault. FLR Kurukshetra : 117Kms & Nakodar : 129.3Kms.
[7 empty] | 2018-01-07 00:08 | 2018-01-08 06:51 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:43 | N/A | N/A | N/A | NR/01/707 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428KV
[7 empty] | 2018-01-08 20:16 | 2018-01-09 09:29 | -- | -- | -- | 0 | 0 | 0 | 0.55069 | N/A | N/A | N/A | NR/01/870 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 423KV
[7 empty] | 2018-01-09 20:29 | 2018-01-10 10:34 | -- | -- | -- | 0 | 0 | 0 | 0.58681 | N/A | N/A | N/A | NR/01/977 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 423KV
[7 empty] | 2018-01-12 20:12 | 2018-01-13 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.42292 | N/A | N/A | N/A | NR/01/1278 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 417kV
[7 empty] | 2018-01-13 19:51 | 2018-01-14 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.42847 | N/A | N/A | N/A | NR/01/1365 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[7 empty] | 2018-01-16 21:36 | 2018-01-17 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/01/1613 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 424kV
[7 empty] | 2018-01-23 12:06 | 2018-01-25 10:16 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 22:10 | N/A | N/A | N/A | NR/01/2201 | LVRD | Line hand tripped for voltage regulation. Kurukshetra=428kV
[7 empty] | 2018-01-26 02:37 | 2018-01-29 07:56 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 05:19 | N/A | N/A | N/A | NR/01/2452 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430kV
[7 empty] | 2018-01-29 21:54 | 2018-01-30 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.33889 | N/A | N/A | N/A | NR/01/2758 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 424kV
[7 empty] | 2018-01-30 13:05 | 2018-01-31 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.71806 | N/A | N/A | N/A | NR/01/2798 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428kV
[7 empty] | 2018-01-31 12:46 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.46806 | N/A | N/A | N/A | NR/01/2870 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[12 empty] | 0 | 0 | 0 | 1900-01-13 04:27 | [7 empty] | 100
1 | 94 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 95 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 96 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 97 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 |  | 2018-01-07 21:23 | 2018-01-08 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.35903 | N/A | N/A | N/A | NR/01/768 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422kV
[7 empty] | 2018-01-14 21:18 | 2018-01-15 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/01/1444 | LVRD | Line hand tripped for voltage regulation. Panchkulla= 422kV
[7 empty] | 2018-01-26 22:02 | 2018-01-27 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.33889 | N/A | N/A | N/A | NR/01/2498 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421kV
[12 empty] | 0 | 0 | 0 | 1899-12-31 01:17 | [7 empty] | 100
1 | 98 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 |  | 2018-01-01 | 2018-01-01 06:04 | -- | -- | -- | 0 | 0 | 0 | 0.25278 | N/A | N/A | N/A | NR/12/4314 | LVRD | Line hand tripped for voltage regulation. Patiala= 425KV
[7 empty] | 2018-01-01 21:47 | 2018-01-02 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/01/119 | LVRD | Line hand tripped for voltage regulation. Patiala= 423KV
[7 empty] | 2018-01-02 21:18 | 2018-01-03 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.3875 | N/A | N/A | N/A | NR/01/223 | LVRD | Line hand tripped for voltage regulation. Patiala= 423KV
[7 empty] | 2018-01-03 21:28 | 2018-01-04 10:02 | -- | -- | -- | 0 | 0 | 0 | 0.52361 | N/A | N/A | N/A | NR/01/342 | LVRD | Line hand tripped for voltage regulation. Patiala= 421KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 12:02 | [7 empty] | 100
1 | 99 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 |  | 2018-01-25 02:18 | 2018-01-25 07:16 | -- | -- | -- | 0 | 0 | 0 | 0.20694 | N/A | N/A | N/A | NR/01/2369 | LVRD | Line hand tripped for voltage regulation. Patiala= 428kV
[7 empty] | 2018-01-25 21:46 | 2018-01-27 06:33 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:47 | N/A | N/A | N/A | NR/01/2447 | LVRD | Line hand tripped for voltage regulation. Patiala= 420kV
[12 empty] | 0 | 0 | 0 | 1899-12-31 13:45 | [7 empty] | 100
1 | 100 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 |  | 2018-01-01 | 2018-01-01 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.25347 | N/A | N/A | N/A | NR/12/4314 | LVRD | Line hand tripped for voltage regulation. Kaithal= 425KV
[7 empty] | 2018-01-01 21:49 | 2018-01-02 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.33681 | N/A | N/A | N/A | NR/01/119 | LVRD | Line hand tripped for voltage regulation. Kaithal= 423KV
[7 empty] | 2018-01-02 21:20 | 2018-01-03 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/01/223 | LVRD | Line hand tripped for voltage regulation. Kaithal= 422KV
[7 empty] | 2018-01-03 21:30 | 2018-01-04 10:01 | -- | -- | -- | 0 | 0 | 0 | 0.52153 | N/A | N/A | N/A | NR/01/342 | LVRD | Line hand tripped for voltage regulation. Kaithal= 420KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 11:58 | [7 empty] | 100
1 | 101 | NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 |  | 2018-01-25 02:19 | 2018-01-25 07:15 | -- | -- | -- | 0 | 0 | 0 | 0.20556 | N/A | N/A | N/A | NR/01/2369 | LVRD | Line hand tripped for voltage regulation. Kaithal= 428kV
[7 empty] | 2018-01-25 21:47 | 2018-01-27 06:34 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:47 | N/A | N/A | N/A | NR/01/2447 | LVRD | Line hand tripped for voltage regulation. Kaithal= 420kV
[12 empty] | 0 | 0 | 0 | 1899-12-31 13:43 | [7 empty] | 100
1 | 102 | NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2018-01-04 05:52 | 2018-01-04 06:34 | -- | -- | -- | 0 | 0.029167 | 0 | 0 | N/A | N/A | N/A | ---- | OMSU | A/R on B-N fault from PSTCL, Rajpura & tripped at BBMB, Dehar. FLR Rajpura: 49.19Kms. (Fault in BBMB portion. POWERGRID portion length is 14.4 km).
[7 empty] | 2018-01-05 15:54 | 2018-01-05 18:37 | -- | -- | -- | 0 | 0 | 0 | 0.11319 | N/A | N/A | N/A | NR/01/554 | OSPD | SD taken by BBMB for TL maintenance works.
[7 empty] | 2018-01-10 08:08 | 2018-01-10 18:33 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/01/1000 | OSPD | SD taken by BBMB for switchyard equipment maintenance at Dehar.
[7 empty] | 2018-01-11 08:32 | 2018-01-11 17:26 | -- | -- | -- | 0 | 0 | 0 | 0.37083 | N/A | N/A | N/A | NR/01/1107 | OSPD | SD taken by BBMB for switchyard equipment maintenance at Dehar.
[7 empty] | 2018-01-27 02:07 | 2018-01-27 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.17292 | N/A | N/A | N/A | NR/01/2512 | LVRD | Line hand tripped for voltage regulation.
[7 empty] | 2018-01-28 00:46 | 2018-01-28 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.22778 | N/A | N/A | N/A | NR/01/2590 | LVRD | Line hand tripped for voltage regulation. Rajpura= 425kV
[9 empty] | -- | -- | -- | 0 | 0.029167 | 0 | 1899-12-31 07:39 | N/A | N/A | N/A |  |  |  |  | 100
1 | 103 | NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2018-01-01 10:33 | 2018-01-01 18:31 | -- | -- | -- | 0 | 0 | 0 | 0.33194 | N/A | N/A | N/A | NR/01/45 | OSPD | SD taken by BBMB for TL maintenance works.
[7 empty] | 2018-01-02 09:36 | 2018-01-02 19:08 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/01/152 | OSPD | SD taken by BBMB for TL maintenance works.
[7 empty] | 2018-01-08 03:59 | 2018-01-08 05:49 | -- | -- | -- | 0 | 0 | 0.076389 | 0 | N/A | N/A | N/A | NR/01/782 | GOVC | Line Tripped on high voltage.
[12 empty] | 0 | 0 | 0.076389 | 0.72917 | [7 empty] | 100
1 | 104 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 |  | 2018-01-01 | 2018-01-01 06:30 | -- | -- | -- | 0 | 0 | 0 | 0.27083 | N/A | N/A | N/A | NR/12/4314 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-01-01 21:39 | 2018-01-02 07:24 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/01/119 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427KV
[7 empty] | 2018-01-02 21:10 | 2018-01-03 09:44 | -- | -- | -- | 0 | 0 | 0 | 0.52361 | N/A | N/A | N/A | NR/01/223 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-01-04 01:31 | 2018-01-07 05:59 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 04:28 | N/A | N/A | N/A | NR/01/347 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-01-13 00:23 | 2018-01-15 06:53 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 06:30 | N/A | N/A | N/A | NR/01/1375 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-01-20 23:01 | 2018-01-21 06:38 | -- | -- | -- | 0 | 0 | 0 | 0.31736 | N/A | N/A | N/A | NR/01/2001 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427kV
[7 empty] | 2018-01-21 22:16 | 2018-01-22 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.30208 | N/A | N/A | N/A | NR/01/2061 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427kV
[7 empty] | 2018-01-25 02:18 | 2018-01-25 07:17 | -- | -- | -- | 0 | 0 | 0 | 0.20764 | N/A | N/A | N/A | NR/01/2369 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 433kV
[7 empty] | 2018-01-25 21:42 | 2018-01-26 07:50 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/01/2447 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[12 empty] | 0 | 0 | 0 | 1900-01-06 21:46 | [7 empty] | 100
1 | 105 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 |  | 2018-01-01 | 2018-01-01 07:29 | -- | -- | -- | 0 | 0 | 0 | 0.31181 | N/A | N/A | N/A | NR/12/4305 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-01-01 19:43 | 2018-01-02 07:21 | -- | -- | -- | 0 | 0 | 0 | 0.48472 | N/A | N/A | N/A | NR/01/106 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-01-02 21:09 | 2018-01-03 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/01/223 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-01-03 21:20 | 2018-01-04 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/01/342 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-01-04 21:38 | 2018-01-05 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.34236 | N/A | N/A | N/A | NR/01/467 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427KV
[7 empty] | 2018-01-05 21:21 | 2018-01-06 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/01/602 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-01-07 23:53 | 2018-01-08 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.275 | N/A | N/A | N/A | NR/01/772 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-01-10 21:20 | 2018-01-11 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.34861 | N/A | N/A | N/A | NR/01/1091 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424V
[7 empty] | 2018-01-11 21:20 | 2018-01-12 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/01/1193 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422kV
[7 empty] | 2018-01-12 20:02 | 2018-01-14 09:04 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 13:02 | N/A | N/A | N/A | NR/01/1278 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-14 21:18 | 2018-01-15 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.36181 | N/A | N/A | N/A | NR/01/1444 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-20 23:02 | 2018-01-21 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.31319 | N/A | N/A | N/A | NR/01/2001 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427kV
[7 empty] | 2018-01-21 22:15 | 2018-01-22 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.30069 | N/A | N/A | N/A | NR/01/2061 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427kV
[7 empty] | 2018-01-23 00:15 | 2018-01-23 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.29375 | N/A | N/A | N/A | NR/01/2156 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-01-23 23:52 | 2018-01-24 07:10 | -- | -- | -- | 0 | 0 | 0 | 0.30417 | N/A | N/A | N/A | NR/01/2255 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429kV
[7 empty] | 2018-01-24 21:33 | 2018-01-25 07:16 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/01/2358 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-25 21:43 | 2018-01-27 06:21 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:38 | N/A | N/A | N/A | NR/01/2447 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-01-27 23:34 | 2018-01-29 07:15 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:41 | N/A | N/A | N/A | NR/01/2589 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425kV
[7 empty] | 2018-01-29 21:49 | 2018-01-30 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/01/2758 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-01-31 00:16 | 2018-01-31 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.29444 | N/A | N/A | N/A | NR/01/2830 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427kV
[12 empty] | 0 | 0 | 0 | 1900-01-09 01:08 | [7 empty] | 100
1 | 106 | NR240116 | 400KV Dadri-Kaithal | 213 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 107 | NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 |  | 2018-01-24 11:43 | 2018-01-24 11:59 | -- | -- | -- | 0.011111 | 0 | 0 | 0 | N/A | N/A | N/A | - | OSFT | Line tripped during checking of control wiring at Kaithal.
[12 empty] | 0.011111 | 0 | 0 | 0 | [7 empty] | 99.96
1 | 108 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 |  | 2018-01-09 19:43 | 2018-01-10 19:51 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 00:08 | N/A | N/A | N/A | NR/01/973 | OSPD | SD taken by NHPC for rectification of damaged BUS BAR at Parbati 2.
[12 empty] | 0 | 0 | 0 | 1899-12-31 00:08 | [7 empty] | 100
1 | 109 | NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 |  | 2018-01-23 12:19 | 2018-01-23 14:01 | -- | -- | -- | 0 | 0 | 0.070833 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage.
[12 empty] | 0 | 0 | 0.070833 | 0 | [7 empty] | 100
1 | 110 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 111 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 112 | NR240122 | 400KV Kurukshetra - Jind - I | 103.6 | NR2 |  | 2018-01-01 | 2018-01-01 07:31 | -- | -- | -- | 0 | 0 | 0 | 0.31319 | N/A | N/A | N/A | NR/12/4307 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429KV
[7 empty] | 2018-01-02 03:08 | 2018-01-02 07:53 | -- | -- | -- | 0 | 0 | 0 | 0.19792 | N/A | N/A | N/A | NR/01/127 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 433KV
[7 empty] | 2018-01-02 21:27 | 2018-01-03 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.34583 | N/A | N/A | N/A | NR/01/223 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 426KV
[7 empty] | 2018-01-03 21:53 | 2018-01-04 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.33264 | N/A | N/A | N/A | NR/01/342 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 420KV
[7 empty] | 2018-01-06 02:26 | 2018-01-06 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.16875 | N/A | N/A | N/A | NR/01/607 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 433KV
[7 empty] | 2018-01-08 00:48 | 2018-01-08 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.24097 | N/A | N/A | N/A | NR/01/775 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 431KV
[7 empty] | 2018-01-10 21:33 | 2018-01-11 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/01/1091 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 426KV
[7 empty] | 2018-01-11 21:35 | 2018-01-12 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/01/1193 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 422kV
[7 empty] | 2018-01-13 19:56 | 2018-01-14 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/01/1365 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[7 empty] | 2018-01-16 21:42 | 2018-01-17 06:11 | -- | -- | -- | 0 | 0 | 0 | 0.35347 | N/A | N/A | N/A | NR/01/1613 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 424kV
[7 empty] | 2018-01-17 21:46 | 2018-01-18 08:24 | -- | -- | -- | 0 | 0 | 0 | 0.44306 | N/A | N/A | N/A | NR/01/1704 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 420kV
[7 empty] | 2018-01-18 21:36 | 2018-01-19 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.32361 | N/A | N/A | N/A | NR/01/1819 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 423kV
[7 empty] | 2018-01-19 23:55 | 2018-01-20 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.22569 | N/A | N/A | N/A | NR/01/1910 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 424kV
[7 empty] | 2018-01-23 14:58 | 2018-01-24 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.68056 | N/A | N/A | N/A | NR/01/2212 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 433KV
[7 empty] | 2018-01-27 00:29 | 2018-01-27 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.24236 | N/A | N/A | N/A | NR/01/2502 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 426kV
[7 empty] | 2018-01-28 01:49 | 2018-01-28 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.17431 | N/A | N/A | N/A | NR/01/2595 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 426kV
[7 empty] | 2018-01-28 13:43 | 2018-01-29 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.76181 | N/A | N/A | N/A | NR/01/2636 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[7 empty] | 2018-01-29 21:59 | 2018-01-30 07:18 | -- | -- | -- | 0 | 0 | 0 | 0.38819 | N/A | N/A | N/A | NR/01/2758 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 424kV
[7 empty] | 2018-01-30 13:06 | 2018-01-30 20:23 | -- | -- | -- | 0 | 0 | 0 | 0.30347 | N/A | N/A | N/A | NR/01/2797 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428kV
[7 empty] | 2018-01-31 00:20 | 2018-01-31 07:23 | -- | -- | -- | 0 | 0 | 0 | 0.29375 | N/A | N/A | N/A | NR/01/2830 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427kV
[7 empty] | 2018-01-31 12:58 | 2018-01-31 18:51 | -- | -- | -- | 0 | 0 | 0 | 0.24514 | N/A | N/A | N/A | NR/01/2870 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV
[12 empty] | 0 | 0 | 0 | 1900-01-06 03:58 | [7 empty] | 100
1 | 113 | NR240123 | 400KV Kurukshetra - Jind - II | 103.6 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 114 | NR240124 | 400KV KISHENPUR-Dulhasti - II |  | NR2 |  | --- | 2018-01-19 17:05 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/1875 | --- | First Time Charging. Line charged from Kishenpur end only. Not Synchronised from Dulhasti end As per NRLDC instructions.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 115 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 |  | 2018-01-01 | 2018-01-01 15:07 | -- | -- | -- | 0 | 0 | 0 | 0.62986 | N/A | N/A | N/A | NR/12/4306 NLDC/1779 | LVRD | Line hand tripped for voltage regulation. Moga=799 KV
[7 empty] | 2018-01-01 19:36 | 2018-01-02 10:22 | -- | -- | -- | 0 | 0 | 0 | 0.61528 | N/A | N/A | N/A | NR/01/107 NLDC/41 | LVRD | Line hand tripped for voltage regulation. Moga=802 KV
[7 empty] | 2018-01-02 10:22 | 2018-01-02 18:51 | -- | -- | -- | 0 | 0 | 0 | 0.35347 | N/A | N/A | N/A | NR/01/164 NLDC/68 | LCSD | SD taken for Gantry tower erection work of 765KV Bikaner- Moga DC under construction.
[7 empty] | 2018-01-02 20:37 | 2018-01-03 07:23 | -- | -- | -- | 0 | 0 | 0 | 0.44861 | N/A | N/A | N/A | NR/01/221 NLDC/94 | LVRD | Line hand tripped for voltage regulation. Moga= 799KV
[7 empty] | 2018-01-03 20:55 | 2018-01-04 08:05 | -- | -- | -- | 0 | 0 | 0 | 0.46528 | N/A | N/A | N/A | NR/01/341 NLDC/167 | LVRD | Line hand tripped for voltage regulation. Moga= 801KV
[7 empty] | 2018-01-04 11:41 | 2018-01-04 13:23 | -- | -- | -- | 0.070833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/400 NLDC/197 | OSPT | SD taken for rectification of sparking Isolator at Meerut.
[7 empty] | 2018-01-04 20:03 | 2018-01-05 10:12 | -- | -- | -- | 0 | 0 | 0 | 0.58958 | N/A | N/A | N/A | NR/01/460 NLDC/218 | LVRD | Line hand tripped for voltage regulation. Moga= 797KV
[7 empty] | 2018-01-05 20:27 | 2018-01-06 09:57 | -- | -- | -- | 0 | 0 | 0 | 0.5625 | N/A | N/A | N/A | NR/01/597 NLDC/272 | LVRD | Line hand tripped for voltage regulation. Moga= 798KV
[7 empty] | 2018-01-06 20:13 | 2018-01-07 07:27 | -- | -- | -- | 0 | 0 | 0 | 0.46806 | N/A | N/A | N/A | NR/01/690 NLDC/330 | LVRD | Line hand tripped for voltage regulation. Moga= 797KV
[7 empty] | 2018-01-07 15:10 | 2018-01-08 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.63403 | N/A | N/A | N/A | NR/01/743 NLDC/353 | LVRD | Line hand tripped for voltage regulation. Moga= 797KV
[7 empty] | 2018-01-08 20:12 | 2018-01-09 07:47 | -- | -- | -- | 0 | 0 | 0 | 0.48264 | N/A | N/A | N/A | NR/01/869 NLDC/426 | LVRD | Line hand tripped for voltage regulation. Moga= 802KV
[7 empty] | 2018-01-09 20:26 | 2018-01-10 07:35 | -- | -- | -- | 0 | 0 | 0 | 0.46458 | N/A | N/A | N/A | NR/01/978 NLDC/501 | LVRD | Line hand tripped for voltage regulation. Moga= 799KV
[7 empty] | 2018-01-10 21:36 | 2018-01-11 07:11 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/01/1092 NLDC/557 | LVRD | Line hand tripped for voltage regulation. Moga= 797kV
[7 empty] | 2018-01-11 19:41 | 2018-01-12 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.46806 | N/A | N/A | N/A | NR/01/1187 NLDC/620 | LVRD | Line hand tripped for voltage regulation. Moga= 795kV
[7 empty] | 2018-01-12 20:30 | 2018-01-13 07:30 | -- | -- | -- | 0 | 0 | 0 | 0.45833 | N/A | N/A | N/A | NR/01/1279 NL/01/681 | LVRD | Line hand tripped for voltage regulation. Moga= 793kV
[7 empty] | 2018-01-13 20:29 | 2018-01-14 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.47986 | N/A | N/A | N/A | NR/01/1366 NL/01/742 | LVRD | Line hand tripped for voltage regulation. Moga= 804kV
[7 empty] | 2018-01-14 13:15 | 2018-01-15 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.70833 | N/A | N/A | N/A | NR/01/1411 NL/01/760 | LVRD | Line hand tripped for voltage regulation. Moga= 802kV
[7 empty] | 2018-01-15 20:15 | 2018-01-16 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.44167 | N/A | N/A | N/A | NR/01/11528 NL/01/811 | LVRD | Line hand tripped for voltage regulation. Moga= 796kV
[7 empty] | 2018-01-16 19:36 | 2018-01-17 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.45833 | N/A | N/A | N/A | NR/01/1605 NL/01/858 | LVRD | Line hand tripped for voltage regulation. Moga= 795kV
[7 empty] | 2018-01-17 20:20 | 2018-01-18 07:36 | -- | -- | -- | 0 | 0 | 0 | 0.46944 | N/A | N/A | N/A | NR/01/1693 NL/01/915 | LVRD | Line hand tripped for voltage regulation. Moga= 796KV.
[7 empty] | 2018-01-18 20:54 | 2018-01-19 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/01/1818 NLDC/966 | LVRD | Line hand tripped for voltage regulation. Moga= 796KV
[7 empty] | 2018-01-19 21:45 | 2018-01-20 07:24 | -- | -- | -- | 0 | 0 | 0 | 0.40208 | N/A | N/A | N/A | NR/01/1906 NLDC/1032 | LVRD | Line hand tripped for voltage regulation. Moga= 799KV
[7 empty] | 2018-01-20 19:55 | 2018-01-21 07:41 | -- | -- | -- | 0 | 0 | 0 | 0.49028 | N/A | N/A | N/A | NR/01/1988 NLDC/1080 | LVRD | Line hand tripped for voltage regulation. Moga= 795KV
[7 empty] | 2018-01-21 13:51 | 2018-01-22 09:07 | -- | -- | -- | 0 | 0 | 0 | 0.80278 | N/A | N/A | N/A | NR/01/2035 NLDC/1107 | LVRD | Line hand tripped for voltage regulation. Moga= 798KV
[7 empty] | 2018-01-22 19:43 | 2018-01-23 07:10 | -- | -- | -- | 0 | 0 | 0 | 0.47708 | N/A | N/A | N/A | NR/01/2144 NLDC/1179 | LVRD | Line hand tripped for voltage regulation. Moga= 796KV
[7 empty] | 2018-01-23 13:09 | 2018-01-24 07:41 | -- | -- | -- | 0 | 0 | 0 | 0.77222 | N/A | N/A | N/A | NR/01/2209 NLDC/1218 | LVRD | Line hand tripped for voltage regulation. Moga= 809KV
[7 empty] | 2018-01-24 20:45 | 2018-01-25 07:05 | -- | -- | -- | 0 | 0 | 0 | 0.43056 | N/A | N/A | N/A | NR/01/2352 | LVRD | Line hand tripped for voltage regulation. Moga= 804kV
[7 empty] | 2018-01-25 20:28 | 2018-01-26 08:12 | -- | -- | -- | 0 | 0 | 0 | 0.48889 | N/A | N/A | N/A | NR/01/2439 | LVRD | Line hand tripped for voltage regulation. Moga= 800kV
[7 empty] | 2018-01-26 13:16 | 2018-01-27 07:28 | -- | -- | -- | 0 | 0 | 0 | 0.75833 | N/A | N/A | N/A | NR/01/2475 NLDC/1353 | LVRD | Line hand tripped for voltage regulation. Moga= 803kV
[7 empty] | 2018-01-27 21:00 | 2018-01-28 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.42083 | N/A | N/A | N/A | NR/01/2583 NLDC/1401 | LVRD | Line hand tripped for voltage regulation. Moga= 797kV
[7 empty] | 2018-01-28 14:08 | 2018-01-29 09:22 | -- | -- | -- | 0 | 0 | 0 | 0.80139 | N/A | N/A | N/A | NR/01/2640 NLDC/1420 | LVRD | Line hand tripped for voltage regulation. Moga= 796kV
[7 empty] | 2018-01-29 19:51 | 2018-01-30 07:37 | -- | -- | -- | 0 | 0 | 0 | 0.49028 | N/A | N/A | N/A | NR/01/2750 NLDC/1749 | LVRD | Line hand tripped for voltage regulation. Moga= 797kV
[7 empty] | 2018-01-30 13:39 | 2018-01-31 07:22 | -- | -- | -- | 0 | 0 | 0 | 0.73819 | N/A | N/A | N/A | NR/01/2800 NLDC/1506 | LVRD | Line hand tripped for voltage regulation. Moga= 801kV
[7 empty] | 2018-01-31 13:06 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.45417 | N/A | N/A | N/A | NR/01/2872 NLDC/1547 | LVRD | Line hand tripped for voltage regulation. Moga= 803kV
[12 empty] | 0.070833 | 0 | 0 | 1900-01-16 13:00 | [7 empty] | 99.77
1 | 116 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 117 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 118 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 119 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 120 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 121 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 122 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 |  | 2018-01-01 | 2018-01-23 13:02 | -- | -- | -- | 0 | 0 | 0 | 1900-01-21 13:02 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R handtripped for voltage regulation. Wagoora =393KV
[7 empty] | 2018-01-23 18:13 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 05:47 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R handtripped for voltage regulation. Wagoora =395KV
[12 empty] | 0 | 0 | 0 | 1900-01-29 18:49 | [7 empty] | 100
1 | 123 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 124 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 125 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 126 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 127 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 128 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 129 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 130 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 131 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 132 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 133 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 134 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 135 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 136 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 137 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 138 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 139 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 140 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 141 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 142 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 143 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 144 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 145 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 146 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 |  | 2018-01-01 | 2018-02-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R handtripped for voltage regulation. New Wanpoh =393KV
[12 empty] | 0 | 0 | 0 | 1900-01-30 | [7 empty] | 100
1 | 147 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 148 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 149 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 150 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 151 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 |  | 2018-01-02 12:31 | 2018-01-02 15:20 | -- | -- | -- | 0.11736 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/173 | OSPT | SD taken for replacement of PRD.
[7 empty] | 2018-01-08 11:25 | 2018-01-10 15:25 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 04:00 | N/A | N/A | N/A | NR/01/825 | OSPD | SD taken by BBMB for replacement of defective CT.
[12 empty] | 0.11736 | 0 | 0 | 1900-01-01 04:00 | [7 empty] | 100
1 | 152 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 |  | 2018-01-02 12:31 | 2018-01-02 15:20 | -- | -- | -- | 0.11736 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/173 | OSPT | SD taken for replacement of PRD.
[7 empty] | 2018-01-08 11:25 | 2018-01-10 15:25 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 04:00 | N/A | N/A | N/A | NR/01/825 | OSPD | SD taken by BBMB for replacement of defective CT.
[12 empty] | 0.11736 | 0 | 0 | 1900-01-01 04:00 | [7 empty] | 100
1 | 153 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 |  | 2018-01-18 10:26 | 2018-01-18 14:25 | -- | -- | -- | 0.16597 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/1752 | OSPT | SD taken for AMP works.
[12 empty] | 0.16597 | 0 | 0 | 0 | [7 empty] | 99.46
1 | 154 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 155 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 156 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 157 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 158 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 159 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 160 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 |  | 2018-01-01 | 2018-01-21 23:27 | -- | -- | -- | 1900-01-19 23:27 | 0 | 0 | 0 | N/A | N/A | N/A | NR/12/1357 | OSPT | SD taken for rectification work after ICT tripped on Buchholz & REF Fault.
[12 empty] | 1900-01-19 23:27 | 0 | 0 | 0 | [7 empty] | 100
1 | 161 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 162 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 163 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 164 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 165 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 166 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 167 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 168 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 169 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 170 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 171 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 |  | 2018-01-22 20:40 | 2018-01-22 20:55 | -- | -- | -- | 0.010417 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2152 | OSFT | ICT Tripped on over flux protection operation.
[12 empty] | 0.010417 | 0 | 0 | 0 | [7 empty] | 99.97
1 | 172 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 173 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 174 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 175 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 176 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 177 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 178 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 |  | 2018-01-10 14:58 | 2018-01-10 15:22 | -- | -- | -- | 0.016667 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/1045 | OSPT | Sd for taking spare unit in service in place of B-ph unit for AMP works.
[12 empty] | 0.016667 | 0 | 0 | 0 | [7 empty] | 99.95
1 | 179 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 180 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 181 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 182 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 183 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 184 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 185 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 |  | 2018-01-18 11:06 | 2018-01-18 19:13 | -- | -- | -- | 0.33819 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/1748 | OSPT | SD taken for AMP works.
[12 empty] | 0.33819 | 0 | 0 | 0 | [7 empty] | 98.91
1 | 186 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 187 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 188 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 189 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 190 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 191 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 192 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 |  | 2018-01-09 10:59 | 2018-01-09 18:45 | -- | -- | -- | 0.32361 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/924 | OSPT | SD taken for AMP works & Insulation Coating of Tertiary Winding.
[12 empty] | 0.32361 | 0 | 0 | 0 | [7 empty] | 98.96
1 | 193 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 194 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 195 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 99.02
1 | 196 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 197 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 198 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 |  | 2018-01-01 11:45 | 2018-01-01 17:12 | -- | -- | -- | 0 | 0 | 0 | 0.22708 | N/A | N/A | N/A | NR/01/58 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[7 empty] | 2018-01-02 09:13 | 2018-01-02 17:18 | -- | -- | -- | 0 | 0 | 0 | 0.33681 | N/A | N/A | N/A | NR/01/155 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[7 empty] | 2018-01-03 09:38 | 2018-01-03 15:47 | -- | -- | -- | 0 | 0 | 0 | 0.25625 | N/A | N/A | N/A | NR/01/262 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[12 empty] | 0 | 0 | 0 | 0.82014 | [7 empty] | 100
1 | 199 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 200 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 |  | 2018-01-04 09:10 | 2018-01-04 17:33 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/01/378 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[7 empty] | 2018-01-05 09:49 | 2018-01-05 17:24 | -- | -- | -- | 0 | 0 | 0 | 0.31597 | N/A | N/A | N/A | NR/01/502 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[7 empty] | 2018-01-06 09:26 | 2018-01-06 17:59 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/01/628 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[7 empty] | 2018-01-07 09:41 | 2018-01-07 17:02 | -- | -- | -- | 0 | 0 | 0 | 0.30625 | N/A | N/A | N/A | NR/01/729 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[7 empty] | 2018-01-08 09:04 | 2018-01-08 18:19 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/01/811 | SCSD | SD Taken for GIB (Gas Insulated Bus) duct erection for ICT-3 under construction.
[12 empty] | 0 | 0 | 0 | 1899-12-31 17:07 | [7 empty] | 100
1 | 201 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 202 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 203 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 |  | 2018-01-29 11:49 | 2018-01-29 13:37 | -- | -- | -- | 0.075 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2708 | OSPT | SD taken for DGA oil samplibg of 220KV side R Ph CT due to raised level of bellow from normal level.
[12 empty] | 0.075 | 0 | 0 | 0 | [7 empty] | 99.76
1 | 204 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 205 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 |  | 2018-01-08 13:08 | 2018-01-08 16:08 | -- | -- | -- | 0.125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/833 | OSPT | SD taken for AMP works & Insulation Coating of Tertiary Winding.
[12 empty] | 0.125 | 0 | 0 | 0 | [7 empty] | 99.6
1 | 206 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 207 | NR2ICT73 | KAITHAL 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 208 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 |  | 2018-01-10 03:55 | 2018-01-10 04:33 | -- | -- | -- | 0.026389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/988 | SEMT | Tripped due to low water level in thyrister valve cooling system.
[12 empty] | 0.026389 | 0 | 0 | 0 | [7 empty] | 99.91
1 | 209 | NR2SVC02 | New Wanpoh -200/+300 MVAR SVC |  | NR2 |  | 2018-01-19 11:19 | 2018-01-19 16:48 | -- | -- | -- | 0.22847 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/1858 | OSPT | SD taken for rectification of problem in cooling system.
[12 empty] | 0.22847 | 0 | 0 | 0 | [7 empty] | 99.26
1 | 210 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 |  | 2018-01-03 17:08 | 2018-01-03 17:57 | -- | -- | -- | 0.034028 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/317 NLDC/150 WRLDC/340 | OMST | Pole Blocked due to Maloperation of control system at Kurukshetra.
[7 empty] | 2018-01-06 16:15 | 2018-01-06 17:13 | -- | -- | -- | 0.040278 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/316 | OMST | Pole Blocked due to DC differential protection Optd. At Champa.
[7 empty] | 2018-01-09 14:33 | 2018-01-09 16:42 | -- | -- | -- | 0.089583 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/937 NLDC/481 | OSPT | SD taken for attending SF6 leakage in bushing of convertor transformer at Kurukshetra.
[7 empty] | 2018-01-30 08:38 | 2018-01-30 19:00 | -- | -- | -- | 0.43194 | 0 | 0 | 0 | N/A | N/A | N/A | NL/01/1498 | OSPT | SD taken for Software Updation
[12 empty] | 0.59583 | 0 | 0 | 0 | [7 empty] | 98.08
1 | 211 | NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 |  | 2018-01-03 15:13 | 2018-01-03 17:40 | -- | -- | -- | 0.10208 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/311 NLDC/146 WRLDC/335 | OMST | Pole Blocked due to commutation failure at Kurukshetra.
[7 empty] | 2018-01-18 15:58 | 2018-01-18 17:18 | -- | -- | -- | 0.055556 | 0 | 0 | 0 | N/A | N/A | N/A | NL/01/951 | OMST | Pole blocked due to VBE major fault at Kurukshetra end
[7 empty] | 2018-01-27 15:35 | 2018-01-27 16:00 | -- | -- | -- | 0.017361 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2568 NLDC/1387 WRLDC/277 | OMST | Pole Blocked due to "External Block from valve colling system" optd. At Champa end.
[7 empty] | 2018-01-31 08:55 | 2018-01-31 18:51 | -- | -- | -- | 0.41389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2850 NLDC/1540 WR/01/3094 | OSPT | SD taken for Software Updation
[7 empty] | 2018-01-31 19:00 | 2018-01-31 19:59 | -- | -- | -- | 0.040972 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/1562 | OMST | Pole blocked due to Converter Tap position stuck at Champa.
[12 empty] | 0.62986 | 0 | 0 | 0 | [7 empty] | 97.97

## NR2 Feb
Standard of Performance data for month of FEBRUARY 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
Annexure-A
| S.No | ELEMENT CODE | ELEMENT NAME | DESCRIPTION (Length/Nos/MVA/MVAr/etc) | Region | Type of Failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration time more than Specified (Y/N) | Difference between Actual and specified | NRLDC Code | Category Code | REASON OF OUTAGE | Outage certifying Agency and reference documents (NRPC) | % Availability as certified by certifying agency
[7 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | POWERGRID | OTHERS | System constraints / Natural calamity/ Militancy | Deemed Available
[12 empty] | @ (T) | # (U) | & ( C ) | * (D)
[12 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
1 | 1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 |  | 2018-02-01 10:02 | 2018-02-01 18:32 | -- | -- | -- | 0.35417 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/23 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-02 09:35 | 2018-02-02 18:34 | -- | -- | -- | 0.37431 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/99A | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-03 09:02 | 2018-02-03 15:33 | -- | -- | -- | 0.27153 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/181 | OSPT | SD taken for installation of additional jumper.
[12 empty] | 1899-12-31 | 0 | 0 | 0 | [7 empty] | 96.43
1 | 2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 |  | 2018-02-05 09:10 | 2018-02-05 18:27 | -- | -- | -- | 0.38681 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/346 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-06 08:19 | 2018-02-06 18:35 | -- | -- | -- | 0.42778 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/410 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-07 08:35 | 2018-02-07 17:32 | -- | -- | -- | 0.37292 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/496 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-08 08:45 | 2018-02-08 18:16 | -- | -- | -- | 0.39653 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/591 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-08 18:40 | 2018-02-08 19:59 | -- | -- | -- | 0 | 0.054861 | 0 | 0 | N/A | N/A | N/A | NR/02/641 | OMSU | Line tripped due to fault in Switchyard at Sewa2 end (Zone-4 fault)
[7 empty] | 2018-02-09 09:43 | 2018-02-09 16:44 | -- | -- | -- | 0.29236 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/688 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-12 13:10 | 2018-02-12 13:57 | -- | -- | -- | 0 | 0.032639 | 0 | 0 | N/A | N/A | N/A | NR/02/1003 | OMSU | Line tripped from Sewa2 end only and remained charged from Mahampur.
[12 empty] | 1899-12-31 21:02 | 0.0875 | 0 | 0 | [7 empty] | 93.3
1 | 3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 |  | 2018-02-01 | 2018-02-01 18:35 | -- | -- | -- | 0.77431 | 0 | 0 | 0 | N/A | N/A | N/A | NR/01/2851 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-02 09:35 | 2018-02-02 18:35 | -- | -- | -- | 0.375 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/99A | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-03 09:02 | 2018-02-03 15:33 | -- | -- | -- | 0.27153 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/181 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-08 18:40 | 2018-02-08 19:54 | -- | -- | -- | 0 | 0.051389 | 0 | 0 | N/A | N/A | N/A | NR/02/641 | OMSU | Line tripped due to fault in Switchyard at Sewa2 end (Zone-4 fault)
[7 empty] | 2018-02-12 06:45 | 2018-02-12 15:06 | -- | -- | -- | 0 | 0 | 0 | 0.34792 | N/A | N/A | N/A | NR/02/941 | LVRD | Line hand tripped for voltage regulation.Sewa2-140KV
[12 empty] | 1899-12-31 10:06 | 0.051389 | 0 | 0.34792 | [7 empty] | 94.93
1 | 4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 |  | 2018-02-10 10:36 | 2018-02-10 18:15 | -- | -- | -- | 0.31875 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/773 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-11 08:47 | 2018-02-11 17:58 | -- | -- | -- | 0.38264 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/851 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-12 13:10 | 2018-02-12 13:45 | -- | -- | -- | 0.024306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1003 | LEFT | Line tripped on Y-N fault. FLR Mahanpur - 5.14 Kms, Iy-0.604 Kamp.
[12 empty] | 0.72569 | 0 | 0 | 0 | [7 empty] | 97.41
1 | 5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 |  | 2018-02-05 08:49 | 2018-02-05 18:23 | -- | -- | -- | 0.39861 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/346 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-06 08:28 | 2018-02-06 18:43 | -- | -- | -- | 0.42708 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/410 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-07 08:24 | 2018-02-07 17:18 | -- | -- | -- | 0.37083 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/496 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-08 08:44 | 2018-02-08 18:14 | -- | -- | -- | 0.39583 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/591 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-08 18:40 | 2018-02-08 20:04 | -- | -- | -- | 0 | 0.058333 | 0 | 0 | N/A | N/A | N/A | NR/02/641 | OMSU | Line tripped due to fault in Switchyard at Sewa2 end (Zone-4 fault)
[7 empty] | 2018-02-09 09:49 | 2018-02-09 17:24 | -- | -- | -- | 0.31597 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/688 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-10 10:34 | 2018-02-10 18:02 | -- | -- | -- | 0.31111 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/773 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-11 08:36 | 2018-02-11 17:58 | -- | -- | -- | 0.39028 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/851 | OSPT | SD taken for installation of additional jumper.
[7 empty] | 2018-02-12 12:47 | 2018-02-12 13:56 | -- | -- | -- | 0.047917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1003 | LEFT | Line tripped on Y-N fault. FLR Kathua: 11.4 Kms, IY-1.8 Kamps.
[12 empty] | 1900-01-01 15:47 | 0.058333 | 0 | 0 | [7 empty] | 90.51
1 | 6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 |  | 2018-02-01 21:32 | 2018-02-02 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.34097 | N/A | N/A | N/A | NR/02/77 | LVRD | Line hand tripped for voltage regulation. Berasuil= 230kV
[7 empty] | 2018-02-02 22:44 | 2018-02-03 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.27917 | N/A | N/A | N/A | NR/02/155 | LVRD | Line hand tripped for voltage regulation. Berasuil= 235kV
[7 empty] | 2018-02-03 22:36 | 2018-02-04 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.29583 | N/A | N/A | N/A | NR/02/262 | LVRD | Line hand tripped for voltage regulation. Berasuil= 235kV
[7 empty] | 2018-02-04 22:44 | 2018-02-05 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.28681 | N/A | N/A | N/A | NR/02/328 | LVRD | Line hand tripped for voltage regulation. Berasuil= 233kV
[7 empty] | 2018-02-05 22:43 | 2018-02-06 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.30208 | N/A | N/A | N/A | NR/02/395 | LVRD | Line hand tripped for voltage regulation. Berasuil= 232kV
[7 empty] | 2018-02-07 00:26 | 2018-02-07 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.20833 | N/A | N/A | N/A | NR/02/483 | LVRD | Line hand tripped for voltage regulation. Berasuil= 238kV.
[7 empty] | 2018-02-12 01:15 | 2018-02-12 01:40 | -- | -- | -- | 0 | 0 | 0.017361 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Bairasuil end only and remained charged at Jessore.
[7 empty] | 2018-02-12 01:40 | 2018-02-12 10:10 | -- | -- | -- | 0 | 0 | 0 | 0.35417 | N/A | N/A | N/A | NR/02/914 | LVRD | Line hand tripped for voltage regulation.
[7 empty] | 2018-02-12 22:02 | 2018-02-13 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.37778 | N/A | N/A | N/A | NR/02/1037 | LVRD | Line hand tripped for voltage regulation. Berasuil= 241kV.
[7 empty] | 2018-02-13 22:08 | 2018-02-14 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.33958 | N/A | N/A | N/A | NR/02/1170 | LVRD | Line hand tripped for voltage regulation. Bairasuil= 237kV.
[7 empty] | 2018-02-14 22:11 | 2018-02-15 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.29236 | N/A | N/A | N/A | NR/02/1228 | LVRD | Line hand tripped for voltage regulation. Bairasuil= 238kV.
[12 empty] | 0 | 0 | 0.017361 | 1900-01-02 01:51 | [7 empty] | 100
1 | 7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 |  | 2018-02-01 | 2018-02-01 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.22986 | N/A | N/A | N/A | NR/01/2917 | LVRD | Line hand tripped for voltage regulation . Berasuil=235kV.
[7 empty] | 2018-02-01 02:59 | 2018-02-01 03:18 | -- | -- | -- | 0 | 0 | 0.013194 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Bairasuil end only and remained charged at Jessore.
[7 empty] | 2018-02-01 03:18 | 2018-02-01 06:59 | -- | -- | -- | 0 | 0 | 0 | 0.15347 | N/A | N/A | N/A | NR/02/03 | LVRD | Line hand tripped for voltage regulation.
[7 empty] | 2018-02-01 22:10 | 2018-02-02 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.30694 | N/A | N/A | N/A | NR/02/77 | LVRD | Line hand tripped for voltage regulation. Berasuil= 230kV
[7 empty] | 2018-02-02 22:41 | 2018-02-03 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.28125 | N/A | N/A | N/A | NR/02/155 | LVRD | Line hand tripped for voltage regulation. Berasuil= 235kV
[7 empty] | 2018-02-03 22:26 | 2018-02-04 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.30208 | N/A | N/A | N/A | NR/02/262 | LVRD | Line hand tripped for voltage regulation. Berasuil= 235kV
[7 empty] | 2018-02-04 22:41 | 2018-02-05 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.28819 | N/A | N/A | N/A | NR/02/328 | LVRD | Line hand tripped for voltage regulation. Berasuil= 233kV
[7 empty] | 2018-02-05 22:29 | 2018-02-06 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.3 | N/A | N/A | N/A | NR/02/395 | LVRD | Line hand tripped for voltage regulation. Berasuil= 232kV
[7 empty] | 2018-02-07 00:36 | 2018-02-07 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.20625 | N/A | N/A | N/A | NR/02/483 | LVRD | Line hand tripped for voltage regulation. Berasuil= 238kV.
[7 empty] | 2018-02-12 01:37 | 2018-02-12 01:40 | -- | -- | -- | 0 | 0 | 0.0020833 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Bairasuil end only and remained charged at Jessore.
[7 empty] | 2018-02-12 01:40 | 2018-02-12 07:21 | -- | -- | -- | 0 | 0 | 0 | 0.23681 | N/A | N/A | N/A | NR/02/914 | LVRD | Line hand tripped for voltage regulation from Pong End
[7 empty] | 2018-02-12 22:01 | 2018-02-13 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | N/A | N/A | N/A | NR/02/1037 | LVRD | Line hand tripped for voltage regulation. Berasuil= 241kV.
[7 empty] | 2018-02-13 22:06 | 2018-02-14 05:04 | -- | -- | -- | 0 | 0 | 0 | 0.29028 | N/A | N/A | N/A | NR/02/1170 | LVRD | Line hand tripped for voltage regulation. Bairasuil= 237kV.
[7 empty] | 2018-02-14 22:05 | 2018-02-15 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.29861 | N/A | N/A | N/A | NR/02/1228 | LVRD | Line hand tripped for voltage regulation. Bairasuil= 238kV.
[7 empty] | 2018-02-24 23:01 | 2018-02-24 23:33 | -- | -- | -- | 0 | 0.022222 | 0 | 0 | N/A | N/A | N/A | NR/02/2006 | OMSU | Line tripped from Pong end only and remained charged from Bairasiul.
[12 empty] | 0 | 0.022222 | 0.015278 | 1900-01-02 05:08 | [7 empty] | 100
1 | 8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 |  | 2018-02-08 15:55 | 2018-02-08 16:36 | -- | -- | -- | 0 | 0.028472 | 0 | 0 | N/A | N/A | N/A | NR/02/623 | OMSU | Line tripped on R-Y fault created by kite thread. FLR Jalandhar : 11.4 KAmps & 12.98Km.
[7 empty] | 2018-02-26 11:53 | 2018-02-26 16:25 | -- | -- | -- | 0 | 0 | 0 | 0.18889 | N/A | N/A | N/A | NR/02/2103 | OSPD | SD taken by PSTCL for maintenance work at Dasuya end.
[12 empty] | 0 | 0.028472 | 0 | 0.18889 | [7 empty] | 100
1 | 10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 |  | 2018-02-18 08:15 | 2018-02-18 14:46 | -- | -- | -- | 0 | 0 | 0 | 0.27153 | N/A | N/A | N/A | NR/02/1470 | OSPD | SD taken by JKPDD for General maintenance works at Udhampur Grid.
[12 empty] | 0 | 0 | 0 | 0.27153 | [7 empty] | 100
1 | 15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 |  | 2018-02-18 08:15 | 2018-02-18 14:49 | -- | -- | -- | 0 | 0 | 0 | 0.27361 | N/A | N/A | N/A | NR/02/1470 | OSPD | SD taken by JKPDD for General maintenance works at Udhampur Grid.
[12 empty] | 0 | 0 | 0 | 0.27361 | [7 empty] | 100
1 | 16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 |  | 2018-02-12 18:45 | 2018-02-12 19:28 | -- | -- | -- | 0 | 0.029861 | 0 | 0 | N/A | N/A | N/A | NR/02/1026 | OMSU | Line tripped on R-Y-B fault caused by heavy thunderstorm in the area. All six lines connected to Salal tripped at the same moment.
[12 empty] | 0 | 0.029861 | 0 | 0 | [7 empty] | 100
1 | 17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 |  | 2018-02-12 18:45 | 2018-02-12 19:33 | -- | -- | -- | 0 | 0.033333 | 0 | 0 | N/A | N/A | N/A | NR/02/1027 | OMSU | Line tripped on R-Y-B fault caused by heavy thunderstorm in the area. All six lines connected to Salal tripped at the same moment.
[12 empty] | 0 | 0.033333 | 0 | 0 | [7 empty] | 100
1 | 18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 |  | 2018-02-12 18:46 | 2018-02-12 19:41 | -- | -- | -- | 0 | 0.038194 | 0 | 0 | N/A | N/A | N/A | NR/02/1027 | OMSU | Line tripped on R-Y-B fault caused by heavy thunderstorm in the area. All six lines connected to Salal tripped at the same moment.FLR Kishanpur- 56.3 Km, Zone-2.
[12 empty] | 0 | 0.038194 | 0 | 0 | [7 empty] | 100
1 | 19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 |  | 2018-02-12 18:46 | 2018-02-12 20:27 | -- | -- | -- | 0.070139 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1027 | OSFT | Line tripped on R-Y-B fault caused by heavy thunderstorm in the area. All six lines connected to Salal tripped at the same moment.FLR Kishanpur- 51.84 Km, Zone-2.
[7 empty] | 2018-02-12 20:27 | 2018-02-14 13:12 | -- | -- | -- | 1899-12-31 16:45 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1033 | OSPT | SD taken for rectification of snapped conductor.
[12 empty] | 1899-12-31 18:26 | 0 | 0 | 0 | [7 empty] | 93.69
1 | 20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 |  | 2018-02-12 18:46 | 2018-02-12 20:15 | -- | -- | -- | 0 | 0.061806 | 0 | 0 | N/A | N/A | N/A | NR/02/1027 | OMSU | Line tripped on R-Y-B fault caused by heavy thunderstorm in the area. All six lines connected to Salal tripped at the same moment.FLR Kishanpur- 61.05 Km, Zone-2.
[12 empty] | 0 | 0.061806 | 0 | 0 | [7 empty] | 100
1 | 21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 |  | 2018-02-12 18:46 | 2018-02-12 19:21 | -- | -- | -- | 0 | 0.024306 | 0 | 0 | N/A | N/A | N/A | NR/02/1026 | OMSU | Line tripped on R-Y-B fault caused by heavy thunderstorm in the area. All six lines connected to Salal tripped at the same moment.
[12 empty] | 0 | 0.024306 | 0 | 0 | [7 empty] | 100
1 | 22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 |  | 2018-02-04 23:33 | 2018-02-05 00:10 | -- | -- | -- | 0.025694 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/329 | LEFT | Line tripped on R-N fault. FLR Sarna -18.08KM, Ir-6.45KA.
[7 empty] | 2018-02-23 12:46 | 2018-02-23 15:07 | -- | -- | -- | 0 | 0 | 0 | 0.097917 | N/A | N/A | N/A | NR/02/1890 | OSPD | SD taken by PSTCL for attending hotspot in R ph CT clamp at Sarna end.
[12 empty] | 0.025694 | 0 | 0 | 0.097917 | [7 empty] | 99.91
1 | 24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:15 | -- | -- | -- | 0.035417 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.035417 | 0 | 0 | 0 | [7 empty] | 99.88
1 | 25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:13 | -- | -- | -- | 0.034028 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.034028 | 0 | 0 | 0 | [7 empty] | 99.89
1 | 26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 |  | 2018-02-13 15:41 | 2018-02-13 16:13 | -- | -- | -- | 0 | 0.022222 | 0 | 0 | N/A | N/A | N/A | NR/02/1139 | OMSU | Line tripped from Chamera3 end only and remained charged at Chamba. Line tripped due to fault in 200kV Chamera3-Budhil line.
[12 empty] | 0 | 0.022222 | 0 | 0 | [7 empty] | 100
1 | 28 | NR222028 | 220KV Jallandhar-Hamirpur(PG) -I | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 29 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 |  | 2018-02-20 09:38 | 2018-02-20 17:31 | -- | -- | -- | 0.32847 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1602 | OSPT | SD taken for AMP works.
[12 empty] | 0.32847 | 0 | 0 | 0 | [7 empty] | 99.83
1 | 30 | NR222030 | 220KV Jallandhar-Hamirpur(PG) -II | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0
1 | 31 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 |  | 2018-02-21 09:13 | 2018-02-21 17:03 | -- | -- | -- | 0.32639 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1682 | OSPT | SD taken for AMP works.
[12 empty] | 0.32639 | 0 | 0 | 0 | [7 empty] | 98.83
1 | 32 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 33 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 34 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 35 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 36 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 |  | 2018-02-13 00:40 | 2018-02-13 01:18 | -- | -- | -- | 0 | 0 | 0.026389 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on over voltage.
[7 empty] | 2018-02-13 01:18 | 2018-02-13 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.18611 | N/A | N/A | N/A | NR/02/1050 | LVRD | Line kept open on voltage regulation.
[7 empty] | 2018-02-25 00:24 | 2018-02-25 01:55 | -- | -- | -- | 0 | 0.063194 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | Line tripped from Chamera2 end only due to high voltage.
[7 empty] | 2018-02-25 01:56 | 2018-02-25 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.15 | N/A | N/A | N/A | NR/02/2016 | LVRD | Line kept opened for voltage regulation.
[12 empty] | 0 | 0.063194 | 0.026389 | 0.33611 | [7 empty] | 100
1 | 37 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 |  | 2018-02-12 03:06 | 2018-02-12 03:09 | -- | -- | -- | 0 | 0 | 0.0020833 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on over voltage .
[7 empty] | 2018-02-12 03:09 | 2018-02-12 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.13264 | N/A | N/A | N/A | NR/02/925 | LVRD | Line kept open on high voltage after tripped on over voltage
[7 empty] | 2018-02-12 12:10 | 2018-02-12 12:25 | -- | -- | -- | 0 | 0 | 0.010417 | 0 | N/A | N/A | N/A | NR/993 | GOVC | Line tripped on system over voltage.
[7 empty] | 2018-02-13 01:16 | 2018-02-13 01:38 | -- | -- | -- | 0 | 0 | 0.015278 | 0 | N/A | N/A | N/A | NR/02/1048 | GOVC | Line Tripped on High Voltage from Chamera-II end only and remained charged from Kishenpur.
[7 empty] | 2018-02-25 00:24 | 2018-02-25 02:43 | -- | -- | -- | 0 | 0.096528 | 0 | 0 | N/A | N/A | N/A | NR/02/2013 | OMSU | Line tripped from Chamera2 end only due to high voltage at Chamera2.
[12 empty] | 0 | 0.096528 | 0.027778 | 0.13264 | [7 empty] | 100
1 | 38 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 |  | 2018-02-02 20:20 | 2018-02-03 06:11 | -- | -- | -- | 0 | 0 | 0 | 0.41042 | N/A | N/A | N/A | NR/02/152 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV.
[7 empty] | 2018-02-09 20:34 | 2018-02-10 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/02/741 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-02-13 01:16 | 2018-02-13 02:15 | -- | -- | -- | 0 | 0 | 0.040972 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on High Voltage from Chamera-I end only and remained charged from Jalandhar.
[7 empty] | 2018-02-13 02:15 | 2018-02-13 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.14444 | N/A | N/A | N/A | NR/02/1055 | LVRD | Line kept open on voltage regulation.
[7 empty] | 2018-02-13 20:17 | 2018-02-14 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.40208 | N/A | N/A | N/A | NR/02/1157 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-02-14 20:26 | 2018-02-15 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.42639 | N/A | N/A | N/A | NR/02/1225 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[12 empty] | 0 | 0 | 0.040972 | 1899-12-31 19:05 | [7 empty] | 100
1 | 39 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 |  | 2018-02-01 | 2018-02-01 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.23958 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV.
[7 empty] | 2018-02-01 20:09 | 2018-02-02 06:49 | -- | -- | -- | 0 | 0 | 0 | 0.44444 | N/A | N/A | N/A | NR/02/68 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430kV.
[7 empty] | 2018-02-03 20:12 | 2018-02-04 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/02/253 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-02-04 20:02 | 2018-02-05 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.425 | N/A | N/A | N/A | NR/02/315 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430kV
[7 empty] | 2018-02-05 20:33 | 2018-02-06 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.39514 | N/A | N/A | N/A | NR/02/385 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-02-06 21:34 | 2018-02-07 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/02/479 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-02-07 21:08 | 2018-02-08 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/02/573 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-02-08 20:46 | 2018-02-09 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/02/648 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-02-10 21:22 | 2018-02-12 06:14 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:52 | N/A | N/A | N/A | NR/02/834 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-02-12 08:09 | 2018-02-13 18:09 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:00 | N/A | N/A | N/A | NR/02/959 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 431KV
[7 empty] | 2018-02-15 13:42 | 2018-02-16 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.70417 | N/A | N/A | N/A | NR/02/1274 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 431KV
[7 empty] | 2018-02-16 20:17 | 2018-02-17 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.40556 | N/A | N/A | N/A | NR/02/1378 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-02-17 13:08 | 2018-02-18 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.71111 | N/A | N/A | N/A | NR/02/1421 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 432KV
[7 empty] | 2018-02-18 20:11 | 2018-02-19 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/02/1505 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-02-19 21:35 | 2018-02-20 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | N/A | N/A | N/A | NR/02/1574 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-20 20:12 | 2018-02-21 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/02/1648 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-02-21 21:48 | 2018-02-22 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | N/A | N/A | N/A | NR/02/1742 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427KV
[7 empty] | 2018-02-22 20:38 | 2018-02-23 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | N/A | N/A | N/A | NR/02/1841 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-02-23 20:33 | 2018-02-24 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/02/1936 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-02-24 20:20 | 2018-02-25 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.42708 | N/A | N/A | N/A | NR/02/1996 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-02-25 21:27 | 2018-02-26 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.35417 | N/A | N/A | N/A | NR/02/2070 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-26 20:32 | 2018-02-27 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/02/2137 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-02-27 20:28 | 2018-02-28 06:58 | -- | -- | -- | 0 | 0 | 0 | 0.4375 | N/A | N/A | N/A | NR/02/2221 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-28 20:37 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.14097 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[12 empty] | 0 | 0 | 0 | 1900-01-10 13:45 | [7 empty] | 100
1 | 40 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 |  | 2018-02-12 03:01 | 2018-02-14 15:13 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 12:12 | N/A | N/A | N/A | NR/02/922 | LVRD | Line hand tripped for voltage regulation. Kishanpur= 430KV
[12 empty] | 0 | 0 | 0 | 1900-01-01 12:12 | [7 empty] | 100
1 | 41 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 |  | 2018-02-13 01:16 | 2018-02-13 01:20 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on over voltage
[7 empty] | 2018-02-13 01:20 | 2018-02-16 07:35 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 06:15 | N/A | N/A | N/A | NR/02/1046 | LVRD | Line kept open on voltage regulation.
[12 empty] | 0 | 0 | 0.0027778 | 1900-01-02 06:15 | [7 empty] | 100
1 | 42 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 43 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 |  | 2018-02-24 13:51 | 2018-02-24 17:48 | -- | -- | -- | 0.16458 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1966 | OSPT | SD taken for replacement of damaged contacts of B-phase Isolator 41289B at Malerkotla.
[12 empty] | 0.16458 | 0 | 0 | 0 | [7 empty] | 99.41
1 | 44 | NR240024 | 400KV Moga-Hissar | 209.39 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 45 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 46 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 |  | 2018-02-02 20:12 | 2018-02-03 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/02/152 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-05 22:29 | 2018-02-06 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.29444 | N/A | N/A | N/A | NR/02/395 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-02-06 21:30 | 2018-02-07 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.37014 | N/A | N/A | N/A | NR/02/479 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-02-09 20:29 | 2018-02-10 06:11 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/02/741 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-02-11 20:19 | 2018-02-12 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/02/898 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-12 08:22 | 2018-02-12 18:54 | -- | -- | -- | 0 | 0 | 0 | 0.43889 | N/A | N/A | N/A | NR/02/962 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 428KV
[7 empty] | 2018-02-14 20:20 | 2018-02-15 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.38125 | N/A | N/A | N/A | NR/02/1225 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-17 21:33 | 2018-02-18 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/02/1456 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-02-18 20:13 | 2018-02-19 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/02/1505 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-20 21:11 | 2018-02-21 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.37431 | N/A | N/A | N/A | NR/02/1656 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-21 21:58 | 2018-02-22 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.33403 | N/A | N/A | N/A | NR/02/1743 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426KV
[7 empty] | 2018-02-22 21:23 | 2018-02-23 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/02/1848 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-24 22:09 | 2018-02-25 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.30903 | N/A | N/A | N/A | NR/02/2002 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-25 20:10 | 2018-02-26 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/02/2068 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-26 21:43 | 2018-02-27 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/02/2141 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-02-27 21:32 | 2018-02-28 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/02/2223 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-28 21:12 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.11667 | N/A | N/A | N/A | NR/02/2323 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-05 01:47 | [7 empty] | 100
1 | 47 | NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 |  | 2018-02-01 09:08 | 2018-02-01 18:38 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NR/02/25 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-02 08:48 | 2018-02-02 18:30 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/02/103 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-03 09:09 | 2018-02-03 18:21 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | N/A | N/A | N/A | NR/02/182 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-04 09:10 | 2018-02-04 18:07 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/02/286 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-12 11:24 | 2018-02-12 12:20 | -- | -- | -- | 0.038889 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.038889 | 0 | 0 | 1899-12-31 13:21 | [7 empty] | 100
1 | 48 | NR240031 | 400KV URI-WAGOORA-II | 94.99 | NR2 |  | 2018-02-01 09:09 | 2018-02-01 18:37 | -- | -- | -- | 0 | 0 | 0 | 0.39444 | N/A | N/A | N/A | NR/02/25 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-02 08:48 | 2018-02-02 18:29 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/02/103 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-03 09:11 | 2018-02-03 18:23 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | N/A | N/A | N/A | NR/02/182 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-04 09:10 | 2018-02-04 18:08 | -- | -- | -- | 0 | 0 | 0 | 0.37361 | N/A | N/A | N/A | NR/02/286 | OSPD | SD taken by NRSS XXIX Transmission Co Ltd. (Sterlite) for crossing of 400KV Samba-Amargarh D/C line under construction.
[7 empty] | 2018-02-12 08:21 | 2018-02-12 09:15 | -- | -- | -- | 0 | 0 | 0 | 0.0375 | N/A | N/A | N/A | NR/02/964 | LVRD | Line hand tripped for voltage regulation. Wagoora= 430KV
[7 empty] | 2018-02-12 11:24 | 2018-02-12 12:33 | -- | -- | -- | 0.047917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.047917 | 0 | 0 | 1899-12-31 14:13 | [7 empty] | 100
1 | 49 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 |  | 2018-02-12 12:07 | 2018-02-12 12:18 | -- | -- | -- | 0.0076389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line tripped on DEF protection operation.
[12 empty] | 0.0076389 | 0 | 0 | 0 | [7 empty] | 100
1 | 50 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 |  | 2018-02-12 12:07 | 2018-02-12 12:37 | -- | -- | -- | 0.020833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line tripped on DEF protection operation.
[12 empty] | 0.020833 | 0 | 0 | 0 | [7 empty] | 100
1 | 51 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 52 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 53 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 |  | 2018-02-01 00:08 | 2018-02-01 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.22708 | N/A | N/A | N/A | NR/02/01 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-01 21:33 | 2018-02-02 07:20 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/02/77 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-03 20:12 | 2018-02-04 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/02/253 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-02-04 20:00 | 2018-02-05 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | NR/02/315 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-02-08 20:40 | 2018-02-09 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/02/648 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-02-12 22:23 | 2018-02-13 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.32708 | N/A | N/A | N/A | NR/02/1038 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-02-13 20:12 | 2018-02-14 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/02/1157 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-15 20:48 | 2018-02-16 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.35903 | N/A | N/A | N/A | NR/02/1301 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-16 21:30 | 2018-02-17 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.32292 | N/A | N/A | N/A | NR/02/1379 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-19 20:08 | 2018-02-20 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/02/1568 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-23 20:31 | 2018-02-24 05:27 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/02/1939 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[12 empty] | 0 | 0 | 0 | 1900-01-03 00:44 | [7 empty] | 100
1 | 54 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 55 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 56 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 |  | 2018-02-13 00:46 | 2018-02-13 01:38 | -- | -- | -- | 0 | 0 | 0.036111 | 0 | N/A | N/A | N/A | NR/02/1051 | GOVC | Line Tripped on High Voltage from Chamera-II end only and remained charged from Chamba.
[7 empty] | 2018-02-25 00:24 | 2018-02-25 01:55 | -- | -- | -- | 0 | 0.063194 | 0 | 0 | N/A | N/A | N/A | -- | OMSU | Line tripped from Chamera2 end only due to high voltage at Chamera2 end.
[7 empty] | 2018-02-25 01:55 | 2018-02-25 02:50 | -- | -- | -- | 0 | 0 | 0 | 0.038194 | N/A | N/A | N/A | NR/02/2016 | LVRD | Line kept opened for voltage regulation.
[12 empty] | 0 | 0.063194 | 0.036111 | 0.038194 | [7 empty] | 100
1 | 57 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:30 | -- | -- | -- | 0.045833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.045833 | 0 | 0 | 0 | [7 empty] | 100
1 | 58 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 59 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 |  | 2018-02-01 | 2018-02-01 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.25694 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV.
[7 empty] | 2018-02-01 20:06 | 2018-02-02 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/02/68 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-02 20:08 | 2018-02-03 10:19 | -- | -- | -- | 0 | 0 | 0 | 0.59097 | N/A | N/A | N/A | NR/02/152 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-03 20:11 | 2018-02-04 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.43611 | N/A | N/A | N/A | NR/02/253 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-02-04 19:59 | 2018-02-05 06:32 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/02/315 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-02-05 22:26 | 2018-02-06 06:49 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/02/395 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-02-06 21:24 | 2018-02-07 06:46 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/02/479 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-02-07 21:06 | 2018-02-08 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/02/573 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-08 20:39 | 2018-02-09 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/02/648 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-02-09 20:26 | 2018-02-10 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/02/741 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-02-10 21:12 | 2018-02-13 08:27 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 11:15 | N/A | N/A | N/A | NR/02/834 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 420kV
[7 empty] | 2018-02-13 20:10 | 2018-02-14 07:30 | -- | -- | -- | 0 | 0 | 0 | 0.47222 | N/A | N/A | N/A | NR/02/1157 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-14 20:18 | 2018-02-15 08:01 | -- | -- | -- | 0 | 0 | 0 | 0.48819 | N/A | N/A | N/A | NR/02/1225 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-15 13:44 | 2018-02-16 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.70833 | N/A | N/A | N/A | NR/02/1274 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 429KV
[7 empty] | 2018-02-16 20:13 | 2018-02-17 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.42639 | N/A | N/A | N/A | NR/02/1378 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-02-17 21:31 | 2018-02-18 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/02/1456 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-02-18 18:00 | 2018-02-19 07:57 | -- | -- | -- | 0 | 0 | 0 | 0.58125 | N/A | N/A | N/A | NR/02/1495 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427KV
[7 empty] | 2018-02-19 20:08 | 2018-02-20 07:46 | -- | -- | -- | 0 | 0 | 0 | 0.48472 | N/A | N/A | N/A | NR/02/1568 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-20 20:11 | 2018-02-21 06:06 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/02/1648 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-02-21 20:34 | 2018-02-22 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/02/1737 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-02-22 20:34 | 2018-02-23 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/02/1841 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426KV
[7 empty] | 2018-02-23 20:35 | 2018-02-24 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/02/1936 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426KV
[7 empty] | 2018-02-24 15:07 | 2018-02-24 18:23 | -- | -- | -- | 0 | 0 | 0 | 0.13611 | N/A | N/A | N/A | NR/02/1971 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-02-24 20:18 | 2018-02-25 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.42986 | N/A | N/A | N/A | NR/02/1996 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-02-25 20:09 | 2018-02-26 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/02/2068 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-26 20:30 | 2018-02-27 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.4125 | N/A | N/A | N/A | NR/02/2137 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426KV
[7 empty] | 2018-02-27 20:24 | 2018-02-28 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/02/2221 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-02-28 20:38 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.14028 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[12 empty] | 0 | 0 | 0 | 1900-01-12 15:41 | [7 empty] | 100
1 | 60 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 |  | 2018-02-16 09:05 | 2018-02-16 18:20 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/02/1323 | OSPD | SD taken by NTPC Koldam for line equipments maintenance.
[12 empty] | 0 | 0 | 0 | 0.38542 | [7 empty] | 100
1 | 61 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 |  | 2018-02-11 23:38 | 2018-02-12 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.28403 | N/A | N/A | N/A | NR/02/905 | LVRD | Line hand tripped for voltage regulation. Abdullapur= 429KV
[12 empty] | 0 | 0 | 0 | 0.28403 | [7 empty] | 100
1 | 62 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 63 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 |  | 2018-02-04 20:06 | 2018-02-05 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | N/A | N/A | N/A | NR/02/317 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422kV
[7 empty] | 2018-02-06 20:48 | 2018-02-07 05:09 | -- | -- | -- | 0 | 0 | 0 | 0.34792 | N/A | N/A | N/A | NR/02/476 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421kV
[7 empty] | 2018-02-07 09:03 | 2018-02-07 17:05 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/02/500 | OSPD | SD taken by SJVNL, Jhakri for maintenance works at their end.
[7 empty] | 2018-02-08 20:23 | 2018-02-09 05:13 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/02/646 | LVRD | Line hand tripped for voltage regulation. Jhakri= 420kV
[7 empty] | 2018-02-09 09:08 | 2018-02-09 17:12 | -- | -- | -- | 0 | 0 | 0 | 0.33611 | N/A | N/A | N/A | NR/02/683 | OSPD | SD taken by SJVNL, Jhakri for maintenance works at their end.
[7 empty] | 2018-02-10 21:01 | 2018-02-11 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/02/832 | LVRD | Line hand tripped for voltage regulation. Panchkula= 419kV
[7 empty] | 2018-02-12 20:08 | 2018-02-13 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/02/1027 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-02-14 20:09 | 2018-02-15 05:12 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/02/1224 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-02-16 20:05 | 2018-02-17 05:16 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/02/1375 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422kV
[7 empty] | 2018-02-18 20:06 | 2018-02-19 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.3875 | N/A | N/A | N/A | NR/02/1504 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-02-20 20:13 | 2018-02-21 05:17 | -- | -- | -- | 0 | 0 | 0 | 0.37778 | N/A | N/A | N/A | NR/02/1648 | LVRD | Line hand tripped for voltage regulation. Panchkula= 424KV
[7 empty] | 2018-02-22 20:06 | 2018-02-23 05:10 | -- | -- | -- | 0 | 0 | 0 | 0.37778 | N/A | N/A | N/A | NR/02/1839 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-02-24 20:05 | 2018-02-25 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/02/1995 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-02-26 20:03 | 2018-02-27 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/02/2136 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-02-28 20:21 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.15208 | N/A | N/A | N/A | NR/02/2320 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[12 empty] | 0 | 0 | 0 | 1900-01-04 07:43 | [7 empty] | 100
1 | 64 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 |  | 2018-02-01 | 2018-02-01 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.23611 | N/A | N/A | N/A | NR/01/2906 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420kV.
[7 empty] | 2018-02-01 20:25 | 2018-02-02 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/02/71 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422kV.
[7 empty] | 2018-02-02 19:55 | 2018-02-03 05:17 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/02/147 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422kV.
[7 empty] | 2018-02-03 20:03 | 2018-02-04 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/02/250 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422kV
[7 empty] | 2018-02-05 20:15 | 2018-02-06 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/02/381 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420kV
[7 empty] | 2018-02-07 09:04 | 2018-02-07 17:06 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/02/500 | OSPD | SD taken by SJVNL, Jhakri for maintenance works at their end.
[7 empty] | 2018-02-07 20:45 | 2018-02-08 05:05 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/02/571 | LVRD | Line hand tripped for voltage regulation. Jhakri= 423kV
[7 empty] | 2018-02-09 09:09 | 2018-02-09 17:14 | -- | -- | -- | 0 | 0 | 0 | 0.33681 | N/A | N/A | N/A | NR/02/683 | OSPD | SD taken by SJVNL, Jhakri for maintenance works at their end.
[7 empty] | 2018-02-09 20:22 | 2018-02-10 05:02 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/02/739 | LVRD | Line hand tripped for voltage regulation. Jhakri= 423kV
[7 empty] | 2018-02-11 20:01 | 2018-02-12 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.42986 | N/A | N/A | N/A | NR/02/897 | LVRD | Line hand tripped for voltage regulation. Panchkula= 423KV
[7 empty] | 2018-02-13 20:04 | 2018-02-14 05:13 | -- | -- | -- | 0 | 0 | 0 | 0.38125 | N/A | N/A | N/A | NR/02/1156 | LVRD | Line hand tripped for voltage regulation. Panchkula= 423KV
[7 empty] | 2018-02-15 20:08 | 2018-02-16 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/02/1300 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420kV
[7 empty] | 2018-02-17 20:23 | 2018-02-18 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.37431 | N/A | N/A | N/A | NR/02/1451 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-02-19 20:41 | 2018-02-20 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.37014 | N/A | N/A | N/A | NR/02/1570 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-02-21 20:14 | 2018-02-22 05:07 | -- | -- | -- | 0 | 0 | 0 | 0.37014 | N/A | N/A | N/A | NR/02/1735 | LVRD | Line hand tripped for voltage regulation. Panchkula= 419KV
[7 empty] | 2018-02-23 20:09 | 2018-02-24 05:17 | -- | -- | -- | 0 | 0 | 0 | 0.38056 | N/A | N/A | N/A | NR/02/1929 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-02-25 20:07 | 2018-02-26 05:11 | -- | -- | -- | 0 | 0 | 0 | 0.37778 | N/A | N/A | N/A | NR/02/2067 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-02-27 19:58 | 2018-02-28 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.39097 | N/A | N/A | N/A | NR/02/2216 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[12 empty] | 0 | 0 | 0 | 1900-01-05 15:27 | [7 empty] | 100
1 | 65 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 66 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 67 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 |  | 2018-02-01 | 2018-02-01 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.23472 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV.
[7 empty] | 2018-02-01 21:34 | 2018-02-02 06:46 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | N/A | N/A | N/A | NR/02/77 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV.
[7 empty] | 2018-02-02 21:56 | 2018-02-03 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.35069 | N/A | N/A | N/A | NR/02/155 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV.
[7 empty] | 2018-02-03 20:08 | 2018-02-04 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.39306 | N/A | N/A | N/A | NR/02/253 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-02-04 20:01 | 2018-02-05 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.44583 | N/A | N/A | N/A | NR/02/315 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430kV
[7 empty] | 2018-02-05 20:30 | 2018-02-06 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.41736 | N/A | N/A | N/A | NR/02/385 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-02-06 21:35 | 2018-02-07 06:30 | -- | -- | -- | 0 | 0 | 0 | 0.37153 | N/A | N/A | N/A | NR/02/479 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425kV
[7 empty] | 2018-02-07 21:04 | 2018-02-08 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.34306 | N/A | N/A | N/A | NR/02/573 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV
[7 empty] | 2018-02-08 20:47 | 2018-02-09 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | N/A | N/A | N/A | NR/02/648 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-02-09 22:12 | 2018-02-10 07:27 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/02/746 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-02-10 21:15 | 2018-02-12 06:01 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:46 | N/A | N/A | N/A | NR/02/834 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-02-13 00:46 | 2018-02-13 01:57 | -- | -- | -- | 0.049306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1045 | LEFT | Line tripped on R-N fault. FLR Jalandhar: 98 Kms, IR-3.54 Kamps.
[7 empty] | 2018-02-13 20:11 | 2018-02-15 06:43 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:32 | N/A | N/A | N/A | NR/02/1157 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-02-15 13:42 | 2018-02-16 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.70486 | N/A | N/A | N/A | NR/02/1274 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 431KV
[7 empty] | 2018-02-16 20:12 | 2018-02-17 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/02/1378 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-02-17 13:07 | 2018-02-18 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.70694 | N/A | N/A | N/A | NR/02/1421 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 432KV
[7 empty] | 2018-02-18 20:18 | 2018-02-19 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.38819 | N/A | N/A | N/A | NR/02/1505 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-02-19 21:33 | 2018-02-20 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.34236 | N/A | N/A | N/A | NR/02/1574 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-20 20:09 | 2018-02-21 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.40556 | N/A | N/A | N/A | NR/02/1648 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-02-21 21:46 | 2018-02-22 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/02/1742 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427KV
[7 empty] | 2018-02-22 20:35 | 2018-02-23 05:48 | -- | -- | -- | 0 | 0 | 0 | 0.38403 | N/A | N/A | N/A | NR/02/1841 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-02-23 20:32 | 2018-02-24 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/02/1936 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-02-24 15:04 | 2018-02-24 18:36 | -- | -- | -- | 0 | 0 | 0 | 0.14722 | N/A | N/A | N/A | NR/02/1971 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-24 20:17 | 2018-02-25 01:03 | -- | -- | -- | 0 | 0 | 0 | 0.19861 | N/A | N/A | N/A | NR/02/1996 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-25 21:24 | 2018-02-26 06:55 | -- | -- | -- | 0 | 0 | 0 | 0.39653 | N/A | N/A | N/A | NR/02/2070 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-26 20:30 | 2018-02-27 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/02/2137 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 429KV
[7 empty] | 2018-02-27 20:23 | 2018-02-28 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | N/A | N/A | N/A | NR/02/2221 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-28 20:34 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.14306 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[12 empty] | 0.049306 | 0 | 0 | 1900-01-11 06:50 | [7 empty] | 99.82
1 | 68 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 |  | 2018-02-12 02:48 | 2018-02-13 18:06 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:18 | N/A | N/A | N/A | NR/02/921 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 433KV
[7 empty] | 2018-02-25 00:24 | 2018-02-25 01:31 | -- | -- | -- | 0.046528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/2010 | LEFT | Line tripped on R-N Fault. FLR Chamba: 34.698 Kms, IR-4.2 kA.
[7 empty] | 2018-02-25 01:41 | 2018-02-25 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.20139 | N/A | N/A | N/A | NR/02/2015 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 431KV
[7 empty] | 2018-02-26 00:23 | 2018-02-26 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.24444 | N/A | N/A | N/A | NR/02/2072 | LVRD | Line hand tripped for voltage regulation. Fatehabad= 430KV
[12 empty] | 0.046528 | 0 | 0 | 1900-01-01 02:00 | [7 empty] | 99.83
1 | 69 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 |  | 2018-02-12 12:07 | 2018-02-12 12:23 | -- | -- | -- | 0.011111 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line tripped on DEF protection operation.
[12 empty] | 0.011111 | 0 | 0 | 0 | [7 empty] | 99.96
1 | 70 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 |  | 2018-02-12 12:07 | 2018-02-12 12:32 | -- | -- | -- | 0.017361 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line tripped on DEF protection operation.
[12 empty] | 0.017361 | 0 | 0 | 0 | [7 empty] | 99.94
1 | 71 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 |  | 2018-02-01 | 2018-02-01 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.25625 | N/A | N/A | N/A | NR/01/2870 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421kV.
[7 empty] | 2018-02-01 20:07 | 2018-02-02 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.44097 | N/A | N/A | N/A | NR/02/68 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424kV.
[7 empty] | 2018-02-02 20:09 | 2018-02-03 07:47 | -- | -- | -- | 0 | 0 | 0 | 0.48472 | N/A | N/A | N/A | NR/02/152 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424kV.
[7 empty] | 2018-02-03 20:10 | 2018-02-04 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.43681 | N/A | N/A | N/A | NR/02/253 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422kV
[7 empty] | 2018-02-04 19:58 | 2018-02-05 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.43958 | N/A | N/A | N/A | NR/02/315 | LVRD | Line hand tripped for voltage regulation. Amritsar= 425kV
[7 empty] | 2018-02-05 20:31 | 2018-02-06 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.42778 | N/A | N/A | N/A | NR/02/385 | LVRD | Line hand tripped for voltage regulation. Amritsar= 423kV
[7 empty] | 2018-02-06 21:23 | 2018-02-07 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/02/479 | LVRD | Line hand tripped for voltage regulation. Amritsar = 424kV.
[7 empty] | 2018-02-07 21:05 | 2018-02-08 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | NR/02/573 | LVRD | Line hand tripped for voltage regulation. Amritsar = 426kV.
[7 empty] | 2018-02-08 20:38 | 2018-02-09 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/02/648 | LVRD | Line hand tripped for voltage regulation. Amritsar = 422kV.
[7 empty] | 2018-02-09 20:34 | 2018-02-10 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/02/741 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422kV
[7 empty] | 2018-02-10 21:11 | 2018-02-11 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/02/834 | LVRD | Line hand tripped for voltage regulation. Amritsar = 418kV.
[7 empty] | 2018-02-11 20:15 | 2018-02-13 17:51 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 21:36 | N/A | N/A | N/A | NR/02/898 | LVRD | Line hand tripped for voltage regulation. Amritsar = 422KV.
[7 empty] | 2018-02-13 20:09 | 2018-02-14 07:29 | -- | -- | -- | 0 | 0 | 0 | 0.47222 | N/A | N/A | N/A | NR/02/1157 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-02-14 20:17 | 2018-02-15 08:00 | -- | -- | -- | 0 | 0 | 0 | 0.48819 | N/A | N/A | N/A | NR/02/1225 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-02-15 20:07 | 2018-02-16 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/02/1300 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420KV
[7 empty] | 2018-02-16 20:13 | 2018-02-17 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/02/1378 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424KV
[7 empty] | 2018-02-17 13:07 | 2018-02-18 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.72153 | N/A | N/A | N/A | NR/02/1421 | LVRD | Line hand tripped for voltage regulation. Amritsar= 426KV
[7 empty] | 2018-02-18 20:23 | 2018-02-19 07:56 | -- | -- | -- | 0 | 0 | 0 | 0.48125 | N/A | N/A | N/A | NR/02/1505 | LVRD | Line hand tripped for voltage regulation. Amritsar= 423KV
[7 empty] | 2018-02-19 20:10 | 2018-02-20 07:45 | -- | -- | -- | 0 | 0 | 0 | 0.48264 | N/A | N/A | N/A | NR/02/1568 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-02-20 20:10 | 2018-02-21 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/02/1648 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424KV
[7 empty] | 2018-02-21 20:33 | 2018-02-22 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/02/1737 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-02-22 20:33 | 2018-02-23 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.40694 | N/A | N/A | N/A | NR/02/1841 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-02-23 20:36 | 2018-02-24 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/02/1936 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424KV
[7 empty] | 2018-02-24 15:05 | 2018-02-25 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.64653 | N/A | N/A | N/A | NR/02/1971 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-02-25 08:14 | 2018-02-25 19:24 | -- | -- | -- | 0.46528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/2030 | OSPT | SD taken for AMP works.
[7 empty] | 2018-02-25 20:08 | 2018-02-26 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/02/2068 | LVRD | Line hand tripped for voltage regulation. Amritsar= 423KV
[7 empty] | 2018-02-26 20:27 | 2018-02-27 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.41389 | N/A | N/A | N/A | NR/02/2137 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424KV
[7 empty] | 2018-02-27 20:26 | 2018-02-28 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.40556 | N/A | N/A | N/A | NR/02/2221 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-02-28 20:34 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.14306 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420KV
[12 empty] | 0.46528 | 0 | 0 | 1900-01-12 11:53 | [7 empty] | 98.34
1 | 72 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 73 | NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:19 | -- | -- | -- | 0.038194 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.038194 | 0 | 0 | 0 | [7 empty] | 99.87
1 | 74 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:23 | -- | -- | -- | 0.040972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[7 empty] | 2018-02-13 10:09 | 2018-02-13 10:13 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | NR/02/1110 | LNCC | Line tripped on B-N fault caused by heavy snowfall in the area. FLR New Wanpoh: 34.9km & Kishenpur: FL=84.35km.
[12 empty] | 0.040972 | 0 | 0.0027778 | 0 | [7 empty] | 99.86
1 | 75 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:12 | -- | -- | -- | 0.033333 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line tripped on DEF protection due to non clearance of fault on Kishenpur New Wanpoh - III.
[12 empty] | 0.033333 | 0 | 0 | 0 | [7 empty] | 99.89
1 | 76 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:21 | -- | -- | -- | 0.039583 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line tripped on DEF protection due to non clearance of fault on Kishenpur New Wanpoh - III.
[7 empty] | 2018-02-24 20:58 | 2018-02-24 20:58 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on Y-N fault. FLR New Wanpoh :99.86km, Iy=1.99 kA.
[12 empty] | 0.039583 | 0 | 0 | 0 | [7 empty] | 99.87
1 | 77 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 |  | 2018-02-12 07:05 | 2018-02-12 13:45 | -- | -- | -- | 0 | 0.27778 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | Line tripped on R-N fault caused by pilot wire hanging during OPGW laying work under ULDC scheme.
[7 empty] | 2018-02-12 13:45 | 2018-02-12 18:09 | -- | -- | -- | 0 | 0.18333 | 0 | 0 | N/A | N/A | N/A | NR/02/1004 | OMSU | Line tripped on R-N fault caused by pilot wire hanging during OPGW laying work under ULDC scheme.
[7 empty] | 2018-02-13 02:39 | 2018-02-13 03:31 | -- | -- | -- | 0 | 0.036111 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | Line tripped on R-N fault caused by pilot wire snapping during OPGW laying work under ULDC scheme. . FLR Hamirpur : 27.862KM.
[7 empty] | 2018-02-13 03:31 | 2018-02-13 17:49 | -- | -- | -- | 0 | 0 | 0 | 0.59583 | N/A | N/A | N/A | NR/02/1059 | LCSD | SD taken for rectification of snapped pilot wire broken during OPGW laying under ULDC scheme.
[7 empty] | 2018-02-23 08:45 | 2018-02-23 18:54 | -- | -- | -- | 0.42292 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1867 | OSPT | SD taken for AMP works.
[12 empty] | 0.42292 | 0.49722 | 0 | 0.59583 | [7 empty] | 98.49
1 | 78 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 |  | 2018-02-06 09:12 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-21 14:48 | N/A | N/A | N/A | NR/02/418 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[12 empty] | 0 | 0 | 0 | 1900-01-21 14:48 | [7 empty] | 100
1 | 79 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 |  | 2018-02-08 08:42 | 2018-02-08 17:32 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/02/592 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-09 12:31 | 2018-02-09 15:51 | -- | -- | -- | 0 | 0 | 0 | 0.13889 | N/A | N/A | N/A | NR/02/704 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-10 09:58 | 2018-02-10 16:38 | -- | -- | -- | 0 | 0 | 0 | 0.27778 | N/A | N/A | N/A | NR/02/768 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-13 20:19 | 2018-02-14 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/02/1157 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-15 20:49 | 2018-02-16 05:22 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/02/1301 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-17 08:51 | 2018-02-19 17:03 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:12 | N/A | N/A | N/A | NR/02/1408 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-19 20:24 | 2018-02-20 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.39306 | N/A | N/A | N/A | NR/02/1568 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-20 14:48 | 2018-02-20 15:26 | -- | -- | -- | 0 | 0.026389 | 0 | 0 | N/A | N/A | N/A | NR/02/1622 | OMSU | Line tripped due to DC E/F operated at Rampur end. DT received at Nalagarh end.
[7 empty] | 2018-02-22 09:37 | 2018-02-22 17:26 | -- | -- | -- | 0 | 0 | 0 | 0.32569 | N/A | N/A | N/A | NR/02/1771 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-23 20:29 | 2018-02-24 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/02/1939 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-02-24 08:50 | 2018-02-24 17:21 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/02/1958 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-25 21:28 | 2018-02-26 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | N/A | N/A | N/A | NR/02/2070 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-26 21:40 | 2018-02-27 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | N/A | N/A | N/A | NR/02/2141 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-02-27 21:33 | 2018-02-28 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.36319 | N/A | N/A | N/A | NR/02/2223 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[12 empty] | 0 | 0.026389 | 0 | 1900-01-05 08:44 | [7 empty] | 100
1 | 80 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 81 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 |  | 2018-02-06 08:55 | 2018-02-06 17:26 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/02/413 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-07 09:06 | 2018-02-07 17:49 | -- | -- | -- | 0 | 0 | 0 | 0.36319 | N/A | N/A | N/A | NR/02/501 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-08 09:17 | 2018-02-08 17:23 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/02/597 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-09 09:19 | 2018-02-09 16:58 | -- | -- | -- | 0 | 0 | 0 | 0.31875 | N/A | N/A | N/A | NR/02/685 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-10 10:05 | 2018-02-10 17:09 | -- | -- | -- | 0 | 0 | 0 | 0.29444 | N/A | N/A | N/A | NR/02/769 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-11 10:26 | 2018-02-11 16:49 | -- | -- | -- | 0 | 0 | 0 | 0.26597 | N/A | N/A | N/A | NR/02/863 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-13 12:38 | 2018-02-13 17:16 | -- | -- | -- | 0 | 0 | 0 | 0.19306 | N/A | N/A | N/A | NR/02/1120 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-19 09:20 | 2018-02-19 16:58 | -- | -- | -- | 0 | 0 | 0 | 0.31806 | N/A | N/A | N/A | NR/02/1529 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-22 09:27 | 2018-02-22 17:08 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | N/A | N/A | N/A | NR/02/1772 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-24 09:11 | 2018-02-24 17:31 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/02/1961 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-26 09:09 | 2018-02-26 17:11 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/02/2093 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-27 09:28 | 2018-02-27 17:25 | -- | -- | -- | 0 | 0 | 0 | 0.33125 | N/A | N/A | N/A | NR/02/2164 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[12 empty] | 0 | 0 | 0 | 1900-01-02 18:42 | [7 empty] | 100
1 | 82 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 |  | 2018-02-01 | 2018-02-01 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.23125 | N/A | N/A | N/A | NR/01/2909 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421kV.
[7 empty] | 2018-02-01 21:31 | 2018-02-02 04:57 | -- | -- | -- | 0 | 0 | 0 | 0.30972 | N/A | N/A | N/A | NR/02/77 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-02 20:13 | 2018-02-03 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.40694 | N/A | N/A | N/A | NR/02/152 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-03 21:46 | 2018-02-04 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.32153 | N/A | N/A | N/A | NR/02/261 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-04 21:11 | 2018-02-05 05:14 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/02/326 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 426kV
[7 empty] | 2018-02-05 22:25 | 2018-02-06 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.29028 | N/A | N/A | N/A | NR/02/395 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424kV
[7 empty] | 2018-02-06 21:27 | 2018-02-07 05:18 | -- | -- | -- | 0 | 0 | 0 | 0.32708 | N/A | N/A | N/A | NR/02/479 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423kV
[7 empty] | 2018-02-07 15:23 | 2018-02-07 16:04 | -- | -- | -- | 0 | 0.028472 | 0 | 0 | N/A | N/A | N/A | NR/02/538 | OMSU | Line tripped on Y-N fault in Zone-2 due to problem at Rampur end. F .Loc-128Km from Nalagarh, total Line lenth is 126.48 Km.
[7 empty] | 2018-02-07 21:17 | 2018-02-08 05:19 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/02/576 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 427kV
[7 empty] | 2018-02-08 09:22 | 2018-02-08 17:36 | -- | -- | -- | 0 | 0 | 0 | 0.34306 | N/A | N/A | N/A | NR/02/602 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-09 12:31 | 2018-02-09 15:55 | -- | -- | -- | 0 | 0 | 0 | 0.14167 | N/A | N/A | N/A | NR/02/704 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-10 10:04 | 2018-02-10 16:41 | -- | -- | -- | 0 | 0 | 0 | 0.27569 | N/A | N/A | N/A | NR/02/769 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-11 20:23 | 2018-02-12 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/02/898 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-02-12 08:20 | 2018-02-12 16:55 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/02/962 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 428KV
[7 empty] | 2018-02-12 22:22 | 2018-02-13 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.31181 | N/A | N/A | N/A | NR/02/1038 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-02-14 20:29 | 2018-02-15 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/02/1225 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-16 21:31 | 2018-02-17 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/02/1379 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-19 09:13 | 2018-02-19 17:03 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/02/1529 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-20 09:09 | 2018-02-22 17:20 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:11 | N/A | N/A | N/A | NR/02/1601 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-22 21:33 | 2018-02-23 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | N/A | N/A | N/A | NR/02/1848 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-24 09:00 | 2018-02-24 17:23 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/02/1960 | OSPD | SD taken by SJVNL, Rampur for maintenance works at their end.
[7 empty] | 2018-02-24 22:07 | 2018-02-25 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.30833 | N/A | N/A | N/A | NR/02/2002 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-02-28 21:14 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.11528 | N/A | N/A | N/A | NR/02/2323 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[12 empty] | 0 | 0.028472 | 0 | 1900-01-07 20:32 | [7 empty] | 100
1 | 83 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 |  | 2018-02-01 | 2018-02-01 19:08 | -- | -- | -- | 0 | 0 | 0 | 0.79722 | N/A | N/A | N/A | NR/01/2018 | OSPD | SD taken BBMB, Panipat for TL maintenance work.
[12 empty] | 0 | 0 | 0 | 0.79722 | [7 empty] | 100
1 | 84 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 |  | 2018-02-13 01:03 | 2018-02-13 07:17 | -- | -- | -- | 0 | 0 | 0 | 0.25972 | N/A | N/A | N/A | NR/02/1044 | LVRD | Line hand tripped for voltage regulation. Panchkula= 430KV
[12 empty] | 0 | 0 | 0 | 0.25972 | [7 empty] | 100
1 | 85 | NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 86 | NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 87 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 |  | 2018-02-08 23:38 | 2018-02-08 23:51 | -- | -- | -- | 0 | 0 | 0 | 0.0090278 | N/A | N/A | N/A | NR/02/659 | LVRD | Line hand tripped for voltage regulation. Abdullapur= 423kV
[12 empty] | 0 | 0 | 0 | 0.0090278 | [7 empty] | 100
1 | 88 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 89 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 |  | 2018-02-01 21:22 | 2018-02-02 06:52 | -- | -- | -- | 0 | 0 | 0 | 0.39583 | N/A | N/A | N/A | NR/02/77 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430kV.
[12 empty] | 0 | 0 | 0 | 0.39583 | [7 empty] | 100
1 | 90 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 |  | 2018-02-19 11:48 | 2018-02-19 15:02 | -- | -- | -- | 0.13472 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1538 | OSPT | S/D taken to attend hot spot at line isolator at Sonipat.
[12 empty] | 0.13472 | 0 | 0 | 0 | [7 empty] | 99.52
1 | 91 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 |  | 2018-02-01 | 2018-02-01 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.25833 | N/A | N/A | N/A | NR/01/2867 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV.
[7 empty] | 2018-02-01 20:08 | 2018-02-02 07:26 | -- | -- | -- | 0 | 0 | 0 | 0.47083 | N/A | N/A | N/A | NR/02/68 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430kV.
[7 empty] | 2018-02-02 11:57 | 2018-02-02 13:19 | -- | -- | -- | 0.056944 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/122 | SBBT | Line tripped due to sectional busbar protection optd at Kurushetra.
[7 empty] | 2018-02-02 20:12 | 2018-02-03 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/02/152 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430kV.
[7 empty] | 2018-02-03 21:48 | 2018-02-04 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | NR/02/261 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430kV.
[7 empty] | 2018-02-04 21:21 | 2018-02-05 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/02/326 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 421kV.
[7 empty] | 2018-02-07 21:15 | 2018-02-08 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/02/573 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427kV.
[7 empty] | 2018-02-11 13:45 | 2018-02-12 06:49 | -- | -- | -- | 0 | 0 | 0 | 0.71111 | N/A | N/A | N/A | NR/02/870 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427KV.
[7 empty] | 2018-02-12 07:53 | 2018-02-13 15:08 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:15 | N/A | N/A | N/A | NR/02/956 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-02-14 00:10 | 2018-02-15 07:05 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:55 | N/A | N/A | N/A | NR/02/1230 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427KV
[7 empty] | 2018-02-15 20:50 | 2018-02-16 07:27 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/02/1301 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 421KV
[7 empty] | 2018-02-16 21:27 | 2018-02-17 07:35 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/02/1379 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 423kV.
[7 empty] | 2018-02-17 13:11 | 2018-02-19 05:44 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 16:33 | N/A | N/A | N/A | NR/02/1421 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 432KV
[7 empty] | 2018-02-19 21:35 | 2018-02-20 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/02/1574 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-20 21:15 | 2018-02-21 10:29 | -- | -- | -- | 0 | 0 | 0 | 0.55139 | N/A | N/A | N/A | NR/02/1656 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-23 20:30 | 2018-02-26 08:15 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 11:45 | N/A | N/A | N/A | NR/02/1939 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-26 21:43 | 2018-02-27 09:09 | -- | -- | -- | 0 | 0 | 0 | 0.47639 | N/A | N/A | N/A | NR/02/2141 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-02-27 21:43 | 2018-02-28 07:28 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/02/2223 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422KV
[7 empty] | 2018-02-28 21:18 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.1125 | N/A | N/A | N/A | NR/02/2323 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[12 empty] | 0.056944 | 0 | 0 | 1900-01-11 13:36 | [7 empty] | 99.81
1 | 92 | NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 93 | NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 |  | 2018-02-01 | 2018-02-01 06:11 | -- | -- | -- | 0 | 0 | 0 | 0.25764 | N/A | N/A | N/A | NR/01/2870 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429kV.
[7 empty] | 2018-02-01 20:10 | 2018-02-08 23:44 | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 03:34 | N/A | N/A | N/A | NR/02/68 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430kV.
[7 empty] | 2018-02-24 10:00 | 2018-02-24 10:00 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N Fault. FLR Kurukshetra : 189.8km, 2.182 kA.
[12 empty] | 0 | 0 | 0 | 1900-01-06 09:45 | [7 empty] | 100
1 | 94 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 95 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 96 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 97 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 |  | 2018-02-11 23:35 | 2018-02-12 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.29653 | N/A | N/A | N/A | NR/02/905 | LVRD | Line hand tripped for voltage regulation. Patiala= 425KV
[7 empty] | 2018-02-12 22:25 | 2018-02-13 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.32778 | N/A | N/A | N/A | NR/02/1038 | LVRD | Line hand tripped for voltage regulation. Patiala= 423KV
[12 empty] | 0 | 0 | 0 | 0.62431 | [7 empty] | 100
1 | 98 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 |  | 2018-02-12 00:08 | 2018-02-12 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.26389 | N/A | N/A | N/A | NR/02/908 | LVRD | Line hand tripped for voltage regulation. Patiala= 425KV
[7 empty] | 2018-02-12 22:19 | 2018-02-13 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/02/1038 | LVRD | Line hand tripped for voltage regulation. Patiala= 423KV
[7 empty] | 2018-02-14 01:57 | 2018-02-14 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.15556 | N/A | N/A | N/A | NR/02/1175 | LVRD | Line hand tripped for voltage regulation. Patiala= 427KV
[12 empty] | 0 | 0 | 0 | 0.75486 | [7 empty] | 100
1 | 99 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 100 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 |  | 2018-02-12 00:09 | 2018-02-12 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.26389 | N/A | N/A | N/A | NR/02/908 | LVRD | Line hand tripped for voltage regulation. Kaithal= 425KV
[7 empty] | 2018-02-12 22:20 | 2018-02-13 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.33403 | N/A | N/A | N/A | NR/02/1038 | LVRD | Line hand tripped for voltage regulation. Kaithal= 423KV
[7 empty] | 2018-02-14 01:58 | 2018-02-14 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.15417 | N/A | N/A | N/A | NR/02/1175 | LVRD | Line hand tripped for voltage regulation. Kaithal 426KV
[12 empty] | 0 | 0 | 0 | 0.75208 | [7 empty] | 100
1 | 101 | NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 102 | NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2018-02-12 02:02 | 2018-02-12 07:07 | -- | -- | -- | 0 | 0 | 0 | 0.21181 | N/A | N/A | N/A | NR/02/915 | LVRD | Line hand tripped for voltage regulation.
[12 empty] | 0 | 0 | 0 | 0.21181 | [7 empty] | 100
1 | 103 | NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2018-02-12 02:42 | 2018-02-12 03:20 | -- | -- | -- | 0 | 0 | 0.026389 | 0 | N/A | N/A | N/A | --- | GOVC | Line Tripped on over voltage
[7 empty] | 2018-02-12 03:20 | 2018-02-12 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.125 | N/A | N/A | N/A | NR/02/925 | LVRD | Line kept open on voltage regulation.
[7 empty] | 2018-02-16 04:11 | 2018-02-16 05:02 | -- | -- | -- | 0 | 0 | 0.035417 | 0 | N/A | N/A | N/A | NR/02/1308 | GOVC | Line Tripped on over voltage from Bhiwani end. DT received at Rajpura end.
[7 empty] | 2018-02-23 12:21 | 2018-02-23 19:00 | -- | -- | -- | 0 | 0.27708 | 0 | 0 | N/A | N/A | N/A | NR/02/1894 | OMSU | Line tripped due to problem in DC E/Fault at Bhiwani end. POWERGRID Line length is 14.4 km from Rajpura.
[12 empty] | 0 | 0.27708 | 0.061806 | 0.125 | [7 empty] | 100
1 | 104 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 |  | 2018-02-10 21:17 | 2018-02-11 09:52 | -- | -- | -- | 0 | 0 | 0 | 0.52431 | N/A | N/A | N/A | NR/02/834 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 421kV
[7 empty] | 2018-02-12 00:12 | 2018-02-13 09:03 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:51 | N/A | N/A | N/A | NR/02/908 | LVRD | Line hand tripped for voltage regulation. Amritsar = 424KV.
[12 empty] | 0 | 0 | 0 | 1899-12-31 21:26 | [7 empty] | 100
1 | 105 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 |  | 2018-02-01 00:11 | 2018-02-01 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.30139 | N/A | N/A | N/A | NR/02/01 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430kV
[7 empty] | 2018-02-01 20:05 | 2018-02-02 07:31 | -- | -- | -- | 0 | 0 | 0 | 0.47639 | N/A | N/A | N/A | NR/02/68 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430kV.
[7 empty] | 2018-02-02 20:07 | 2018-02-03 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.42361 | N/A | N/A | N/A | NR/02/152 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428kV.
[7 empty] | 2018-02-05 22:30 | 2018-02-06 06:30 | -- | -- | -- | 0 | 0 | 0 | 0.33333 | N/A | N/A | N/A | NR/02/395 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426kV
[7 empty] | 2018-02-06 21:36 | 2018-02-07 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/02/479 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424kV
[7 empty] | 2018-02-09 20:25 | 2018-02-10 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/02/741 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423kV
[7 empty] | 2018-02-11 20:17 | 2018-02-12 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.42292 | N/A | N/A | N/A | NR/02/898 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-02-13 20:14 | 2018-02-14 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.4 | N/A | N/A | N/A | NR/02/1157 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-02-14 20:22 | 2018-02-15 06:56 | -- | -- | -- | 0 | 0 | 0 | 0.44028 | N/A | N/A | N/A | NR/02/1225 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-02-15 20:49 | 2018-02-16 07:25 | -- | -- | -- | 0 | 0 | 0 | 0.44167 | N/A | N/A | N/A | NR/02/1301 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-16 20:12 | 2018-02-17 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.42639 | N/A | N/A | N/A | NR/02/1378 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-02-17 21:29 | 2018-02-18 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/02/1456 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-02-18 21:24 | 2018-02-19 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/02/1508 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-02-21 21:49 | 2018-02-22 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.34931 | N/A | N/A | N/A | NR/02/1742 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427KV
[7 empty] | 2018-02-22 21:24 | 2018-02-23 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/02/1848 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-23 20:27 | 2018-02-24 07:37 | -- | -- | -- | 0 | 0 | 0 | 0.46528 | N/A | N/A | N/A | NR/02/1939 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-24 22:07 | 2018-02-25 08:25 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/02/2002 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-25 21:25 | 2018-02-26 06:56 | -- | -- | -- | 0 | 0 | 0 | 0.39653 | N/A | N/A | N/A | NR/02/2070 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-02-26 21:45 | 2018-02-27 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.35 | N/A | N/A | N/A | NR/02/2141 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-06 11:47 | [7 empty] | 100
1 | 106 | NR240116 | 400KV Dadri-Kaithal | 213 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 107 | NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 |  | 2018-02-08 01:58 | 2018-02-08 01:58 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on Y-N Fault. FLR Kaithal : 165.5km, 2.249KA.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 108 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 109 | NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 110 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:51 | -- | -- | -- | 0 | 0 | 0.060417 | 0 | N/A | N/A | N/A | --- | LNCC | Line tripped on R-N fault caused by snapping of earthwire caused by heavy snowfall and rain in the area.
[7 empty] | 2018-02-12 12:51 | 2018-02-13 12:21 | -- | -- |  | 0 | 0 | 0.97917 | 0 | N/A | N/A | N/A | NR/02/1004 | LNCC | SD taken for rectification of snapped earthwire caused due to heavy snow fall in the area.
[12 empty] | 0 | 0 | 1899-12-31 00:57 | 0 | [7 empty] | 100
1 | 111 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 |  | 2018-02-12 08:09 | 2018-02-12 17:09 | -- | -- | -- | 0 | 0 | 0 | 0.375 | N/A | N/A | N/A | NR/02/959 | LVRD | Line hand tripped for voltage regulation. Kishenpur=429kV
[7 empty] | 2018-02-13 09:20 | 2018-02-13 09:41 | -- | -- | -- | 0.014583 | 0 | 0 | 0 | N/A | N/A | N/A | --- | OSFT | Line tripped on B-N fault due to snapping of OPGW Wire.
[7 empty] | 2018-02-13 09:41 | 2018-02-13 17:43 | -- | -- | -- | 0.33472 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1102 | OSPT | SD taken for rectification of snapped OPGW wire.
[7 empty] | 2018-02-26 11:28 | 2018-02-26 13:52 | -- | -- | -- | 0.1 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/2099 | OSPT | SD taken for rectification of snapped jumper on Tower No 325.
[12 empty] | 0.44931 | 0 | 0 | 0.375 | [7 empty] | 99.64
1 | 112 | NR240122 | 400KV KURUKSHETRA - JIND - I | 103.6 | NR2 |  | 2018-02-01 21:25 | 2018-02-02 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/02/77 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430kV.
[7 empty] | 2018-02-05 22:12 | 2018-02-06 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/02/395 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427kV.
[7 empty] | 2018-02-11 04:13 | 2018-02-11 09:56 | -- | -- | -- | 0 | 0 | 0 | 0.23819 | N/A | N/A | N/A | NR/02/840 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 423kV
[7 empty] | 2018-02-12 23:03 | 2018-02-13 08:27 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | NR/02/1040 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 425KV
[7 empty] | 2018-02-13 22:40 | 2018-02-14 07:12 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/02/1170 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 424KV
[12 empty] | 0 | 0 | 0 | 1899-12-31 17:37 | [7 empty] | 100
1 | 113 | NR240123 | 400KV KURUKSHETRA - JIND - II | 103.6 | NR2 |  | 2018-02-02 21:36 | 2018-02-03 06:14 | -- | -- | -- | 0 | 0 | 0 | 0.35972 | N/A | N/A | N/A | NR/02/154 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427kV.
[7 empty] | 2018-02-04 21:12 | 2018-02-05 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/02/324 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 421kV.
[7 empty] | 2018-02-07 21:32 | 2018-02-08 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.35 | N/A | N/A | N/A | NR/02/573 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427kV.
[7 empty] | 2018-02-11 20:19 | 2018-02-12 06:43 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/02/898 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 425KV
[7 empty] | 2018-02-14 00:12 | 2018-02-15 06:56 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:44 | N/A | N/A | N/A | NR/02/1230 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427KV
[7 empty] | 2018-02-16 21:33 | 2018-02-17 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.35347 | N/A | N/A | N/A | NR/02/1379 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 427KV
[7 empty] | 2018-02-18 17:56 | 2018-02-19 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.49583 | N/A | N/A | N/A | NR/02/1495 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429KV
[7 empty] | 2018-02-23 20:38 | 2018-02-24 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/02/1939 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 429KV
[12 empty] | 0 | 0 | 0 | 1900-01-03 00:19 | [7 empty] | 100
1 | 114 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 |  | 2018-02-01 | 2018-02-01 07:00 | -- | -- | -- | 0 | 0 | 0 | 0.29167 | N/A | N/A | N/A | NR/01/2872 NLDC/1547 | LVRD | Line hand tripped for voltage regulation. Moga= 803kV.
[7 empty] | 2018-02-01 20:41 | 2018-02-02 07:49 | -- | -- | -- | 0 | 0 | 0 | 0.46389 | N/A | N/A | N/A | NR/02/72 NL/02/37 | LVRD | Line hand tripped for voltage regulation. Moga= 800kV.
[7 empty] | 2018-02-02 20:04 | 2018-02-03 10:10 | -- | -- | -- | 0 | 0 | 0 | 0.5875 | N/A | N/A | N/A | NR/02/149 NLDC/86 | LVRD | Line hand tripped for voltage regulation. Moga= 800kV.
[7 empty] | 2018-02-03 20:44 | 2018-02-04 07:16 | -- | -- | -- | 0 | 0 | 0 | 0.43889 | N/A | N/A | N/A | NR/02/256 NLDC/153 | LVRD | Line hand tripped for voltage regulation. Moga= 801kV.
[7 empty] | 2018-02-04 20:03 | 2018-02-05 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/02/316 NLDC/193 | LVRD | Line hand tripped for voltage regulation. Moga= 803kV.
[7 empty] | 2018-02-05 21:05 | 2018-02-06 08:12 | -- | -- | -- | 0 | 0 | 0 | 0.46319 | N/A | N/A | N/A | NR/02/389 NLDC/254 | LVRD | Line hand tripped for voltage regulation. Moga= 800kV.
[7 empty] | 2018-02-06 10:41 | 2018-02-06 19:12 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | NR/02/429 NLDC/279 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-07 00:06 | 2018-02-07 07:43 | -- | -- | -- | 0 | 0 | 0 | 0.31736 | N/A | N/A | N/A | NR/02/481 NLDC/301 | LVRD | Line hand tripped for voltage regulation. Moga= 804kV.
[7 empty] | 2018-02-07 09:38 | 2018-02-07 20:53 | -- | -- | -- | 0 | 0 | 0 | 0.46875 | N/A | N/A | N/A | NR/02/505 NLDC/318 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-07 20:58 | 2018-02-08 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/02/572 NLDC/355 | LVRD | Line hand tripped for voltage regulation. Moga= 805kV
[7 empty] | 2018-02-08 08:59 | 2018-02-08 19:17 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/02/593 NLDC/368 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-08 21:43 | 2018-02-09 06:53 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/02/655 NLDC/406 | LVRD | Line hand tripped for voltage regulation. Moga= 797kV
[7 empty] | 2018-02-09 08:51 | 2018-02-09 20:16 | -- | -- | -- | 0 | 0 | 0 | 0.47569 | N/A | N/A | N/A | NR/02/680 NLDC/422 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-09 20:30 | 2018-02-10 09:24 | -- | -- | -- | 0 | 0 | 0 | 0.5375 | N/A | N/A | N/A | NR/02/742 NLDC/469 | LVRD | Line hand tripped for voltage regulation. Moga= 798kV
[7 empty] | 2018-02-10 09:24 | 2018-02-10 19:50 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | NR/02/761 NLDC/481 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-10 20:49 | 2018-02-11 07:06 | -- | -- | -- | 0 | 0 | 0 | 0.42847 | N/A | N/A | N/A | NR/02/830 NLDC/506 | LVRD | Line hand tripped for voltage regulation. Moga= 798kV
[7 empty] | 2018-02-11 08:58 | 2018-02-11 19:05 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/02/857 NLDC/517 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-11 20:36 | 2018-02-12 07:22 | -- | -- | -- | 0 | 0 | 0 | 0.44861 | N/A | N/A | N/A | NR/02/900 NLDC/539 | LVRD | Line hand tripped for voltage regulation. Moga= 796kV
[7 empty] | 2018-02-12 08:02 | 2018-02-12 10:58 | -- | -- | -- | 0 | 0 | 0 | 0.12222 | N/A | N/A | N/A | NR/02/958 NLDC/559 | LVRD | Line hand tripped for voltage regulation. Moga= 796kV
[7 empty] | 2018-02-12 11:53 | 2018-02-13 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.81875 | N/A | N/A | N/A | NR/02/995 NLDC/580 | LVRD | Line hand tripped for voltage regulation. Moga= 796kV
[7 empty] | 2018-02-13 10:43 | 2018-02-13 19:15 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/02/1113 NLDC/632 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-13 20:48 | 2018-02-14 07:40 | -- | -- | -- | 0 | 0 | 0 | 0.45278 | N/A | N/A | N/A | NR/02/1164 NLDC/660 | LVRD | Line hand tripped for voltage regulation. Moga= 795KV
[7 empty] | 2018-02-14 08:56 | 2018-02-14 19:08 | -- | -- | -- | 0 | 0 | 0 | 0.425 | N/A | N/A | N/A | NR/02/1193 NLDC/681 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-14 21:42 | 2018-02-15 07:39 | -- | -- | -- | 0 | 0 | 0 | 0.41458 | N/A | N/A | N/A | NR/02/1226 NLDC/715 | LVRD | Line hand tripped for voltage regulation. Moga= 800KV
[7 empty] | 2018-02-15 08:58 | 2018-02-15 19:51 | -- | -- | -- | 0 | 0 | 0 | 0.45347 | N/A | N/A | N/A | NR/02/1249 NLDC/724 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-15 20:57 | 2018-02-16 07:35 | -- | -- | -- | 0 | 0 | 0 | 0.44306 | N/A | N/A | N/A | NR/02/1302 NLDC/752 | LVRD | Line hand tripped for voltage regulation. Moga= 798KV
[7 empty] | 2018-02-16 09:01 | 2018-02-16 19:40 | -- | -- | -- | 0 | 0 | 0 | 0.44375 | N/A | N/A | N/A | NR/02/1328 NLDC/767 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-16 20:00 | 2018-02-17 07:08 | -- | -- | -- | 0 | 0 | 0 | 0.46389 | N/A | N/A | N/A | NR/02/1373 NLDC/790 | LVRD | Line hand tripped for voltage regulation. Moga= 804KV
[7 empty] | 2018-02-17 08:41 | 2018-02-17 19:32 | -- | -- | -- | 0 | 0 | 0 | 0.45208 | N/A | N/A | N/A | NR/02/1407 NLDC/803 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-17 21:23 | 2018-02-18 08:33 | -- | -- | -- | 0 | 0 | 0 | 0.46528 | N/A | N/A | N/A | NR/02/1455 NLDC/844 | LVRD | Line hand tripped for voltage regulation. Moga= 798KV
[7 empty] | 2018-02-18 08:33 | 2018-02-18 19:26 | -- | -- | -- | 0 | 0 | 0 | 0.45347 | N/A | N/A | N/A | NR/02/1475 NLDC/852 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-18 21:12 | 2018-02-19 08:25 | -- | -- | -- | 0 | 0 | 0 | 0.46736 | N/A | N/A | N/A | NR/02/1507 NLDC/884 | LVRD | Line hand tripped for voltage regulation. Moga= 798KV
[7 empty] | 2018-02-19 08:25 | 2018-02-19 19:52 | -- | -- | -- | 0 | 0 | 0 | 0.47708 | N/A | N/A | N/A | NR/02/1525 NLDC/894 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-19 20:55 | 2018-02-20 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/02/1572 NLDC/936 | LVRD | Line hand tripped for voltage regulation. Moga= 796KV
[7 empty] | 2018-02-20 08:30 | 2018-02-20 19:28 | -- | -- | -- | 0 | 0 | 0 | 0.45694 | N/A | N/A | N/A | NR/02/1595 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-20 20:50 | 2018-02-21 07:02 | -- | -- | -- | 0 | 0 | 0 | 0.425 | N/A | N/A | N/A | NR/02/1653 | LVRD | Line hand tripped for voltage regulation. Panchkula= 804KV
[7 empty] | 2018-02-21 08:33 | 2018-02-21 19:33 | -- | -- | -- | 0 | 0 | 0 | 0.45833 | N/A | N/A | N/A | NR/02/1681 NLDC/1004 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-21 21:15 | 2018-02-22 07:05 | -- | -- | -- | 0 | 0 | 0 | 0.40972 | N/A | N/A | N/A | NR/02/1741 | LVRD | Line hand tripped for voltage regulation. Moga = 802KV
[7 empty] | 2018-02-22 08:59 | 2018-02-22 19:26 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | N/A | N/A | N/A | NR/02/1768 NLDC/1053 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-22 20:44 | 2018-02-23 07:08 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/02/1844 NL/02/1077 | LVRD | Line hand tripped for voltage regulation. Moga = 800KV
[7 empty] | 2018-02-23 09:10 | 2018-02-23 20:10 | -- | -- | -- | 0 | 0 | 0 | 0.45833 | N/A | N/A | N/A | NR/02/1871 NLDC/1093 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-23 20:20 | 2018-02-24 06:54 | -- | -- | -- | 0 | 0 | 0 | 0.44028 | N/A | N/A | N/A | NR/02/1931 NL/02/1117 | LVRD | Line hand tripped for voltage regulation. Moga = 800KV
[7 empty] | 2018-02-24 08:57 | 2018-02-24 20:15 | -- | -- | -- | 0 | 0 | 0 | 0.47083 | N/A | N/A | N/A | NR/02/1956 NLDC/1131 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-24 20:25 | 2018-02-25 07:14 | -- | -- | -- | 0 | 0 | 0 | 0.45069 | N/A | N/A | N/A | NR/02/1997 NLDC/1149 | LVRD | Line hand tripped for voltage regulation. Moga = 796KV
[7 empty] | 2018-02-25 09:01 | 2018-02-25 20:22 | -- | -- | -- | 0 | 0 | 0 | 0.47292 | N/A | N/A | N/A | NR/02/2035 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-25 20:22 | 2018-02-26 06:59 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | NR/02/2069 NLDC/1183 | LVRD | Line kept open for voltage regulation. Moga = 794KV.
[7 empty] | 2018-02-26 08:50 | 2018-02-26 20:05 | -- | -- | -- | 0 | 0 | 0 | 0.46875 | N/A | N/A | N/A | NR/02/2092 | LCSD | SD taken for Erection of 04 no. 7CC Towers, 04 no. peaks & 06 no. Beams and Reactor Firewall (Adjoining to existing 765 kV Meerut Line Reactor) of 765 kV Moga Bikaner-II Bay under construction at Moga.
[7 empty] | 2018-02-26 20:27 | 2018-02-27 09:15 | -- | -- | -- | 0 | 0 | 0 | 0.53333 | N/A | N/A | N/A | NR/02/2138 NLDC/1218 | LVRD | Line hand tripped for voltage regulation. Moga = 796KV
[7 empty] | 2018-02-27 12:40 | 2018-02-27 16:45 | -- | -- | -- | 0 | 0 | 0 | 0.17014 | N/A | N/A | N/A | NR/02/2181 NLDC/1250 | LVRD | Line hand tripped for voltage regulation. Moga = 797KV
[7 empty] | 2018-02-27 20:22 | 2018-02-28 07:08 | -- | -- | -- | 0 | 0 | 0 | 0.44861 | N/A | N/A | N/A | NR/02/2220 | LVRD | Line hand tripped for voltage regulation. Moga = 797KV
[7 empty] | 2018-02-28 12:41 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 0.47153 | N/A | N/A | N/A | NR/02/2270 NLDC/1292 | LVRD | Line hand tripped for voltage regulation. Moga = 789KV
[12 empty] | 0 | 0 | 0 | 1900-01-21 07:58 | [7 empty] | 100
1 | 115 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 116 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 117 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 118 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 119 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 120 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 121 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 |  | 2018-02-01 | 2018-02-12 02:41 | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 02:41 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=395KV.
[7 empty] | 2018-02-12 17:02 | 2018-02-13 00:29 | -- | -- | -- | 0 | 0 | 0 | 0.31042 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=390KV.
[7 empty] | 2018-02-13 14:52 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-14 09:08 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=390KV.
[12 empty] | 0 | 0 | 0 | 1900-01-25 19:16 | [7 empty] | 100
1 | 122 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 123 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 124 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 125 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 126 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 127 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 128 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 129 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 130 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 131 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 132 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 133 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 134 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 135 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 136 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 137 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 138 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 139 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 140 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 141 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 142 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 143 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 144 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 145 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 |  | 2018-02-01 | 2018-02-12 08:35 | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 08:35 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. New Wanpoh=395KV.
[7 empty] | 2018-02-12 11:20 | 2018-03-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-15 12:40 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. New Wanpoh=393KV.
[12 empty] | 0 | 0 | 0 | 1900-01-26 21:15 | [7 empty] | 100
1 | 146 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 147 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 148 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 149 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 150 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 151 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 152 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 153 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 |  | 2018-02-10 10:04 | 2018-02-10 12:15 | -- | -- | -- | 0.090972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/772 | OSPT | SD taken for attending oil leakage from OLTC surge relay of Y Ph.
[12 empty] | 0.090972 | 0 | 0 | 0 | [7 empty] | 99.68
1 | 154 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 155 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 |  | 2018-02-21 10:11 | 2018-02-21 17:47 | -- | -- | -- | 0.31667 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1688 | OSPT | SD taken for AMP works.
[12 empty] | 0.31667 | 0 | 0 | 0 | [7 empty] | 98.87
1 | 156 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 |  | 2018-02-20 10:10 | 2018-02-20 17:47 | -- | -- | -- | 0.31736 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1609 | OSPT | SD taken for AMP works.
[12 empty] | 0.31736 | 0 | 0 | 0 | [7 empty] | 98.87
1 | 157 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 158 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 159 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 160 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 161 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 162 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 163 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:10 | -- | -- | -- | 0 | 0 | 0.031944 | 0 | N/A | N/A | N/A | NR/993 | GOFC | ICT tripped on overflux due to system over voltage.
[12 empty] | 0 | 0 | 0.031944 | 0 | [7 empty] | 100
1 | 164 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 |  | 2018-02-22 09:55 | 2018-02-22 18:45 | -- | -- | -- | 0.36806 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1776 | OSPT | SD taken for AMP works.
[12 empty] | 0.36806 | 0 | 0 | 0 | [7 empty] | 98.69
1 | 165 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 |  | 2018-02-07 08:25 | 2018-02-07 09:58 | -- | -- | -- | 0 | 0.064583 | 0 | 0 | N/A | N/A | N/A | NR/02/512 | OMSU | ICT tripped from 220 kV side on BB operation at PSTCL station due to jumper broken of 220KV Malerkotla-Amloh Line in their yard. 220 CB of ICT is in PSTCL yard.
[12 empty] | 0 | 0.064583 | 0 | 0 | [7 empty] | 100
1 | 166 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 |  | 2018-02-07 08:25 | 2018-02-07 09:54 | -- | -- | -- | 0 | 0.061806 | 0 | 0 | N/A | N/A | N/A | NR/02/512 | OMSU | ICT tripped from 220 kV side on BB operation at PSTCL station due to jumper broken of 220KV Malerkotla-Amloh Line in their yard. 220 CB of ICT is in PSTCL yard.
[7 empty] | 2018-02-09 09:57 | 2018-02-09 18:46 | -- | -- | -- | 0.36736 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/691 | OSPT | SD taken for Amp works
[12 empty] | 0.36736 | 0.061806 | 0 | 0 | [7 empty] | 98.69
1 | 167 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 168 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 |  | 2018-02-21 12:20 | 2018-02-21 12:55 | -- | -- | -- | 0.024306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1696 | SICT | ICT tripped on backup earth fault relay optd on 220KV side.
[12 empty] | 0.024306 | 0 | 0 | 0 | [7 empty] | 99.92
1 | 169 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 170 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 171 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 172 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 173 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 174 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 175 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 176 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:33 | -- | -- | -- | 0.047917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.047917 | 0 | 0 | 0 | [7 empty] | 99.84
1 | 177 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:17 | -- | -- | -- | 0.036806 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.036806 | 0 | 0 | 0 | [7 empty] | 99.88
1 | 178 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:24 | -- | -- | -- | 0.041667 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.041667 | 0 | 0 | 0 | [7 empty] | 99.85
1 | 179 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 180 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 181 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 182 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 |  | 2018-02-12 11:24 | 2018-02-12 12:27 | -- | -- | -- | 0.04375 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Line handtripped as BUS voltage became zero.
[12 empty] | 0.04375 | 0 | 0 | 0 | [7 empty] | 99.85
1 | 183 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 184 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 |  | 2018-02-07 08:25 | 2018-02-07 09:25 | -- | -- | -- | 0 | 0.041667 | 0 | 0 | N/A | N/A | N/A | NR/02/513 | OMSU | ICT tripped from 220 kV side on BB operation at PSTCL station due to jumper broken of 220KV Malerkotla-Amloh Line in their yard. 220 CB of ICT is in PSTCL yard.
[12 empty] | 0 | 0.041667 | 0 | 0 | [7 empty] | 100
1 | 185 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 186 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 187 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 188 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 189 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 190 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 |  | 2018-02-10 16:30 | 2018-02-10 17:01 | -- | -- | -- | 0.021528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/761 NLDC/481 | OSPT | Shutdown taken for atteding oil leakage observed from top of Rediator.
[12 empty] | 0.021528 | 0 | 0 | 0 | [7 empty] | 99.92
1 | 191 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0
1 | 192 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 |  | 2018-02-23 09:52 | 2018-02-23 18:05 | -- | -- | -- | 0.34236 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1876 | OSPT | SD taken for AMP works.
[12 empty] | 0.34236 | 0 | 0 | 0 | [7 empty] | 98.78
1 | 193 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 194 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 195 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 196 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 197 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 198 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 |  | 2018-02-12 12:07 | 2018-02-12 12:10 | -- | -- | -- | 0 | 0 | 0.0020833 | 0 | N/A | N/A | N/A | NR/993 | GOFC | ICT tripped on overflux due to system over voltage.
[7 empty] | 2018-02-16 10:01 | 2018-02-16 19:04 | -- | -- | -- | 0.37708 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/1335 | OSPT | SD taken for AMP works
[12 empty] | 0.37708 | 0 | 0.0020833 | 0 | [7 empty] | 99.65
1 | 199 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 200 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 201 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 202 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 |  | 2018-02-06 14:54 | 2018-02-06 18:50 | -- | -- | -- | 0.16389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/443 | OSPT | SD taken for replacement of 220 kV R-Phase CT due to violation of Hydrogen during DGA.
[12 empty] | 0.16389 | 0 | 0 | 0 | [7 empty] | 99.41
1 | 203 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 204 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 205 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 |  | 2018-02-28 13:03 | 2018-02-28 14:12 | -- | -- | -- | 0.047917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/2273 | OSPT | SD taken for rectification of oil leakage from transformer.
[12 empty] | 0.047917 | 0 | 0 | 0 | [7 empty] | 99.83
1 | 206 | NR2ICT73 | KAITHAL 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 207 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 |  | 2018-02-19 16:16 | 2018-02-19 16:48 | -- | -- | -- | 0 | 0.022222 | 0 | 0 | N/A | N/A | N/A | NR/02/1557 | OMSU | SVC Tripped due to E/F created by Cat jumped on 26KV terminal of coupling transformer.
[12 empty] | 0 | 0.022222 | 0 | 0 | [7 empty] | 100
1 | 208 | NR2SVC02 | NEW WANPOH -200/+300 MVAR SVC |  | NR2 |  | 2018-02-12 08:06 | 2018-02-12 08:55 | -- | -- | -- | 0.034028 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/969 | OSFT | SVC tripped due to main bay CB problem.
[7 empty] | 2018-02-12 11:24 | 2018-02-12 12:18 | -- | -- | -- | 0.0375 | 0 | 0 | 0 | N/A | N/A | N/A | NR/993 | OSFT | Handtripped as BUS voltage became zero.
[12 empty] | 0.071528 | 0 | 0 | 0 | [7 empty] | 99.76
1 | 209 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 |  | 2018-02-01 08:03 | 2018-02-01 19:23 | -- | -- | -- | 0.47222 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/26 NL/02/08 | OSPT | Pole SD taken for upgradation of new software version.
[7 empty] | 2018-02-02 10:38 | 2018-02-02 19:22 | -- | -- | -- | 0.36389 | 0 | 0 | 0 | N/A | N/A | N/A | NL/02/57 | OSPT | Pole SD taken for upgradation of new software version.
[7 empty] | 2018-02-07 09:58 | 2018-02-07 10:21 | -- | -- | -- | 0.015972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/515 NLDC/325 WR/02/626 | OMST | Pole blocked/tripped due to auxiliary supply faliure at Kurukshetra end
[7 empty] | 2018-02-09 01:56 | 2018-02-09 04:25 | -- | -- | -- | 0.10347 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC-212 | OMST | Pole Blocked due to software mal operation at Champa. Converter differential operated at Champa.
[7 empty] | 2018-02-17 13:04 | 2018-02-17 13:53 | -- | -- | -- | 0 | 0 | 0.034028 | 0 | N/A | N/A | N/A | NLDC/818 | GOVC | Pole blocked due to filter switch out due to over voltage.
[12 empty] | 0.95556 | 0 | 0.034028 | 0 | [7 empty] | 96.58
1 | 210 | NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 |  | 2018-02-01 08:03 | 2018-02-01 19:25 | -- | -- | -- | 0.47361 | 0 | 0 | 0 | N/A | N/A | N/A | NR/02/26 NL/02/09 | OSPT | Pole SD taken for upgradation of new software version.
[7 empty] | 2018-02-02 10:38 | 2018-02-02 19:22 | -- | -- | -- | 0.36389 | 0 | 0 | 0 | N/A | N/A | N/A | NL/02/57 | OSPT | Pole SD taken for upgradation of new software version.
[12 empty] | 0.8375 | 0 | 0 | 0 | [7 empty] | 97.01
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(M8:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM(N8:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM(O8:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM(P8:[Deemed Available, row above])

## NR2 mar
Standard of Performance data for month of MARCH 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
Annexure-A
| S.no | ELEMENT CODE | ELEMENT NAME | DESCRIPTION (Length/Nos/MVA/MVAr/etc) | Region | Type of Failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration time more than Specified (Y/N) | Difference between Actual and specified | NRLDC Code | Category Code | REASON OF OUTAGE | Outage certifying Agency and reference documents (NRPC) | % Availability as certified by certifying agency
[7 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | POWERGRID | OTHERS | System constraints / Natural calamity/ Militancy | Deemed Available
[12 empty] | @ (T) | # (U) | & ( C ) | * (D)
[12 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
1 | 1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 |  | 2018-03-21 11:13 | 2018-03-21 12:08 | -- | -- | -- | 0 | 0.038194 | 0 | 0 | N/A | N/A | N/A | NR/03/1759 | OMSU | Line Tripped on R-N fault in Zone-3 from Sewa-2 due to non clearance of fault from JKPDD. FLR Sewa2:- 675.76A , 102 Km.
[12 empty] | 0 | 0.038194 | 0 | 0 | [7 empty] | 100
1 | 3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 |  | 2018-03-21 11:13 | 2018-03-21 12:07 | -- | -- | -- | 0 | 0.0375 | 0 | 0 | N/A | N/A | N/A | NR/03/1759 | OMSU | Line Tripped on R-N fault in Zone-3 from Sewa-2 due to non clearance of fault from JKPDD. FLR Sewa2:- 698.9A , 90 Km.
[12 empty] | 0 | 0.0375 | 0 | 0 | [7 empty] | 100
1 | 6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 |  | 2018-03-06 12:25 | 2018-03-06 20:03 | -- | -- | -- | 0 | 0 | 0 | 0.31806 | N/A | N/A | N/A | NR/03/335 | OSPD | SD taken by HPSEB for maintenance work at Jessore.
[7 empty] | 2018-03-08 13:03 | 2018-03-08 17:38 | -- | -- | -- | 0 | 0 | 0 | 0.19097 | N/A | N/A | N/A | NR/03/529 | OSPD | SD taken by HPSEB for maintenance work at Jessore.
[7 empty] | 2018-03-11 23:23 | 2018-03-12 04:20 | -- | -- | -- | 0 | 0.20625 | 0 | 0 | N/A | N/A | N/A | NR/03/829 | OMSU | Line tripped due to DC Failure problem at NHPC, Bairasuil. Due to this all machines tripped & consequently line tripped at Bairsiul..
[7 empty] | 2018-03-12 10:02 | 2018-03-12 18:38 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/03/843 | OSPD | SD taken by HPSEB for maintenance work at Jessore.
[7 empty] | 2018-03-14 13:24 | 2018-03-14 19:14 | -- | -- | -- | 0 | 0 | 0 | 0.24306 | N/A | N/A | N/A | NR/03/1079 | OSPD | SD taken by HPSEB for maintenance work at Jessore.
[12 empty] | 0 | 0.20625 | 0 | 1899-12-31 02:39 | [7 empty] | 100
1 | 7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 |  | 2018-03-02 02:30 | 2018-03-02 02:35 | -- | -- | -- | 0 | 0 | 0.0034722 | 0 | N/A | N/A | N/A | --- | GOVC | Line tripped on system high voltage. Bairasuil = 245KV.
[7 empty] | 2018-03-02 02:35 | 2018-03-02 07:34 | -- | -- | -- | 0 | 0 | 0 | 0.20764 | N/A | N/A | N/A | NR/03/56 | LVRD | Line kept open for voltage regulation.
[7 empty] | 2018-03-03 02:00 | 2018-03-03 02:10 | -- | -- | -- | 0 | 0 | 0.0069444 | 0 | N/A | N/A | N/A | --- | GOVC | Line tripped on system high voltage. Bairasuil = 244KV.
[7 empty] | 2018-03-03 02:10 | 2018-03-03 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.175 | N/A | N/A | N/A | NR/03/94 | LVRD | Line kept open for voltage regulation.
[7 empty] | 2018-03-11 23:23 | 2018-03-12 05:29 | -- | -- | -- | 0 | 0.25417 | 0 | 0 | N/A | N/A | N/A | NR/03/829 | OMSU | Line tripped due to DC Failure problem at NHPC, Bairasuil. Due to this all machines tripped & consequently line tripped at Bairsiul..
[7 empty] | 2018-03-21 03:32 | 2018-03-21 06:36 | -- | -- | -- | 0 | 0 | 0.12778 | 0 | N/A | N/A | N/A | NR/03/1699 | GOVC | Line tripped from Bairasuil on high voltage. Bairasuil = 243KV.
[12 empty] | 0 | 0.25417 | 0.13819 | 0.38264 | [7 empty] | 100
1 | 8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 |  | 2018-03-08 15:16 | 2018-03-08 18:25 | -- | -- | -- | 0 | 0 | 0 | 0.13125 | N/A | N/A | N/A | NR/03/537 | OSPD | SD taken by PSTCL for attending hotspot at Dasuya.
[12 empty] | 0 | 0 | 0 | 0.13125 | [7 empty] | 100
1 | 10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 |  | 2018-03-06 10:56 | 2018-03-08 18:51 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 07:55 | N/A | N/A | N/A | NR/03/333 | OSPD | SD taken by HPSEB for maintenance work at Jessore.
[7 empty] | 2018-03-12 09:25 | 2018-03-12 20:00 | -- | -- | -- | 0 | 0 | 0 | 0.44097 | N/A | N/A | N/A | NR/03/844 | OSPD | SD taken by HPSEB for maintenance work at Jessore.
[7 empty] | 2018-03-14 13:56 | 2018-03-14 20:41 | -- | -- | -- | 0 | 0 | 0 | 0.28125 | N/A | N/A | N/A | NR/03/1080 | OSPD | SD taken by HPSEB for maintenance work at Jessore.
[12 empty] | 0 | 0 | 0 | 1900-01-02 01:15 | [7 empty] | 100
1 | 12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 |  | 2018-03-21 10:09 | 2018-03-21 10:24 | -- | -- | -- | 0.010417 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1736 | LEFT | Line tripped on R-N fault. FLR kishenpur: 75.25 km.
[12 empty] | 0.010417 | 0 | 0 | 0 | [7 empty] | 99.97
1 | 14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 |  | 2018-03-15 06:54 | 2018-03-15 08:09 | -- | -- | -- | 0.052083 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1156 | LEFT | Line tripped on R-Y-B ph. Fault. FLR Salal : 11.53Km., Ir=Iy=Ib=9.0 KAmp.
[7 empty] | 2018-03-18 12:32 | 2018-03-18 13:12 | -- | -- | -- | 0 | 0.027778 | 0 | 0 | N/A | N/A | N/A | NR/03/1457 | OMSU | Line tripped from Salal only due to VT fuse failure at NHPC, Salal. There was no fault on the line.
[12 empty] | 0.052083 | 0.027778 | 0 | 0 | [7 empty] | 99.83
1 | 17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 |  | 2018-03-15 06:35 | 2018-03-15 08:09 | -- | -- | -- | 0.065278 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1156 | LPPT | Line tripped on Y-B ph fault. FLR Salal : 20Km., Iy=6.7 KA and Ib=7.8 KA.
[7 empty] | 2018-03-18 12:32 | 2018-03-18 13:14 | -- | -- | -- | 0 | 0.029167 | 0 | 0 | N/A | N/A | N/A | NR/03/1457 | OMSU | Line tripped from Salal only due to VT fuse failure at NHPC, Salal. There was no fault on the line.
[12 empty] | 0.065278 | 0.029167 | 0 | 0 | [7 empty] | 99.79
1 | 18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 |  | 2018-03-14 10:35 | 2018-03-14 16:51 | -- | -- | -- | 0.26111 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1062 | OSPT | SD taken for attending hotspot and damaged conductor on wave trap at Kishanpur.
[7 empty] | 2018-03-18 10:01 | 2018-03-18 17:50 | -- | -- | -- | 0 | 0 | 0 | 0.32569 | N/A | N/A | N/A | NR/03/1448 | OSPD | SD taken by NHPC for construction of new bay at Salal.
[7 empty] | 2018-03-30 09:43 | 2018-03-30 17:59 | -- | -- | -- | 0 | 0 | 0 | 0.34444 | N/A | N/A | N/A | NR/03/2685 | OSPD | SD taken by NHPC for construction of new bay at Salal.
[12 empty] | 0.26111 | 0 | 0 | 0.67014 | [7 empty] | 99.16
1 | 19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 |  | 2018-03-18 12:32 | 2018-03-18 13:16 | -- | -- | -- | 0 | 0.030556 | 0 | 0 | N/A | N/A | N/A | NR/03/1457 | OMSU | Line tripped from Salal only due to VT fuse failure at NHPC, Salal. There was no fault on the line.
[7 empty] | 2018-03-19 10:35 | 2018-03-19 17:50 | -- | -- | -- | 0 | 0 | 0 | 0.30208 | N/A | N/A | N/A | NR/03/1516 | OSPD | SD taken by NHPC for construction of new bay at Salal.
[12 empty] | 0 | 0.030556 | 0 | 0.30208 | [7 empty] | 100
1 | 20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 |  | 2018-03-21 11:09 | 2018-03-21 16:09 | -- | -- | -- | 0 | 0 | 0 | 0.20833 | N/A | N/A | N/A | NR/03/1746 | OSPD | SD taken by NHPC for maintenance work at salal.
[7 empty] | 2018-03-28 10:04 | 2018-03-29 19:20 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:16 | N/A | N/A | N/A | NR/03/2464 | OSPD | SD taken by NHPC for maintenance work at salal.
[12 empty] | 0 | 0 | 0 | 1899-12-31 14:16 | [7 empty] | 100
1 | 21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 |  | 2018-03-23 10:10 | 2018-03-23 17:51 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | N/A | N/A | N/A | NR/03/1994 | OSPD | SD taken by NHPC for maintenance work at salal.
[7 empty] | 2018-03-31 10:17 | 2018-03-31 16:24 | -- | -- | -- | 0 | 0 | 0 | 0.25486 | N/A | N/A | N/A | NR/03/2771 | OSPD | SD taken by NHPC for construction of new bay at Salal.
[12 empty] | 0 | 0 | 0 | 0.575 | [7 empty] | 100
1 | 22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 |  | 2018-03-10 09:55 | 2018-03-10 10:26 | -- | -- | -- | 0.021528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | OSPT | Line manually opened for normalisation after bus voltage becoming zero at Wagoora..
[12 empty] | 0.021528 | 0 | 0 | 0 | [7 empty] | 99.93
1 | 25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 |  | 2018-03-10 09:55 | 2018-03-10 10:02 | -- | -- | -- | 0.0048611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | OSPT | Line manually opened for normalisation after bus voltage becoming zero at Wagoora..
[12 empty] | 0.0048611 | 0 | 0 | 0 | [7 empty] | 99.98
1 | 26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 28 | NR222028 | 220KV Jallandhar-Hamirpur(PG) -I | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 29 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 30 | NR222030 | 220KV Jallandhar-Hamirpur(PG) -II | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 31 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 32 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 |  | 2018-03-21 10:22 | 2018-03-21 10:52 | -- | -- | -- | 0.020833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1744 | LPPT | Line tripped on R-Y to N fault .FLR Samba : 39.31 kM.
[7 empty] | 2018-03-22 10:20 | 2018-03-22 15:55 | -- | -- | -- | 0.23264 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1881 | OSPT | SD taken for rectification of DT fitting at location no. 29 which was damaged due lightening.
[12 empty] | 0.25347 | 0 | 0 | 0 | [7 empty] | 99.18
1 | 33 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 34 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 35 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 |  | 2018-03-30 10:16 | 2018-03-30 17:24 | -- | -- | -- | 0.29722 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2691 | OSPT | SD taken for AMP works.
[12 empty] | 0.29722 | 0 | 0 | 0 | [7 empty] | 99.04
1 | 36 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 |  | 2018-03-30 09:57 | 2018-03-30 10:19 | -- | -- | -- | 0 | 0 | 0 | 0.015278 | N/A | N/A | N/A | NR/03/2690 | OSPD | SD taken by NHPC to facilitate BUS-I shutdown at chamera-I .
[12 empty] | 0 | 0 | 0 | 0.015278 | [7 empty] | 100
1 | 37 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 38 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 |  | 2018-03-30 09:56 | 2018-03-30 10:23 | -- | -- | -- | 0 | 0 | 0 | 0.01875 | N/A | N/A | N/A | NR/03/2690 | OSPD | SD taken by NHPC to facilitate BUS-I shutdown at chamera-I .
[12 empty] | 0 | 0 | 0 | 0.01875 | [7 empty] | 100
1 | 39 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 |  | 2018-03-01 | 2018-03-01 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.26875 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-03-01 21:44 | 2018-03-02 06:32 | -- | -- | -- | 0 | 0 | 0 | 0.36667 | N/A | N/A | N/A | NR/03/50 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-03-02 08:37 | 2018-03-03 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.92153 | N/A | N/A | N/A | NR/03/61 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430KV
[7 empty] | 2018-03-03 20:28 | 2018-03-04 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/03/144 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-04 20:44 | 2018-03-05 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/03/207 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-05 20:16 | 2018-03-06 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/03/293 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-06 21:20 | 2018-03-07 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.37847 | N/A | N/A | N/A | NR/03/393 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-07 21:12 | 2018-03-08 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/03/484 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422KV
[7 empty] | 2018-03-08 20:24 | 2018-03-09 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.41042 | N/A | N/A | N/A | NR/03/570 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-09 20:20 | 2018-03-10 05:24 | -- | -- | -- | 0 | 0 | 0 | 0.37778 | N/A | N/A | N/A | NR/03/683 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-10 21:57 | 2018-03-11 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/03/772 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-11 21:00 | 2018-03-12 05:47 | -- | -- | -- | 0 | 0 | 0 | 0.36597 | N/A | N/A | N/A | NR/03/822 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-03-12 20:18 | 2018-03-13 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.39306 | N/A | N/A | N/A | NR/03/929 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-13 20:52 | 2018-03-14 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/03/1027 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-14 20:46 | 2018-03-15 06:13 | -- | -- | -- | 0 | 0 | 0 | 0.39375 | N/A | N/A | N/A | NR/03/1139 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-03-15 20:13 | 2018-03-16 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.40417 | N/A | N/A | N/A | NR/03/1230 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-16 20:09 | 2018-03-17 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.38958 | N/A | N/A | N/A | NR/03/1351 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-17 21:17 | 2018-03-18 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.34583 | N/A | N/A | N/A | NR/03/1430 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-18 21:24 | 2018-03-19 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/03/1486 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-20 21:26 | 2018-03-21 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.38819 | N/A | N/A | N/A | NR/03/1690 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-21 21:49 | 2018-03-22 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/03/1834 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[7 empty] | 2018-03-22 20:33 | 2018-03-23 05:56 | -- | -- | -- | 0 | 0 | 0 | 0.39097 | N/A | N/A | N/A | NR/03/1953 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[7 empty] | 2018-03-23 20:45 | 2018-03-24 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/03/2046 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 422KV
[7 empty] | 2018-03-24 21:41 | 2018-03-25 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.32431 | N/A | N/A | N/A | NR/03/2140 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-25 21:27 | 2018-03-26 05:52 | -- | -- | -- | 0 | 0 | 0 | 0.35069 | N/A | N/A | N/A | NR/03/2204 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 428KV
[7 empty] | 2018-03-26 21:16 | 2018-03-27 06:10 | -- | -- | -- | 0 | 0 | 0 | 0.37083 | N/A | N/A | N/A | NR/03/2301 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-27 21:47 | 2018-03-28 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/03/2432 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 425KV
[7 empty] | 2018-03-28 21:11 | 2018-03-29 06:26 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/03/2548 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 425KV
[7 empty] | 2018-03-29 21:47 | 2018-03-30 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/03/2657 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 425KV
[12 empty] | 0 | 0 | 0 | 1900-01-10 08:29 | [7 empty] | 100
1 | 40 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 |  | 2018-03-31 09:40 | 2018-04-01 | -- | -- | -- | 0.59722 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2766 | OSPT | SD taken for replacement of bend tower at Loc. No. 210 & general maintenece work of Tr.line.
[12 empty] | 0.59722 | 0 | 0 | 0 | [7 empty] | 98.01
1 | 41 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 |  | 2018-03-27 06:10 | 2018-03-27 06:10 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | .------- | LART | Line A/R on R-N fault. FLR Jalandhar : 60.74kM & Moga : 26.8 kM.
[7 empty] | 2018-03-29 09:44 | 2018-03-29 15:26 | -- | -- | -- | 0.2375 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2580 | OSPT | SD taken for AMP works.
[12 empty] | 0.2375 | 0 | 0 | 0 | [7 empty] | 99.23
1 | 42 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 43 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 44 | NR240024 | 400KV Moga-Hissar | 209.39 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 45 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 46 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 |  | 2018-03-01 | 2018-03-01 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.23472 | N/A | N/A | N/A | NR/02/2323 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-03-02 02:05 | 2018-03-02 07:19 | -- | -- | -- | 0 | 0 | 0 | 0.21806 | N/A | N/A | N/A | NR/03/55 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 429KV
[7 empty] | 2018-03-04 20:42 | 2018-03-05 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.40486 | N/A | N/A | N/A | NR/03/207 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-03-06 21:19 | 2018-03-07 06:44 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/03/393 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-10 21:56 | 2018-03-11 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.32361 | N/A | N/A | N/A | NR/03/772 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-03-17 21:09 | 2018-03-18 05:43 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/03/1430 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 422KV
[7 empty] | 2018-03-18 21:18 | 2018-03-19 05:57 | -- | -- | -- | 0 | 0 | 0 | 0.36042 | N/A | N/A | N/A | NR/03/1486 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 422KV
[7 empty] | 2018-03-20 21:23 | 2018-03-21 07:09 | -- | -- | -- | 0 | 0 | 0 | 0.40694 | N/A | N/A | N/A | NR/03/1690 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 427KV
[7 empty] | 2018-03-25 21:28 | 2018-03-26 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.37083 | N/A | N/A | N/A | NR/03/2204 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 427KV
[7 empty] | 2018-03-29 09:03 | 2018-03-29 19:51 | -- | -- | -- | 0.45 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2570 | OSPT | SD taken for AMP works.
[12 empty] | 0.45 | 0 | 0 | 1900-01-02 01:39 | [7 empty] | 98.55
1 | 47 | NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 |  | 2018-03-05 11:16 | 2018-03-05 17:47 | -- | -- | -- | 0 | 0 | 0 | 0.27153 | N/A | N/A | N/A | NR/03/243 | OSPD | SD taken by NRSS-XXIX Trans. Co Ltd - Sterlite for making LILO of Uri1-Wagoora-II at Amargarh.
[7 empty] | 2018-03-06 09:47 | 2018-03-06 17:33 | -- | -- | -- | 0 | 0 | 0 | 0.32361 | N/A | N/A | N/A | NR/03/322 | OSPD | SD taken by NRSS-XXIX Trans. Co Ltd - Sterlite for making LILO of Uri1-Wagoora-II at Amargarh.
[7 empty] | 2018-03-08 09:33 | 2018-03-08 17:36 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/03/510 | OSPD | SD taken by NRSS-XXIX Trans. Co Ltd - Sterlite for making LILO of Uri1-Wagoora-II at Amargarh.
[7 empty] | 2018-03-09 09:11 | 2018-03-09 17:31 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/03/602 | OSPD | SD taken by NRSS-XXIX Trans. Co Ltd - Sterlite for making LILO of Uri1-Wagoora-II at Amargarh.
[7 empty] | 2018-03-10 09:51 | 2018-03-10 10:34 | -- | -- | -- | 0.029861 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | Line tripped due to BB prptection operation at Wagoora.
[7 empty] | 2018-03-29 10:00 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 14:00 | N/A | N/A | N/A | NR/03/2567 | OSPD | SD taken by NRSS-XXIX Trans. Co Ltd - Sterlite for making LILO of Uri1-Wagoora-II at Amargarh.
[12 empty] | 0.029861 | 0 | 0 | 1900-01-02 20:40 | [7 empty] | 99.9
1 | 48 | NR240031 | 400KV URI-WAGOORA-II | 94.99 | NR2 |  | 2018-03-05 11:11 | 2018-03-15 16:52 | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 05:41 | N/A | N/A | N/A | NR/03/243 | OSPD | SD taken by NRSS-XXIX Trans. Co Ltd - Sterlite for making LILO at Amargarh.
[12 empty] | 0 | 0 | 0 | 1900-01-09 05:41
1 | 49 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 50 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 |  | 2018-03-12 09:14 | 2018-03-12 19:10 | -- | -- | -- | 0.41389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/845 | OSPT | SD taken for AMP works.
[12 empty] | 0.41389 | 0 | 0 | 0 | [7 empty] | 98.66
1 | 51 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 52 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 |  | 2018-03-08 10:59 | 2018-03-08 17:20 | -- | -- | -- | 0.26458 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/524 | OSPT | SD taken for CVT replacement at Malerkotla.
[12 empty] | 0.26458 | 0 | 0 | 0 | [7 empty] | 99.15
1 | 53 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 |  | 2018-03-02 17:23 | 2018-03-03 05:53 | -- | -- | -- | 0 | 0 | 0 | 0.52083 | N/A | N/A | N/A | NR/03/79 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-03-03 21:35 | 2018-03-04 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.325 | N/A | N/A | N/A | NR/03/149 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-03-20 16:54 | 2018-03-20 16:54 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | - | LART | Line A/R on B-N Fault.FLR Nalagarh:-10.95 Km & Patiala:- 82.16Km
[7 empty] | 2018-03-28 08:42 | 2018-03-28 19:34 | -- | -- | -- | 0.45278 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2450 | OSPT | SD taken for AMP Works
[7 empty] | 2018-03-29 00:58 | 2018-03-29 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.22917 | N/A | N/A | N/A | NR/03/2555 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 425KV
[7 empty] | 2018-03-05 20:50 | 2018-03-06 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/03/297 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[12 empty] | 0.45278 | 0 | 0 | 1899-12-31 11:29 | [7 empty] | 98.54
1 | 54 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 55 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 56 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 57 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 |  | 2018-03-07 11:25 | 2018-03-07 14:20 | -- | -- | -- | 0.12153 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/440 | OSPT | SD taken for rectification of jumper at location no. 8.
[7 empty] | 2018-03-10 09:51 | 2018-03-10 10:38 | -- | -- | -- | 0.032639 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | Line tripped due to BB prptection operation at Wagoora.
[7 empty] | 2018-03-22 16:00 | 2018-03-22 17:18 | -- | -- | -- | 0 | 0 | 0 | 0.054167 | N/A | N/A | N/A | NR/03/1915 | OSPD | SD taken by NHPC for conducting HV test at Uri 2.
[7 empty] | 2018-03-24 16:02 | 2018-03-24 17:20 | -- | -- | -- | 0 | 0 | 0 | 0.054167 | N/A | N/A | N/A | NR/03/2101 | OSPD | SD taken by NHPC for Leakage Current test of Surge Arrestor at Uri2.
[12 empty] | 0.15417 | 0 | 0 | 0.10833 | [7 empty] | 99.5
1 | 58 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 |  | 2018-03-22 16:07 | 2018-03-22 17:36 | -- | -- | -- | 0 | 0 | 0 | 0.061806 | N/A | N/A | N/A | NR/03/1915 | OSPD | SD taken by NHPC for conducting HV test at Uri 2.
[7 empty] | 2018-03-24 16:04 | 2018-03-24 17:26 | -- | -- | -- | 0 | 0 | 0 | 0.056944 | N/A | N/A | N/A | NR/03/2101 | OSPD | SD taken by NHPC for Leakage Current test of Surge Arrestor at Uri2.
[12 empty] | 0 | 0 | 0 | 0.11875 | [7 empty] | 100
1 | 59 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 |  | 2018-03-01 | 2018-03-01 06:16 | -- | -- | -- | 0 | 0 | 0 | 0.26111 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-03-01 21:41 | 2018-03-02 06:52 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/03/50 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-02 08:34 | 2018-03-03 06:03 | -- | -- | -- | 0 | 0 | 0 | 0.89514 | N/A | N/A | N/A | NR/03/61 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-03-03 14:07 | 2018-03-05 06:25 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 16:18 | N/A | N/A | N/A | NR/03/128 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-03-05 20:10 | 2018-03-06 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.44514 | N/A | N/A | N/A | NR/03/293 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 423KV
[7 empty] | 2018-03-06 21:18 | 2018-03-07 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/03/393 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-07 21:08 | 2018-03-08 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.35972 | N/A | N/A | N/A | NR/03/484 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-08 20:09 | 2018-03-09 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.42431 | N/A | N/A | N/A | NR/03/570 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421KV
[7 empty] | 2018-03-09 21:50 | 2018-03-10 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.33958 | N/A | N/A | N/A | NR/03/694 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-03-10 21:52 | 2018-03-11 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/03/772 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-03-11 20:59 | 2018-03-12 05:55 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/03/822 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 428KV
[7 empty] | 2018-03-12 20:16 | 2018-03-13 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/03/929 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 421KV
[7 empty] | 2018-03-13 22:47 | 2018-03-14 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.31944 | N/A | N/A | N/A | NR/03/1030 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-15 20:08 | 2018-03-16 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.41042 | N/A | N/A | N/A | NR/03/1230 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-16 20:05 | 2018-03-17 05:38 | -- | -- | -- | 0 | 0 | 0 | 0.39792 | N/A | N/A | N/A | NR/03/1351 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-17 21:08 | 2018-03-18 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/03/1430 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 422KV
[7 empty] | 2018-03-18 21:17 | 2018-03-19 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.39236 | N/A | N/A | N/A | NR/03/1486 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 422KV
[7 empty] | 2018-03-20 21:19 | 2018-03-21 06:41 | -- | -- | -- | 0 | 0 | 0 | 0.39028 | N/A | N/A | N/A | NR/03/1690 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 427KV
[7 empty] | 2018-03-21 21:38 | 2018-03-22 07:27 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | NR/03/1834 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 429KV
[7 empty] | 2018-03-22 21:25 | 2018-03-23 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/03/1954 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 429KV
[7 empty] | 2018-03-23 21:05 | 2018-03-24 07:41 | -- | -- | -- | 0 | 0 | 0 | 0.44167 | N/A | N/A | N/A | NR/03/2050 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 426KV
[7 empty] | 2018-03-24 21:39 | 2018-03-25 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/03/2140 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 426KV
[7 empty] | 2018-03-25 21:27 | 2018-03-26 07:22 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/03/2204 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 427KV
[7 empty] | 2018-03-26 21:12 | 2018-03-27 06:17 | -- | -- | -- | 0 | 0 | 0 | 0.37847 | N/A | N/A | N/A | NR/03/2301 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 426KV
[7 empty] | 2018-03-27 21:46 | 2018-03-28 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.35903 | N/A | N/A | N/A | NR/03/2432 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 424KV
[7 empty] | 2018-03-28 21:13 | 2018-03-29 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.38333 | N/A | N/A | N/A | NR/03/2548 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 423KV
[7 empty] | 2018-03-29 21:43 | 2018-03-30 07:24 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/03/2657 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 423KV
[7 empty] | 2018-03-31 21:19 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 0.11181 | N/A | N/A | N/A | NR/03/2817 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 423KV
[12 empty] | 0 | 0 | 0 | 1900-01-11 05:10 | [7 empty] | 100
1 | 60 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 61 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 |  | 2018-03-16 10:30 | 2018-03-16 15:32 | -- | -- | -- | 0.20972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1269 | OSPT | SD taken for replacement of damaged clamp connector of line isolator at Abdullapur.
[12 empty] | 0.20972 | 0 | 0 | 0 | [7 empty] | 99.32
1 | 62 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 63 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 |  | 2018-03-01 | 2018-03-01 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.24028 | N/A | N/A | N/A | NR/02/2320 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-03 20:29 | 2018-03-04 05:34 | -- | -- | -- | 0 | 0 | 0 | 0.37847 | N/A | N/A | N/A | NR/03/143 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-07 20:17 | 2018-03-08 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.39097 | N/A | N/A | N/A | NR/03/476 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-03-09 20:19 | 2018-03-10 05:16 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/03/683 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-03-11 20:36 | 2018-03-12 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.36042 | N/A | N/A | N/A | NR/03/819 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-03-13 20:43 | 2018-03-14 05:16 | -- | -- | -- | 0 | 0 | 0 | 0.35625 | N/A | N/A | N/A | NR/03/1025 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-15 13:52 | 2018-03-15 13:52 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N fault. FLR Panchkula:125.2 km & Naphta Jhakri: 31.61 km.
[7 empty] | 2018-03-15 20:35 | 2018-03-16 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/03/1233 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-03-16 20:11 | 2018-03-17 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.38819 | N/A | N/A | N/A | NR/03/1352 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-18 20:28 | 2018-03-19 05:35 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/03/1483 | LVRD | Line hand tripped for voltage regulation. Panchkula= 423KV
[7 empty] | 2018-03-20 20:32 | 2018-03-21 05:28 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/03/1687 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-22 20:41 | 2018-03-23 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.38194 | N/A | N/A | N/A | NR/03/1951 | LVRD | Line hand tripped for voltage regulation. Panchkula= 424KV
[7 empty] | 2018-03-24 20:33 | 2018-03-25 05:29 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/03/2134 | LVRD | Line hand tripped for voltage regulation. Panchkula= 424KV
[7 empty] | 2018-03-26 20:43 | 2018-03-27 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/03/2298 | LVRD | Line hand tripped for voltage regulation. Panchkula= 424KV
[7 empty] | 2018-03-28 20:46 | 2018-03-29 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.36458 | N/A | N/A | N/A | NR/03/2546 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-03-29 17:16 | 2018-03-29 18:04 | -- | -- | -- | 0.033333 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2628 | OSFT | Line tripped on R-N fault caused by heavy thunderstrom & rain in Jhakri area.
[7 empty] | 2018-03-30 02:03 | 2018-03-30 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.15208 | N/A | N/A | N/A | NR/03/2665 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-31 21:21 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 0.11042 | N/A | N/A | N/A | NR/03/2818 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[12 empty] | 0.033333 | 0 | 0 | 1900-01-04 08:52 | [7 empty] | 99.89
1 | 64 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 |  | 2018-03-01 20:02 | 2018-03-02 05:17 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/03/43 | LVRD | Line hand tripped for voltage regulation. Panchkula= 418KV
[7 empty] | 2018-03-02 20:43 | 2018-03-03 05:21 | -- | -- | -- | 0 | 0 | 0 | 0.35972 | N/A | N/A | N/A | NR/03/84 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-04 20:41 | 2018-03-05 05:27 | -- | -- | -- | 0 | 0 | 0 | 0.36528 | N/A | N/A | N/A | NR/03/204 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-05 20:40 | 2018-03-06 05:30 | -- | -- | -- | 0 | 0 | 0 | 0.36806 | N/A | N/A | N/A | NR/03/296 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-03-06 20:13 | 2018-03-07 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/03/387 | LVRD | Line hand tripped for voltage regulation. Panchkula= 421KV
[7 empty] | 2018-03-08 20:09 | 2018-03-09 05:41 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/03/568 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-03-10 20:39 | 2018-03-11 05:15 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/03/765 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-12 20:43 | 2018-03-13 05:32 | -- | -- | -- | 0 | 0 | 0 | 0.36736 | N/A | N/A | N/A | NR/03/931 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[7 empty] | 2018-03-14 20:35 | 2018-03-15 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/03/1135 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV.
[7 empty] | 2018-03-17 20:25 | 2018-03-18 05:31 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | N/A | N/A | N/A | NR/03/1428 | LVRD | Line hand tripped for voltage regulation. Panchkula = 420KV
[7 empty] | 2018-03-19 20:24 | 2018-03-20 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.38125 | N/A | N/A | N/A | NR/03/1565 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-21 20:39 | 2018-03-22 05:40 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/03/1826 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-23 20:07 | 2018-03-24 05:42 | -- | -- | -- | 0 | 0 | 0 | 0.39931 | N/A | N/A | N/A | NR/03/2042 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-25 20:24 | 2018-03-26 05:26 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/03/2202 | LVRD | Line hand tripped for voltage regulation. Panchkula= 418KV
[7 empty] | 2018-03-27 20:56 | 2018-03-28 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/03/2428 | LVRD | Line hand tripped for voltage regulation. Panchkula= 422KV
[7 empty] | 2018-03-29 17:16 | 2018-03-29 18:08 | -- | -- | -- | 0.036111 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2628 | OSFT | Line tripped on R-N fault caused by heavy thunderstrom & rain in Jhakri area.
[7 empty] | 2018-03-30 21:07 | 2018-03-31 05:27 | -- | -- | -- | 0 | 0 | 0 | 0.34722 | N/A | N/A | N/A | NR/03/2743 | LVRD | Line hand tripped for voltage regulation. Panchkula= 420KV
[12 empty] | 0.036111 | 0 | 0 | 1900-01-04 23:28 | [7 empty] | 99.88
1 | 65 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 66 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 67 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 |  | 2018-03-01 | 2018-03-01 06:09 | -- | -- | -- | 0 | 0 | 0 | 0.25625 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-03-01 21:42 | 2018-03-02 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/03/50 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-03-02 08:34 | 2018-03-03 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.89653 | N/A | N/A | N/A | NR/03/61 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 430KV
[7 empty] | 2018-03-03 20:28 | 2018-03-04 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.41111 | N/A | N/A | N/A | NR/03/144 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-04 20:41 | 2018-03-05 06:36 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/03/207 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-05 20:08 | 2018-03-06 06:29 | -- | -- | -- | 0 | 0 | 0 | 0.43125 | N/A | N/A | N/A | NR/03/293 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-06 21:19 | 2018-03-07 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.37639 | N/A | N/A | N/A | NR/03/393 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-07 21:07 | 2018-03-08 05:37 | -- | -- | -- | 0 | 0 | 0 | 0.35417 | N/A | N/A | N/A | NR/03/484 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 422KV
[7 empty] | 2018-03-08 13:39 | 2018-03-08 14:02 | -- | -- | -- | 0.015972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/535 | LEFT | Line tripped on Y-N fault.FLR Jalandhar: FL=99.57km.
[7 empty] | 2018-03-08 20:11 | 2018-03-09 06:02 | -- | -- | -- | 0 | 0 | 0 | 0.41042 | N/A | N/A | N/A | NR/03/570 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-09 20:16 | 2018-03-10 06:41 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/03/683 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-10 21:54 | 2018-03-11 05:44 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/03/772 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-11 20:58 | 2018-03-12 05:49 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | NR/03/822 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-03-12 20:14 | 2018-03-13 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.39722 | N/A | N/A | N/A | NR/03/929 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-13 20:51 | 2018-03-14 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/03/1027 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-14 13:00 | 2018-03-14 13:28 | -- | -- | -- | 0.019444 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1083 | LEFT | Line tripped on Y-N fault.FLR Jalandhar: 20.41 Km & Chamba: 141.57 Km.
[7 empty] | 2018-03-14 20:45 | 2018-03-15 06:33 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/03/1139 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 425KV
[7 empty] | 2018-03-15 20:10 | 2018-03-16 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.40556 | N/A | N/A | N/A | NR/03/1230 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-17 21:10 | 2018-03-18 06:27 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/03/1430 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-18 21:22 | 2018-03-19 06:48 | -- | -- | -- | 0 | 0 | 0 | 0.39306 | N/A | N/A | N/A | NR/03/1486 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-19 20:24 | 2018-03-20 06:48 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/03/1568 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 424KV
[7 empty] | 2018-03-20 20:26 | 2018-03-22 08:21 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:55 | N/A | N/A | N/A | NR/03/1688 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-22 20:32 | 2018-03-23 07:43 | -- | -- | -- | 0 | 0 | 0 | 0.46597 | N/A | N/A | N/A | NR/03/1953 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[7 empty] | 2018-03-23 20:44 | 2018-03-24 07:10 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | NR/03/2046 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 422KV
[7 empty] | 2018-03-25 01:58 | 2018-03-26 06:05 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:07 | N/A | N/A | N/A | NR/03/2145 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 430KV
[7 empty] | 2018-03-26 21:14 | 2018-03-27 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | NR/03/2301 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-27 21:44 | 2018-03-28 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/03/2432 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 425KV
[7 empty] | 2018-03-28 21:09 | 2018-03-29 06:23 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | NR/03/2548 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 425KV
[7 empty] | 2018-03-29 21:43 | 2018-03-30 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/03/2657 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 425KV
[7 empty] | 2018-03-31 01:42 | 2018-03-31 01:43 | -- | -- | -- | 0 | 0 | 0.00069444 | 0 | N/A | N/A | N/A | --- | GOVC | Line tripped on system high voltage.
[7 empty] | 2018-03-31 01:43 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 0.92847 | N/A | N/A | N/A | NR/03/2755 | LVRD | Line kept opened after tripped on system high voltage.
[12 empty] | 0.035417 | 0 | 0.00069444 | 1900-01-12 20:19 | [7 empty] | 99.89
1 | 68 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 |  | 2018-03-16 20:08 | 2018-03-17 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/03/1351 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[12 empty] | 0 | 0 | 0 | 0.42153 | [7 empty] | 100
1 | 69 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 70 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 71 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 |  | 2018-03-01 | 2018-03-01 06:15 | -- | -- | -- | 0 | 0 | 0 | 0.26042 | N/A | N/A | N/A | NR/02/2321 | LVRD | Line hand tripped for voltage regulation. Amritsar= 420KV
[7 empty] | 2018-03-01 21:44 | 2018-03-02 06:51 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/03/50 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-03-02 08:35 | 2018-03-03 07:01 | -- | -- | -- | 0 | 0 | 0 | 0.93472 | N/A | N/A | N/A | NR/03/61 | LVRD | Line hand tripped for voltage regulation. Amritsar= 426KV
[7 empty] | 2018-03-03 14:08 | 2018-03-05 06:24 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 16:16 | N/A | N/A | N/A | NR/03/128 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-03-05 20:24 | 2018-03-06 06:49 | -- | -- | -- | 0 | 0 | 0 | 0.43403 | N/A | N/A | N/A | NR/03/293 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-03-06 21:17 | 2018-03-07 06:32 | -- | -- | -- | 0 | 0 | 0 | 0.38542 | N/A | N/A | N/A | NR/03/393 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-03-07 21:08 | 2018-03-08 05:45 | -- | -- | -- | 0 | 0 | 0 | 0.35903 | N/A | N/A | N/A | NR/03/484 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-03-08 20:08 | 2018-03-09 06:18 | -- | -- | -- | 0 | 0 | 0 | 0.42361 | N/A | N/A | N/A | NR/03/570 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-03-09 21:49 | 2018-03-10 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.34028 | N/A | N/A | N/A | NR/03/694 | LVRD | Line hand tripped for voltage regulation. Amritsar= 423KV
[7 empty] | 2018-03-10 21:52 | 2018-03-11 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.34236 | N/A | N/A | N/A | NR/03/772 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-03-11 20:58 | 2018-03-12 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.37222 | N/A | N/A | N/A | NR/03/822 | LVRD | Line hand tripped for voltage regulation. Amritsar= 424KV
[7 empty] | 2018-03-12 20:15 | 2018-03-13 05:51 | -- | -- | -- | 0 | 0 | 0 | 0.4 | N/A | N/A | N/A | NR/03/929 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-13 22:46 | 2018-03-14 06:28 | -- | -- | -- | 0 | 0 | 0 | 0.32083 | N/A | N/A | N/A | NR/03/1030 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-15 20:06 | 2018-03-16 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.41181 | N/A | N/A | N/A | NR/03/1230 | LVRD | Line hand tripped for voltage regulation. Amritsar= 421KV
[7 empty] | 2018-03-16 20:04 | 2018-03-17 06:11 | -- | -- | -- | 0 | 0 | 0 | 0.42153 | N/A | N/A | N/A | NR/03/1351 | LVRD | Line hand tripped for voltage regulation. Amritsar= 422KV
[7 empty] | 2018-03-17 21:07 | 2018-03-18 06:08 | -- | -- | -- | 0 | 0 | 0 | 0.37569 | N/A | N/A | N/A | NR/03/1430 | LVRD | Line hand tripped for voltage regulation. Amritsar = 423KV
[7 empty] | 2018-03-18 21:16 | 2018-03-19 06:39 | -- | -- | -- | 0 | 0 | 0 | 0.39097 | N/A | N/A | N/A | NR/03/1486 | LVRD | Line hand tripped for voltage regulation. Amritsar = 423KV
[7 empty] | 2018-03-19 20:25 | 2018-03-20 06:35 | -- | -- | -- | 0 | 0 | 0 | 0.42361 | N/A | N/A | N/A | NR/03/1568 | LVRD | Line hand tripped for voltage regulation. Amritsar = 421KV
[7 empty] | 2018-03-20 20:27 | 2018-03-21 06:40 | -- | -- | -- | 0 | 0 | 0 | 0.42569 | N/A | N/A | N/A | NR/03/1688 | LVRD | Line hand tripped for voltage regulation. Amritsar = 423KV
[7 empty] | 2018-03-21 21:37 | 2018-03-22 07:26 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | NR/03/1834 | LVRD | Line hand tripped for voltage regulation. Amritsar = 423KV
[7 empty] | 2018-03-22 21:25 | 2018-03-23 07:33 | -- | -- | -- | 0 | 0 | 0 | 0.42222 | N/A | N/A | N/A | NR/03/1954 | LVRD | Line hand tripped for voltage regulation. Amritsar = 424KV
[7 empty] | 2018-03-23 21:04 | 2018-03-24 06:50 | -- | -- | -- | 0 | 0 | 0 | 0.40694 | N/A | N/A | N/A | NR/03/2049 | LVRD | Line hand tripped for voltage regulation. Amritsar = 422KV
[7 empty] | 2018-03-24 21:40 | 2018-03-25 06:12 | -- | -- | -- | 0 | 0 | 0 | 0.35556 | N/A | N/A | N/A | NR/03/2140 | LVRD | Line hand tripped for voltage regulation. Amritsar = 422KV
[7 empty] | 2018-03-25 21:26 | 2018-03-26 07:21 | -- | -- | -- | 0 | 0 | 0 | 0.41319 | N/A | N/A | N/A | NR/03/2204 | LVRD | Line hand tripped for voltage regulation. Amritsar = 424KV
[7 empty] | 2018-03-26 21:12 | 2018-03-27 06:19 | -- | -- | -- | 0 | 0 | 0 | 0.37986 | N/A | N/A | N/A | NR/03/2301 | LVRD | Line hand tripped for voltage regulation. Amritsar = 423KV
[7 empty] | 2018-03-27 21:46 | 2018-03-28 06:21 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/03/2432 | LVRD | Line hand tripped for voltage regulation. Amritsar = 422KV
[7 empty] | 2018-03-28 21:13 | 2018-03-29 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.38264 | N/A | N/A | N/A | NR/03/2548 | LVRD | Line hand tripped for voltage regulation. Amritsar = 422KV
[7 empty] | 2018-03-29 21:43 | 2018-03-30 07:23 | -- | -- | -- | 0 | 0 | 0 | 0.40278 | N/A | N/A | N/A | NR/03/2657 | LVRD | Line hand tripped for voltage regulation. Amritsar = 421KV
[7 empty] | 2018-03-31 21:15 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 0.11458 | N/A | N/A | N/A | NR/03/2817 | LVRD | Line hand tripped for voltage regulation. Amritsar = 421KV
[12 empty] | 0 | 0 | 0 | 1900-01-11 17:23 | [7 empty] | 100
1 | 72 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 |  | 2018-03-21 21:38 | 2018-03-21 21:58 | -- | -- | -- | 0 | 0 | 0.013889 | 0 | N/A | N/A | N/A | NR/03/1839 | GOVC | Line tripped on system high voltage.
[7 empty] | 2018-03-29 16:47 | 2018-03-29 17:23 | -- | -- | -- | 0 | 0.025 | 0 | 0 | N/A | N/A | N/A | NR/03/2621 | OMSU | Line tripped on DEF prtn operation on R-N ph at Banala cause by fault at or beyond NHPC, Parbati3. Fault location shown is 8.4KM and line length is 6.8 km.
[12 empty] | 0 | 0.025 | 0.013889 | 0 | [7 empty] | 100
1 | 73 | NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 |  | 2018-03-10 09:51 | 2018-03-10 10:02 | -- | -- | -- | 0.0076389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | Line tripped due to BB prptection operation at Wagoora.
[12 empty] | 0.0076389 | 0 | 0 | 0 | [7 empty] | 99.98
1 | 74 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 |  | 2018-03-10 09:51 | 2018-03-10 10:12 | -- | -- | -- | 0.014583 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | Line tripped due to BB prptection operation at Wagoora.
[12 empty] | 0.014583 | 0 | 0 | 0 | [7 empty] | 99.95
1 | 75 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 |  | 2018-03-05 21:56 | 2018-03-05 21:56 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on Y-N Fault. FLR New Wanpoh:- 4 km and Kishenpur: 133.7km
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 76 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 77 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 |  | 2018-03-03 15:16 | 2018-03-03 16:07 | -- | -- | -- | 0 | 0.035417 | 0 | 0 | N/A | N/A | N/A | NR/03/131 | OMSU | Line tripped on R-N fault caused by snapping of Pilot wire while laying OPGW under ULDC scheme. FLR Hamirpur: 27.6KM.
[7 empty] | 2018-03-27 13:27 | 2018-03-27 16:47 | -- | -- | -- | 0 | 0.13889 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | Line tripped on R-N fault caused by snapping of Pilot wire while laying OPGW under ULDC scheme. FLR Hamirpur: 28.865KM & Banala: 46.7 kM.
[7 empty] | 2018-03-29 16:47 | 2018-03-29 17:04 | -- | -- | -- | 0 | 0.011806 | 0 | 0 | N/A | N/A | N/A | NR/03/2618 | OMSU | Line tripped on R-N fault caused by snapping of Pilot wire while laying OPGW under ULDC scheme.
[12 empty] | 0 | 0.18611 | 0 | 0 | [7 empty] | 100
1 | 78 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 |  | 2018-03-08 09:12 | 2018-03-10 18:09 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:57 | N/A | N/A | N/A | NR/03/508 | OSPD | SD taken by SJVNL, Rampur for HV testing of replaced GIS CB pole.
[7 empty] | 2018-03-29 17:20 | 2018-03-29 18:06 | -- | -- | -- | 0.031944 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2628 | OSFT | Line tripped on R-N fault caused by heavy thunderstrom & rain in Jhakri area.
[12 empty] | 0.031944 | 0 | 0 | 1900-01-01 08:57 | [7 empty] | 99.89
1 | 79 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 |  | 2018-03-03 21:03 | 2018-03-04 05:33 | -- | -- | -- | 0 | 0 | 0 | 0.35417 | N/A | N/A | N/A | NR/03/148 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 428KV
[7 empty] | 2018-03-05 21:56 | 2018-03-06 05:39 | -- | -- | -- | 0 | 0 | 0 | 0.32153 | N/A | N/A | N/A | NR/03/304 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[7 empty] | 2018-03-09 09:57 | 2018-03-09 17:41 | -- | -- | -- | 0 | 0 | 0 | 0.32222 | N/A | N/A | N/A | NR/03/613 | OSPD | SD taken by SJVNL, Rampur for HV testing of replaced GIS CB pole.
[7 empty] | 2018-03-20 08:47 | 2018-03-20 17:11 | -- | -- | -- | 0 | 0 | 0 | 0.35 | N/A | N/A | N/A | NR/03/1593 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[7 empty] | 2018-03-21 08:51 | 2018-03-21 17:10 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/03/1717 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[7 empty] | 2018-03-21 21:40 | 2018-03-22 05:54 | -- | -- | -- | 0 | 0 | 0 | 0.34306 | N/A | N/A | N/A | NR/03/1834 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 429KV
[7 empty] | 2018-03-22 09:11 | 2018-03-22 16:59 | -- | -- | -- | 0 | 0 | 0 | 0.325 | N/A | N/A | N/A | NR/03/1871 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[7 empty] | 2018-03-23 09:46 | 2018-03-23 17:13 | -- | -- | -- | 0 | 0 | 0 | 0.31042 | N/A | N/A | N/A | NR/03/1986 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[7 empty] | 2018-03-23 00:47 | 2018-03-24 05:49 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 05:02 | N/A | N/A | N/A | NR/03/2054 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 427KV
[7 empty] | 2018-03-25 02:02 | 2018-03-25 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.14097 | N/A | N/A | N/A | NR/03/2145 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 427KV
[12 empty] | 0 | 0 | 0 | 1900-01-03 00:34 | [7 empty] | 100
1 | 80 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 81 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 |  | 2018-03-08 09:16 | 2018-03-08 17:18 | -- | -- | -- | 0 | 0 | 0 | 0.33472 | N/A | N/A | N/A | NR/03/509 | OSPD | SD taken by SJVNL, Rampur for HV testing of replaced GIS CB pole.
[7 empty] | 2018-03-09 09:11 | 2018-03-09 17:11 | -- | -- | -- | 0 | 0 | 0 | 0.33333 | N/A | N/A | N/A | NR/03/598 | OSPD | SD taken by SJVNL, Rampur for HV testing of replaced GIS CB pole.
[7 empty] | 2018-03-10 09:12 | 2018-03-10 17:06 | -- | -- | -- | 0 | 0 | 0 | 0.32917 | N/A | N/A | N/A | NR/03/711 | OSPD | SD taken by SJVNL, Rampur for HV testing of replaced GIS CB pole.
[7 empty] | 2018-03-29 17:18 | 2018-03-29 18:06 | -- | -- | -- | 0.033333 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2628 | OSFT | Line tripped on Y-N fault caused by heavy thunderstrom & rain in Jhakri area.
[12 empty] | 0.033333 | 0 | 0 | 0.99722 | [7 empty] | 99.89
1 | 82 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 |  | 2018-03-01 | 2018-03-01 05:08 | -- | -- | -- | 0 | 0 | 0 | 0.21389 | N/A | N/A | N/A | NR/02/2323 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 422KV
[7 empty] | 2018-03-02 02:07 | 2018-03-02 05:20 | -- | -- | -- | 0 | 0 | 0 | 0.13403 | N/A | N/A | N/A | NR/03/55 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 429KV
[7 empty] | 2018-03-02 17:21 | 2018-03-03 06:01 | -- | -- | -- | 0 | 0 | 0 | 0.52778 | N/A | N/A | N/A | NR/03/79 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 430KV
[7 empty] | 2018-03-04 23:52 | 2018-03-05 05:25 | -- | -- | -- | 0 | 0 | 0 | 0.23125 | N/A | N/A | N/A | NR/03/212 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 429KV
[7 empty] | 2018-03-06 21:17 | 2018-03-07 05:36 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | N/A | N/A | N/A | NR/03/393 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-07 21:11 | 2018-03-08 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.35764 | N/A | N/A | N/A | NR/03/484 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 424KV
[7 empty] | 2018-03-09 09:58 | 2018-03-09 17:39 | -- | -- | -- | 0 | 0 | 0 | 0.32014 | N/A | N/A | N/A | NR/03/613 | OSPD | SD taken by SJVNL, Rampur for HV testing of replaced GIS CB pole.
[7 empty] | 2018-03-20 09:02 | 2018-03-20 17:07 | -- | -- | -- | 0 | 0 | 0 | 0.33681 | N/A | N/A | N/A | NR/03/1598 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[7 empty] | 2018-03-21 09:59 | 2018-03-21 17:08 | -- | -- | -- | 0 | 0 | 0 | 0.29792 | N/A | N/A | N/A | NR/03/1727 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[7 empty] | 2018-03-22 09:24 | 2018-03-22 17:04 | -- | -- | -- | 0 | 0 | 0 | 0.31944 | N/A | N/A | N/A | NR/03/1872 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[7 empty] | 2018-03-22 21:23 | 2018-03-23 06:05 | -- | -- | -- | 0 | 0 | 0 | 0.3625 | N/A | N/A | N/A | NR/03/1954 | LVRD | Line hand tripped for voltage regulation. Nalagarh = 429KV
[7 empty] | 2018-03-23 09:47 | 2018-03-23 17:24 | -- | -- | -- | 0 | 0 | 0 | 0.31736 | N/A | N/A | N/A | NR/03/1986 | OSPD | SD taken by SJVNL, Rampur for maintenance work.
[12 empty] | 0 | 0 | 0 | 1900-01-02 18:22 | [7 empty] | 100
1 | 83 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 |  | 2018-03-02 13:08 | 2018-03-02 13:08 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on Y-N fault. FLR BBMB Panipat :-42.78km & Panchkula : 120.9km.
[7 empty] | 2018-03-20 12:19 | 2018-03-20 12:51 | -- | -- | -- | 0 | 0.022222 | 0 | 0 | N/A | N/A | N/A | NR/03/1627 | OMSU | Line tripped due to fault in 400KV Panipat-Dadri line from Panipat (BBMB) only and remained charged from Panchkula.
[12 empty] | 0 | 0.022222 | 0 | 0 | [7 empty] | 100
1 | 84 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 85 | NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 86 | NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 87 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 |  | 2018-03-03 21:44 | 2018-03-03 23:23 | -- | -- | -- | 0 | 0 | 0 | 0.06875 | N/A | N/A | N/A | NR/03/150 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 431KV
[12 empty] | 0 | 0 | 0 | 0.06875 | [7 empty] | 100
1 | 88 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 |  | 2018-03-22 08:54 | 2018-03-24 19:40 | -- | -- | -- | 1900-01-01 10:46 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1868 | OSPT | SD taken for replacement of GIS CB of Bus Reactor and Abdullapur-2 tie bay No. 427 & removal of aerial gloves for OPGW laying.
[12 empty] | 1900-01-01 10:46 | 0 | 0 | 0 | [7 empty] | 92.1
1 | 89 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 |  | 2018-03-22 09:45 | 2018-03-22 20:17 | -- | -- | -- | 0.43889 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1867 | OSPT | SD taken for removal of aerial gloves for OPGW laying.
[7 empty] | 2018-03-23 09:18 | 2018-03-23 19:09 | -- | -- | -- | 0.41042 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1981 | OSPT | SD taken for removal of aerial gloves for OPGW laying.
[7 empty] | 2018-03-24 09:23 | 2018-03-24 19:06 | -- | -- | -- | 0.40486 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2078 | OSPT | SD taken for removal of aerial gloves for OPGW laying.
[12 empty] | 1899-12-31 06:06 | 0 | 0 | 0 | [7 empty] | 95.95
1 | 90 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 |  | 2018-03-21 | 2018-03-21 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on R-N fault. FLR Kurukshetra :-80km &Sonipat : 19.1km.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 91 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 |  | 2018-03-01 | 2018-03-05 07:24 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 07:24 | N/A | N/A | N/A | NR/02/2323 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-03-05 21:34 | 2018-03-06 07:34 | -- | -- | -- | 0 | 0 | 0 | 0.41667 | N/A | N/A | N/A | NR/03/302 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-03-06 20:39 | 2018-03-11 09:45 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 13:06 | N/A | N/A | N/A | NR/03/390 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-03-18 21:17 | 2018-03-19 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | NR/03/1486 | LVRD | Line hand tripped for voltage regulation. Kurukshetra = 425KV
[7 empty] | 2018-03-21 04:07 | 2018-03-22 10:52 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:45 | N/A | N/A | N/A | NR/03/1696 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 433KV
[7 empty] | 2018-03-22 21:24 | 2018-03-27 07:50 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 10:26 | N/A | N/A | N/A | NR/03/1954 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[7 empty] | 2018-03-29 00:59 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 23:01 | N/A | N/A | N/A | NR/03/2555 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[12 empty] | 0 | 0 | 0 | 1900-01-17 07:56 | [7 empty] | 100
1 | 92 | NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 93 | NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 94 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 |  | 2018-03-21 06:33 | 2018-03-21 06:33 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N fault. FLR Kaithal :-119.24km & Bagpat: 27.4km.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 95 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 96 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 97 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 98 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 |  | 2018-03-02 22:26 | 2018-03-03 05:59 | -- | -- | -- | 0 | 0 | 0 | 0.31458 | N/A | N/A | N/A | NR/03/89 | LVRD | Line hand tripped for voltage regulation. Patiala= 424KV
[7 empty] | 2018-03-09 09:53 | 2018-03-09 18:57 | -- | -- | -- | 0.37778 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/617 | OSPT | SD taken for AMP works.
[7 empty] | 2018-03-10 09:18 | 2018-03-10 20:09 | -- | -- | -- | 0.45208 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/712 | OSPT | SD taken for AMP works.
[12 empty] | 0.82986 | 0 | 0 | 0.31458 | [7 empty] | 97.32
1 | 99 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 |  | 2018-03-12 09:56 | 2018-03-12 19:03 | -- | -- | -- | 0.37986 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/855 | OSPT | SD for AMP and rectfifaction of damaged fittings.
[7 empty] | 2018-03-13 09:32 | 2018-03-13 19:31 | -- | -- | -- | 0.41597 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/966 | OSPT | SD for AMP and rectfifaction of damaged fittings.
[12 empty] | 0.79583 | 0 | 0 | 0 | [7 empty] | 97.43
1 | 100 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 |  | 2018-03-02 22:25 | 2018-03-03 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.31597 | N/A | N/A | N/A | NR/03/89 | LVRD | Line hand tripped for voltage regulation. Kaithal= 425KV
[7 empty] | 2018-03-14 09:43 | 2018-03-14 19:55 | -- | -- | -- | 0.425 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1055 | OSPT | SD for AMP and rectfifaction of damaged fittings.
[7 empty] | 2018-03-15 10:11 | 2018-03-15 20:18 | -- | -- | -- | 0.42153 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1172 | OSPT | SD for AMP and rectfifaction of damaged fittings.
[7 empty] | 2018-03-18 13:00 | 2018-03-18 15:50 | -- | -- | -- | 0.11806 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1454 | OSPT | SD taken for rectification of damaged fittings at Tower Loc. No. 117.
[12 empty] | 0.96458 | 0 | 0 | 0.31597 | [7 empty] | 96.89
1 | 101 | NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 |  | 2018-03-16 09:50 | 2018-03-16 19:38 | -- | -- | -- | 0.40833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1273 | OSPT | SD for AMP and rectfifaction of damaged fittings.
[7 empty] | 2018-03-17 09:45 | 2018-03-17 19:39 | -- | -- | -- | 0.4125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1377 | OSPT | SD for AMP and rectfifaction of damaged fittings.
[12 empty] | 0.82083 | 0 | 0 | 0 | [7 empty] | 97.35
1 | 102 | NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2018-03-03 01:12 | 2018-03-03 06:25 | -- | -- | -- | 0 | 0 | 0 | 0.21736 | N/A | N/A | N/A | NR/03/92 | LVRD | Line hand tripped for voltage regulation. Dehar= 428KV
[12 empty] | 0 | 0 | 0 | 0.21736 | [7 empty] | 100
1 | 103 | NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 104 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 |  | 2018-03-02 17:25 | 2018-03-03 06:07 | -- | -- | -- | 0 | 0 | 0 | 0.52917 | N/A | N/A | N/A | NR/03/79 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 427KV
[12 empty] | 0 | 0 | 0 | 0.52917 | [7 empty] | 100
1 | 105 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 |  | 2018-03-02 02:03 | 2018-03-03 06:34 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:31 | N/A | N/A | N/A | NR/03/55 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-03-03 21:33 | 2018-03-05 07:18 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:45 | N/A | N/A | N/A | NR/03/149 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 428KV
[7 empty] | 2018-03-05 21:54 | 2018-03-06 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.35278 | N/A | N/A | N/A | NR/03/304 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 426KV
[7 empty] | 2018-03-06 21:16 | 2018-03-07 06:20 | -- | -- | -- | 0 | 0 | 0 | 0.37778 | N/A | N/A | N/A | NR/03/393 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-09 20:17 | 2018-03-10 05:23 | -- | -- | -- | 0 | 0 | 0 | 0.37917 | N/A | N/A | N/A | NR/03/683 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 423KV
[7 empty] | 2018-03-10 21:53 | 2018-03-11 05:46 | -- | -- | -- | 0 | 0 | 0 | 0.32847 | N/A | N/A | N/A | NR/03/772 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-13 22:50 | 2018-03-14 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/03/1030 | LVRD | Line hand tripped for voltage regulation. Jalandhar= 424KV
[7 empty] | 2018-03-18 21:19 | 2018-03-19 06:37 | -- | -- | -- | 0 | 0 | 0 | 0.3875 | N/A | N/A | N/A | NR/03/1486 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-20 21:54 | 2018-03-21 07:35 | -- | -- | -- | 0 | 0 | 0 | 0.40347 | N/A | N/A | N/A | NR/03/1692 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 427KV
[7 empty] | 2018-03-21 21:39 | 2018-03-22 07:48 | -- | -- | -- | 0 | 0 | 0 | 0.42292 | N/A | N/A | N/A | NR/03/1834 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[7 empty] | 2018-03-22 21:20 | 2018-03-23 06:00 | -- | -- | -- | 0 | 0 | 0 | 0.36111 | N/A | N/A | N/A | NR/03/1954 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[7 empty] | 2018-03-23 00:45 | 2018-03-24 05:43 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:58 | N/A | N/A | N/A | NR/03/2054 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 431KV
[7 empty] | 2018-03-25 21:24 | 2018-03-26 05:58 | -- | -- | -- | 0 | 0 | 0 | 0.35694 | N/A | N/A | N/A | NR/03/2204 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 428KV
[12 empty] | 0 | 0 | 0 | 1900-01-06 11:39 | [7 empty] | 100
1 | 106 | NR240116 | 400KV Dadri-Kaithal | 213 | NR2 |  | 2018-03-09 11:20 | 2018-03-09 17:53 | -- | -- | -- | 0.27292 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/632 | OSPT | SD taken for CVT replacement at Malerkotla.
[12 empty] | 0.27292 | 0 | 0 | 0 | [7 empty] | 99.78
1 | 107 | NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 |  | 2018-03-21 11:46 | 2018-03-21 12:07 | -- | -- | -- | 0.014583 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1753 | OSPT | SD taken for taking LR out for carrying out testing on LR.
[7 empty] | 2018-03-21 19:57 | 2018-03-21 21:14 | -- | -- | -- | 0.053472 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1821 | OSPT | SD taken for taking the line reactor into service after testing.
[12 empty] | 0.068056 | 0 | 0 | 0 | [7 empty] | 99.12
1 | 108 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 109 | NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 |  | 2018-03-21 21:38 | 2018-03-21 23:53 | -- | -- | -- | 0 | 0 | 0.09375 | 0 | N/A | N/A | N/A | NR/03/1839 | GOVC | Line tripped on system high voltage.
[12 empty] | 0 | 0 | 0.09375 | 0 | [7 empty] | 100
1 | 110 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 111 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 |  | 2018-03-15 02:45 | 2018-03-15 02:45 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | ---- | LART | Line A/R on Y-N fault. FLR New Wanpoh: 70.7kms & Kishenpur: 64.93 Km.
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 112 | NR240122 | 400KV KURUKSHETRA - JIND - I | 103.6 | NR2 |  | 2018-03-02 15:49 | 2018-03-03 07:30 | -- | -- | -- | 0 | 0 | 0 | 0.65347 | N/A | N/A | N/A | NR/03/71 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 432KV
[7 empty] | 2018-03-03 13:26 | 2018-03-04 06:31 | -- | -- | -- | 0 | 0 | 0 | 0.71181 | N/A | N/A | N/A | NR/03/126 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 435KV
[7 empty] | 2018-03-04 23:59 | 2018-03-05 07:22 | -- | -- | -- | 0 | 0 | 0 | 0.30764 | N/A | N/A | N/A | NR/03/212 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 428KV
[7 empty] | 2018-03-05 21:47 | 2018-03-06 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.40625 | N/A | N/A | N/A | NR/03/302 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-03-06 21:05 | 2018-03-07 06:22 | -- | -- | -- | 0 | 0 | 0 | 0.38681 | N/A | N/A | N/A | NR/03/390 | LVRD | Line hand tripped for voltage regulation. Kurukshetra= 430KV
[7 empty] | 2018-03-22 21:45 | 2018-03-23 05:50 | -- | -- | -- | 0 | 0 | 0 | 0.33681 | N/A | N/A | N/A | NR/03/1954 | LVRD | Line hand tripped for voltage regulation. Kurukshetra = 431KV
[12 empty] | 0 | 0 | 0 | 1900-01-01 19:16
[9 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  |  | 100
1 | 113 | NR240123 | 400KV KURUKSHETRA - JIND - II | 103.6 | NR2 | [6 empty] | 0 | 0 | 0 | 0
[9 empty] | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  |  |  | 100
1 | 114 | NR240125 | 400KV URI 1 - AMARGARH - II | 61.95 | NR2 |  | 2018-03-20 11:14 | 2018-03-26 15:28 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 04:14 | N/A | N/A | N/A | NR/03/1618 | OSPD | SD taken by NHPC for maintenance work at Uri1.
[7 empty] | 2018-03-29 09:57 | 2018-03-29 18:13 | -- | -- | -- | 0 | 0 | 0 | 0.34444 | N/A | N/A | N/A | NR/03/2569 | OSPD | SD taken by NRSS-XXIX Trans. Co. Ltd - Sterlite for making LILO of 400 kV Uri1-Wagoora-I at Amargarh.
[7 empty] | 2018-03-30 09:48 | 2018-03-30 17:54 | -- | -- | -- | 0 | 0 | 0 | 0.3375 | N/A | N/A | N/A | NR/03/2683 | OSPD | SD taken by NRSS-XXIX Trans. Co. Ltd - Sterlite for making LILO of 400 kV Uri1-Wagoora-I at Amargarh.
[7 empty] | 2018-03-31 09:39 | 2018-03-31 17:42 | -- | -- | -- | 0 | 0 | 0 | 0.33542 | N/A | N/A | N/A | NR/03/2768 | OSPD | SD taken by NRSS-XXIX Trans. Co. Ltd - Sterlite for making LILO of 400 kV Uri1-Wagoora-I at Amargarh.
[12 empty] | 0 | 0 | 0 | 1900-01-06 04:39 | [7 empty] | 100
1 | 115 | NR240126 | 400KV AMARGARH - WAGOORA- II | 39.34 | NR2 |  | 2018-03-21 13:17 | 2018-03-23 19:02 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 05:45 | N/A | N/A | N/A | NR/03/1766 | OSPD | SD taken by NRSS-XXIX Trans. Co. Ltd - Sterlite for construction work at Amargarh.
[7 empty] | 2018-03-29 09:59 | 2018-03-29 17:54 | -- | -- | -- | 0 | 0 | 0 | 0.32986 | N/A | N/A | N/A | NR/03/2568 | OSPD | SD taken by NRSS-XXIX Trans. Co. Ltd - Sterlite for making LILO of 400 kV Uri1-Wagoora-I at Amargarh.
[7 empty] | 2018-03-30 09:52 | 2018-03-30 17:48 | -- | -- | -- | 0 | 0 | 0 | 0.33056 | N/A | N/A | N/A | NR/03/2683 | OSPD | SD taken by NRSS-XXIX Trans. Co. Ltd - Sterlite for making LILO of 400 kV Uri1-Wagoora-I at Amargarh.
[7 empty] | 2018-03-31 09:44 | 2018-03-31 17:34 | -- | -- | -- | 0 | 0 | 0 | 0.32639 | N/A | N/A | N/A | NR/03/2767 | OSPD | SD taken by NRSS-XXIX Trans. Co. Ltd - Sterlite for making LILO of 400 kV Uri1-Wagoora-I at Amargarh.
[12 empty] | 0 | 0 | 0 | 1900-01-02 05:26 | [7 empty] | 100
1 | 116 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 |  | 2018-03-01 | 2018-03-01 07:26 | -- | -- | -- | 0 | 0 | 0 | 0.30972 | N/A | N/A | N/A | NR/02/2270 NLDC/1292 | LVRD | Line hand tripped for voltage regulation. Moga = 789KV
[7 empty] | 2018-03-01 17:39 | 2018-03-05 06:44 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 13:05 | N/A | N/A | N/A | NR/03/37 NLDC/28 | LVRD | Line hand tripped for voltage regulation. Moga = 798KV
[7 empty] | 2018-03-05 13:14 | 2018-03-05 18:55 | -- | -- | -- | 0 | 0 | 0 | 0.23681 | N/A | N/A | N/A | NR/03/257 NLDC/158 | LVRD | Line hand tripped for voltage regulation. Moga = 794KV
[7 empty] | 2018-03-05 20:54 | 2018-03-06 08:27 | -- | -- | -- | 0 | 0 | 0 | 0.48125 | N/A | N/A | N/A | NR/03/299 NLDC/181 | LVRD | Line hand tripped for voltage regulation. Moga = 800KV
[7 empty] | 2018-03-06 13:03 | 2018-03-07 07:42 | -- | -- | -- | 0 | 0 | 0 | 0.77708 | N/A | N/A | N/A | NR/03/349 NL/03/209 | LVRD | Line hand tripped for voltage regulation. Moga = 800 KV
[7 empty] | 2018-03-07 21:13 | 2018-03-08 07:07 | -- | -- | -- | 0 | 0 | 0 | 0.4125 | N/A | N/A | N/A | NR/03/485 NL/03/283 | LVRD | Line hand tripped for voltage regulation. Moga = 796 KV
[7 empty] | 2018-03-08 20:49 | 2018-03-09 10:09 | -- | -- | -- | 0 | 0 | 0 | 0.55556 | N/A | N/A | N/A | NR/03/573 NL/03/325 | LVRD | Line hand tripped for voltage regulation. Moga = 794 KV
[7 empty] | 2018-03-09 20:53 | 2018-03-10 08:22 | -- | -- | -- | 0 | 0 | 0 | 0.47847 | N/A | N/A | N/A | NR/03/688 NL/03/373 | LVRD | Line hand tripped for voltage regulation. Moga = 805 KV
[7 empty] | 2018-03-10 20:45 | 2018-03-11 08:26 | -- | -- | -- | 0 | 0 | 0 | 0.48681 | N/A | N/A | N/A | NR/03/769 NL/03/421 | LVRD | Line hand tripped for voltage regulation. Moga = 795 KV
[7 empty] | 2018-03-11 21:08 | 2018-03-12 06:56 | -- | -- | -- | 0 | 0 | 0 | 0.40833 | N/A | N/A | N/A | NR/03/823 NL/03/451 | LVRD | Line hand tripped for voltage regulation. Moga = 801 KV
[7 empty] | 2018-03-12 21:34 | 2018-03-13 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.38403 | N/A | N/A | N/A | NR/03/935 NLDC/493 | LVRD | Line hand tripped for voltage regulation. Moga = 792 KV
[7 empty] | 2018-03-14 20:47 | 2018-03-15 07:28 | -- | -- | -- | 0 | 0 | 0 | 0.44514 | N/A | N/A | N/A | NR/03/1140 NLDC/571 | LVRD | Line hand tripped for voltage regulation. Moga = 800 KV
[7 empty] | 2018-03-15 21:06 | 2018-03-16 07:47 | -- | -- | -- | 0 | 0 | 0 | 0.44514 | N/A | N/A | N/A | NR/03/1236 NLDC/613 | LVRD | Line hand tripped for voltage regulation. Moga = 800 KV
[7 empty] | 2018-03-16 21:08 | 2018-03-17 07:07 | -- | -- | -- | 0 | 0 | 0 | 0.41597 | N/A | N/A | N/A | NR/03/1356 NLDC/658 | LVRD | Line hand tripped for voltage regulation. Moga = 792 KV
[7 empty] | 2018-03-17 21:16 | 2018-03-18 09:26 | -- | -- | -- | 0 | 0 | 0 | 0.50694 | N/A | N/A | N/A | NR/03/1431 | LVRD | Line hand tripped for voltage regulation. Moga = 798 KV
[7 empty] | 2018-03-18 20:53 | 2018-03-19 08:02 | -- | -- | -- | 0 | 0 | 0 | 0.46458 | N/A | N/A | N/A | NR/03/1485 NLDC/726 | LVRD | Line hand tripped for voltage regulation. Moga = 801 KV
[7 empty] | 2018-03-19 21:39 | 2018-03-20 06:42 | -- | -- | -- | 0 | 0 | 0 | 0.37708 | N/A | N/A | N/A | NR/03/1573 NLDC/764 | LVRD | Line hand tripped for voltage regulation. Moga = 794 KV
[7 empty] | 2018-03-20 21:07 | 2018-03-21 07:31 | -- | -- | -- | 0 | 0 | 0 | 0.43333 | N/A | N/A | N/A | NR/03/1689 NLDC/802 | LVRD | Line hand tripped for voltage regulation. Moga = 796 KV
[7 empty] | 2018-03-21 07:36 | 2018-03-21 07:36 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N fault. FLR Moga :-2.5kA, 235 km & FLR Merrut : 7.2kA,110.2km.
[7 empty] | 2018-03-21 08:19 | 2018-03-21 12:39 | -- | -- | -- | 0 | 0 | 0 | 0.18056 | N/A | N/A | N/A | NR/03/1713 NLDC/814 | LVRD | Line hand tripped for voltage regulation. Moga = 800 KV
[7 empty] | 2018-03-21 21:41 | 2018-03-22 07:59 | -- | -- | -- | 0 | 0 | 0 | 0.42917 | N/A | N/A | N/A | NR/03/1833 NLDC/852 | LVRD | Line hand tripped for voltage regulation. Moga = 803 KV
[7 empty] | 2018-03-24 00:53 | 2018-03-24 07:57 | -- | -- | -- | 0 | 0 | 0 | 0.29444 | N/A | N/A | N/A | NR/03/2055 NLDC/957 | LVRD | Line hand tripped for voltage regulation. Moga = 800 KV
[7 empty] | 2018-03-25 02:06 | 2018-03-25 06:56 | -- | -- | -- | 0 | 0 | 0 | 0.20139 | N/A | N/A | N/A | NR/03/2146 NLDC/945 | LVRD | Line hand tripped for voltage regulation. Moga = 802 KV
[7 empty] | 2018-03-25 15:18 | 2018-03-25 18:42 | -- | -- | -- | 0 | 0 | 0 | 0.14167 | N/A | N/A | N/A | NR/03/2185 NLDC/1012 | LVRD | Line hand tripped for voltage regulation. Moga = 800 KV
[7 empty] | 2018-03-26 00:55 | 2018-03-26 10:42 | -- | -- | -- | 0 | 0 | 0 | 0.40764 | N/A | N/A | N/A | NR/03/2214 NLDC/1028 | LVRD | Line hand tripped for voltage regulation. Moga = 800 KV
[7 empty] | 2018-03-27 01:36 | 2018-03-27 09:48 | -- | -- | -- | 0 | 0 | 0 | 0.34167 | N/A | N/A | N/A | NR/03/2311 NLDC/1081 | LVRD | Line hand tripped for voltage regulation. Moga = 798 KV
[7 empty] | 2018-03-29 01:18 | 2018-03-29 07:42 | -- | -- | -- | 0 | 0 | 0 | 0.26667 | N/A | N/A | N/A | NR/03/2556 NLDC/1187 | LVRD | Line hand tripped for voltage regulation. Moga = 798 KV
[7 empty] | 2018-03-31 03:09 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 0.86875 | N/A | N/A | N/A | NR/03/2758 NLDC/1270 | LVRD | Line hand tripped for voltage regulation. Moga = 802 KV
[12 empty] | 0 | 0 | 0 | 1900-01-13 07:06 | [7 empty] | 100
1 | 117 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 118 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 119 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 120 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 121 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 122 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 123 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 |  | 2018-03-01 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=390KV.
[12 empty] | 0 | 0 | 0 | 1900-01-30 | [7 empty] | 100
1 | 124 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 125 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 126 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 127 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 128 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 129 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 130 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 131 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 132 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 133 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 134 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 135 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 136 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 137 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 138 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 139 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 140 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 141 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 142 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 143 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 144 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 145 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 146 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 147 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 |  | 2018-03-01 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. New Wanpoh=393KV.
[12 empty] | 0 | 0 | 0 | 1900-01-30 | [7 empty] | 100
1 | 148 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 |  | 2018-03-09 10:09 | 2018-03-09 22:25 | -- | -- | -- | 0.51111 | 0 | 0 | 0 | N/A | N/A | N/A | --- | SRET | B Ph. Unit of L/R tripped on Bucholtz trip while switching as Bus reactor.
[12 empty] | 0.51111 | 0 | 0 | 0 | [7 empty] | 98.35
1 | 149 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 |  | 2018-03-22 08:58 | 2018-03-24 19:42 | -- | -- | -- | 1900-01-01 10:44 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1866 | OSPT | SD taken for replacement of CB of Bus Reactor and Abdullapur-2 tie bay No. 427 at Kurukshetra.
[12 empty] | 1900-01-01 10:44 | 0 | 0 | 0 | [7 empty] | 91.84
1 | 150 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 151 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 152 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 |  | 2018-03-19 13:31 | 2018-03-19 21:52 | -- | -- | -- | 0.34792 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1528 | OSPT | SD taken for rectification work of 400KV Bus-1 side isolator drive mechanism problem .
[7 empty] | 2018-03-20 13:11 | 2018-03-20 18:22 | -- | -- | -- | 0.21597 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1628 | OSPT | SD taken for rectification work of 400KV Bus-2 side isolator drive mechanism problem .
[12 empty] | 0.56389 | 0 | 0 | 0 | [7 empty] | 98.12
1 | 153 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 |  | 2018-03-19 13:31 | 2018-03-19 21:52 | -- | -- | -- | 0.34792 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1528 | OSPT | SD taken for rectification work of 400KV Bus-1 side isolator drive mechanism problem .
[7 empty] | 2018-03-20 13:11 | 2018-03-20 18:22 | -- | -- | -- | 0.21597 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1628 | OSPT | SD taken for rectification work of 400KV Bus-2 side isolator drive mechanism problem .
[12 empty] | 0.56389 | 0 | 0 | 0 | [7 empty] | 98.12
1 | 154 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 155 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 |  | 2018-03-13 11:55 | 2018-03-13 13:14 | -- | -- | -- | 0.054861 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/984 | OSFT | ICT tripped on PRD-2 protection operation due to exension of tripping due to crack developed in TB.
[12 empty] | 0.054861 | 0 | 0 | 0 | [7 empty] | 99.82
1 | 156 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 |  | 2018-03-22 10:00 | 2018-03-22 13:24 | -- | -- | -- | 0.14167 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1888 | OSPT | SD taken for Tan delta measurement of B ph HV bushing.
[12 empty] | 0.14167 | 0 | 0 | 0 | [7 empty] | 99.54
1 | 157 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 158 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 159 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 160 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 |  | 2018-03-15 10:15 | 2018-03-15 18:45 | -- | -- | -- | 0.35417 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1175 | OSPT | SD taken for AMP works.
[12 empty] | 0.35417 | 0 | 0 | 0 | [7 empty] | 98.86
1 | 161 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 162 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 163 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 |  | 2018-03-19 09:20 | 2018-03-19 18:40 | -- | -- | -- | 0.38889 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1503 | OSPT | SD taken for AMP works
[12 empty] | 0.38889 | 0 | 0 | 0 | [7 empty] | 98.75
1 | 164 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 165 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 166 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 167 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 168 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 169 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 170 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 171 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 172 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 |  | 2018-03-26 09:36 | 2018-03-29 19:51 | -- | -- | -- | 1900-01-02 10:15 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2204 | OSPT | SD taken for replacement of 02 no. Tertiary Bushings due to tan delta violation.
[12 empty] | 1900-01-02 10:15 | 0 | 0 | 0 | [7 empty] | 88.94
1 | 173 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 174 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 175 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 176 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 177 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 178 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 |  | 2018-03-10 09:51 | 2018-03-10 10:02 | -- | -- | -- | 0.0076389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | ICT tripped due to BB protection operation at Wagoora.
[12 empty] | 0.0076389 | 0 | 0 | 0 | [7 empty] | 99.98
1 | 179 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 |  | 2018-03-10 09:51 | 2018-03-10 10:14 | -- | -- | -- | 0.015972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | ICT tripped due to BB protection operation at Wagoora.
[12 empty] | 0.015972 | 0 | 0 | 0 | [7 empty] | 99.95
1 | 180 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 |  | 2018-03-10 09:51 | 2018-03-10 10:22 | -- | -- | -- | 0.021528 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | ICT tripped due to BB protection operation at Wagoora.
[12 empty] | 0.021528 | 0 | 0 | 0 | [7 empty] | 99.93
1 | 181 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 |  | 2018-03-27 09:56 | 2018-03-27 15:55 | -- | -- | -- | 0.24931 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2340 | OSPT | SD taken for AMP works.
[12 empty] | 0.24931 | 0 | 0 | 0 | [7 empty] | 99.2
1 | 182 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 183 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 184 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 |  | 2018-03-10 09:51 | 2018-03-10 10:30 | -- | -- | -- | 0.027083 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/714 | SBBT | ICT tripped due to BB protection operation at Wagoora.
[12 empty] | 0.027083 | 0 | 0 | 0 | [7 empty] | 99.91
1 | 185 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 186 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 |  | 2018-03-13 11:46 | 2018-03-13 12:56 | -- | -- | -- | 0.048611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/980 | OSPT | Emergency SD taken for attending hotspot on 220KV R-ph CB-pole at 220KV PSTCL switch yard.
[12 empty] | 0.048611 | 0 | 0 | 0 | [7 empty] | 99.84
1 | 187 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 188 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 189 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 190 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 191 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 192 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 193 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 194 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 195 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 196 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 197 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 198 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 199 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 200 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 201 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 202 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 203 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 204 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 |  | 2018-03-15 09:26 | 2018-03-15 18:07 | -- | -- | -- | 0.36181 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1166 | OSPT | SD taken for AMP.
[7 empty] | 2018-03-16 06:56 | 2018-03-16 08:53 | -- | -- | -- | 0.08125 | 0 | 0 | 0 | N/A | N/A | N/A | --- | SICT | ICT tripped on differential protection operation due to leakage current seen in neutral.
[7 empty] | 2018-03-16 08:53 | 2018-03-16 12:06 | -- | -- | -- | 0.13403 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1260 | OSPT | SD taken for checking & rectification after tripping on differential protection.
[12 empty] | 0.57708 | 0 | 0 | 0 | [7 empty] | 98.14
1 | 205 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 206 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 207 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 |  | 2018-03-11 13:09 | 2018-03-11 21:41 | -- | -- | -- | 0.35556 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/820 | SICT | ICT tripped on differential protection operation.
[7 empty] | 2018-03-20 12:43 | 2018-03-20 12:50 | -- | -- | -- | 0.0048611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/1626 | OSPT | SD taken to shift ICT from Bus-1 to Bus-2 to facilitate shutdown on 400KV bus-1 at Dehar.
[12 empty] | 0.36042 | 0 | 0 | 0 | [7 empty] | 98.84
1 | 208 | NR2ICT73 | KAITHAL 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 209 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[12 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
1 | 210 | NR2SVC02 | NEW WANPOH -200/+300 MVAR SVC |  | NR2 |  | 2018-03-05 21:56 | 2018-03-05 22:53 | -- | -- | -- | 0.039583 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/305 | OMST | SVC tripped due to SPR relay operated on Y-phase.
[12 empty] | 0.039583 | 0 | 0 | 0 | [7 empty] | 98.35
1 | 211 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 |  | 2018-03-03 20:23 | 2018-03-03 22:51 | -- | -- | -- | 0.10278 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/151 WR/03/205 NLDC/108 | OMST | Pole blocked due to Converter Differential Protection latch at Kurukshetra.
[7 empty] | 2018-03-30 08:00 | 2018-03-31 23:34 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:34 | N/A | N/A | N/A | NLDC/1239 | LCSD | SD taken for erection of Jack Bus for Pole -II & IV under construction over common area of Pole-I & II and crossing of 765KV DC Jabalpur Vidhayanchal line.
[12 empty] | 0.10278 | 0 | 0 | 1899-12-31 15:34 | [7 empty] | 99.67
1 | 212 | NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 |  | 2018-03-05 21:08 | 2018-03-05 22:08 | -- | -- | -- | 0.041667 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/182 | OMST | Pole blocked due to control mal-operation at Kurukshetra.
[7 empty] | 2018-03-27 11:10 | 2018-03-27 11:35 | -- | -- | -- | 0.017361 | 0 | 0 | 0 | N/A | N/A | N/A | NR/03/2361 NLDC/1102 WR/03/2413 | OMST | Pole-II Blocked due to "External Block from valve cooling system" optd. at Champa end.
[7 empty] | 2018-03-29 08:11 | 2018-03-29 23:54 | -- | -- | -- | 0 | 0 | 0 | 0.65486 | N/A | N/A | N/A | NR/03/2564 NLDC/1195 WR/03/2622 | LCSD | SD taken for erection of Strung Bus over Pole II for Pole IV under construction.
[7 empty] | 2018-03-30 08:06 | 2018-04-01 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 15:54 | N/A | N/A | N/A | NLDC/1240 | LCSD | SD taken for erection of Jack Bus for Pole -II & IV under construction over common area of Pole-I & II and crossing of 765KV DC Jabalpur Vidhayanchal line.
[12 empty] | 0.059028 | 0 | 0 | 1900-01-01 07:37 | [7 empty] | 99.81
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM([DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM([OTHERS, row above])
Hrs:Min = IF(RIGHT([Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM([Hrs:Min, row above])
Deemed Available = IF(RIGHT([Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM([Deemed Available, row above])