## Sheet2 (2)
Standard of Performance data for the month of March - 2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
Annexure - A
S.No. | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 | -- | 2019-03-17 | 10:22 | 2019-03-17 | 17:33 | -- | -- | -- | 0 | 0 | 0 | 0.29931 | N/A | N/A | N/A | SD taken by JKPDD for general maintenance & rectification work in Hiranagar SS.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.29931 | [5 empty] | 100
2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 | -- | 2019-03-13 | 5:25 | 2019-03-13 | 6:14 | -- | -- | -- | 0.034028 | 0 | 0 | 0 | N/A | N/A | N/A | Line tripped on R-N fault. FLR Sewa2 : 55.39kM , 1.248kA.
[6 empty] | 2019-03-17 | 10:22 | 2019-03-17 | 17:32 |  |  |  | 0 | 0 | 0 | 0.29861 |  |  |  | SD taken by JKPDD for general maintenance & rectification work in Hiranagar SS.
[6 empty] | Sub Total --> | [6 empty] | 0.034028 | 0 | 0 | 0.29861 | [5 empty] | 99.89
4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 | -- | 2019-03-01 | 0:00 | 2019-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | N/A | N/A | N/A | SD taken by NHPC, Bairasiul power station for renovation work.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-30 | [5 empty] | 100
7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 | -- | 2019-03-01 | 0:00 | 2019-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | N/A | N/A | N/A | SD taken by NHPC, Bairasiul power station for renovation work.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-30 | [5 empty] | 100
8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 | -- | 2019-03-02 | 8:12 | 2019-03-02 | 10:59 | -- | -- | -- | 0 | 0.11597 | 0 | 0 | N/A | N/A | N/A | Line tripped due to B-phase CT droper damaged at JKPDD, Hiranagar and SD taken by JKPDD for rectification.
[6 empty] | 2019-03-17 | 10:08 | 2019-03-17 | 19:10 |  |  |  | 0 | 0 | 0 | 0.37639 |  |  |  | SD taken by JKPDD for general maintenance & rectification work in Hiranagar SS.
[6 empty] | 2019-03-22 | 13:27 | 2019-03-22 | 14:25 |  |  |  | 0 | 0 | 0 | 0.040278 |  |  |  | Shutdown taken by PSTCL for attending hot spot in their switchyard.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.11597 | 0 | 0.41667 | [5 empty] | 100
9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 | -- | 2019-03-03 | 2:59 | 2019-03-03 | 3:46 | -- | -- | -- | 0 | 0 | 0.032639 | 0 | N/A | N/A | N/A | Line tripped from HPSEB Jessore only on over voltage protection optd.
[6 empty] | 2019-03-03 | 3:56 | 2019-03-03 | 4:25 |  |  |  | 0 | 0 | 0.020139 | 0 |  |  |  | Line tripped from HPSEB Jessore only on over voltage protection optd.
[6 empty] | 2019-03-03 | 4:25 | 2019-03-03 | 6:06 |  |  |  | 0 | 0 | 0 | 0.070139 |  |  |  | Line kept open for voltage regulation after tripped from Jessore on over voltage protection.
[6 empty] | 2019-03-04 | 3:01 | 2019-03-04 | 6:16 |  |  |  | 0 | 0 | 0.13542 | 0 |  |  |  | Line tripped from Jessore only on over voltage protection optd.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.18819 | 0.070139 | [5 empty] | 100
12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 | -- | 2019-03-03 | 9:11 | 2019-03-03 | 14:07 | -- | -- | -- | 0 | 0 | 0 | 0.20556 | N/A | N/A | N/A | SD taken by JKPDD for complete 220 kV Bus-1 & 2 maintenance at Jammu (Gladni).
[6 empty] | 2019-03-14 | 15:11 | 2019-03-14 | 16:11 |  |  |  | 0 | 0.041667 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | 2019-03-18 | 18:42 | 2019-03-18 | 20:06 |  |  |  | 0 | 0.058333 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.1 | 0 | 0.20556 | [5 empty] | 100
17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 | -- | 2019-03-03 | 9:11 | 2019-03-03 | 14:07 | -- | -- | -- | 0 | 0 | 0 | 0.20556 | N/A | N/A | N/A | SD taken by JKPDD for complete 220 kV Bus-1 & 2 maintenance at Jammu (Gladni).
[6 empty] | 2019-03-14 | 15:11 | 2019-03-14 | 17:07 |  |  |  | 0 | 0.080556 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | 2019-03-18 | 18:42 | 2019-03-19 | 11:35 |  |  |  | 0 | 0.70347 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.78403 | 0 | 0.20556 | [5 empty] | 100
18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 | -- | 2019-03-14 | 15:11 | 2019-03-14 | 15:28 | -- | -- | -- | 0 | 0.011806 | 0 | 0 | N/A | N/A | N/A | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | 2019-03-18 | 18:42 | 2019-03-18 | 19:22 |  |  |  | 0 | 0.027778 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.039583 | 0 | 0 | [5 empty] | 100
19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 | -- | 2019-03-14 | 15:11 | 2019-03-14 | 15:44 | -- | -- | -- | 0 | 0.022917 | 0 | 0 | N/A | N/A | N/A | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | 2019-03-18 | 18:42 | 2019-03-18 | 19:25 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.052778 | 0 | 0 | [5 empty] | 100
20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 | -- | 2019-03-14 | 15:11 | 2019-03-14 | 15:48 | -- | -- | -- | 0 | 0.025694 | 0 | 0 | N/A | N/A | N/A | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | 2019-03-18 | 18:42 | 2019-03-19 | 21:44 |  |  |  | 0 | 1899-12-31 03:02 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | 2019-03-30 | 13:55 | 2019-03-30 | 18:06 |  |  |  | 0 | 0 | 0 | 0.17431 |  |  |  | SD taken by NHPC Slal on emergency basis for some rectification work at their end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1899-12-31 03:39 | 0 | 0.17431 | [5 empty] | 100
21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 | -- | 2019-03-14 | 15:11 | 2019-03-14 | 15:55 | -- | -- | -- | 0 | 0.030556 | 0 | 0 | N/A | N/A | N/A | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | 2019-03-18 | 18:42 | 2019-03-18 | 20:06 |  |  |  | 0 | 0.058333 | 0 | 0 |  |  |  | Line tripped due to Bus Bar protection operation at NHPC Salal.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.088889 | 0 | 0 | [5 empty] | 100
22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 | -- | 2019-03-20 | 12:01 | 2019-03-20 | 16:49 | -- | -- | -- | 0 | 0 | 0 | 0.2 | N/A | N/A | N/A | SD taken by PSTCL to attend hotspot in Bus Bur jumper.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.2 | [5 empty] | 100
24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 | -- | 2019-03-17 | 10:35 | 2019-03-17 | 19:00 | -- | -- | -- | 0.35069 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for rectification of damaged OPGW damaged during Heavy snow fall.
[6 empty] | 2019-03-17 | 19:00 | 2019-03-17 | 21:19 |  |  |  | 0 | 0 | 0 | 0.096528 |  |  |  | Line kept open by NHPC chamera-3 due to constraint at their end.
[6 empty] | Sub Total --> | [6 empty] | 0.35069 | 0 | 0 | 0.096528 | [5 empty] | 98.87
27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
28 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 | -- | 2019-03-23 | 9:14 | 2019-03-23 | 17:40 | -- | -- | -- | 0.35139 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for AMP works.
[6 empty] | Sub Total --> | [6 empty] | 0.35139 | 0 | 0 | 0 | [5 empty] | 98.87
29 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 | -- | 2019-03-24 | 8:48 | 2019-03-24 | 18:25 | -- | -- | -- | 0.40069 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for AMP works.
[6 empty] | Sub Total --> | [6 empty] | 0.40069 | 0 | 0 | 0 | [5 empty] | 98.71
30 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 | -- | 2019-03-03 | 9:17 | 2019-03-03 | 14:04 | -- | -- | -- | 0 | 0 | 0 | 0.19931 | N/A | N/A | N/A | SD taken by JKPDD for complete 220 kV Bus-1 & 2 maintenance at Jammu (Gladni).
[6 empty] | 2019-03-27 | 6:49 | 2019-03-27 | 7:05 |  |  |  | 0.011111 | 0 | 0 | 0 |  |  |  | Line A/R on R-N fault from Samba but tripped from Jammu due to A/R problem. FLR Samba:- 37.135 Km & 3.893 KA
[6 empty] | Sub Total --> | [6 empty] | 0.011111 | 0 | 0 | 0.19931 | [5 empty] | 99.96
31 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 | -- | 2019-03-17 | 10:47 | 2019-03-17 | 18:57 | -- | -- | -- | 0 | 0 | 0 | 0.34028 | N/A | N/A | N/A | SD taken by JKPDD for complete 220 kV Bus-1 & 2 maintenance at Hiranagar.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.34028 | [5 empty] | 100
32 | NR222034 | 220KV KISHANGANGA(NHPC)-DELINA(JKPDD)-I | 41.62 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
33 | NR222035 | 220KV KISHANGANGA(NHPC)-DELINA(JKPDD)-II | 41.62 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
34 | NR222036 | 220KV JALANDHAR-NEHRIAN (HPSEB)-I | 72.93 | NR2 | -- | 2019-03-08 | 21:44 | 2019-03-09 | 6:15 | -- | -- | -- | 0 | 0 | 0 | 0.35486 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Jalandhar=236KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.35486 | [5 empty] | 100
35 | NR222037 | 220KV JALANDHAR-NEHRIAN (HPSEB)-II | 72.93 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
36 | NR222038 | 220KV HAMIRPUR-NEHRIAN (HPSEB)-I | 55.4 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
37 | NR222039 | 220KV HAMIRPUR-NEHRIAN (HPSEB)-II | 55.4 | NR2 | -- | [7 empty] | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
38 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
39 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
40 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 | -- | 2019-03-16 | 9:48 | 2019-03-16 | 18:40 | -- | -- | -- | 0.36944 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for rectification of damaged OPGW.
[6 empty] | 2019-03-29 | 9:49 | 2019-03-29 | 18:22 |  |  |  | 0 | 0 | 0 | 0.35625 |  |  |  | SD taken by NHPC, Chamera2 for testing purpose.
[6 empty] | Sub Total --> | [6 empty] | 0.36944 | 0 | 0 | 0.35625 | [5 empty] | 98.81
41 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 | -- | 2019-03-16 | 9:20 | 2019-03-16 | 18:55 | -- | -- | -- | 0.39931 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for rectification of damaged OPGW.
[6 empty] | 2019-03-27 | 9:40 | 2019-03-27 | 18:28 |  |  |  | 0 | 0 | 0 | 0.36667 |  |  |  | SD taken by NHPC Chamera2 for relay testing at their end.
[6 empty] | 2019-03-28 | 9:38 | 2019-03-28 | 17:42 |  |  |  | 0 | 0 | 0 | 0.33611 |  |  |  | SD taken by NHPC Chamera2 for relay testing at their end.
[6 empty] | Sub Total --> | [6 empty] | 0.39931 | 0 | 0 | 0.70278 | [5 empty] | 98.71
42 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 | -- | 2019-03-01 | 21:42 | 2019-03-02 | 6:08 | -- | -- | -- | 0 | 0 | 0 | 0.35139 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | 2019-03-05 | 21:48 | 2019-03-06 | 5:41 |  |  |  | 0 | 0 | 0 | 0.32847 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | 2019-03-08 | 21:36 | 2019-03-09 | 6:10 |  |  |  | 0 | 0 | 0 | 0.35694 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=426KV
[6 empty] | 2019-03-12 | 21:49 | 2019-03-13 | 5:56 |  |  |  | 0 | 0 | 0 | 0.33819 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=426KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1899-12-31 09:00 | [5 empty] | 100
43 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 5:55 | -- | -- | -- | 0 | 0 | 0 | 0.24653 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Jalandhar=426KV
[6 empty] | 2019-03-04 | 20:36 | 2019-03-05 | 5:47 |  |  |  | 0 | 0 | 0 | 0.38264 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-09 | 21:39 | 2019-03-10 | 5:53 |  |  |  | 0 | 0 | 0 | 0.34306 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | 2019-03-13 | 21:33 | 2019-03-14 | 5:17 |  |  |  | 0 | 0 | 0 | 0.32222 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-18 | 1:57 | 2019-03-18 | 5:59 |  |  |  | 0 | 0 | 0 | 0.16806 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-20 | 21:34 | 2019-03-21 | 6:07 |  |  |  | 0 | 0 | 0 | 0.35625 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-24 | 23:54 | 2019-03-25 | 6:05 |  |  |  | 0 | 0 | 0 | 0.25764 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=428KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-01 01:50 | [5 empty] | 100
44 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
45 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
46 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
47 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
48 | NR240024 | 400KV Moga-Hissar | 209.39 | NR2 | -- | 2019-03-04 | 21:43 | 2019-03-05 | 8:31 | -- | -- | -- | 0 | 0 | 0 | 0.45 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Moga=426KV
[6 empty] | 2019-03-05 | 22:08 | 2019-03-06 | 7:25 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | Line hand tripped for voltage regulation. Moga=426KV
[6 empty] | 2019-03-14 | 13:01 | 2019-03-14 | 13:07 |  |  |  | 0 | 0 | 0.0041667 | 0 |  |  |  | Line tripped due to Over Voltage protection operation at Hisar.
[6 empty] | 2019-03-14 | 13:07 | 2019-03-14 | 20:14 |  |  |  | 0 | 0 | 0 | 0.29653 |  |  |  | Line kept open after tripped due to system over voltage.
[6 empty] | 2019-03-20 | 16:54 | 2019-03-20 | 17:19 |  |  |  | 0 | 0 | 0.017361 | 0 |  |  |  | Line tripped due to Over Voltage protection operation at Hisar.
[6 empty] | 2019-03-22 | 14:33 | 2019-03-22 | 15:48 |  |  |  | 0 | 0 | 0.052083 | 0 |  |  |  | Line tripped due to Over Voltage protection operation at Hisar.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.073611 | 1899-12-31 03:12 | [5 empty] | 100
49 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
50 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 6:19 | -- | -- | -- | 0 | 0 | 0 | 0.26319 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-01 | 20:04 | 2019-03-02 | 6:16 |  |  |  | 0 | 0 | 0 | 0.425 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-05 | 21:54 | 2019-03-06 | 5:45 |  |  |  | 0 | 0 | 0 | 0.32708 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-08 | 19:40 | 2019-03-09 | 6:34 |  |  |  | 0 | 0 | 0 | 0.45417 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-12 | 21:43 | 2019-03-13 | 5:47 |  |  |  | 0 | 0 | 0 | 0.33611 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-13 | 20:12 | 2019-03-14 | 5:15 |  |  |  | 0 | 0 | 0 | 0.37708 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=434KV
[6 empty] | 2019-03-16 | 20:58 | 2019-03-17 | 5:47 |  |  |  | 0 | 0 | 0 | 0.36736 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-19 | 9:19 | 2019-03-19 | 18:17 |  |  |  | 0.37361 | 0 | 0 | 0 |  |  |  | SD Taken for AMP works.
[6 empty] | 2019-03-20 | 21:39 | 2019-03-21 | 6:51 |  |  |  | 0 | 0 | 0 | 0.38333 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=434KV
[6 empty] | 2019-03-21 | 20:14 | 2019-03-22 | 6:28 |  |  |  | 0 | 0 | 0 | 0.42639 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=422KV
[6 empty] | 2019-03-25 | 20:01 | 2019-03-26 | 6:16 |  |  |  | 0 | 0 | 0 | 0.42708 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=425KV
[6 empty] | Sub Total --> | [6 empty] | 0.37361 | 0 | 0 | 1900-01-02 18:53 | [5 empty] | 98.79
51 | NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
52 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
53 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
54 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
55 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
56 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 | -- | 2019-03-02 | 20:09 | 2019-03-03 | 5:33 | -- | -- | -- | 0 | 0 | 0 | 0.39167 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-03 | 14:45 | 2019-03-04 | 5:33 |  |  |  | 0 | 0 | 0 | 0.61667 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=429KV
[6 empty] | 2019-03-04 | 21:57 | 2019-03-05 | 5:41 |  |  |  | 0 | 0 | 0 | 0.32222 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-06 | 23:33 | 2019-03-07 | 5:21 |  |  |  | 0 | 0 | 0 | 0.24167 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=428KV
[6 empty] | 2019-03-07 | 23:39 | 2019-03-08 | 5:38 |  |  |  | 0 | 0 | 0 | 0.24931 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=425KV
[6 empty] | 2019-03-10 | 20:26 | 2019-03-11 | 6:14 |  |  |  | 0 | 0 | 0 | 0.40833 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-11 | 19:39 | 2019-03-12 | 5:36 |  |  |  | 0 | 0 | 0 | 0.41458 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=423KV
[6 empty] | 2019-03-14 | 20:09 | 2019-03-15 | 5:26 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-15 | 21:36 | 2019-03-16 | 5:42 |  |  |  | 0 | 0 | 0 | 0.3375 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-17 | 19:58 | 2019-03-18 | 5:49 |  |  |  | 0 | 0 | 0 | 0.41042 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-18 | 9:21 | 2019-03-18 | 20:06 |  |  |  | 0.44792 | 0 | 0 | 0 |  |  |  | SD Taken for AMP works.
[6 empty] | 2019-03-19 | 21:14 | 2019-03-20 | 5:42 |  |  |  | 0 | 0 | 0 | 0.35278 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=425KV
[6 empty] | 2019-03-27 | 20:14 | 2019-03-28 | 9:05 |  |  |  | 0 | 0 | 0 | 0.53542 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=420KV
[6 empty] | 2019-03-28 | 20:07 | 2019-03-29 | 6:15 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=418KV
[6 empty] | Sub Total --> | [6 empty] | 0.44792 | 0 | 0 | 1900-01-04 02:09 | [5 empty] | 98.56
57 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
58 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
59 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
60 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
61 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 | -- | 2019-03-30 | 15:14 | 2019-03-30 | 16:36 | -- | -- | -- | 0 | 0.056944 | 0 | 0 | N/A | N/A | N/A | line tripped from NHPC, URI-2 due to CB problem at their end.
[6 empty] | 2019-03-30 | 16:36 | 2019-03-30 | 18:49 |  |  |  | 0 | 0 | 0 | 0.092361 |  |  |  | SD taken by NHPC, URI-2 after tripping to rectify CB problem at their end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.056944 | 0 | 0.092361 | [5 empty] | 100
62 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 7:30 | -- | -- | -- | 0 | 0 | 0 | 0.3125 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-01 | 20:05 | 2019-03-05 | 6:43 |  |  |  | 0 | 0 | 0 | 1900-01-02 10:38 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-05 | 13:17 | 2019-03-06 | 7:50 |  |  |  | 0 | 0 | 0 | 0.77292 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=429KV
[6 empty] | 2019-03-06 | 19:55 | 2019-03-07 | 7:20 |  |  |  | 0 | 0 | 0 | 0.47569 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=424KV
[6 empty] | 2019-03-07 | 19:55 | 2019-03-08 | 7:16 |  |  |  | 0 | 0 | 0 | 0.47292 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=424KV
[6 empty] | 2019-03-08 | 19:45 | 2019-03-09 | 7:49 |  |  |  | 0 | 0 | 0 | 0.50278 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-09 | 20:21 | 2019-03-11 | 6:28 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:07 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-11 | 19:45 | 2019-03-12 | 17:27 |  |  |  | 0 | 0 | 0 | 0.90417 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=423KV
[6 empty] | 2019-03-12 | 20:25 | 2019-03-13 | 6:28 |  |  |  | 0 | 0 | 0 | 0.41875 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=431KV
[6 empty] | 2019-03-13 | 20:15 | 2019-03-14 | 6:56 |  |  |  | 0 | 0 | 0 | 0.44514 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=430KV
[6 empty] | 2019-03-14 | 20:13 | 2019-03-17 | 7:41 |  |  |  | 0 | 0 | 0 | 1900-01-01 11:28 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-17 | 19:55 | 2019-03-18 | 7:34 |  |  |  | 0 | 0 | 0 | 0.48542 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-18 | 20:53 | 2019-03-19 | 6:14 |  |  |  | 0 | 0 | 0 | 0.38958 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-19 | 21:15 | 2019-03-22 | 6:36 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:21 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=425KV
[6 empty] | 2019-03-22 | 20:53 | 2019-03-25 | 7:35 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:42 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-25 | 20:04 | 2019-04-01 | 0:00 |  |  |  | 0 | 0 | 0 | 1900-01-05 03:56 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=425KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-22 12:31 | [5 empty] | 100
63 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 | -- | 2019-03-12 | 9:07 | 2019-03-12 | 19:33 | -- | -- | -- | 0 | 0 | 0 | 0.43472 | N/A | N/A | N/A | SD Taken by NTPC, Koldam for CVT replacement.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.43472 | [5 empty] | 100
64 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 | -- | 2019-03-29 | 9:19 | 2019-03-29 | 17:50 | -- | -- | -- | 0.35486 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for AMP work.
[6 empty] | Sub Total --> | [6 empty] | 0.35486 | 0 | 0 | 0 | [5 empty] | 98.86
65 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 | -- | 2019-03-30 | 9:19 | 2019-03-30 | 17:47 | -- | -- | -- | 0.35278 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for AMP work.
[6 empty] | Sub Total --> | [6 empty] | 0.35278 | 0 | 0 | 0 | [5 empty] | 98.86
66 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 | -- | 2019-03-01 | 20:48 | 2019-03-02 | 5:39 | -- | -- | -- | 0 | 0 | 0 | 0.36875 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Panchkula=423KV.
[6 empty] | 2019-03-03 | 20:08 | 2019-03-04 | 5:35 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | Line hand tripped for voltage regulation. Panchkula=422KV
[6 empty] | 2019-03-05 | 19:58 | 2019-03-06 | 5:22 |  |  |  | 0 | 0 | 0 | 0.39167 |  |  |  | Line hand tripped for voltage regulation. Panchkula=424KV
[6 empty] | 2019-03-07 | 19:53 | 2019-03-08 | 5:36 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  | Line hand tripped for voltage regulation. Panchkula=423KV
[6 empty] | 2019-03-11 | 20:35 | 2019-03-12 | 5:34 |  |  |  | 0 | 0 | 0 | 0.37431 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421KV
[6 empty] | 2019-03-13 | 19:40 | 2019-03-14 | 5:09 |  |  |  | 0 | 0 | 0 | 0.39514 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421KV
[6 empty] | 2019-03-15 | 20:07 | 2019-03-16 | 5:09 |  |  |  | 0 | 0 | 0 | 0.37639 |  |  |  | Line hand tripped for voltage regulation. Panchkula=420KV
[6 empty] | 2019-03-17 | 20:56 | 2019-03-18 | 5:31 |  |  |  | 0 | 0 | 0 | 0.35764 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421KV
[6 empty] | 2019-03-20 | 19:57 | 2019-03-21 | 5:36 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | Line hand tripped for voltage regulation. Panchkula=422KV
[6 empty] | 2019-03-22 | 20:19 | 2019-03-23 | 5:26 |  |  |  | 0 | 0 | 0 | 0.37986 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421KV
[6 empty] | 2019-03-24 | 20:14 | 2019-03-25 | 5:28 |  |  |  | 0 | 0 | 0 | 0.38472 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421KV
[6 empty] | 2019-03-26 | 23:26 | 2019-03-27 | 5:31 |  |  |  | 0 | 0 | 0 | 0.25347 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421V
[6 empty] | 2019-03-28 | 20:19 | 2019-03-29 | 5:03 |  |  |  | 0 | 0 | 0 | 0.36389 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421V
[6 empty] | 2019-03-30 | 22:42 | 2019-03-31 | 5:34 |  |  |  | 0 | 0 | 0 | 0.28611 |  |  |  | Line hand tripped for voltage regulation. Panchkula=422V
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-04 03:11 | [5 empty] | 100
67 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 5:12 | -- | -- | -- | 0 | 0 | 0 | 0.21667 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Panchkula=424KV.
[6 empty] | 2019-03-02 | 20:27 | 2019-03-03 | 5:45 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | Line hand tripped for voltage regulation. Panchkula=422KV.
[6 empty] | 2019-03-04 | 19:55 | 2019-03-05 | 5:27 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | Line hand tripped for voltage regulation. Panchkula=422KV
[6 empty] | 2019-03-06 | 19:50 | 2019-03-07 | 5:22 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | Line hand tripped for voltage regulation. Panchkula=423KV
[6 empty] | 2019-03-08 | 19:50 | 2019-03-09 | 5:25 |  |  |  | 0 | 0 | 0 | 0.39931 |  |  |  | Line hand tripped for voltage regulation. Panchkula=428KV
[6 empty] | 2019-03-09 | 20:32 | 2019-03-10 | 4:59 |  |  |  | 0 | 0 | 0 | 0.35208 |  |  |  | Line hand tripped for voltage regulation. Panchkula=423KV
[6 empty] | 2019-03-10 | 19:53 | 2019-03-11 | 5:23 |  |  |  | 0 | 0 | 0 | 0.39583 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421KV
[6 empty] | 2019-03-12 | 20:08 | 2019-03-13 | 5:29 |  |  |  | 0 | 0 | 0 | 0.38958 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421KV
[6 empty] | 2019-03-14 | 19:44 | 2019-03-15 | 5:29 |  |  |  | 0 | 0 | 0 | 0.40625 |  |  |  | Line hand tripped for voltage regulation. Panchkula=420KV
[6 empty] | 2019-03-16 | 21:02 | 2019-03-17 | 5:22 |  |  |  | 0 | 0 | 0 | 0.34722 |  |  |  | Line hand tripped for voltage regulation. Panchkula=420KV
[6 empty] | 2019-03-18 | 20:03 | 2019-03-19 | 5:41 |  |  |  | 0 | 0 | 0 | 0.40139 |  |  |  | Line hand tripped for voltage regulation. Panchkula=424KV
[6 empty] | 2019-03-19 | 19:51 | 2019-03-20 | 5:40 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | Line hand tripped for voltage regulation. Panchkula=422KV
[6 empty] | 2019-03-21 | 20:16 | 2019-03-22 | 5:32 |  |  |  | 0 | 0 | 0 | 0.38611 |  |  |  | Line hand tripped for voltage regulation. Panchkula=423KV
[6 empty] | 2019-03-23 | 20:05 | 2019-03-24 | 5:18 |  |  |  | 0 | 0 | 0 | 0.38403 |  |  |  | Line hand tripped for voltage regulation. Panchkula=420KV
[6 empty] | 2019-03-25 | 20:23 | 2019-03-26 | 5:41 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | Line hand tripped for voltage regulation. Panchkula=422V
[6 empty] | 2019-03-27 | 20:18 | 2019-03-28 | 4:48 |  |  |  | 0 | 0 | 0 | 0.35417 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421V
[6 empty] | 2019-03-29 | 20:32 | 2019-03-30 | 5:26 |  |  |  | 0 | 0 | 0 | 0.37083 |  |  |  | Line hand tripped for voltage regulation. Panchkula=421V
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-05 09:10 | [5 empty] | 100
68 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 6:25 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | 2019-03-02 | 20:26 | 2019-03-03 | 6:47
[6 empty] | 2019-03-03 | 21:19 | 2019-03-04 | 5:44
[6 empty] | 2019-03-04 | 22:00 | 2019-03-05 | 7:25
[6 empty] | 2019-03-05 | 21:46 | 2019-03-06 | 6:23
[6 empty] | 2019-03-14 | 2:16 | 2019-03-14 | 9:04
[6 empty] | 2019-03-14 | 12:59 | 2019-03-14 | 13:07
[6 empty] | 2019-03-14 | 13:07 | 2019-03-14 | 14:44
[6 empty] | 2019-03-14 | 22:00 | 2019-03-15 | 11:44
[6 empty] | 2019-03-15 | 21:07 | 2019-03-16 | 6:47
[6 empty] | 2019-03-18 | 20:40 | 2019-03-19 | 5:51
[6 empty] | 2019-03-20 | 3:43 | 2019-03-20 | 6:35
[6 empty] | 2019-03-20 | 20:35 | 2019-03-21 | 7:48
[6 empty] | 2019-03-21 | 21:04 | 2019-03-23 | 6:30
[6 empty] | 2019-03-24 | 4:00 | 2019-03-24 | 6:41
[6 empty] | 2019-03-24 | 23:47 | 2019-03-25 | 7:36
[6 empty] | 2019-03-26 | 2:57 | 2019-03-26 | 9:58
[6 empty] | 2019-03-28 | 3:08 | 2019-03-28 | 9:29
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
69 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
70 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 | -- | 2019-03-17 | 19:57 | 2019-03-18 | 8:47 | -- | -- | -- | 0 | 0 | 0 | 0.53472 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Jalandher=427KV
[6 empty] | 2019-03-28 | 9:06 | 2019-03-28 | 21:40 |  |  |  | 0.52361 | 0 | 0 | 0 |  |  |  | SD taken for AMP work
[6 empty] | Sub Total --> | [6 empty] | 0.52361 | 0 | 0 | 0.53472 | [5 empty] | 98.31
71 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 7:19 | -- | -- | -- | 0 | 0 | 0 | 0.30486 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Jalandhar=423KV
[6 empty] | 2019-03-01 | 21:36 | 2019-03-03 | 5:37 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:01 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | 2019-03-03 | 14:23 | 2019-03-04 | 5:35 |  |  |  | 0 | 0 | 0 | 0.63333 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | 2019-03-04 | 20:33 | 2019-03-05 | 6:33 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-05 | 13:13 | 2019-03-06 | 7:48 |  |  |  | 0 | 0 | 0 | 0.77431 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-06 | 19:56 | 2019-03-07 | 7:19 |  |  |  | 0 | 0 | 0 | 0.47431 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=426KV
[6 empty] | 2019-03-07 | 19:53 | 2019-03-08 | 7:12 |  |  |  | 0 | 0 | 0 | 0.47153 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=426KV
[6 empty] | 2019-03-08 | 19:47 | 2019-03-09 | 7:44 |  |  |  | 0 | 0 | 0 | 0.49792 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=428KV
[6 empty] | 2019-03-09 | 20:16 | 2019-03-11 | 5:30 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:14 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=426KV
[6 empty] | 2019-03-11 | 19:38 | 2019-03-12 | 5:42 |  |  |  | 0 | 0 | 0 | 0.41944 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=422KV
[6 empty] | 2019-03-12 | 20:11 | 2019-03-13 | 6:20 |  |  |  | 0 | 0 | 0 | 0.42292 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=431KV
[6 empty] | 2019-03-13 | 20:09 | 2019-03-14 | 5:48 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-14 | 13:28 | 2019-03-17 | 7:26 |  |  |  | 0 | 0 | 0 | 1900-01-01 17:58 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-19 | 21:11 | 2019-03-20 | 5:40 |  |  |  | 0 | 0 | 0 | 0.35347 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=426KV
[6 empty] | 2019-03-20 | 19:59 | 2019-03-21 | 6:32 |  |  |  | 0 | 0 | 0 | 0.43958 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=429KV
[6 empty] | 2019-03-21 | 20:11 | 2019-03-22 | 6:31 |  |  |  | 0 | 0 | 0 | 0.43056 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=422KV
[6 empty] | 2019-03-22 | 20:51 | 2019-03-24 | 6:39 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:48 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=424KV
[6 empty] | 2019-03-24 | 23:50 | 2019-03-25 | 7:25 |  |  |  | 0 | 0 | 0 | 0.31597 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=428KV
[6 empty] | 2019-03-26 | 21:37 | 2019-03-27 | 6:44 |  |  |  | 0 | 0 | 0 | 0.37986 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | 2019-03-28 | 0:42 | 2019-03-28 | 5:50 |  |  |  | 0 | 0 | 0 | 0.21389 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | 2019-03-29 | 1:42 | 2019-03-29 | 5:57 |  |  |  | 0 | 0 | 0 | 0.17708 |  |  |  | Line hand tripped for voltage regulation. Jalandhar=425KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-13 00:05 | [5 empty] | 100
72 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
73 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
74 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 7:29 | -- | -- | -- | 0 | 0 | 0 | 0.31181 | N/A | N/A | N/A | Line hand tripped for voltage regulation.Amritsar=425KV
[6 empty] | 2019-03-01 | 20:06 | 2019-03-05 | 6:41 |  |  |  | 0 | 0 | 0 | 1900-01-02 10:35 |  |  |  | Line hand tripped for voltage regulation.Amritsar=425KV
[6 empty] | 2019-03-05 | 13:17 | 2019-03-06 | 7:50 |  |  |  | 0 | 0 | 0 | 0.77292 |  |  |  | Line hand tripped for voltage regulation.Amritsar=427KV
[6 empty] | 2019-03-06 | 19:58 | 2019-03-07 | 7:19 |  |  |  | 0 | 0 | 0 | 0.47292 |  |  |  | Line hand tripped for voltage regulation.Amritsar=4273V
[6 empty] | 2019-03-07 | 19:58 | 2019-03-08 | 7:16 |  |  |  | 0 | 0 | 0 | 0.47083 |  |  |  | Line hand tripped for voltage regulation.Amritsar=4273V
[6 empty] | 2019-03-08 | 19:46 | 2019-03-09 | 7:48 |  |  |  | 0 | 0 | 0 | 0.50139 |  |  |  | Line hand tripped for voltage regulation.Amritsar=427V
[6 empty] | 2019-03-09 | 20:20 | 2019-03-11 | 6:28 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:08 |  |  |  | Line hand tripped for voltage regulation.Amritsar=425V
[6 empty] | 2019-03-11 | 19:45 | 2019-03-13 | 6:29 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:44 |  |  |  | Line hand tripped for voltage regulation.Amritsar=421V
[6 empty] | 2019-03-13 | 20:15 | 2019-03-14 | 6:58 |  |  |  | 0 | 0 | 0 | 0.44653 |  |  |  | Line hand tripped for voltage regulation.Amritsar=422V
[6 empty] | 2019-03-14 | 20:13 | 2019-03-17 | 7:41 |  |  |  | 0 | 0 | 0 | 1900-01-01 11:28 |  |  |  | Line hand tripped for voltage regulation.Amritsar=423V
[6 empty] | 2019-03-17 | 19:56 | 2019-03-18 | 7:36 |  |  |  | 0 | 0 | 0 | 0.48611 |  |  |  | Line hand tripped for voltage regulation.Amritsar=424V
[6 empty] | 2019-03-18 | 20:53 | 2019-03-19 | 6:13 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | Line hand tripped for voltage regulation.Amritsar=423KV
[6 empty] | 2019-03-19 | 21:17 | 2019-03-22 | 6:35 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:18 |  |  |  | Line hand tripped for voltage regulation.Amritsar=421V
[6 empty] | 2019-03-22 | 20:56 | 2019-03-25 | 7:35 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:39 |  |  |  | Line hand tripped for voltage regulation.Amritsar=422V
[6 empty] | 2019-03-25 | 20:04 | 2019-03-26 | 9:05 |  |  |  | 0 | 0 | 0 | 0.54236 |  |  |  | Line hand tripped for voltage regulation.Amritsar=422V
[6 empty] | 2019-03-26 | 9:05 | 2019-03-26 | 19:20 |  |  |  | 0.42708 | 0 | 0 | 0 |  |  |  | SD taken for AMP work
[6 empty] | 2019-03-26 | 21:43 | 2019-04-01 | 0:00 |  |  |  | 0 | 0 | 0 | 1900-01-04 02:17 |  |  |  | Line hand tripped for voltage regulation.Amritsar=422V
[6 empty] | Sub Total --> | [6 empty] | 0.42708 | 0 | 0 | 1900-01-22 02:36 | [5 empty] | 98.62
75 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
76 | NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
77 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
78 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 | -- | 2019-03-02 | 14:33 | 2019-03-03 | 14:09 | -- | -- | -- | 0 | 0 | 0.98333 | 0 | N/A | N/A | N/A | Line tripped on Y-N fault caused by heavy snow fall and avlanche. FLR Kishanpur : 100.2kM, 2.99kA. & N.Wanpoh : 40.2kM , 3.3kA.
[6 empty] | 2019-03-04 | 3:54 | 2019-03-04 | 3:54 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault. FLR New Wanpoh : 22.7 Km , 3.7kA & Kishanpur:-107.2Km , 3.186 KA
[6 empty] | 2019-03-04 | 5:23 | 2019-03-04 | 11:24 |  |  |  | 0 | 0 | 0.25069 | 0 |  |  |  | Line tripped on Y-N fault caused by heavy snow fall and avlanche. FLR Kishanpur : 97.723kM, 3.37kA. & N.Wanpoh :32.67kM ,4.239kA.
[6 empty] | 2019-03-05 | 12:57 | 2019-03-06 | 15:25 |  |  |  | 0 | 0 | 1899-12-31 02:28 | 0 |  |  |  | Line tripped on Y-N fault caused by heavy snow fall and avlanche. FLR Kishanpur : 103.4kM, 3.2kA. & N.Wanpoh :26.2kM , 3.9kA.
[6 empty] | 2019-03-09 | 14:36 | 2019-03-09 | 16:14 |  |  |  | 0.068056 | 0 | 0 | 0 |  |  |  | SD taken to rectify Y-PH broken strand at Loc No 14-15.
[6 empty] | 2019-03-29 | 15:18 | 2019-03-29 | 17:03 |  |  |  | 0.072917 | 0 | 0 | 0 |  |  |  | SD taken for loping of trees in span 239-240.
[6 empty] | Sub Total --> | [6 empty] | 0.14097 | 0 | 1900-01-01 08:05 | 0 | [5 empty] | 99.51
79 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 | -- | 2019-03-11 | 11:10 | 2019-03-11 | 12:36 | -- | -- | -- | 0.059722 | 0 | 0 | 0 | N/A | N/A | N/A | Line tripped on Y-N fault caused by heavy snow fall and avlanche. FLR Kishenpur : 78.45kM , 3.964kA & Wanpoh : 44.16kM , 5.7kA.
[6 empty] | Sub Total --> | [6 empty] | 0.059722 | 0 | 0 | 0 | [5 empty] | 99.81
80 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 | -- | 2019-03-09 | 9:17 | 2019-03-09 | 19:25 | -- | -- | -- | 0.42222 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for AMP works.
[6 empty] | Sub Total --> | [6 empty] | 0.42222 | 0 | 0 | 0 | [5 empty] | 98.64
81 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 | -- | 2019-03-17 | 8:54 | 2019-03-19 | 16:31 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 07:37 | N/A | N/A | N/A | SD taken by SJVNL for HV testing in GIS at their end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-01 07:37 | [5 empty] | 100
82 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 | -- | 2019-03-01 | 21:50 | 2019-03-02 | 5:55 | -- | -- | -- | 0 | 0 | 0 | 0.33681 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-02 | 21:16 | 2019-03-03 | 5:35 |  |  |  | 0 | 0 | 0 | 0.34653 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-06 | 23:36 | 2019-03-07 | 5:36 |  |  |  | 0 | 0 | 0 | 0.25 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=428KV
[6 empty] | 2019-03-07 | 23:37 | 2019-03-08 | 5:50 |  |  |  | 0 | 0 | 0 | 0.25903 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=425KV
[6 empty] | 2019-03-08 | 21:40 | 2019-03-09 | 5:54 |  |  |  | 0 | 0 | 0 | 0.34306 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-10 | 21:21 | 2019-03-11 | 5:24 |  |  |  | 0 | 0 | 0 | 0.33542 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-11 | 21:05 | 2019-03-12 | 5:39 |  |  |  | 0 | 0 | 0 | 0.35694 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-14 | 13:33 | 2019-03-14 | 17:22 |  |  |  | 0 | 0 | 0 | 0.15903 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=430KV
[6 empty] | 2019-03-15 | 8:27 | 2019-03-18 | 18:14 |  |  |  | 0 | 0 | 0 | 1900-01-02 09:47 |  |  |  | SD taken by SJVNL for HV testing in GIS at their end.
[6 empty] | 2019-03-20 | 21:38 | 2019-03-21 | 6:02 |  |  |  | 0 | 0 | 0 | 0.35 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-21 | 21:12 | 2019-03-22 | 5:32 |  |  |  | 0 | 0 | 0 | 0.34722 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-24 | 23:52 | 2019-03-25 | 5:54 |  |  |  | 0 | 0 | 0 | 0.25139 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-27 | 20:16 | 2019-03-28 | 4:53 |  |  |  | 0 | 0 | 0 | 0.35903 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=420KV
[6 empty] | 2019-03-28 | 20:18 | 2019-03-29 | 6:00 |  |  |  | 0 | 0 | 0 | 0.40417 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=420KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-06 12:09 | [5 empty] | 100
83 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 | -- | 2019-03-14 | 13:00 | 2019-03-14 | 13:05 | -- | -- | -- | 0 | 0.0034722 | 0 | 0 | N/A | N/A | N/A | Line tripped due to DT receipt from NTPC Koldam. Over Voltage protection is reported to have operated at Koldam.
[6 empty] | 2019-03-14 | 13:05 | 2019-03-14 | 16:23 |  |  |  | 0 | 0 | 0 | 0.1375 |  |  |  | Line kept open after tripped due to system over voltage.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.0034722 | 0 | 0.1375 | [5 empty] | 100
84 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 | -- | 2019-03-17 | 8:58 | 2019-03-17 | 16:15 | -- | -- | -- | 0 | 0 | 0 | 0.30347 | N/A | N/A | N/A | SD taken by SJVNL for HV testing in GIS at their end.
[6 empty] | 2019-03-18 | 9:20 | 2019-03-18 | 16:30 |  |  |  | 0 | 0 | 0 | 0.29861 |  |  |  | SD taken by SJVNL for HV testing in GIS at their end.
[6 empty] | 2019-03-19 | 9:21 | 2019-03-19 | 16:21 |  |  |  | 0 | 0 | 0 | 0.29167 |  |  |  | SD taken by SJVNL for HV testing in GIS at their end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.89375 | [5 empty] | 100
85 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 5:34 | -- | -- | -- | 0 | 0 | 0 | 0.23194 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-04 | 20:37 | 2019-03-05 | 5:30 |  |  |  | 0 | 0 | 0 | 0.37014 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=430KV
[6 empty] | 2019-03-05 | 21:59 | 2019-03-06 | 5:33 |  |  |  | 0 | 0 | 0 | 0.31528 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-09 | 21:37 | 2019-03-10 | 5:49 |  |  |  | 0 | 0 | 0 | 0.34167 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=425KV
[6 empty] | 2019-03-12 | 21:46 | 2019-03-13 | 5:37 |  |  |  | 0 | 0 | 0 | 0.32708 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=427KV
[6 empty] | 2019-03-13 | 20:13 | 2019-03-14 | 5:12 |  |  |  | 0 | 0 | 0 | 0.37431 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=434KV
[6 empty] | 2019-03-14 | 21:25 | 2019-03-14 | 21:25 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on R-N Fault. FLR Nalagarh :- 83.4 KM, 4.3 kA.
[6 empty] | 2019-03-14 | 21:29 | 2019-03-15 | 5:38 |  |  |  | 0 | 0 | 0 | 0.33958 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=426KV
[6 empty] | 2019-03-18 | 9:26 | 2019-03-18 | 16:57 |  |  |  | 0 | 0 | 0 | 0.31319 |  |  |  | SD taken by SJVNL for HV testing in GIS at their end.
[6 empty] | 2019-03-27 | 22:55 | 2019-03-28 | 6:17 |  |  |  | 0 | 0 | 0 | 0.30694 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=420KV
[6 empty] | 2019-03-28 | 23:00 | 2019-03-29 | 5:03 |  |  |  | 0 | 0 | 0 | 0.25208 |  |  |  | Line hand tripped for voltage regulation. Nalagarh=420KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-02 04:08 | [5 empty] | 100
86 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
87 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 | -- | 2019-03-23 | 16:17 | 2019-03-23 | 17:07 | -- | -- | -- | 0.034722 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for rectification of I string (pilot string) of R Ph at gantry of Panchkula S/stn
[6 empty] | Sub Total --> | [6 empty] | 0.034722 | 0 | 0 | 0 | [5 empty] | 99.89
88 | NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
89 | NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
90 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 | -- | 2019-03-28 | 9:44 | 2019-03-28 | 18:33 | -- | -- | -- | 0.36736 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for AMP work.
[6 empty] | Sub Total --> | [6 empty] | 0.36736 | 0 | 0 | 0 | [5 empty] | 98.81
91 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 | -- | 2019-03-26 | 9:29 | 2019-03-26 | 19:02 | -- | -- | -- | 0.39792 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for AMP work
[6 empty] | Sub Total --> | [6 empty] | 0.39792 | 0 | 0 | 0 | [5 empty] | 98.72
92 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 | -- | 2019-03-01 | 20:09 | 2019-03-02 | 6:46 | -- | -- | -- | 0 | 0 | 0 | 0.44236 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-03 | 14:52 | 2019-03-04 | 6:13 |  |  |  | 0 | 0 | 0 | 0.63958 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=430KV
[6 empty] | 2019-03-04 | 20:40 | 2019-03-05 | 6:39 |  |  |  | 0 | 0 | 0 | 0.41597 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=430KV
[6 empty] | 2019-03-08 | 20:48 | 2019-03-09 | 6:50 |  |  |  | 0 | 0 | 0 | 0.41806 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=423KV
[6 empty] | 2019-03-10 | 21:22 | 2019-03-11 | 5:58 |  |  |  | 0 | 0 | 0 | 0.35833 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=425KV
[6 empty] | 2019-03-11 | 19:41 | 2019-03-12 | 6:11 |  |  |  | 0 | 0 | 0 | 0.4375 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=421KV
[6 empty] | 2019-03-14 | 20:22 | 2019-03-15 | 7:03 |  |  |  | 0 | 0 | 0 | 0.44514 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-18 | 21:25 | 2019-03-19 | 6:57 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=421KV
[6 empty] | 2019-03-19 | 21:43 | 2019-03-20 | 6:14 |  |  |  | 0 | 0 | 0 | 0.35486 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=422KV
[6 empty] | 2019-03-20 | 20:32 | 2019-03-21 | 6:47 |  |  |  | 0 | 0 | 0 | 0.42708 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=432KV
[6 empty] | 2019-03-22 | 21:19 | 2019-03-23 | 6:36 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=432KV
[6 empty] | 2019-03-25 | 13:28 | 2019-03-26 | 6:52 |  |  |  | 0 | 0 | 0 | 0.725 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=432KV
[6 empty] | 2019-03-28 | 0:47 | 2019-03-28 | 5:58 |  |  |  | 0 | 0 | 0 | 0.21597 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=426KV
[6 empty] | 2019-03-29 | 1:53 | 2019-03-29 | 6:09 |  |  |  | 0 | 0 | 0 | 0.17778 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=425KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-04 20:12 | [5 empty] | 100
93 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 6:34 | -- | -- | -- | 0 | 0 | 0 | 0.27361 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-02 | 13:17 | 2019-03-03 | 6:53 |  |  |  | 0 | 0 | 0 | 0.73333 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-05 | 20:27 | 2019-03-06 | 6:50 |  |  |  | 0 | 0 | 0 | 0.43264 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-06 | 20:05 | 2019-03-07 | 6:30 |  |  |  | 0 | 0 | 0 | 0.43403 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-07 | 20:02 | 2019-03-08 | 6:56 |  |  |  | 0 | 0 | 0 | 0.45417 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-12 | 21:49 | 2019-03-13 | 10:48 |  |  |  | 0 | 0 | 0 | 0.54097 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=423KV
[6 empty] | 2019-03-13 | 20:18 | 2019-03-14 | 6:00 |  |  |  | 0 | 0 | 0 | 0.40417 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-21 | 20:17 | 2019-03-22 | 6:39 |  |  |  | 0 | 0 | 0 | 0.43194 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=430KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-02 16:55 | [5 empty] | 100
94 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-05 | 7:31 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 07:31 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-05 | 13:11 | 2019-03-14 | 9:08 |  |  |  | 0 | 0 | 0 | 1900-01-07 19:57 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-14 | 20:12 | 2019-03-20 | 9:49 |  |  |  | 0 | 0 | 0 | 1900-01-04 13:37 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-20 | 20:30 | 2019-04-01 | 0:00 |  |  |  | 0 | 0 | 0 | 1900-01-10 03:30 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=432KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-03 07:31 | [5 empty] | 100
95 | NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
96 | NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 6:36 | -- | -- | -- | 0 | 0 | 0 | 0.275 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-01 | 20:07 | 2019-03-02 | 6:28 |  |  |  | 0 | 0 | 0 | 0.43125 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-02 | 13:07 | 2019-03-04 | 5:56 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:49 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-04 | 14:06 | 2019-03-05 | 6:30 |  |  |  | 0 | 0 | 0 | 0.68333 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=432KV
[6 empty] | 2019-03-05 | 13:25 | 2019-03-07 | 6:23 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:58 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-07 | 20:00 | 2019-03-08 | 6:32 |  |  |  | 0 | 0 | 0 | 0.43889 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-08 | 19:44 | 2019-03-09 | 6:36 |  |  |  | 0 | 0 | 0 | 0.45278 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-09 | 20:17 | 2019-03-11 | 5:48 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:31 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=424KV
[6 empty] | 2019-03-11 | 15:11 | 2019-03-16 | 6:41 |  |  |  | 0 | 0 | 0 | 1900-01-03 15:30 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=431KV
[6 empty] | 2019-03-16 | 21:00 | 2019-03-17 | 7:43 |  |  |  | 0 | 0 | 0 | 0.44653 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=424KV
[6 empty] | 2019-03-17 | 19:55 | 2019-03-18 | 6:35 |  |  |  | 0 | 0 | 0 | 0.44444 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=425KV
[6 empty] | 2019-03-18 | 20:01 | 2019-03-19 | 6:19 |  |  |  | 0 | 0 | 0 | 0.42917 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-19 | 21:16 | 2019-03-20 | 6:09 |  |  |  | 0 | 0 | 0 | 0.37014 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=422KV
[6 empty] | 2019-03-20 | 20:01 | 2019-03-24 | 6:31 |  |  |  | 0 | 0 | 0 | 1900-01-02 10:30 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-24 | 13:11 | 2019-03-25 | 5:59 |  |  |  | 0 | 0 | 0 | 0.7 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-25 | 20:30 | 2019-03-26 | 6:19 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=426KV
[6 empty] | 2019-03-26 | 21:40 | 2019-03-28 | 5:51 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:11 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=426KV
[6 empty] | 2019-03-28 | 20:47 | 2019-03-30 | 6:18 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:31 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=425KV
[6 empty] | 2019-03-30 | 20:33 | 2019-04-01 | 0:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:27 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-20 20:23 | [5 empty] | 100
97 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
98 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
99 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 | -- | 2019-03-03 | 3:10 | 2019-03-05 | 7:28 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 04:18 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Panchkula=430KV.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-01 04:18 | [5 empty] | 100
100 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
101 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 | -- | 2019-03-02 | 21:13 | 2019-03-03 | 6:27 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Patiala=426KV
[6 empty] | 2019-03-03 | 21:12 | 2019-03-04 | 6:39 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | Line hand tripped for voltage regulation. Patiala=423KV
[6 empty] | 2019-03-04 | 21:52 | 2019-03-05 | 8:04 |  |  |  | 0 | 0 | 0 | 0.425 |  |  |  | Line hand tripped for voltage regulation. Patiala=426KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1899-12-31 04:53 | [5 empty] | 100
102 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 | -- | 2019-03-05 | 22:16 | 2019-03-06 | 6:30 | -- | -- | -- | 0 | 0 | 0 | 0.34306 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Patiala=425KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.34306 | [5 empty] | 100
103 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 | -- | 2019-03-02 | 21:14 | 2019-03-03 | 6:28 | -- | -- | -- | 0 | 0 | 0 | 0.38472 | N/A | N/A | N/A | Line hand tripped for voltage regulation. kaithal=425KV
[6 empty] | 2019-03-03 | 21:13 | 2019-03-04 | 6:40 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | Line hand tripped for voltage regulation. kaithal=427KV
[6 empty] | 2019-03-04 | 21:50 | 2019-03-05 | 8:02 |  |  |  | 0 | 0 | 0 | 0.425 |  |  |  | Line hand tripped for voltage regulation. kaithal=425KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1899-12-31 04:53 | [5 empty] | 100
104 | NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 | -- | 2019-03-05 | 22:15 | 2019-03-06 | 6:32 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Kaithal=425KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.34514 | [5 empty] | 100
105 | NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 | -- | 2019-03-09 | 11:50 | 2019-03-09 | 16:18 | -- | -- | -- | 0 | 0 | 0 | 0.18611 | N/A | N/A | N/A | SD taken by BBMB for attending hotspot in line at tower no. 301,302,306 &340.
[6 empty] | 2019-03-13 | 12:53 | 2019-03-13 | 17:04 |  |  |  | 0.17431 | 0 | 0 | 0 |  |  |  | SD taken for replacement of damaged long rod polymer insulator of bottom phase (B- Ph) at Loc. no. 43.
[6 empty] | Sub Total --> | [6 empty] | 0.17431 | 0 | 0 | 0.18611 | [5 empty] | 99.44
106 | NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 9:49 | -- | -- | -- | 0 | 0 | 0 | 0.40903 | N/A | N/A | N/A | Line hand tripped for voltage regulation.
[6 empty] | 2019-03-02 | 23:15 | 2019-03-04 | 10:48 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:33 |  |  |  | Line hand tripped for voltage regulation.
[6 empty] | 2019-03-04 | 21:01 | 2019-03-06 | 11:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 14:26 |  |  |  | Line hand tripped for voltage regulation.
[6 empty] | 2019-03-07 | 2:20 | 2019-03-08 | 10:41 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:21 |  |  |  | Line hand tripped for voltage regulation.
[6 empty] | 2019-03-14 | 21:19 | 2019-03-18 | 8:52 |  |  |  | 0 | 0 | 0 | 1900-01-02 11:33 |  |  |  | Line hand tripped for voltage regulation.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-07 07:42 | [5 empty] | 100
107 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 | -- | 2019-03-27 | 9:16 | 2019-03-27 | 20:52 | -- | -- | -- | 0.48333 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for AMP work
[6 empty] | Sub Total --> | [6 empty] | 0.48333 | 0 | 0 | 0 | [5 empty] | 98.44
108 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 | -- | 2019-03-25 | 9:18 | 2019-03-25 | 20:03 | -- | -- | -- | 0.44792 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for AMP works.
[6 empty] | Sub Total --> | [6 empty] | 0.44792 | 0 | 0 | 0 | [5 empty] | 98.56
109 | NR240116 | 400KV Dadri-Kaithal | 213 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
110 | NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 | -- | 2019-03-08 | 17:49 | 2019-03-08 | 18:22 | -- | -- | -- | 0 | 0 | 0 | 0.022917 | N/A | N/A | N/A | SD taken by NTPC, Dadri for first time charging of 400KV Bus-4 section at Dadri.
[6 empty] | 2019-03-17 | 2:07 | 2019-03-17 | 2:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault. FLR Kaithal: 210.4KM, 1.812kA & Dadri: 0.77kms.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.022917 | [5 empty] | 100
111 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
112 | NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
113 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
114 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-10 | 18:23 | -- | -- | -- | 0 | 0 | 1900-01-08 18:23 | 0 | N/A | N/A | N/A | Line tripped on B-N fault caused by heavy snow fall and avlanche. FLR Kishanpur : 96.8kM, 3.6kA. & N.Wanpoh : 33.8kM , 5.1kA.
[6 empty] | 2019-03-11 | 10:58 | 2019-03-11 | 10:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on B-N fault. FLR Kishenpur : 67.1kM , 4.4kA & Wanpoh : 65.74kM , 3.4kA.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1900-01-08 18:23 | 0 | [5 empty] | 100
115 | NR240122 | 400KV KURUKSHETRA - JIND - I | 103.6 | NR2 | -- | 2019-03-01 | 20:10 | 2019-03-02 | 6:22 | -- | -- | -- | 0 | 0 | 0 | 0.425 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-11 | 19:45 | 2019-03-12 | 5:40 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=421KV
[6 empty] | 2019-03-14 | 20:19 | 2019-03-15 | 6:54 |  |  |  | 0 | 0 | 0 | 0.44097 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-16 | 21:02 | 2019-03-17 | 7:56 |  |  |  | 0 | 0 | 0 | 0.45417 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=424KV
[6 empty] | 2019-03-22 | 21:22 | 2019-03-23 | 6:27 |  |  |  | 0 | 0 | 0 | 0.37847 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=424KV
[6 empty] | 2019-03-25 | 20:34 | 2019-03-26 | 6:28 |  |  |  | 0 | 0 | 0 | 0.4125 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=426KV
[6 empty] | 2019-03-28 | 0:47 | 2019-03-28 | 6:00 |  |  |  | 0 | 0 | 0 | 0.21736 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=426KV
[6 empty] | 2019-03-28 | 20:49 | 2019-03-29 | 6:00 |  |  |  | 0 | 0 | 0 | 0.38264 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=425KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-02 02:59 | [5 empty] | 100
116 | NR240123 | 400KV KURUKSHETRA - JIND - II | 103.6 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-01 | 6:26 | -- | -- | -- | 0 | 0 | 0 | 0.26806 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-02 | 13:17 | 2019-03-03 | 6:33 |  |  |  | 0 | 0 | 0 | 0.71944 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-03 | 14:52 | 2019-03-04 | 6:20 |  |  |  | 0 | 0 | 0 | 0.64444 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=430KV
[6 empty] | 2019-03-04 | 14:13 | 2019-03-05 | 6:35 |  |  |  | 0 | 0 | 0 | 0.68194 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=432KV
[6 empty] | 2019-03-05 | 20:18 | 2019-03-06 | 7:51 |  |  |  | 0 | 0 | 0 | 0.48125 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-06 | 20:07 | 2019-03-07 | 6:30 |  |  |  | 0 | 0 | 0 | 0.43264 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-07 | 19:58 | 2019-03-08 | 6:35 |  |  |  | 0 | 0 | 0 | 0.44236 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-08 | 19:49 | 2019-03-09 | 6:36 |  |  |  | 0 | 0 | 0 | 0.44931 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=427KV
[6 empty] | 2019-03-09 | 20:21 | 2019-03-09 | 21:47 |  |  |  | 0 | 0 | 0 | 0.059722 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=424KV
[6 empty] | 2019-03-10 | 15:25 | 2019-03-11 | 5:26 |  |  |  | 0 | 0 | 0 | 0.58403 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=421KV
[6 empty] | 2019-03-12 | 21:54 | 2019-03-13 | 6:08 |  |  |  | 0 | 0 | 0 | 0.34306 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=423KV
[6 empty] | 2019-03-13 | 20:18 | 2019-03-14 | 5:58 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-17 | 19:59 | 2019-03-18 | 6:31 |  |  |  | 0 | 0 | 0 | 0.43889 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=425KV
[6 empty] | 2019-03-18 | 20:07 | 2019-03-19 | 5:44 |  |  |  | 0 | 0 | 0 | 0.40069 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-19 | 21:33 | 2019-03-20 | 6:01 |  |  |  | 0 | 0 | 0 | 0.35278 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=422KV
[6 empty] | 2019-03-20 | 20:05 | 2019-03-21 | 6:37 |  |  |  | 0 | 0 | 0 | 0.43889 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=429KV
[6 empty] | 2019-03-21 | 20:15 | 2019-03-22 | 6:33 |  |  |  | 0 | 0 | 0 | 0.42917 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=430KV
[6 empty] | 2019-03-24 | 13:18 | 2019-03-25 | 6:03 |  |  |  | 0 | 0 | 0 | 0.69792 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | 2019-03-26 | 21:44 | 2019-03-27 | 9:43 |  |  |  | 0 | 0 | 0 | 0.49931 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=426KV
[6 empty] | 2019-03-28 | 20:49 | 2019-03-29 | 6:00 |  |  |  | 0 | 0 | 0 | 0.38264 |  |  |  | Line hand tripped for voltage regulation Kurukshetra=425 KV
[6 empty] | 2019-03-29 | 21:32 | 2019-03-30 | 6:21 |  |  |  | 0 | 0 | 0 | 0.36736 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=426KV
[6 empty] | 2019-03-30 | 20:35 | 2019-04-01 | 0:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:25 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-09 15:49 | [5 empty] | 100
117 | NR240124 | 400KV DULHASTI-KISHENPUR-II | 119.44 | NR2 | -- | 2019-03-22 | 9:47 | 2019-03-22 | 15:09 | -- | -- | -- | 0.22361 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for replacement of flashed insulator on Loc. No. 265
[6 empty] | 2019-03-22 | 15:09 | 2019-03-22 | 22:01 |  |  |  | 0 | 0 | 0 | 0.28611 |  |  |  | Line kept open by NHPC Dulhasti after returning of SD by PG for CVT replacement at their end.
[6 empty] | Sub Total --> | [6 empty] | 0.22361 | 0 | 0 | 0.28611 | [5 empty] | 99.28
118 | NR240125 | 400KV URI 1 - AMARGARH - I | 61.95 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
119 | NR240126 | 400KV AMARGARH - WAGOORA- I | 39.34 | NR2 | -- | 2019-03-12 | 9:54 | 2019-03-12 | 17:30 | -- | -- | -- | 0.31667 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for AMP works.
[6 empty] | Sub Total --> | [6 empty] | 0.31667 | 0 | 0 | 0 | [5 empty] | 98.98
120 | NR240127 | 400KV URI 1 - AMARGARH - II | 61.95 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
121 | NR240128 | 400KV AMARGARH - WAGOORA - II | 39.34 | NR2 | -- | 2019-03-13 | 10:02 | 2019-03-13 | 17:38 | -- | -- | -- | 0.31667 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for AMP works.
[6 empty] | Sub Total --> | [6 empty] | 0.31667 | 0 | 0 | 0 | [5 empty] | 98.79
122 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-02 | 10:29 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 10:29 | N/A | N/A | N/A | Line hand tripped for voltage regulation. Moga=791KV
[6 empty] | 2019-03-02 | 14:57 | 2019-03-04 | 10:52 |  |  |  | 0 | 0 | 0 | 1899-12-31 19:55 |  |  |  | Line hand tripped for voltage regulation. Moga=786KV
[6 empty] | 2019-03-04 | 20:38 | 2019-03-05 | 7:56 |  |  |  | 0 | 0 | 0 | 0.47083 |  |  |  | Line hand tripped for voltage regulation. Moga=794KV
[6 empty] | 2019-03-05 | 22:00 | 2019-03-06 | 7:46 |  |  |  | 0 | 0 | 0 | 0.40694 |  |  |  | Line hand tripped for voltage regulation. Moga=794KV
[6 empty] | 2019-03-06 | 20:03 | 2019-03-07 | 6:57 |  |  |  | 0 | 0 | 0 | 0.45417 |  |  |  | Line hand tripped for voltage regulation. Moga=790KV
[6 empty] | 2019-03-07 | 20:01 | 2019-03-08 | 6:32 |  |  |  | 0 | 0 | 0 | 0.43819 |  |  |  | Line hand tripped for voltage regulation. Moga=790KV
[6 empty] | 2019-03-08 | 19:38 | 2019-03-10 | 9:26 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:48 |  |  |  | Line hand tripped for voltage regulation. Moga=790KV
[6 empty] | 2019-03-10 | 20:43 | 2019-03-11 | 7:07 |  |  |  | 0 | 0 | 0 | 0.43333 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV
[6 empty] | 2019-03-11 | 20:41 | 2019-03-12 | 11:14 |  |  |  | 0 | 0 | 0 | 0.60625 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV
[6 empty] | 2019-03-12 | 20:19 | 2019-03-13 | 9:31 |  |  |  | 0 | 0 | 0 | 0.55 |  |  |  | Line hand tripped for voltage regulation. Moga=798KV
[6 empty] | 2019-03-13 | 19:49 | 2019-03-14 | 9:45 |  |  |  | 0 | 0 | 0 | 0.58056 |  |  |  | Line hand tripped for voltage regulation. Moga=795KV
[6 empty] | 2019-03-14 | 13:09 | 2019-03-15 | 6:38 |  |  |  | 0 | 0 | 0 | 0.72847 |  |  |  | Line hand tripped for voltage regulation. Moga=795KV
[6 empty] | 2019-03-15 | 21:09 | 2019-03-16 | 6:28 |  |  |  | 0 | 0 | 0 | 0.38819 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV
[6 empty] | 2019-03-16 | 20:27 | 2019-03-18 | 8:15 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:48 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV
[6 empty] | 2019-03-19 | 21:51 | 2019-03-20 | 8:58 |  |  |  | 0 | 0 | 0 | 0.46319 |  |  |  | Line hand tripped for voltage regulation. Moga=791KV
[6 empty] | 2019-03-20 | 8:58 | 2019-03-20 | 21:35 |  |  |  | 0.52569 | 0 | 0 | 0 |  |  |  | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | 2019-03-20 | 21:36 | 2019-03-22 | 8:15 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:39 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV
[6 empty] | 2019-03-22 | 15:10 | 2019-03-23 | 8:46 |  |  |  | 0 | 0 | 0 | 0.73333 |  |  |  | Line hand tripped for voltage regulation. Moga=791KV
[6 empty] | 2019-03-23 | 21:25 | 2019-03-24 | 9:56 |  |  |  | 0 | 0 | 0 | 0.52153 |  |  |  | Line hand tripped for voltage regulation. Moga=785KV
[6 empty] | 2019-03-25 | 0:22 | 2019-03-25 | 8:31 |  |  |  | 0 | 0 | 0 | 0.33958 |  |  |  | Line hand tripped for voltage regulation. Moga=792KV
[6 empty] | 2019-03-25 | 21:20 | 2019-03-26 | 9:24 |  |  |  | 0 | 0 | 0 | 0.50278 |  |  |  | Line hand tripped for voltage regulation. Moga=795KV
[6 empty] | 2019-03-26 | 20:51 | 2019-03-27 | 8:50 |  |  |  | 0 | 0 | 0 | 0.49931 |  |  |  | Line hand tripped for voltage regulation. Moga=795KV
[6 empty] | 2019-03-27 | 20:20 | 2019-03-28 | 9:18 |  |  |  | 0 | 0 | 0 | 0.54028 |  |  |  | Line hand tripped for voltage regulation. Moga=788KV
[6 empty] | 2019-03-28 | 20:50 | 2019-03-29 | 6:45 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV
[6 empty] | 2019-03-29 | 6:45 | 2019-03-29 | 12:31 |  |  |  | 0.24028 | 0 | 0 | 0 |  |  |  | SD taken for rectification of failed drive mechanism of R-Ph LR CB.
[6 empty] | 2019-03-29 | 21:43 | 2019-03-30 | 8:17 |  |  |  | 0 | 0 | 0 | 0.44028 |  |  |  | Line hand tripped for voltage regulation. Moga=790KV
[6 empty] | 2019-03-30 | 23:36 | 2019-04-01 | 0:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:24 |  |  |  | Line hand tripped for voltage regulation. Moga=788KV
[6 empty] | Sub Total --> | [6 empty] | 0.76597 | 0 | 0 | 1900-01-17 07:18 | [5 empty] | 97.53
123 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
124 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
125 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
126 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
127 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
128 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
129 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 | -- | 2019-03-01 | 0:00 | 2019-03-02 | 6:49 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:49 | N/A | N/A | N/A | B/R hand tripped for voltage regulation. Wagoora=393KV.
[6 empty] | 2019-03-16 | 10:28 | 2019-03-19 | 2:09 |  |  |  | 0 | 0 | 0 | 1900-01-01 15:41 |  |  |  | B/R hand tripped for voltage regulation. Wagoorae =393KV.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-02 22:30 | [5 empty] | 100
130 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
131 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
132 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
133 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
134 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
135 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
136 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
137 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
138 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
139 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
140 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
141 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
142 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 | -- | 2019-03-29 | 17:00 | 2019-03-29 | 17:16 | -- | -- | -- | 0 | 0 | 0 | 0.011111 | N/A | N/A | N/A | SD taken for observing reactive power response of STATCOM under construction at Nalagarh.
[6 empty] | 2019-03-29 | 17:31 | 2019-03-29 | 17:41 |  |  |  | 0 | 0 | 0 | 0.0069444 |  |  |  | SD taken for observing reactive power response of STATCOM under construction at Nalagarh.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.018056 | [5 empty] | 100
143 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
144 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 | -- | 2019-03-23 | 9:02 | 2019-03-23 | 19:52 | -- | -- | -- | 0.45139 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | 2019-03-24 | 10:23 | 2019-03-24 | 18:54 |  |  |  | 0.35486 | 0 | 0 | 0 |  |  |  | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | Sub Total --> | [6 empty] | 0.80625 | 0 | 0 | 0 | [5 empty] | 97.4
145 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 | -- | 2019-03-25 | 9:11 | 2019-03-25 | 18:22 | -- | -- | -- | 0.38264 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | Sub Total --> | [6 empty] | 0.38264 | 0 | 0 | 0 | [5 empty] | 98.77
146 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
147 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
148 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
149 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
150 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
151 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
152 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
153 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
154 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
155 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
156 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
157 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
158 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
159 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
160 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
161 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
162 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 | -- | 2019-03-27 | 9:40 | 2019-03-27 | 15:40 | -- | -- | -- | 0.25 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for AMP work
[6 empty] | Sub Total --> | [6 empty] | 0.25 | 0 | 0 | 0 | [5 empty] | 99.19
163 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
164 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
165 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
166 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
167 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
168 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
169 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 | -- | 2019-03-26 | 9:45 | 2019-03-26 | 18:37 | -- | -- | -- | 0.36944 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for AMP work
[6 empty] | Sub Total --> | [6 empty] | 0.36944 | 0 | 0 | 0 | [5 empty] | 98.81
170 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
171 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
172 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
173 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
174 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
175 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
176 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
177 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
178 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
179 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
180 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
181 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 | -- | 2019-03-07 | 10:14 | 2019-03-07 | 17:00 | -- | -- | -- | 0 | 0 | 0 | 0.28194 | N/A | N/A | N/A | SD taken by BBMB for half yearly maintenace work in their switchyard.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.28194 | [5 empty] | 100
182 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
183 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 | -- | 2019-03-18 | 10:30 | 2019-03-18 | 10:41 | -- | -- | -- | 0.0076389 | 0 | 0 | 0 | N/A | N/A | N/A | ICT Tripped during SD of 400kV Bus-I.
[6 empty] | Sub Total --> | [6 empty] | 0.0076389 | 0 | 0 | 0 | [5 empty] | 99.98
184 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
185 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
186 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
187 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
188 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
189 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
190 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
191 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
192 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
193 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
194 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
195 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
196 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
197 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 | -- | 2019-03-29 | 13:09 | 2019-03-29 | 20:45 | -- | -- | -- | 0.31667 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | 2019-03-30 | 9:41 | 2019-03-30 | 16:46 |  |  |  | 0.29514 | 0 | 0 | 0 |  |  |  | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | Sub Total --> | [6 empty] | 0.61181 | 0 | 0 | 0 | [5 empty] | 98.03
198 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 | -- | 2019-03-27 | 9:01 | 2019-03-27 | 19:40 | -- | -- | -- | 0.44375 | 0 | 0 | 0 | N/A | N/A | N/A | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | 2019-03-28 | 9:27 | 2019-03-28 | 16:27 |  |  |  | 0.29167 | 0 | 0 | 0 |  |  |  | SD taken for replacement of disc insulatoe with composite polymer long rod insulator in switch yard at Moga.
[6 empty] | Sub Total --> | [6 empty] | 0.73542 | 0 | 0 | 0 | [5 empty] | 97.63
199 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
200 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
201 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
202 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
203 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 | -- | 2019-03-03 | 2:20 | 2019-03-03 | 2:24 | -- | -- | -- | 0 | 0 | 0.0027778 | 0 | N/A | N/A | N/A | ICT tripped due to overflux protection optd in 220 kV side.
[6 empty] | 2019-03-03 | 2:24 | 2019-03-03 | 6:36 |  |  |  | 0 | 0 | 0 | 0.175 |  |  |  | ICT kept open on prevalent system over voltage after tripping on over flux protection.
[6 empty] | 2019-03-15 | 9:07 | 2019-03-15 | 18:01 |  |  |  | 0.37083 | 0 | 0 | 0 |  |  |  | SD taken for AMP works.
[6 empty] | Sub Total --> | [6 empty] | 0.37083 | 0 | 0.0027778 | 0.175 | [5 empty] | 98.8
204 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 | -- | 2019-03-15 | 9:39 | 2019-03-15 | 19:59 | -- | -- | -- | 0 | 0 | 0 | 0.43056 | N/A | N/A | N/A | SD taken for installation & connection of tertiary transformer for STATCOM under construction
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.43056 | [5 empty] | 100
205 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
206 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
207 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 | -- | 2019-03-19 | 9:05 | 2019-03-22 | 21:22 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 12:17 | N/A | N/A | N/A | SD taken for extension of 400 kV GIS Bus Bar-2 for ICT-3 under construction.
[6 empty] | 2019-03-23 | 9:46 | 2019-03-26 | 19:11 |  |  |  | 0 | 0 | 0 | 1900-01-02 09:25 |  |  |  | SD taken for extension of 400 kV GIS Bus Bar-1 for ICT-3 under construction.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-05 21:42 | [5 empty] | 100
208 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
209 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
210 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
211 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
212 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
213 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
214 | NR2ICT73 | KAITHAL 315MVA ICT-III | 315 | NR2 | -- | 2019-03-25 | 9:47 | 2019-03-25 | 15:56 | -- | -- | -- | 0.25625 | 0 | 0 | 0 | N/A | N/A | N/A | SD Taken for R ph OLTC oil replacement due to low BDV value.
[6 empty] | Sub Total --> | [6 empty] | 0.25625 | 0 | 0 | 0 | [5 empty] | 99.17
215 | NR2ICT71 | KURUKSHETRA 500MVA ICT-I | 500 | NR2 | -- | 2019-03-22 | 15:34 | 2019-03-22 | 15:58 |  |  |  | 0.016667 | 0 | 0 | 0 |  |  |  | ICT tripped during Relay Firmware Up-gradation.
[6 empty] | Sub Total --> | [6 empty] | 0.016667 | 0 | 0 | 0 | [5 empty] | 99.95
216 | NR2ICT72 | KURUKSHETRA 500MVA ICT-II | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
217 | NR2ICT74 | BANALA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
218 | NR2ICT75 | BANALA 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
219 | NR2ICT76 | FATEHABAD 315MVA ICT-III | 315 | NR2 | -- | 2019-03-03 | 4:25 | 2019-03-03 | 4:28 |  |  |  | 0 | 0 | 0.0020833 | 0 |  |  |  | ICT tripped due to overflux protection optd in 220 kV side.
[6 empty] | 2019-03-03 | 4:28 | 2019-03-03 | 6:30 |  |  |  | 0 | 0 | 0 | 0.084722 |  |  |  | ICT kept open on prevalent system over voltage after tripping on over flux protection.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.0020833 | 0.084722
220 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 | -- | 2019-03-27 | 12:57 | 2019-03-27 | 14:29 | -- | -- | -- | 0.063889 | 0 | 0 | 0 | N/A | N/A | N/A | SVC tripped due to B-PH differential protection caused while tightening loose CT wire.
[6 empty] | Sub Total --> | [6 empty] | 0.063889 | 0 | 0 | 0 | [5 empty] | 99.79
221 | NR2SVC02 | NEW WANPOH -200/+300 MVAR SVC |  | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
222 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 | -- | 2019-03-09 | 9:41 | 2019-03-18 | 13:37 | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 03:56 | N/A | N/A | N/A | Shutdown taken for integration of pole-3 and offline testing
[6 empty] | 2019-03-19 | 14:36 | 2019-03-20 | 0:12 |  |  |  | 0 | 0 | 0 | 0.4 |  |  |  | Shutdown taken for integration of pole-3 and offline testing.
[6 empty] | 2019-03-20 | 12:42 | 2019-03-20 | 20:00 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | Pole tripped on Filter Power Limit while carrying out online integration and testing of Pole-1 & Pole-3 under construction.
[6 empty] | 2019-03-22 | 10:24 | 2019-03-22 | 19:50 |  |  |  | 0 | 0 | 0 | 0.39306 |  |  |  | Shutdown taken for integration of pole-3 with uploading of New Software and offline testing.
[6 empty] | 2019-03-23 | 12:54 | 2019-03-24 | 10:11 |  |  |  | 0 | 0 | 0 | 0.88681 |  |  |  | Pole blocked due to Common Neutral Area Protection (CNAP) optd. while carrying out online integration and testing of Pole-1 & Pole-3 under construction.
[6 empty] | 2019-03-26 | 14:11 | 2019-03-26 | 16:18 |  |  |  | 0 | 0 | 0 | 0.088194 |  |  |  | Pole-1 tripped due to fault on DC Line while carrying out online integration and testing of Pole-1 & Pole-3 under construction.
[6 empty] | 2019-03-27 | 16:40 | 2019-03-27 | 19:29 |  |  |  | 0 | 0 | 0 | 0.11736 |  |  |  | Pole Blocked During Testing of Pole-3 under construction.
[6 empty] | 2019-03-28 | 7:14 | 2019-03-28 | 8:08 |  |  |  | 0 | 0 | 0 | 0.0375 |  |  |  | Pole tripped on Filter Power Limit while carrying out online integration and testing of Pole-1 & Pole-3 under construction.
[6 empty] | 2019-03-28 | 9:18 | 2019-03-28 | 9:45 |  |  |  | 0 | 0 | 0 | 0.01875 |  |  |  | Pole-1 blocked during testing/ ramp up power on Pole-3 under construction.
[6 empty] | 2019-03-28 | 12:27 | 2019-03-28 | 14:22 |  |  |  | 0 | 0 | 0 | 0.079861 |  |  |  | Pole-1 blocked during testing/ ramp up power on Pole-3 under construction.
[6 empty] | 2019-03-30 | 16:33 | 2019-03-30 | 18:53 |  |  |  | 0.097222 | 0 | 0 | 0 |  |  |  | Bi-Pole blocked Due to Earth Fault Over current protection optd.
[6 empty] | Sub Total --> | [6 empty] | 0.097222 | 0 | 0 | 1900-01-10 11:45 | [5 empty] | 99.69
| NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 | -- | 2019-03-09 | 14:09 | 2019-03-18 | 22:12 | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 08:03 | N/A | N/A | N/A | Shutdown taken for integration of pole-3 and offline testing
[6 empty] | 2019-03-19 | 3:34 | 2019-03-19 | 5:12 |  |  |  | 0 | 0 | 0 | 0.068056 |  |  |  | Pole blocked while carrying out online integration and testing of Pole-3 under construcction.
[6 empty] | 2019-03-19 | 9:22 | 2019-03-19 | 12:02 |  |  |  | 0 | 0 | 0 | 0.11111 |  |  |  | POLE blocked due to control changover from CURRENT mode to POWER mode while carrying out testing for Pole-3 under construction..
[6 empty] | 2019-03-19 | 14:28 | 2019-03-19 | 23:37 |  |  |  | 0 | 0 | 0 | 0.38125 |  |  |  | Shutdown taken for integration of pole-3 and offline testing
[6 empty] | 2019-03-20 | 12:42 | 2019-03-20 | 20:04 |  |  |  | 0 | 0 | 0 | 0.30694 |  |  |  | Pole tripped on Filter Power Limit while carrying out online integration and testing of Pole-1 & Pole-3 under construction.
[6 empty] | 2019-03-22 | 10:24 | 2019-03-22 | 19:50 |  |  |  | 0 | 0 | 0 | 0.39306 |  |  |  | Shutdown taken for integration of pole-3 with uploading of New Software and offline testing.
[6 empty] | 2019-03-23 | 12:54 | 2019-03-27 | 9:42 |  |  |  | 0 | 0 | 0 | 1900-01-02 20:48 |  |  |  | Pole blocked due to Common Neutral Area Protection (CNAP) optd. while carrying out online integration and testing of Pole-1 & Pole-3 under construction.
[6 empty] | 2019-03-28 | 7:54 | 2019-03-28 | 8:23 |  |  |  | 0 | 0 | 0 | 0.020139 |  |  |  | SD taken to reboot the Pole-2 for rectify the issue of Pole-1 Filter Power limit observed while carrying out online integration and sofware uploading for Pole-3 under construction.
[6 empty] | 2019-03-28 | 10:00 | 2019-03-28 | 15:16 |  |  |  | 0 | 0 | 0 | 0.21944 |  |  |  | Pole-1 blocked during testing/ ramp up power on Pole-3 under construction.
[6 empty] | 2019-03-28 | 15:44 | 2019-03-28 | 16:26 |  |  |  | 0 | 0 | 0 | 0.029167 |  |  |  | Pole blocked due to Common Neutral Area Protection (CNAP) optd. while carrying out online integration and testing of Pole-1 & Pole-3 under construction.
[6 empty] | 2019-03-30 | 8:52 | 2019-03-30 | 10:00 |  |  |  | 0.047222 | 0 | 0 | 0 |  |  |  | Pole-2 blocked Due to CNAP protection optd at Champa end.
[6 empty] | 2019-03-30 | 16:33 | 2019-03-30 | 18:59 |  |  |  | 0.10139 | 0 | 0 | 0 |  |  |  | Bi-Pole blocked Due to Earth Over current protection optd.
[6 empty] | 2019-03-30 | 21:50 | 2019-03-30 | 23:02 |  |  |  | 0.05 | 0 | 0 | 0 |  |  |  | Pole tripped due to CLD HV Cable protection operated at Kurukshetra.
[6 empty] | Sub Total --> | [6 empty] | 0.19861 | 0 | 0 | 1900-01-13 17:33 | [5 empty] | 99.36
Formulas:
ISTS Licensee = IF(RIGHT(T8)="T",(+[Date]-[Date]),0)
ISTS Licensee = SUM([ISTS Licensee, row above])
OTHERS = IF(RIGHT(T8)="U",(+[Date]-[Date]),0)
OTHERS = SUM([OTHERS, row above])
Deemed Available = IF(RIGHT(T8)="D",(+[Date]-[Date]),0)