## Sheet2 (2)
Standard of Performance data for the month of - May 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II (JAMMU)
ELEMENT CODE | ELEMENT NAME | DESCRIPTION (Length/Nos/MVA/MVAr/etc) | Region | Type of Failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration time more than Specified (Y/N) | Difference between Actual and specified | NRLDC Code | Category Code | REASON OF OUTAGE | Outage certifying Agency and reference documents (NRPC) | % Availability as certified by certifying agency
[5 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | POWERGRID | OTHERS | System constraints / Natural calamity/ Militancy | Deemed Available
[10 empty] | @ (T) | # (U) | & ( C ) | * (D)
[10 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 |  | 2018-05-13 06:06 | 2018-05-13 11:56 | -- | -- | -- | 0 | 0 | 0 | 0.24306 | N/A | N/A | N/A | NR/05/1059 | OSPD | SD taken by JKPDD for maintenance work at Hiranagar.
[5 empty] | 2018-05-29 18:15 | 2018-05-29 19:57 | -- | -- | -- | 0 | 0.070833 | 0 | 0 | N/A | N/A | N/A | NR/05/2521 | OMSU | Line tripped due to fault created by failure of R-ph CT installed on 200MVA ICT at JKPDD Hiranagar.
[10 empty] | 0 | 0.070833 | 0 | 0.24306 | [7 empty] | 100
NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 |  | 2018-05-13 06:06 | 2018-05-13 11:56 | -- | -- | -- | 0 | 0 | 0 | 0.24306 | N/A | N/A | N/A | NR/05/1059 | OSPD | SD taken by JKPDD for maintenance work at Hiranagar.
[5 empty] | 2018-05-29 18:15 | 2018-05-29 19:57 | -- | -- | -- | 0 | 0.070833 | 0 | 0 | N/A | N/A | N/A | NR/05/2521 | OMSU | Line tripped due to fault created by failure of R-ph CT installed on 200MVA ICT at JKPDD Hiranagar.
[10 empty] | 0 | 0.070833 | 0 | 0.24306 | [7 empty] | 100
NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 |  | 2018-05-22 00:41 | 2018-05-22 01:34 | -- | -- | -- | 0 | 0.036806 | 0 | 0 | N/A | N/A | N/A | NR/05/1869 | OMSU | Line tripped at NHPC Bairasuil only & remain charged from Jessore.
[5 empty] | 2018-05-23 10:38 | 2018-05-23 11:07 | -- | -- | -- | 0 | 0.020139 | 0 | 0 | N/A | N/A | N/A | NR/05/1988 | OMSU | Line tripped at NHPC Bairasuil only & remain charged from Jessore.
[5 empty] | 2018-05-28 14:09 | 2018-05-28 14:35 | -- | -- | -- | 0 | 0.018056 | 0 | 0 | N/A | N/A | N/A | NR/05/2406 | OMSU | Line tripped on B-N fault caused by Forest fire from Bairasul only.FLR Bairasul : 71 kM, 0.804 kA
[10 empty] | 0 | 0.075 | 0 | 0 | [7 empty] | 100
NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 |  | 2018-05-02 11:15 | 2018-05-02 12:29 | -- | -- | -- | 0 | 0.051389 | 0 | 0 | N/A | N/A | N/A | NR/05/107 | OMSU | Line tripped due to BUS BAR Protection operated at BBMB, Pong.
[5 empty] | 2018-05-22 23:15 | 2018-05-23 01:22 | -- | -- | -- | 0 | 0.088194 | 0 | 0 | N/A | N/A | N/A | NR/05/1945 | OMSU | Line tripped due to BUS BAR Protection operated at BBMB, Pong.
[5 empty] | 2018-05-25 15:19 | 2018-05-25 16:09 | -- | -- | -- | 0 | 0.034722 | 0 | 0 | N/A | N/A | N/A | NR/05/2178 | OMSU | Line tripped on R-N fault caused by Forest Fire. FLR Bairasuil : 70.4kM & FLR Pong : 11.65kM.
[5 empty] | 2018-05-26 13:17 | 2018-05-26 14:04 | -- | -- | -- | 0 | 0.032639 | 0 | 0 | N/A | N/A | N/A | NR/05/2256 | OMSU | Line tripped on R-N fault.FLR Bairrasul : Z-3.
[5 empty] | 2018-05-26 14:54 | 2018-05-26 18:57 | -- | -- | -- | 0 | 0.16875 | 0 | 0 | N/A | N/A | N/A | NR/05/2286 | OMSU | Line tripped on R-N fault caused by Forest Fire in hlly areas between tower location no. 232-242.
[5 empty] | 2018-05-28 14:16 | 2018-05-28 14:40 | -- | -- | -- | 0 | 0.016667 | 0 | 0 | N/A | N/A | N/A | NR/05/2409 | OMSU | Line tripped on R-N fault caused by Forest fire. FLR Bairasul : 91 kM & Pong: 7.321 kM.
[5 empty] | 2018-05-29 13:53 | 2018-05-29 18:23 | -- | -- | -- | 0.1875 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2494 | OSPT | SD taken for final testing of protection circuits, auto-reclose, interlock etc after retrofitting of CB at Pong BBMB.
[10 empty] | 0.1875 | 0.39236 | 0 | 0 | [7 empty] | 99.38
NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 |  | 2018-05-25 17:27 | 2018-05-25 19:38 | -- | -- | -- | 0 | 0.090972 | 0 | 0 | N/A | N/A | N/A | NR/05/2196 | OMSU | Line tripped on B-N fault caused by falling of tree for on Tr. Line between loc. 51 & 52. FLR Sarna : 22.13kM, 2.167kA.
[5 empty] | 2018-05-26 14:40 | 2018-05-26 16:20 | -- | -- | -- | 0 | 0.069444 | 0 | 0 | N/A | N/A | N/A | NR/05/2274 | OMSU | Line tripped on Y-B fault caused by Forest Fire. FLR Sarna: 22.13kM, Iy=7.25kA, Ib=6.8kA.
[10 empty] | 0 | 0.16042 | 0 | 0 | [7 empty] | 100
NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 |  | 2018-05-10 10:50 | 2018-05-10 18:02 | -- | -- | -- | 0 | 0 | 0 | 0.3 | N/A | N/A | N/A | NR/05/854 | OSPD | SD taken by PSTCL for general maintenace work at Dasuya.
[5 empty] | 2018-05-13 15:12 | 2018-05-13 15:59 | -- | -- | -- | 0.032639 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1079 | OSFT | Line tripped on Y-B fault created by Jack bus Jumper snapping over Sarna Dasua-I at PSTCL Dasua.
[10 empty] | 0.032639 | 0 | 0 | 0.3 | [7 empty] | 99.89
NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 |  | 2018-05-13 15:12 | 2018-05-13 15:19 | -- | -- | -- | 0.0048611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1079 | OSFT | Line tripped on Y-B fault created by Jack bus Jumper snapping over Sarna Dasua-I at PSTCL Dasua.
[5 empty] | 2018-05-25 10:26 | 2018-05-25 11:53 | -- | -- | -- | 0 | 0 | 0 | 0.060417 | N/A | N/A | N/A | NR/05/2144 | OSPD | SD taken by PSTCL to attend the hotspot in CB at Dasuya.
[10 empty] | 0.0048611 | 0 | 0 | 0.060417 | [7 empty] | 99.98
NR222011 | 220KV Jessore-Pong | 37.7 | NR2 |  | 2018-05-02 11:15 | 2018-05-02 11:50 | -- | -- | -- | 0 | 0.024306 | 0 | 0 | N/A | N/A | N/A | NR/05/102 | OMSU | Line tripped due to BUS BAR Protection operated at BBMB, Pong.
[5 empty] | 2018-05-05 08:25 | 2018-05-05 17:22 | -- | -- | -- | 0 | 0 | 0 | 0.37292 | N/A | N/A | N/A | NR/05/452 | OSPD | SD taken by BBMB Pong for CB maintenance works
[5 empty] | 2018-05-22 23:15 | 2018-05-23 00:07 | -- | -- | -- | 0 | 0.036111 | 0 | 0 | N/A | N/A | N/A | NR/05/1944 | OMSU | Line tripped from Jessore only due to Bus-I operated at Pong.
[5 empty] | 2018-05-24 22:33 | 2018-05-24 23:17 | -- | -- | -- | 0 | 0.030556 | 0 | 0 | N/A | N/A | N/A | NR/05/2121 | OMSU | Line tripped due to failure of Y-phase CT of machine no. 4 at BBMB, Pong.
[5 empty] | 2018-05-25 15:15 | 2018-05-25 16:20 | -- | -- | -- | 0 | 0.045139 | 0 | 0 | N/A | N/A | N/A | NR/05/2176 | OMSU | Line tripped on Y-B fault caused by heavy Forest Fire. FLR Pong: 11.65kM and Jessore : 25.1kM.
[5 empty] | 2018-05-26 13:20 | 2018-05-26 14:01 | -- | -- | -- | 0 | 0.028472 | 0 | 0 | N/A | N/A | N/A | NR/05/2254 | OMSU | Line tripped on R-N fault from Jessore only and remained charged from Pong. FLR Jessore : 71.7kM , Z-3.
[5 empty] | 2018-05-26 16:30 | 2018-05-26 18:52 | -- | -- | -- | 0 | 0.098611 | 0 | 0 | N/A | N/A | N/A | NR/05/2286 | OMSU | Line tripped on B-N fault caused by Forest Fire in hlly areas. FLR Jessore : 25.25kM & 2.56kA, Pong: 11kM.
[5 empty] | 2018-05-28 14:09 | 2018-05-28 14:52 | -- | -- | -- | 0 | 0.029861 | 0 | 0 | N/A | N/A | N/A | NR/05/2409 | OMSU | Line tripped on B-N fault Forest Fire. FLR Jessore: 28.76kM & Pong: 6.221 kM.
[10 empty] | 0 | 0.29306 | 0 | 0.37292 | [7 empty] | 100
NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 |  | 2018-05-21 13:41 | 2018-05-21 15:08 | -- | -- | -- | 0 | 0.060417 | 0 | 0 | N/A | N/A | N/A | NR/05/1828 | OMSU | Line tripped on R-Y fault caused by heavy Forest Fire at Location 15-16. FLR Kishenpur:4.84kM, 15.12kA, 14.82kA.
[10 empty] | 0 | 0.060417 | 0 | 0 | [7 empty] | 100
NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 |  | 2018-05-21 08:33 | 2018-05-21 08:51 | -- | -- | -- | 0 | 0.0125 | 0 | 0 | N/A | N/A | N/A | NR/05/1797 | OMSU | Line tripped in Zone-3 from Kishenpur due to fault in JKPDD 200KV Udhampur-Sarna line.
[10 empty] | 0 | 0.0125 | 0 | 0 | [7 empty] | 100
NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 |  | 2018-05-24 07:00 | 2018-05-24 13:50 | -- | -- | -- | 0 | 0 | 0 | 0.28472 | N/A | N/A | N/A | NR/05/2047 | OSPD | SD taken by JKPDD for maintenance work at Gladni (Jammu) substation.
[5 empty] | 2018-05-25 15:48 | 2018-05-25 16:18 | -- | -- | -- | 0.020833 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2179 | LEFT | Line tripped on B-N fault. |  | 100
[10 empty] | 0.020833 | 0 | 0 | 0.28472 | [7 empty] | 99.93
NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 |  | 2018-05-24 07:00 | 2018-05-24 14:04 | -- | -- | -- | 0 | 0 | 0 | 0.29444 | N/A | N/A | N/A | NR/05/2047 | OSPD | SD taken by JKPDD for maintenance work at Gladni (Jammu) substation.
[10 empty] | 0 | 0 | 0 | 0.29444 | [7 empty] | 100
NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 |  | 2018-05-13 15:12 | 2018-05-13 17:44 | -- | -- | -- | 0.10556 | 0 | 0 | 0 | N/A | N/A | N/A | --- | OSFT | Line tripped on Y-N fault caused by Jack bus jumper breaking at PSTCL, Dasua.
[5 empty] | 2018-05-13 17:44 | 2018-05-17 18:43 | -- | -- | -- | 1900-01-03 00:59 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1102 | OSPT | SD taken for jumper rectifiction work at Dasuya end.
[10 empty] | 1900-01-03 03:31 | 0 | 0 | 0 | [7 empty] | 86.18
NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 |  | 2018-05-21 10:36 | 2018-05-21 18:06 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1810 | OSPD | SD taken by PSTCL for maintenance works at Dasuya
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 |  | 2018-05-03 13:02 | 2018-05-03 13:35 | -- | -- | -- | 0.022917 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/320 | OSPT | SD taken for removing bird nest/foreign particals from Wave Trap at Wagoora.
[5 empty] | 2018-05-24 14:15 | 2018-05-24 14:32 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2078 | OMSU | Line tripped from Wagoora only on R-N fault in Zone-3 due to fault on other line emanating from JKPDD Pampore. May be due to non operation of protection at Pampore.
[10 empty] | 0.022917 | 0 | 0 | 0 | [7 empty] | 99.92
NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 |  | 2018-05-24 14:15 | 2018-05-24 14:32 | -- | -- | -- | 0 | 0.011806 | 0 | 0 | N/A | N/A | N/A | NR/05/2078 | OMSU | Line tripped from Wagoora only on R-N fault in Zone-3 due to fault on other line emanating from JKPDD Pampore. May be due to non operation of protection at Pampore.
[10 empty] | 0 | 0.011806 | 0 | 0 | [7 empty] | 100
NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222028 | 220KV Jallandhar-Hamirpur(PG) -I | 128.3 | NR2 |  | 2018-05-29 14:23 | 2018-05-29 14:47 | -- | -- | -- | 0 | 0.016667 | 0 | 0 | N/A | N/A | N/A | NR/05/2498 | OMSU | Line tripped on B-N fault created by galoping of broken conductor of 11 KV HP state feeder under crossing this line. FLR Jalandhar : 124 kM & Hamirpur: 4.882 kM.
[10 empty] | 0 | 0.016667 | 0 | 0 | [7 empty] | 100
NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222030 | 220KV Jallandhar-Hamirpur(PG) -II | 128.3 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 |  | 2018-05-12 16:57 | 2018-05-12 16:57 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N fault, FLR Hamirpur : 7.148kM,9.059kA.
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR222032 | 220KV Jammu-Samba | 60.93 | NR2 |  | 2018-05-24 07:06 | 2018-05-24 13:58 | -- | -- | -- | 0 | 0 | 0 | 0.28611 | N/A | N/A | N/A | NR/05/2048 | OSPD | SD taken by JKPDD for maintenance work at Gladni (Jammu) substation.
[10 empty] | 0 | 0 | 0 | 0.28611 | [7 empty] | 100
NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 |  | 2018-05-27 11:21 | 2018-05-27 11:30 | -- | -- | -- | 0 | 0.00625 | 0 | 0 | N/A | N/A | N/A | NR/05/2328 | OMSU | Line tripped on B-N fault caused by Forest Fire near Samba.FLR Samba : 11.21kM.
[10 empty] | 0 | 0.00625 | 0 | 0 | [7 empty] | 100
NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 |  | 2018-05-07 23:17 | 2018-05-07 23:35 | -- | -- | -- | 0.0125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/645 | OSFT | Line A/R on Y-N fault at Abdullapur but tripped from Bawana.
[10 empty] | 0.0125 | 0 | 0 | 0 | [7 empty] | 99.96
NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 |  | 2018-05-29 10:06 | 2018-05-29 17:39 | -- | -- | -- | 0 | 0.31458 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | Line tripped from NHPC Chamera2 only due to bus bar-2 protection operated at chamera2.
[10 empty] | 0 | 0.31458 | 0 | 0 | [7 empty] | 100
NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 |  | 2018-05-02 14:05 | 2018-05-02 14:05 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N fault. FLR Patiala: 10.72kM , 14.349KA.
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240024 | 400KV Moga-Hissar | 209.39 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240030 | 400KV URI-WAGOORA-I | 94.99 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 |  | 2018-05-04 17:23 | 2018-05-04 18:59 | -- | -- | -- | 0.066667 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/426 | OSPT | SD taken for taking Line Reactor in service after overhauling at Moga
[10 empty] | 0.066667 | 0 | 0 | 0 | [7 empty] | 99.78
NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 |  | 2018-05-11 10:59 | 2018-05-11 11:38 | -- | -- | -- | 0.027083 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/929 | OSPT | SD taken for taking out Line Reactor at Moga end for Over-hauling works. For replacement of O-Rings/ gaskets.
[5 empty] | 2018-05-14 09:05 | 2018-05-14 19:12 | -- | -- | -- | 0.42153 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1202 | OSPT | SD taken for replacement of O-Rings/gaskets of bushings during overhauling work of Line Reactor at Moga
[5 empty] | 2018-05-23 17:49 | 2018-05-23 18:34 | -- | -- | -- | 0.03125 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2020 | OSPT | SD taken for taking Line Reactor in service after overhauling at Moga.
[10 empty] | 0.47986 | 0 | 0 | 0 | [7 empty] | 98.4
NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 |  | 2018-05-29 10:06 | 2018-05-29 17:58 | -- | -- | -- | 0 | 0.32778 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | Line tripped on DT receipt due to bus bar-2 protection operated at NHPC chamera2.
[10 empty] | 0 | 0.32778 | 0 | 0 | [7 empty] | 100
NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 |  | 2018-05-13 16:19 | 2018-05-13 16:30 | -- | -- | -- | 0 | 0 | 0.0076389 | 0 | N/A | N/A | N/A | NR/05/1082 | LNCC | Line tripped on R-N fault, FLR Wagoora : 93.64kM , 2.45 kA, Z2 , Carrier received.
[5 empty] | 2018-05-15 11:34 | 2018-05-15 13:13 | -- | -- | -- | 0.06875 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1332 | OSPT | SD taken for jumper cone rectification work at Loc. No. 72
[10 empty] | 0.06875 | 0 | 0.0076389 | 0 | [7 empty] | 99.77
NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 |  | 2018-05-26 13:55 | 2018-05-26 16:00 | -- | -- | -- | 0 | 0.086806 | 0 | 0 | N/A | N/A | N/A | NR/05/2268 | OMSU | Line tripped due to problem at Uri 2.
[10 empty] | 0 | 0.086806 | 0 | 0 | [7 empty] | 100
NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 |  | 2018-05-03 00:25 | 2018-05-03 16:02 | -- | -- | -- | 0 | 0 | 0 | 0.65069 | N/A | N/A | N/A | NR/05/240 | LVRD | Line hand tripped for voltage regulation. Nalagarh= 425KV
[5 empty] | 2018-05-06 14:18 | 2018-05-06 20:18 | -- | -- | -- | 0 | 0 | 0 | 0.25 | N/A | N/A | N/A | NR/05/531 | LVRD | Line handtripped for voltage regulation. Nalagarh :430kV.
[5 empty] | 2018-05-07 04:41 | 2018-05-07 10:00 | -- | -- | -- | 0 | 0 | 0 | 0.22153 | N/A | N/A | N/A | NR/05/577 | LVRD | Line handtripped for voltage regulation. Nalagarh :429kV.
[5 empty] | 2018-05-07 23:21 | 2018-05-08 09:48 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | N/A | N/A | N/A | NR/05/640 | LVRD | Line handtripped for voltage regulation. Nalagarh :423kV.
[5 empty] | 2018-05-13 18:19 | 2018-05-14 09:32 | -- | -- | -- | 0 | 0 | 0 | 0.63403 | N/A | N/A | N/A | NR/05/1117 | LVRD | Line handtripped for voltage regulation. Nalagarh :430kV.
[5 empty] | 2018-05-16 03:10 | 2018-05-16 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.15069 | N/A | N/A | N/A | NR/05/1376 | LVRD | Line handtripped for voltage regulation. Nalagarh :427kV.
[5 empty] | 2018-05-29 15:55 | 2018-05-29 16:06 | -- | -- | -- | 0 | 0.0076389 | 0 | 0 | N/A | N/A | N/A | NR/05/2507 | OMSU | Line tripped on R-N fault in PKTCL portion. FLR Nalagarh: 67.122 kM, 5.821 kA & Banala: 47.9kM, 3.4kA. (POWERGRID Portion 0.84 km from Banala and 45.6 kM from Nalagarh. Total line length = 112.78).
[10 empty] | 0 | 0.0076389 | 0 | 1900-01-01 08:13 | [7 empty] | 100
NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 |  | 2018-05-17 11:29 | 2018-05-17 11:51 | -- | -- | -- | 0.015278 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1533 | OSFT | Line tripped from Nalagarh end only due to DT receipt.
[5 empty] | 2018-05-27 16:12 | 2018-05-27 16:35 | -- | -- | -- | 0 | 0.015972 | 0 | 0 | N/A | N/A | N/A | NR/05/2344 | OMSU | Line tripped on R-N fault due to fire in hills. FLR: Nalagarh=5.015kM & Koldam: FL=50.23kM.
[10 empty] | 0.015278 | 0.015972 | 0 | 0 | [7 empty] | 99.95
NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 |  | 2018-05-05 16:45 | 2018-05-05 17:10 | -- | -- | -- | 0 | 0 | 0.017361 | 0 | N/A | N/A | N/A | NR/05/485 | LNCC | Line tripped on R-N fault caused by heavy wind and thunder storm. FLR Panchkula : 165kM & Jhakri: 13.14kM.
[5 empty] | 2018-05-09 15:20 | 2018-05-09 15:53 | -- | -- | -- | 0 | 0 | 0.022917 | 0 | N/A | N/A | N/A | NR/05/787 | LNCC | Line tripped on R-B-N fault caused by heavy winds and thunderstorm. FLR Panchkula : 154Km, Ir=5.4kA, Ib=4.0kA. FLR Jhakri : 2.9Km.
[5 empty] | 2018-05-28 13:32 | 2018-05-28 13:32 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on R-N fault. FLR Panchkulla - 138.6 Km, 2.52kA & Jhakhri: 9.12km, 3.85kA.
[10 empty] | 0 | 0 | 0.040278 | 0 | [7 empty] | 100
NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 |  | 2018-05-09 15:18 | 2018-05-09 15:18 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N fault.FLR Panchkulla : 165kM , 302kA.
[5 empty] | 2018-05-09 15:20 | 2018-05-09 16:08 | -- | -- | -- | 0 | 0 | 0.033333 | 0 | N/A | N/A | N/A | NR/05/787 | LNCC | Line tripped on R-B-N fault caused by heavy winds and thunderstorm. FLR Panchkula : 155kM, Ir=3.4kA, Ib=3.5A. FLR Jhakri : 4.9Km.
[5 empty] | 2018-05-10 10:02 | 2018-05-10 17:18 | -- | -- | -- | 0 | 0 | 0 | 0.30278 | N/A | N/A | N/A | NR/05/833 | OSPD | SD taken by SJVNL for CVT replacement work of 400KV NJPC-Rampur-II at NJPC.
[10 empty] | 0 | 0 | 0.033333 | 0.30278 | [7 empty] | 100
NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 |  | 2018-05-13 18:48 | 2018-05-13 19:19 | -- | -- | -- | 0 | 0 | 0.021528 | 0 | N/A | N/A | N/A | NR/05/1133 | LNCC | Line tripped on Y-N fault caused by heavy wind and thunder storm. FLR Abdullapur:32 kM.
[10 empty] | 0 | 0 | 0.021528 | 0 | [7 empty] | 100
NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 |  | 2018-05-07 06:29 | 2018-05-07 07:16 | -- | -- | -- | 0 | 0 | 0.032639 | 0 | N/A | N/A | N/A | NR/05/582 | GOVC | Line tripped on system over voltage. Chamba: 437KV
[5 empty] | 2018-05-07 07:16 | 2018-05-07 09:42 | -- | -- | -- | 0 | 0 | 0 | 0.10139 | N/A | N/A | N/A | NR/05/582 | LVRD | Line kept open on system over voltage, Chamba: 436KV
[5 empty] | 2018-05-17 13:56 | 2018-05-17 16:49 | -- | -- | -- | 0.12014 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1543 | OSPT | SD takenfor rectification of B PH CB HMV drive at GIS Chamba.
[10 empty] | 0.12014 | 0 | 0.032639 | 0.10139 | [7 empty] | 99.6
NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 |  | 2018-05-03 04:20 | 2018-05-03 11:58 | -- | -- | -- | 0.31806 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/304 | LEFT | Line tripped on R-N fault.FLR Jalandhar:- 8 Km.
[5 empty] | 2018-05-25 04:46 | 2018-05-25 05:25 | -- | -- | -- | 0.027083 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2126 | LEFT | Line tripped on R-N fault Chamba: 161.98kM & Jalandhar: 9.10kM.
[10 empty] | 0.34514 | 0 | 0 | 0 | [7 empty] | 98.85
NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 |  | 2018-05-03 00:26 | 2018-05-03 16:14 | -- | -- | -- | 0 | 0 | 0 | 0.65833 | N/A | N/A | N/A | NR/05/240 | LVRD | Line hand tripped for voltage regulation. Amritsar = 421KV
[5 empty] | 2018-05-06 14:17 | 2018-05-06 20:17 | -- | -- | -- | 0 | 0 | 0 | 0.25 | N/A | N/A | N/A | NR/05/531 | LVRD | Line handtripped for voltage regulation. Amritsar :425kV.
[5 empty] | 2018-05-07 04:41 | 2018-05-07 09:59 | -- | -- | -- | 0 | 0 | 0 | 0.22083 | N/A | N/A | N/A | NR/05/577 | LVRD | Line handtripped for voltage regulation. Amritsar :428kV.
[5 empty] | 2018-05-07 23:20 | 2018-05-08 09:47 | -- | -- | -- | 0 | 0 | 0 | 0.43542 | N/A | N/A | N/A | NR/05/640 | LVRD | Line handtripped for voltage regulation. Amritsar :423kV.
[5 empty] | 2018-05-16 03:10 | 2018-05-16 06:45 | -- | -- | -- | 0 | 0 | 0 | 0.14931 | N/A | N/A | N/A | NR/05/1376 | LVRD | Line handtripped for voltage regulation. Amritsar :424kV.
[5 empty] | 2018-05-17 12:59 | 2018-05-17 13:22 | -- | -- | -- | 0 | 0 | 0.015972 | 0 | N/A | N/A | N/A | NR/05/1539 | LNCC | Line tripped on R-N fault caused by heavy wind and thunder storm. FLR Amritsar:-112 Km & 2.74 KA & Banala:-183KM & 1.9 KA.
[10 empty] | 0 | 0 | 0.015972 | 1899-12-31 17:08 | [7 empty] | 100
NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240078 | 400kV Hamirpur-Banala | 77 | NR2 |  | 2018-05-12 21:22 | 2018-05-12 22:00 | -- | -- | -- | 0 | 0 | 0.026389 | 0 | N/A | N/A | N/A | NR/05/1051 | LNCC | Line tripped on R-N fault caused by heavy wind and thunder storm. FLR Banala : 12.7kM, 6.15kA & Hamirpur : 57.27kM , 3.5kA.
[5 empty] | 2018-05-16 17:55 | 2018-05-16 18:15 | -- | -- | -- | 0 | 0.013889 | 0 | 0 | N/A | N/A | N/A | --- | OMSU | Line tripped on R-N fault caused by snapping of Pilot wire & rope at Loc No. 38-39 while laying OPGW under ULDC Scheme. FLR Hamirpur : 64.06 Km & Banala : 12.5Km.
[5 empty] | 2018-05-16 18:15 | 2018-05-16 19:34 | -- | -- | -- | 0 | 0 | 0 | 0.054861 | N/A | N/A | N/A | NR/05/1474 | LCSD | SD taken for removal of pully & rope stuck while laying OPGW under ULDC scheme.
[5 empty] | 2018-05-28 18:36 | 2018-05-28 19:34 | -- | -- | -- | 0 | 0 | 0 | 0.040278 | N/A | N/A | N/A | NR/05/2431 | LCSD | SD taken for removal of rope and Pilot wire entangled in top conductor at location 31 while laying OPGW under ULDC scheme.
[10 empty] | 0 | 0.013889 | 0.026389 | 0.095139 | [7 empty] | 100
NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 |  | 2018-05-10 08:59 | 2018-05-10 17:35 | -- | -- | -- | 0 | 0 | 0 | 0.35833 | N/A | N/A | N/A | NR/05/833 | OSPD | SD taken by SJVNL for CVT replacement work of 400KV NJPC-Rampur-II at NJPC.
[10 empty] | 0 | 0 | 0 | 0.35833 | [7 empty] | 100
NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 |  | 2018-05-11 16:22 | 2018-05-11 16:54 | -- | -- | -- | 0 | 0.022222 | 0 | 0 | N/A | N/A | N/A | NR/05/962 | OMSU | Line tripped on R-Y fault caused by heavy Forest Fire at Location 149-150. FLR Nalagarh : 86 Km, 5.4 kA. FLR Rampur :38kkm, 5.1KA.
[10 empty] | 0 | 0.022222 | 0 | 0 | [7 empty] | 100
NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 |  | 2018-05-29 15:49 | 2018-05-29 15:59 | -- | -- | -- | 0 | 0.0069444 | 0 | 0 | N/A | N/A | N/A | NR/05/2506 | OMSU | Line tripped on R-N fault in PKTCL portion. FLR Banala: 4.3 kM, 6.9kA (POWERGRID Portion 0.649 km from Banala and 0.438 kM from Koldam. Total line length = 63.7 km).
[10 empty] | 0 | 0.0069444 | 0 | 0 | [7 empty] | 100
NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 |  | 2018-05-05 16:41 | 2018-05-05 18:15 | -- | -- | -- | 0 | 0 | 0.065278 | 0 | N/A | N/A | N/A | NR/05/485 | LNCC | Line tripped on B-N fault caused by heavy wind and thunder storm . FLR Rampur: 5.1kA, 16kM.
[5 empty] | 2018-05-05 18:15 | 2018-05-06 00:35 | -- | -- | -- | 0.26389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/490 | OSPT | SD taken for rectification of sub conductor snapped in between location 37-38.
[5 empty] | 2018-05-09 15:20 | 2018-05-09 15:57 | -- | -- | -- | 0 | 0 | 0.025694 | 0 | N/A | N/A | N/A | NR/05/787 | LNCC | Line tripped due to thunderstorm at NJPC and DT receive at NJPC.
[5 empty] | 2018-05-09 15:57 | 2018-05-10 20:32 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:35 | N/A | N/A | N/A | NR/05/797 | OSPD | SD taken by NJPC for rectification of CB closing problem at Jhakri.
[5 empty] | 2018-05-11 14:42 | 2018-05-11 16:41 | -- | -- | -- | 0 | 0 | 0 | 0.082639 | N/A | N/A | N/A | NR/05/948 | OSPD | SD taken by NJPC for relay replacement work at Jhakhri.
[5 empty] | 2018-05-12 10:40 | 2018-05-12 18:25 | -- | -- | -- | 0.32292 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/997 | OSPT | SD taken for laying of new sub conductor which got snapped in span. 37-38
[5 empty] | 2018-05-28 13:30 | 2018-05-28 14:07 | -- | -- | -- | 0 | 0 | 0 | 0.025694 | N/A | N/A | N/A | NR/05/2404 | OSPD | SD taken by Naptha Jhakri for maintenance work at their end.
[10 empty] | 0.58681 | 0 | 0.090972 | 1899-12-31 07:11 | [7 empty] | 98.04
NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 |  | 2018-05-05 16:46 | 2018-05-05 17:25 | -- | -- | -- | 0 | 0 | 0.027083 | 0 | N/A | N/A | N/A | NR/05/485 | LNCC | Line tripped on Y-N fault caused by heavy wind and thunder storm. FLR Nalagarh: 123.88kM.
[5 empty] | 2018-05-11 16:22 | 2018-05-11 16:48 | -- | -- | -- | 0 | 0 | 0.018056 | 0 | N/A | N/A | N/A | NR/05/963 | LNCC | Line tripped on B-N fault caused by heavy wind & thunder storm.FLR Nalagarh: 86 Km & Rampur: 38Km.
[5 empty] | 2018-05-31 19:04 | 2018-05-31 19:30 | -- | -- | -- | 0 | 0 | 0.018056 | 0 | N/A | N/A | N/A | NR/05/2687 | LNCC | Line tripped on Y-B fault caused by heavy wind and thunder storm. FLR Nalagarh-122Km,IY-3.2 KA & IB-3.7 KA.
[10 empty] | 0 | 0 | 0.063194 | 0 | [7 empty] | 100
NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 |  | 2018-05-13 18:35 | 2018-05-14 11:12 | -- | -- | -- | 0 | 0.69236 | 0 | 0 | N/A | N/A | N/A | NR/05/1228 | OMSU | Line tripped on Y-N fault in Zone-II.FLR Panchkulla : 137kM, 3.454 kA (POWERGRID portion is up to 9kM from Panchkula).
[10 empty] | 0 | 0.69236 | 0 | 0 | [7 empty] | 100
NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 |  | 2018-05-12 20:58 | 2018-05-12 21:17 | -- | -- | -- | 0 | 0.013194 | 0 | 0 | N/A | N/A | N/A | NR/05/1049 | OMSU | Line A/R on B-N fault at Panchkulla & tripped at BBMB Dehar due to A/R problem at their end. Heavy winds and thunderstorm prevalent in the area.
[5 empty] | 2018-05-25 08:20 | 2018-05-26 15:19 | -- | -- | -- | 1899-12-31 06:59 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2133 | OSPT | SD taken to attend the hotspot on B-ph at tapping point of LILO.
[5 empty] | 2018-05-30 09:35 | 2018-05-30 14:13 | -- | -- | -- | 0.19306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2556 | OSPT | SD taken for safe working on multi circuit tower no. 5, to rectify damaged jumper of 400KV Patiala-Panchkulla-1.
[10 empty] | 1899-12-31 11:37 | 0.013194 | 0 | 0 | [7 empty] | 95.05
NR240089 | 400 KV Hisar - Moga - 2 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240090 | 400 KV Hisar - Moga - 3 | 206 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 |  | 2018-05-28 06:21 | 2018-05-28 06:21 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N fault. FLR Abdullapur :20.63 Km & Kurushetra : 27.50km, 8.7kA.
[5 empty] | 2018-05-29 07:25 | 2018-05-29 07:48 | -- | -- | -- | 0.015972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2460 | OSPT | SD taken for removing bird next at loc. 63.
[10 empty] | 0.015972 | 0 | 0 | 0 | [7 empty] | 99.95
NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 |  | 2018-05-02 17:29 | 2018-05-02 17:29 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on Y-N fault. FLR Kurukshtera: 136.2kM, 2.76KA.
[5 empty] | 2018-05-07 22:48 | 2018-05-08 00:41 | -- | -- | -- | 0 | 0 | 0.078472 | 0 | N/A | N/A | N/A | --- | LNCC | Line tripped on Y-N fault caused by heavy wind and thunder storm. FLR Kurukshetra: 124.7kM & Sonipat : 1.93kM.
[5 empty] | 2018-05-13 18:11 | 2018-05-14 11:33 | -- | -- | -- | 0 | 0 | 0 | 0.72361 | N/A | N/A | N/A | NR/05/1108 | LVRD | Line handtripped for voltage regulation. Kurukshetra :434kV.
[10 empty] | 0 | 0 | 0.078472 | 0.72361 | [7 empty] | 100
NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 |  | 2018-05-02 14:08 | 2018-05-02 15:00 | -- | -- | -- | 0.036111 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/116 | LEFT | Line tripped on R-N fault. FLR : Kurukshetra FL=126.4Km. Ir=3.6KA.
[5 empty] | 2018-05-02 16:42 | 2018-05-04 10:16 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 17:34 | N/A | N/A | N/A | NR/05/132 | LVRD | Line hand tripped for voltage regulation. Jalandhar = 426KV
[5 empty] | 2018-05-07 23:29 | 2018-05-08 09:43 | -- | -- | -- | 0 | 0 | 0 | 0.42639 | N/A | N/A | N/A | NR/05/642 | LVRD | Line handtripped for voltage regulation. Jalandhar :428kV.
[5 empty] | 2018-05-12 15:29 | 2018-05-12 15:29 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on B-N Fault.FLR Jalandhar : 52.8kM , 12.56kA.
[5 empty] | 2018-05-12 15:31 | 2018-05-12 15:56 | -- | -- | -- | 0.017361 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1020 | LEFT | Line tripped on Y-N fault, FLR Kurukshetra : 143kM , 2.3 kA. (Bad Weather)
[5 empty] | 2018-05-13 17:19 | 2018-05-14 14:37 | -- | -- | -- | 0 | 0 | 0 | 0.8875 | N/A | N/A | N/A | NR/05/1091 | LVRD | Line handtripped for voltage regulation. Kurukshetra :434kV.
[5 empty] | 2018-05-16 03:16 | 2018-05-16 10:48 | -- | -- | -- | 0 | 0 | 0 | 0.31389 | N/A | N/A | N/A | NR/05/1376 | LVRD | Line handtripped for voltage regulation. Jalandhar :426kV.
[10 empty] | 0.053472 | 0 | 0 | 1900-01-02 08:38 | [7 empty] | 99.82
NR240100 | 400KV Jalandhar-Nakodar | 42 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240101 | 400KV Kurukshetra-Nakodar | 234 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 |  | 2018-05-07 23:15 | 2018-05-08 00:40 | -- | -- | -- | 0 | 0 | 0.059028 | 0 | N/A | N/A | N/A | --- | LNCC | Line tripped on Y-N fault caused by heavy wind and thunder storm. FLR Kaithal : 153.6kM & Bhagpat: 4.2kM.
[5 empty] | 2018-05-13 18:22 | 2018-05-13 19:58 | -- | -- | -- | 0 | 0 | 0.066667 | 0 | N/A | N/A | N/A | NR/05/1142 | LNCC | Line tripped on Y-N fault caused by heavy wind and thunder storm. FLR Kaithal: 167kM, 2.5 kA.
[10 empty] | 0 | 0 | 0.12569 | 0 | [7 empty] | 100
NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 |  | 2018-05-25 09:56 | 2018-05-25 14:51 | -- | -- | -- | 0.20486 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2140 | OSPT | SD taken for replacement of Y ph LA due to THRC violation at Kaithal.
[10 empty] | 0.20486 | 0 | 0 | 0 | [7 empty] | 99.32
NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 |  | 2018-05-12 20:58 | 2018-05-12 21:34 | -- | -- | -- | 0 | 0 | 0.025 | 0 | N/A | N/A | N/A | NR/05/1050 | LNCC | Line tripped on R-B fault caused by heavy wind and thunder storm.FLR Patiala : 79kM, Ir=4.5kA ,Ib=4.5kA.
[5 empty] | 2018-05-29 09:14 | 2018-05-29 20:42 | -- | -- | -- | 0 | 0 | 0 | 0.47778 | N/A | N/A | N/A | NR/05/2472 | OSPD | SD taken by PSTCL for crossing 220KV Rajpura-Devigarh line.
[5 empty] | 2018-05-30 09:24 | 2018-05-30 14:08 | -- | -- | -- | 0.19722 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2556 | OSPT | SD taken for rectification of damaged jumper of top conductor at tower no. 5
[10 empty] | 0.19722 | 0 | 0.025 | 0.47778 | [7 empty] | 99.34
NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 |  | 2018-05-29 09:17 | 2018-05-29 20:49 | -- | -- | -- | 0 | 0 | 0 | 0.48056 | N/A | N/A | N/A | NR/05/2472 | OSPD | SD taken by PSTCL for crossing 220KV Rajpura-Devigarh line.
[10 empty] | 0 | 0 | 0 | 0.48056 | [7 empty] | 100
NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 |  | 2018-05-02 14:07 | 2018-05-02 15:02 | -- | -- | -- | 0 | 0 | 0.038194 | 0 | N/A | N/A | N/A | NR/05/119 | LNCC | Line tripped on R-N fault caused by heavy wind & thunder storm. FLR Patiala: FL=0Km & Patran: 58.4Km.
[5 empty] | 2018-05-03 15:24 | 2018-05-03 18:23 | -- | -- | -- | 0.12431 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/335 | OSPT | SD taken for install additional counter weights at tower no. 03 LILO portion of line in order to avoid swing of jumper.
[10 empty] | 0.12431 | 0 | 0.038194 | 0 | [7 empty] | 99.59
NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 |  | 2018-05-07 21:53 | 2018-05-07 22:45 | -- | -- | -- | 0 | 0 | 0.036111 | 0 | N/A | N/A | N/A | NR/05/636 | LNCC | Line tripped on Y-N fault caused by heavy wind and thunder storm. FLR Kaithal: 34.19kM & Patran: 11.5kM.
[10 empty] | 0 | 0 | 0.036111 | 0 | [7 empty] | 100
NR240112 | 400 KV Dehar (BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  | 2018-05-06 14:17 | 2018-05-06 16:46 | -- | -- | -- | 0.10347 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/529 | OSPT | SD taken for rectification of hanging dropper which got disconnected from BPI and LA at Rajpura
[10 empty] | 0.10347 | 0 | 0 | 0 | [7 empty] | 99.66
NR240113 | 400KV Bhiwani(BBMB) -Rajpura LILO PORTION | 14.4 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 |  | 2018-05-07 04:37 | 2018-05-07 09:40 | -- | -- | -- | 0 | 0 | 0 | 0.21042 | N/A | N/A | N/A | NR/05/577 | LVRD | Line handtripped for voltage regulation. Jalandhar :430kV.
[5 empty] | 2018-05-07 23:15 | 2018-05-08 07:42 | -- | -- | -- | 0 | 0 | 0 | 0.35208 | N/A | N/A | N/A | NR/05/640 | LVRD | Line handtripped for voltage regulation. Jalandhar :428kV.
[5 empty] | 2018-05-16 03:09 | 2018-05-16 06:47 | -- | -- | -- | 0 | 0 | 0 | 0.15139 | N/A | N/A | N/A | NR/05/1376 | LVRD | Line handtripped for voltage regulation. Jalandhar :426kV.
[10 empty] | 0 | 0 | 0 | 0.71389 | [7 empty] | 100
NR240116 | 400KV Dadri-Kaithal | 213 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240117 | 400 KV Kaithal Malerkotla | 135 | NR2 |  | 2018-05-27 00:01 | 2018-05-27 00:01 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on Y-N fault. FLR Dadri : 39.3 Km. & Kaithal : 159.1km, 2.278kA.
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 |  | 2018-05-12 18:15 | 2018-05-12 20:32 | -- | -- | -- | 0 | 0.095139 | 0 | 0 | N/A | N/A | N/A | NR/05/1034 | OMSU | Line A/R on R-N fault and tripped from Parbati 2 due to A/R problem at their end. FLR Banala : 14.4kM , 7.11kA.
[5 empty] | 2018-05-31 20:01 | 2018-05-31 20:46 | -- | -- | -- | 0 | 0.03125 | 0 | 0 | N/A | N/A | N/A | NR/05/2689 | OMSU | Line AR optd on R-N fault from Banala but tripped from Parbati-2 due to A/R problem at their end. FLR Banala:- 14.4 Km & 7.45 KA.
[10 empty] | 0 | 0.12639 | 0 | 0 | [7 empty] | 100
NR240119 | 400KV Parbati3-Sainj LILO portion | 9.403 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240122 | 400KV KURUKSHETRA - JIND - I | 103.6 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240123 | 400KV KURUKSHETRA - JIND - II | 103.6 | NR2 |  | 2018-05-02 14:55 | 2018-05-02 15:26 | -- | -- | -- | 0 | 0 | 0.021528 | 0 | N/A | N/A | N/A | NR/05/121 | LNCC | Line tripped on B-N fault caused by heavy wind & thunder storm. FLR Kurukshetra: 12.46km.
[5 empty] | 2018-05-03 01:28 | 2018-05-03 14:30 | -- | -- | -- | 0 | 0 | 0 | 0.54306 | N/A | N/A | N/A | NR/05/253 | LVRD | Line hand tripped for voltage regulation. Kurushetra = 430KV
[5 empty] | 2018-05-07 23:57 | 2018-05-08 07:46 | -- | -- | -- | 0 | 0 | 0 | 0.32569 | N/A | N/A | N/A | NR/05/649 | LVRD | Line handtripped for voltage regulation. Kurukshetra :428kV.
[5 empty] | 2018-05-13 18:13 | 2018-05-13 18:49 | -- | -- | -- | 0 | 0 | 0.025 | 0 | N/A | N/A | N/A | NR/05/1122 | LNCC | Line tripped on Y-N fault caused by heavy wind and thunder storm. FLR Kurukshetra : 15.59kM , 24kA.
[5 empty] | 2018-05-18 11:22 | 2018-05-18 19:10 | -- | -- | -- | 0.325 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1622 | OSPT | SD taken for replacement of flashed over insulators at loc. 40, 44 & 211.
[10 empty] | 0.325 | 0 | 0.046528 | 0.86875 | [7 empty] | 98.91
NR240124 | 400KV DULHASTI-KISHENPUR-II | 119.44 | NR2 |  | 2018-05-02 12:20 | 2018-05-02 12:20 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | --- | LART | Line A/R on Y-N fault. FLR Kishenpur: 32.87kM , 8.26KA
[5 empty] | 2018-05-24 11:09 | 2018-05-28 16:12 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 05:03 | N/A | N/A | N/A | NR/05/2061 | OSPD | SD taken by NHPC, Dulhasti for attending R -Phase CVT oil leakage at their end.
[10 empty] | 0 | 0 | 0 | 1900-01-03 05:03 | [7 empty] | 100
NR240125 | 400KV URI 1 - AMARGARH - I | 61.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240126 | 400KV AMARGARH - WAGOORA- I | 39.34 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240127 | 400KV URI 1 - AMARGARH - II | 61.95 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR240128 | 400KV AMARGARH - WAGOORA - II | 39.34 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 |  | 2018-05-02 16:49 | 2018-05-02 22:30 | -- | -- | -- | 0 | 0 | 0 | 0.23681 | N/A | N/A | N/A | NR/05/133 NLDC/78 | LVRD | Line hand tripped for voltage regulation. Moga = 802KV
[5 empty] | 2018-05-03 01:25 | 2018-05-03 14:46 | -- | -- | -- | 0 | 0 | 0 | 0.55625 | N/A | N/A | N/A | NR/05/252 NLDC/112 | LVRD | Line hand tripped for voltage regulation. Moga = 801KV
[5 empty] | 2018-05-06 05:17 | 2018-05-06 19:42 | -- | -- | -- | 0 | 0 | 0 | 0.60069 | N/A | N/A | N/A | NR/05/507 NLDC/252 | LVRD | Line handtripped for voltage regulation. Moga :795kV.
[5 empty] | 2018-05-08 00:53 | 2018-05-08 08:17 | -- | -- | -- | 0 | 0 | 0 | 0.30833 | N/A | N/A | N/A | NR/05/657 NLDC/320 | LVRD | Line handtripped for voltage regulation. Moga :798kV.
[5 empty] | 2018-05-10 06:36 | 2018-05-10 09:28 | -- | -- | -- | 0 | 0 | 0 | 0.11944 | N/A | N/A | N/A | NR/05/822 NLDC/404 | LVRD | Line handtripped for voltage regulation. Moga :793kV.
[5 empty] | 2018-05-13 17:27 | 2018-05-14 09:36 | -- | -- | -- | 0 | 0 | 0 | 0.67292 | N/A | N/A | N/A | NR/05/1095 NLDC/538 | LVRD | Line handtripped for voltage regulation. Moga :802kV.
[5 empty] | 2018-05-16 03:11 | 2018-05-16 06:24 | -- | -- | -- | 0 | 0 | 0 | 0.13403 | N/A | N/A | N/A | NR/05/1377 NLDC/652 | LVRD | Line handtripped for voltage regulation. Moga :804kV.
[5 empty] | 2018-05-09 04:25 | 2018-05-09 10:26 | -- | -- | -- | 0 | 0 | 0 | 0.25069 | N/A | N/A | N/A | NR/05/752 NLDC/353 | LVRD | Line handtripped for voltage regulation. Moga :803kV.
[10 empty] | 0 | 0 | 0 | 1900-01-01 21:06 | [7 empty] | 100
NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 |  | 2018-05-31 13:57 | 2018-05-31 14:10 | -- | -- | -- | 0 | 0 | 0 | 0.0090278 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped to keep open BR-2 on voltage regulation. Kishanpur=395KV.
[10 empty] | 0 | 0 | 0 | 0.0090278 | [7 empty] | 100
NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 |  | 2018-05-01 | 2018-05-03 00:08 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 00:08 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=394KV.
[5 empty] | 2018-05-03 19:46 | 2018-05-06 14:18 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 18:32 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=392KV.
[5 empty] | 2018-05-06 19:43 | 2018-05-07 02:16 | -- | -- | -- | 0 | 0 | 0 | 0.27292 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=394KV.
[5 empty] | 2018-05-07 19:17 | 2018-05-08 00:45 | -- | -- | -- | 0 | 0 | 0 | 0.22778 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=394KV.
[5 empty] | 2018-05-10 19:39 | 2018-06-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-20 04:21 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Wagoora=394KV.
[10 empty] | 0 | 0 | 0 | 1900-01-25 11:02 | [7 empty] | 100
NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 |  | 2018-05-29 15:20 | 2018-05-29 18:34 | -- | -- | -- | 0 | 0 | 0 | 0.13472 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Kaithal=395KV.
[10 empty] | 0 | 0 | 0 | 0.13472 | [7 empty] | 100
NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 |  | 2018-05-02 14:16 | 2018-05-03 00:56 | -- | -- | -- | 0.44444 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/246 | SRET | B/R tripped due to Differential Protection operated at Patiala.
[5 empty] | 2018-05-30 15:04 | 2018-05-30 18:09 | -- | -- | -- | 0 | 0 | 0 | 0.12847 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Patiala=395KV.
[10 empty] | 0.44444 | 0 | 0 | 0.12847 | [7 empty] | 98.52
NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 |  | 2018-05-03 04:20 | 2018-05-03 05:33 | -- | -- | -- | 0.050694 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/269 | SBBT | B/R tripped due to bus-2 protection operation at Chamba
[10 empty] | 0.050694 | 0 | 0 | 0 | [7 empty] | 99.83
NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 |  | 2018-05-31 13:57 | 2018-06-01 | -- | -- | -- | 0 | 0 | 0 | 0.41875 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Kishanpur=395KV.
[10 empty] | 0 | 0 | 0 | 0.41875 | [7 empty] | 100
NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 |  | 2018-05-23 14:11 | 2018-05-23 18:25 | -- | -- | -- | 0 | 0 | 0 | 0.17639 | N/A | N/A | N/A | NR/05/1999 NLDC/1039 | SVRD | B/R hand tripped for voltage regulation. Wagoora=725KV.
[10 empty] | 0 | 0 | 0 | 0.17639 | [7 empty] | 100
NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 |  | 2018-05-01 | 2018-06-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. New Wanpoh=393KV.
[10 empty] | 0 | 0 | 0 | 1900-01-30 | [7 empty] | 100
NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 |  | 2018-05-29 15:20 | 2018-05-29 18:34 | -- | -- | -- | 0 | 0 | 0 | 0.13472 | N/A | N/A | N/A | Standing Instruction | SVRD | B/R hand tripped for voltage regulation. Kaithal=395KV.
[10 empty] | 0 | 0 | 0 | 0.13472 | [7 empty] | 100
NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 |  | 2018-05-19 13:56 | 2018-05-20 11:10 | -- | -- | -- | 0 | 0.88472 | 0 | 0 | N/A | N/A | N/A | NR/05/1729 | OMSU | Reactor tripped due to fire in cables at BBMB Dehar.
[10 empty] | 0 | 0.88472 | 0 | 0 | [7 empty] | 100
NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 |  | 2018-05-19 13:56 | 2018-05-20 11:10 | -- | -- | -- | 0 | 0.88472 | 0 | 0 | N/A | N/A | N/A | NR/05/1729 | OMSU | Reactor tripped due to fire in cables at BBMB Dehar.
[10 empty] | 0 | 0.88472 | 0 | 0 | [7 empty] | 100
NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 |  | 2018-05-14 09:52 | 2018-05-18 23:07 | -- | -- | -- | 1900-01-03 13:15 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1218 | OSPT | SD taken for replacement of R-phase 400KV bushing on tan delta and DGA violation.
[10 empty] | 1900-01-03 13:15 | 0 | 0 | 0 | [7 empty] | 84.83
NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 |  | 2018-05-10 09:16 | 2018-05-10 17:30 | -- | -- | -- | 0.34306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/836 | OSPT | SD taken for replacement of LA (R & Y PH) in 220kv side.
[10 empty] | 0.34306 | 0 | 0 | 0 | [7 empty] | 98.86
NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 |  | 2018-05-18 09:24 | 2018-05-18 18:43 | -- | -- | -- | 0.38819 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1607 | OSPT | SD taken for AMP works.
[10 empty] | 0.38819 | 0 | 0 | 0 | [7 empty] | 98.71
NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 |  | 2018-05-02 14:17 | 2018-05-03 00:27 | -- | -- | -- | 0.42361 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/212 | SICT | ICT tripped due to OLTC Surge relay Operated on (Y-phase).
[10 empty] | 0.42361 | 0 | 0 | 0 | [7 empty] | 98.59
NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 |  | 2018-05-01 09:50 | 2018-05-01 18:25 | -- | -- | -- | 0.35764 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/16 | OSPT | SD taken for AMP works and Tertiary bushing insulation.
[5 empty] | 2018-05-31 11:26 | 2018-05-31 12:40 | -- | -- | -- | 0.051389 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2650 | OSPT | SD taken for takeing out B-phase unit for overhauling and spare unit into service.
[10 empty] | 0.40903 | 0 | 0 | 0 | [7 empty] | 98.64
NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 |  | 2018-05-02 09:40 | 2018-05-02 18:53 | -- | -- | -- | 0.38403 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/89 | OSPT | SD taken for AMP works and Tertiary bushing insulation.
[10 empty] | 0.38403 | 0 | 0 | 0 | [7 empty] | 98.72
NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 |  | 2018-05-03 11:29 | 2018-05-03 19:08 | -- | -- | -- | 0.31875 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/303 | OSPT | SD taken for AMP works and Tertiary bushing insulation.
[10 empty] | 0.31875 | 0 | 0 | 0 | [7 empty] | 98.94
NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 |  | 2018-05-01 10:02 | 2018-05-08 03:52 | -- | -- | -- | 1900-01-05 17:50 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/14 | OSPT | SD taken for replacament of 220KV Y ph bushing due to tan delta violation.
[10 empty] | 1900-01-05 17:50 | 0 | 0 | 0 | [7 empty] | 77.52
NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 |  | 2018-05-04 09:41 | 2018-05-04 18:53 | -- | -- | -- | 0.38333 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/389 | OSPT | SD taken for AMP works and Tertiary bushing insulation.
[10 empty] | 0.38333 | 0 | 0 | 0 | [7 empty] | 98.72
NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 |  | 2018-05-03 04:20 | 2018-05-03 05:48 | -- | -- | -- | 0.061111 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/269 | SBBT | ICT tripped due to bus-2 protection operation at Chamba
[10 empty] | 0.061111 | 0 | 0 | 0 | [7 empty] | 99.8
NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 |  | 2018-05-23 13:22 | 2018-05-23 14:25 | -- | -- | -- | 0.04375 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2001 NLDC/1037 | SICT | ICT tripped on Sudden Pressure Relay operation.
[5 empty] | 2018-05-28 07:00 | 2018-05-28 14:48 | -- | -- | -- | 0.325 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2221 NLDC/1159 | OSPT | SD taken for AMP Works
[10 empty] | 0.36875 | 0 | 0 | 0 | [7 empty] | 98.77
NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 |  | 2018-05-03 17:12 | 2018-05-03 19:34 | -- | -- | -- | 0.098611 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/370 | SICT | ICT tripped due to OLTC PRV relay Operated on (R-phase 765 kv side).
[5 empty] | 2018-05-05 10:21 | 2018-05-05 14:27 | -- | -- | -- | 0.17083 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/468 | SICT | ICT tripped due to OLTC PRV relay Operated on (R-phase 765 kv side).
[5 empty] | 2018-05-23 13:22 | 2018-05-23 14:21 | -- | -- | -- | 0.040972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2000 NLDC/1036 | SICT | ICT tripped on Sudden Pressure Relay operation.
[5 empty] | 2018-05-26 05:59 | 2018-05-26 14:55 | -- | -- | -- | 0.37222 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2221 NLDC/1159 | OSPT | SD taken for AMP Works
[10 empty] | 0.68264 | 0 | 0 | 0 | [7 empty] | 97.72
NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 |  | 2018-05-30 10:42 | 2018-05-30 16:57 | -- | -- | -- | 0 | 0 | 0 | 0.26042 | N/A | N/A | N/A | NR/05/2558 | OSPD | SD taken by HVPNL for rectification of damaged B-phase conductor of 220KV Abdullapur-Tepla Line-1 terminating at Abdullapur. Right below the Tepla-1 line gantry, there is bay of ICT-IV. Earlier Tepla-1 was terminated on the same bay of ICT-IV but later shifted to other bay but termination on the gantry is same as earlier and just above the ICT-IV bay.
[10 empty] | 0 | 0 | 0 | 0.26042 | [7 empty] | 100
NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 |  | 2018-05-28 16:31 | 2018-05-28 16:55 | -- | -- | -- | 0.016667 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2420 | OSPT | SD taken for oil sampling of 220KV side R-phase CT for DGA testing.
[5 empty] | 2018-05-31 11:46 | 2018-05-31 16:48 | -- | -- | -- | 0.20972 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2652 | OSPT | SD taken for replacement of 220KV R-phase CT due to DGA Violation
[10 empty] | 0.22639 | 0 | 0 | 0 | [7 empty] | 99.25
NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 |  | 2018-05-30 11:33 | 2018-05-30 12:29 | -- | -- | -- | 0.038889 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2568 | OSPT | SD taken for oil sampling of 220KV side CT for DGA testing.
[10 empty] | 0.038889 | 0 | 0 | 0 | [7 empty] | 99.87
NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 |  | 2018-05-19 13:57 | 2018-05-19 14:52 | -- | -- | -- | 0 | 0.038194 | 0 | 0 | N/A | N/A | N/A | NR/05/1703 | OMSU | ICT tripped due to fire in cables at BBMB Dehar.
[10 empty] | 0 | 0.038194 | 0 | 0 | [7 empty] | 100
NR2ICT73 | KAITHAL 315MVA ICT-III | 315 | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A
[10 empty] | 0 | 0 | 0 | 0 | [7 empty] | 100
NR2SVC02 | NEW WANPOH -200/+300 MVAR SVC |  | NR2 |  | 2018-05-29 13:43 | 2018-05-29 21:34 | -- | -- | -- | 0.32708 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2495 | OSPT | SD taken for SPR (Sudden Pressure Relay) replacement of coupling transformer.
[10 empty] | 0.32708 | 0 | 0 | 0 | [7 empty] | 98.91
NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 |  | 2018-05-05 13:14 | 2018-05-05 16:28 | -- | -- | -- | 0.13472 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC-234 | OMST | Pole blocked due to external block operated at Champa.
[5 empty] | 2018-05-07 04:22 | 2018-05-07 04:56 | -- | -- | -- | 0.023611 | 0 | 0 | 0 | N/A | N/A | N/A | NL/05/287 | OMST | Pole blocked due to MRLDP protection(Metallic return Line Differential Protection) operated.
[5 empty] | 2018-05-09 19:13 | 2018-05-09 20:28 | -- | -- | -- | 0.052083 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/393 | OMST | POLE blocked due to CLD protection operated.
[5 empty] | 2018-05-13 16:47 | 2018-05-13 18:24 | -- | -- | -- | 0.067361 | 0 | 0 | 0 | N/A | N/A | N/A | NL/544 | OMST | POLE blocked due to DMR short circuit fault.
[5 empty] | 2018-05-17 05:10 | 2018-05-17 08:50 | -- | -- | -- | 0.15278 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1501 NLDC/728 | OSPT | SD taken to attend the hanging earth wire which slipped & fell on the cross arm and creating fault at Loc No: 3216.
[5 empty] | 2018-05-18 06:39 | 2018-05-18 07:43 | -- | -- | -- | 0.044444 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1595 NLDC/780 | OMST | Pole blocked due to FILTER POWER LIMIT protection operated at Champa.
[5 empty] | 2018-05-19 21:47 | 2018-05-19 23:14 | -- | -- | -- | 0.060417 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1741 NLDC/858 | OMST | Pole blocked due to CONVERTOR DIFFERENTIAL protection operated at Kurushetra.
[5 empty] | 2018-05-21 10:49 | 2018-05-22 02:52 | -- | -- | -- | 0.66875 | 0 | 0 | 0 | N/A | N/A | N/A | NL/05/936 | OMST | Pole blocked due to external block at Champa
[5 empty] | 2018-05-24 17:19 | 2018-05-24 18:05 | -- | -- | -- | 0.031944 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/1092 | OMST | Pole blocked due to CLD in DMR2 operated during blocking of Pole-II.
[5 empty] | 2018-05-25 17:19 | 2018-05-25 17:54 | -- | -- | -- | 0.024306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2184 NLDC/1135 WRLDC/2376 | OMST | POLE blocked due to CLD protection operated.
[5 empty] | 2018-05-31 16:51 | 2018-05-31 23:19 | -- | -- | -- | 0.26944 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/2672 WR/05/2989 NL/05/1450 | OSPT | POLE SD taken for the rectification of gas leakage in Voltage divider at Kurushetra.
[10 empty] | 1899-12-31 12:43 | 0 | 0 | 0 | [7 empty] | 95.06
NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 |  | 2018-05-02 22:17 | 2018-05-03 00:05 | -- | -- | -- | 0.075 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC-99 | OMST | Pole-II blocked due to cable Longitudanal differerntail protection opearted at Champa end.
[5 empty] | 2018-05-04 18:40 | 2018-05-04 19:40 | -- | -- | -- | 0.041667 | 0 | 0 | 0 | N/A | N/A | N/A | NL/05/200 | OMST | Pole-II blocked due to external block at Champa
[5 empty] | 2018-05-05 13:14 | 2018-05-05 20:04 | -- | -- | -- | 0.28472 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC-239 | OMST | Pole blocked due to external block at Champa
[5 empty] | 2018-05-06 16:26 | 2018-05-06 17:19 | -- | -- | -- | 0.036806 | 0 | 0 | 0 | N/A | N/A | N/A | NL/05/265 | OMST | Pole-II blocked due to DC line fault.
[5 empty] | 2018-05-07 04:22 | 2018-05-07 04:47 | -- | -- | -- | 0.017361 | 0 | 0 | 0 | N/A | N/A | N/A | NL/05/288 | OMST | Pole blocked due to MRLDP protection(Metallic return Line Differential Protection) operated.
[5 empty] | 2018-05-09 19:11 | 2018-05-09 20:53 | -- | -- | -- | 0.070833 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/394 | OMST | POLE blocked due to CLD protection operated.
[5 empty] | 2018-05-13 16:21 | 2018-05-13 17:01 | -- | -- | -- | 0.027778 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1083 NL/536 WR/1175 | OMST | POLE blocked due to CLD protection operated.
[5 empty] | 2018-05-17 05:10 | 2018-05-17 08:43 | -- | -- | -- | 0.14792 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1500 NL/727 | OSPT | SD taken to attend the hanging earth wire which slipped & fell on the cross arm and creating fault at Loc No: 3216.
[5 empty] | 2018-05-18 06:39 | 2018-05-18 07:44 | -- | -- | -- | 0.045139 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1596 NLDC/781 | OMST | Pole blocked due to FILTER POWER LIMIT protection operated at Champa.
[5 empty] | 2018-05-19 21:47 | 2018-05-19 22:22 | -- | -- | -- | 0.024306 | 0 | 0 | 0 | N/A | N/A | N/A | NR/05/1741 NLDC/859 | OMST | Pole blocked due to external block at Champa
[5 empty] | 2018-05-21 13:17 | 2018-05-21 14:00 | -- | -- | -- | 0.029861 | 0 | 0 | 0 | N/A | N/A | N/A | NL/05/912 | OMST | Pole blocked due to problem at Champa
[5 empty] | 2018-05-24 17:19 | 2018-05-24 18:18 | -- | -- | -- | 0.040972 | 0 | 0 | 0 | N/A | N/A | N/A | NLDC/1093 | OMST | Pole blocked due to DC Line fault due to bad weather / heavy thunderstorm.
[10 empty] | 0.84236 | 0 | 0 | 0 | [7 empty] | 97.28
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUM(K7:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM(L7:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = IF(RIGHT([NRLDC Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = IF(RIGHT([Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM(N31:[Deemed Available, row above])