## Sheet2 (2)
Standard of Performance data for the month of MAY - 2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - II
ANNEXURE-A
Sr. No. | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | NR213201 | 132 KV Sewa-II - Hiranagar ckt-II | 78.48 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:14 | -- | -- | -- | 0.032639 | 0 | 0 | 0 |  |  |  | Line load become zero due to tripping disturbance of Hiranagar Samba caused by bus-2 tripping at Samba. There was no fault & tripping on the line. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.032639 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.89
2 | NR213202 | 132 KV Sewa-II - Mahanpur ckt-II | 31.25 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:14 | -- | -- | -- | 0.032639 | 0 | 0 | 0 |  |  |  | Line load become zero due to tripping disturbance of Hiranagar Samba caused by bus-2 tripping at Samba. There was no fault & tripping on the line. | NRPC
[6 empty] | 2019-05-27 | 14:06 | 2019-05-27 | 14:46 |  |  |  | 0 | 0.027778 | 0 | 0 |  |  |  | Line tripped on R-N fault in Zone-3 from NHPC SEWA-2 due to non-opening of CBs on JKPDD on Mahanpur onwards. CB remained closed at JKPDD Mahanpur. FLR Sewa-2: 113.9Km, 235.1Amp , Zone-3. Total line length=31.2Km and fault locator detail on mail received from NHPC is enclosed. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.032639 | 0.027778 | 0 | 0 |  |  |  |  | NRPC | 99.89
3 | NR213203 | 132 KV Sewa-II - Hiranagar ckt-I | 78.48 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:14 | -- | -- | -- | 0.032639 | 0 | 0 | 0 |  |  |  | Line load become zero due to tripping disturbance of Hiranagar Samba caused by bus-2 tripping at Samba. There was no fault & tripping on the line. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.032639 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.89
4 | NR213204 | 132kV S/C Mahanpur - Kathua | 21.5 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
5 | NR213205 | 132kV S/C Sewa -II - Kathua | 53 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:14 | -- | -- | -- | 0.032639 | 0 | 0 | 0 |  |  |  | Line load become zero due to tripping disturbance of Hiranagar Samba caused by bus-2 tripping at Samba. There was no fault & tripping on the line. | NRPC
[6 empty] | 2019-05-27 | 14:06 | 2019-05-27 | 14:47 |  |  |  | 0 | 0.028472 | 0 | 0 |  |  |  | Line tripped on R-N fault in Zone-3 from NHPC SEWA-2 due to non-opening of CBs on JKPDD on Mahanpur onwards. CB remained closed at JKPDD Mahanpur. FLR Sewa-2 : 82.14Km, 216.2Amp , Zone-3. Total line length=53 Km and fault locator detail on mail received from NHPC is enclosed. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.032639 | 0.028472 | 0 | 0 |  |  |  |  | NRPC | 99.89
6 | NR222001 | 220KV Berasuil-Jessore | 59.12 | NR2 | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 |  |  |  | SD taken by NHPC Bairasiul power station for renovation work. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-30 |  |  |  |  | NRPC | 100
7 | NR222002 | 220KV Berasuil-Pong | 96.82 | NR2 | -- | 2019-05-01 | 0:00 | 2019-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 |  |  |  | SD taken by NHPC Bairasiul power station for renovation work. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-30 |  |  |  |  | NRPC | 100
8 | NR222003 | 220KV Hiranagar-Sarna | 45.29 | NR2 | -- | 2019-05-05 | 9:48 | 2019-05-05 | 12:40 | -- | -- | -- | 0.11944 | 0 | 0 | 0 |  |  |  | SD taken by PSTCL to attend hot spot in R-phase Wave Trap at Sarna. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.11944 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.61
9 | NR222006 | 220KV Jallandhar-Dasuya-I | 49.74 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
10 | NR222007 | 220KV Jallandhar-Dasuya-II | 49.74 | NR2 | -- | 2019-05-10 | 10:26 | 2019-05-10 | 12:35 | -- | -- | -- | 0.089583 | 0 | 0 | 0 |  |  |  | Emergency SD taken by PSTCL to attend hot point on lower side of breaker R phase. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.089583 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.71
11 | NR222011 | 220KV Jessore-Pong | 37.7 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
12 | NR222012 | 220KV Kishenpur-Sarna-I | 103.64 | NR2 | -- | 2019-05-04 | 10:41 | 2019-05-04 | 11:02 | -- | -- | -- | 0 | 0.014583 | 0 | 0 |  |  |  | Line tripped from Kishenpur only due to non-opening of CB at PSTCL Sarna for fault on Sarna-Vadala (PSTCL Line). Mail received from PSTCL is enclosed. FLR Kishenpur : 130.4kM , 1.04kA. Line length : 103.6kM. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.014583 | 0 | 0 |  |  |  |  | NRPC | 100
13 | NR222013 | 220KV Kishenpur-Sarna-II | 103.64 | NR2 | -- | 2019-05-04 | 10:41 | 2019-05-04 | 11:02 | -- | -- | -- | 0 | 0.014583 | 0 | 0 |  |  |  | Line tripped from Kishenpur only due to non-opening of CB at PSTCL Sarna for fault on Sarna-Vadala (PSTCL Line). Mail received from PSTCL is enclosed. FLR Kishenpur : 153.4kM , 1.04kA. Line length : 103.6kM. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.014583 | 0 | 0 |  |  |  |  | NRPC | 100
14 | NR222014 | 220KV KISHENPUR-UDHAMPUR-I | 22.04 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
15 | NR222015 | 220KV KISHENPUR-UDHAMPUR-II | 22.04 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
16 | NR222016 | 220KV SALAL-JAMMU-I | 56.33 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
17 | NR222017 | 220KV SALAL-JAMMU-II | 62.42 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
18 | NR222018 | 220KV SALAL-KISHENPUR-I | 56.8 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
19 | NR222019 | 220KV SALAL-KISHENPUR-II | 56.8 | NR2 | -- | 2019-05-27 | 15:03 | 2019-05-27 | 15:36 | -- | -- | -- | 0.022917 | 0 | 0 | 0 |  |  |  | Line tripped on B-N fault. FLR Kishenpur: B-N, 46.23Km, 1.55KA. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.022917 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.92
20 | NR222020 | 220KV SALAL-KISHENPUR-III | 58.7 | NR2 | -- | 2019-05-14 | 22:55 | 2019-05-14 | 23:02 | -- | -- | -- | 0.0048611 | 0 | 0 | 0 |  |  |  | Line tripped on R-Y fault caused by heavy Thunderstorm and wind.FLR kishenpur :-53km, 2.3KA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.0048611 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.98
21 | NR222021 | 220KV SALAL-KISHENPUR-IV | 58.7 | NR2 | -- | 2019-05-14 | 22:55 | 2019-05-14 | 23:00 | -- | -- | -- | 0.0034722 | 0 | 0 | 0 |  |  |  | Line tripped on R-Y Fault caused by heavy Thunderstorm. FLR kishenpur :- 67.5km, Ir=1.7KA, Iy=2KA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.0034722 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.98
22 | NR222022 | 220KV SARNA-DASUYA-I | 53.07 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
23 | NR222023 | 220KV SARNA-DASUYA-II | 53.07 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
24 | NR222024 | 220KV WAGOORA-PAMPORE-I | 10.29 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
25 | NR222025 | 220KV WAGOORA-PAMPORE-II | 10.29 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
26 | NR222026 | 220KV Chamera-III - Chamba - I | 14.95 | NR2 | -- | 2019-05-14 | 11:56 | 2019-05-14 | 12:45 | -- | -- | -- | 0 | 0.034028 | 0 | 0 |  |  |  | Line tripped from Chamera3 only during SD of 220KV Bus-2 at Chamera3 NHPC. CB remain closed from Chamba and there was no fault on the line. | NRPC
[6 empty] | 2019-05-24 | 8:35 | 2019-05-25 | 19:57 |  |  |  | 1899-12-31 11:22 | 0 | 0 | 0 |  |  |  | SD taken for shifting of damaged tower to ERS at Loc. No. 25. The tower got damaged due to slide of soil mass. | NRPC
[6 empty] | 2019-05-26 | 8:20 | 2019-05-26 | 20:03 |  |  |  | 0.48819 | 0 | 0 | 0 |  |  |  | SD taken for shifting of damaged tower to ERS at Loc. No. 25. The tower got damaged due to slide of soil mass. | NRPC
[6 empty] | 2019-05-27 | 10:50 | 2019-05-27 | 16:47 |  |  |  | 0.24792 | 0 | 0 | 0 |  |  |  | SD taken for shifting of damaged tower to ERS at Loc. No. 25. The tower got damaged due to slide of soil mass. | NRPC
[6 empty] | 2019-05-29 | 13:42 | 2019-05-29 | 14:55 |  |  |  | 0.050694 | 0 | 0 | 0 |  |  |  | Line tripped due to falling of damaged tower on conductors between span of location no. 24 & ERS. Conductors were shifted from damaged tower to ERS. | NRPC
[6 empty] | 2019-05-29 | 14:55 | 2019-05-30 | 22:25 |  |  |  | 1899-12-31 07:30 | 0 | 0 | 0 |  |  |  | SD taken for rectification of damaged conductor at Loc 24-25 caused by falling of damaged tower at location 25. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 1900-01-02 13:45 | 0.034028 | 0 | 0 |  |  |  |  | NRPC | 88.47
27 | NR222027 | 220KV Chamera-III - Chamba -II | 14.95 | NR2 | -- | 2019-05-14 | 11:56 | 2019-05-14 | 16:53 | -- | -- | -- | 0 | 0.20625 | 0 | 0 |  |  |  | Line tripped from Chamera3 only during SD of 220KV Bus-2 at Chamera3 NHPC. CB remain closed from Chamba and there was no fault on the line. | NRPC
[6 empty] | 2019-05-14 | 16:53 | 2019-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 1900-01-16 07:07 |  |  |  | Line taken under SD by NHPC Chamera3 for rectification of GIS CB at their end. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.20625 | 0 | 1900-01-16 07:07 |  |  |  |  | NRPC | 100
28 | NR222029 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-I | 9.5 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
29 | NR222031 | 220KV Hamirpur(PG)-Hamirpur(HPSEB)-II | 9.5 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
30 | NR222032 | 220KV Jammu-Samba | 60.93 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:17 | -- | -- | -- | 0.034722 | 0 | 0 | 0 |  |  |  | Line tripped at Samba on tripping of 220 kV bus-2 caused by droping of bird nest. | NRPC
[6 empty] | 2019-05-29 | 13:27 | 2019-05-29 | 14:21 |  |  |  | 0.0375 | 0 | 0 | 0 |  |  |  | Line tripped on R-N fault.FLR Samba : 39.84kM , | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.072222 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.76
31 | NR222033 | 220kV Samba-Hiranagar | 14.037 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:13 | -- | -- | -- | 0.031944 | 0 | 0 | 0 |  |  |  | Line tripped at Samba on tripping of 220 kV bus-2 caused by droping of bird nest. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.031944 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.89
32 | NR222034 | 220KV KISHANGANGA(NHPC)-DELINA(JKPDD)-I | 41.62 | NR2 | -- | 2019-05-04 | 15:30 | 2019-05-04 | 17:00 | -- | -- | -- | 0 | 0 | 0 | 0.0625 |  |  |  | SD taken by JK PDD to replace the damaged conductor between wavetrap and CT at Delina (JKPDD). | NRPC
[6 empty] | 2019-05-13 | 17:56 | 2019-05-13 | 19:09 |  |  |  | 0 | 0.050694 | 0 | 0 |  |  |  | Line tripped from Amargarh (JKPDD Deline) only and remained closed fron NHPC Kishenganga. | NRPC
[6 empty] | 2019-05-26 | 17:50 | 2019-05-26 | 19:41 |  |  |  | 0 | 0.077083 | 0 | 0 |  |  |  | Line tripped due to fault of 220KV Delina-zainakote line of JKPDD as a result of non-opening of CB at JKPDD end. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.12778 | 0 | 0.0625 |  |  |  |  | NRPC | 100
33 | NR222035 | 220KV KISHANGANGA(NHPC)-DELINA(JKPDD)-II | 41.62 | NR2 | -- | 2019-05-04 | 17:04 | 2019-05-04 | 19:47 | -- | -- | -- | 0 | 0 | 0 | 0.11319 |  |  |  | SD taken by JK PDD to replace the damaged conductor between wavetrap and CT at Delina (JKPDD). | NRPC
[6 empty] | 2019-05-13 | 17:56 | 2019-05-13 | 19:27 |  |  |  | 0.063194 | 0 | 0 | 0 |  |  |  | Line tripped on R-Y fault. FLR Delina : Z1 fault 15.60km , Ir= 2.13 kA , Iy= 1.985kA. | NRPC
[6 empty] | 2019-05-26 | 17:50 | 2019-05-26 | 19:41 |  |  |  | 0 | 0.077083 | 0 | 0 |  |  |  | Line tripped due to fault of 220KV Delina-zainakote line of JKPDD as a result of non-opening of CB at JKPDD end. | NRPC
[6 empty] | 2019-05-31 | 16:22 | 2019-05-31 | 16:32 |  |  |  | 0 | 0 | 0 | 0.0069444 |  |  |  | SD taken by NHPC for shifting of Line from Bus-2 to Bus1 at Kishanganga. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.063194 | 0.077083 | 0 | 0.12014 |  |  |  |  | NRPC | 99.79
34 | NR222036 | 220KV JALANDHAR-NEHRIAN (HPSEB)-I | 72.93 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
35 | NR222037 | 220KV JALANDHAR-NEHRIAN (HPSEB)-II | 72.93 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
36 | NR222038 | 220KV HAMIRPUR-NEHRIAN (HPSEB)-I | 55.4 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
37 | NR222039 | 220KV HAMIRPUR-NEHRIAN (HPSEB)-II | 55.4 | NR2 | -- | [7 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
38 | NR240001 | 400KV Abdullapur-Bawana-I | 166.64 | NR2 | -- | 2019-05-15 | 7:44 | 2019-05-15 | 10:21 | -- | -- | -- | 0 | 0.10903 | 0 | 0 |  |  |  | Line tripped on Y-N Fault in Zone-2 caused by snapping & swinging of jumper of ICT at DTL Bhawana. FLR Abdullapur:- FL=188km, Iy=2.25kA. Line length is 166 kms. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.10903 | 0 | 0 |  |  |  |  | NRPC | 100
39 | NR240005 | 400KV Amritsar-Jalandhar | 59.71 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
40 | NR240008 | 400KV Chamera-I-Chamera-II | 36.16 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
41 | NR240009 | 400KV Chamera-II-Kishenpur | 134.81 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
42 | NR240010 | 400KV Chamera-Jallandhar-I | 152.05 | NR2 | -- | 2019-05-04 | 15:37 | 2019-05-04 | 15:50 | -- | -- | -- | 0 | 0 | 0 | 0.0090278 |  |  |  | SD talen by NHPC for shifting of line from Bus-2 to Bus-1 at Chamera1 end. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.0090278 |  |  |  |  | NRPC | 100
43 | NR240011 | 400KV Chamera-Jallandhar-II | 152.05 | NR2 | -- | 2019-05-06 | 14:05 | 2019-05-06 | 17:02 | -- | -- | -- | 0 | 0.12292 | 0 | 0 |  |  |  | Line tripped on B-N fault caused by heavy smoke and flames generated by burning of agriculture waste. FLR Jalandhar : 6.6kM, 18kA & Chamera1 : 172Km, 4.4KA. | NRPC
[6 empty] | 2019-05-08 | 16:07 | 2019-05-08 | 18:41 |  |  |  | 0 | 0.10694 | 0 | 0 |  |  |  | Line tripped on B-N fault caused by heavy smoke and flames generated by burning of agriculture waste. FLR Jalandhar : 26.10kM, 10.03kA & Chamera1 : 137Km, 4.4KA. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.22986 | 0 | 0 |  |  |  |  | NRPC | 100
44 | NR240013 | 400KV Dulhasti-Kishenpur | 119.72 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
45 | NR240018 | 400KV Jallandhar-Moga-I | 85.15 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
46 | NR240019 | 400KV Jallandhar-Moga-II | 85.15 | NR2 | -- | 2019-05-23 | 6:18 | 2019-05-23 | 6:37 | -- | -- | -- | 0.013194 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault. FLR Moga:- 26.588 Km , 10.933 KA. Jalandhar:-59.460 Km, 5.82 KA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.013194 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.95
47 | NR240023 | 400KV Malerkotla-Patiala | 62.48 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
48 | NR240024 | 400KV Moga-Hissar-I | 209.39 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
49 | NR240025 | 400KV Moga-Fatehabad | 179.281 | NR2 | -- | 2019-05-16 | 16:16 | 2019-05-16 | 16:22 | -- | -- | -- | 0.0041667 | 0 | 0 | 0 |  |  |  | SD taken for taking out the LR for arresting oil leakage from Bucholz relay. | NRPC
[6 empty] | 2019-05-16 | 18:21 | 2019-05-16 | 18:26 |  |  |  | 0.0034722 | 0 | 0 | 0 |  |  |  | SD taken for taking in the LR after arresting oil leakage. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.0076389 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.97
50 | NR240027 | 400KV Nalagarh-Patiala-II | 93.78 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
51 | NR240032 | 800KV KISHENPUR-MOGA-I | 275.38 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
52 | NR240033 | 800KV KISHENPUR-MOGA-II | 287.12 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
53 | NR240034 | 400KV JALANDHAR - LUDHIANA | 84.77 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
54 | NR240035 | 400KV LUDHIANA - MALERKOTLA | 35.735 | NR2 | -- | 2019-05-14 | 2:39 | 2019-05-14 | 3:58 | -- | -- | -- | 0.054861 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault.FLR Ludhiana-2.48 Km,21.246 KA & Malerkotla : 33.5 Km,9.95 KA | NRPC
[6 empty] | 2019-05-19 | 21:42 | 2019-05-19 | 22:47 |  |  |  | 0.045139 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault. FLR Ludhiana: 26kM, 9.3kA & Malerkotla: 5.5kM, 14.8kA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.1 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.67
55 | NR240046 | 400kV Nalagarh-Patiala-I | 93.78 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
56 | NR240048 | 400kV Ludhiana - Patiala -I | 78 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
57 | NR240049 | 400kV Ludhiana - Patiala -II | 78 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
58 | NR240050 | 400kV Chamera-II - Chamba | 0.375 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
59 | NR240051 | 400kV Uri-II - Wagoora | 105 | NR2 | -- | 2019-05-19 | 21:00 | 2019-05-19 | 22:38 | -- | -- | -- | 0.068056 | 0 | 0 | 0 |  |  |  | Line tripped on R-N fault. FLR Wagoora: 71.7kM, 4.172kA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.068056 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.78
60 | NR240052 | 400kV Uri-I - Uri-II | 10.45 | NR2 | -- | 2019-05-19 | 20:45 | 2019-05-20 | 8:39 | -- | -- | -- | 0.49583 | 0 | 0 | 0 |  |  |  | Line tripped due to breaking of R-phase conductor caused by heavy storm in that area. | NRPC
[6 empty] | 2019-05-20 | 8:39 | 2019-05-21 | 15:45 |  |  |  | 1899-12-31 07:06 | 0 | 0 | 0 |  |  |  | Line SD taken for rectification of broken conductor. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 1899-12-31 19:00 | 0 | 0 | 0 |  |  |  |  | NRPC | 94.22
61 | NR240053 | 400KV Nalagarh-Banala | 47.264 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
62 | NR240054 | 400kV Nalagarh - Koldam Line-2 | 46.381 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
63 | NR240055 | 400kV Abdullapur - Panchkula Circuit -I | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
64 | NR240056 | 400kV Abdullapur - Panchkula Circuit -II | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
65 | NR240057 | 400kV Panchkula - Nathpajhakri -I | 165 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
66 | NR240058 | 400kV Panchkula - Nathpajhakri -II | 165 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
67 | NR240062 | 400kV Abdullapur - Depalpur LILO point | 140.547 | NR2 | -- | 2019-05-10 | 9:10 | 2019-05-10 | 15:28 | -- | -- | -- | 0 | 0 | 0 | 0.2625 |  |  |  | SD taken by HVPNL to replace porcelain insulator by polymer. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.2625 |  |  |  |  | NRPC | 100
68 | NR240063 | 400kV Depalpur LILO point - Bawana-II | 26.095 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
69 | NR240064 | 400kV Jalandhar-Chamba (GIS)-I | 162 | NR2 | -- | 2019-05-07 | 14:02 | 2019-05-07 | 20:02 | -- | -- | -- | 0.25 | 0 | 0 | 0 |  |  |  | SD taken for rectification of B-ph jumper at Loc No 232. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.25 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.19
70 | NR240065 | 400kV Jalandhar-Chamba (GIS)-II | 162 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
71 | NR240066 | 400KV Kishenpur-Samba-I | 34.819 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
72 | NR240067 | 400KV Kishenpur-Samba-II | 34.819 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
73 | NR240070 | 400 kV Amritsar-Banala-I | 250.53 | NR2 | -- | 2019-05-05 | 9:19 | 2019-05-05 | 10:06 | -- | -- | -- | 0.032639 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault. FLR Amritsar: 47.33Km, 6.5kA & Banala: 245.6Km, 2.6kA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.032639 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.89
74 | NR240072 | 400KV Parbati3-Banala -I | 3.114 | NR2 | -- | 2019-05-01 | 10:23 | 2019-05-01 | 14:46 | -- | -- | -- | 0 | 0 | 0 | 0.18264 |  |  |  | SD taken by Parbati-3 for replacing faulty R-Phase CB Pole of Unit # 4 with spare one. | NRPC
[6 empty] | 2019-05-06 | 10:12 | 2019-05-06 | 20:43 |  |  |  | 0.43819 | 0 | 0 | 0 |  |  |  | SD taken for rectification of insulator at Loc No 3. | NRPC
75 | [5 empty] | Sub Total --> | [6 empty] | 0.43819 | 0 | 0 | 0.18264 |  |  |  |  | NRPC | 98.58
| NR240073 | 400kV Wagoora-Wanpoh Ckt-I | 57 | NR2 | -- | 2019-05-19 | 22:21 | 2019-05-19 | 22:50 | -- | -- | -- | 0.020139 | 0 | 0 | 0 |  |  |  | Line tripped on Y-B fault. FLR Wagoora: 0.391kM,5.2kA, New Wanpoh: 56.83kM,3.1kA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.020139 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.93
76 | NR240074 | 400kV Wagoora-Wanpoh Ckt-II | 57 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
77 | NR240075 | 400kV Kishenpur-Wanpoh Ckt-I | 129.76 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
78 | NR240076 | 400kV Kishenpur-Wanpoh Ckt-II | 130.25 | NR2 | -- | 2019-05-07 | 12:16 | 2019-05-07 | 20:26 | -- | -- | -- | 0.34028 | 0 | 0 | 0 |  |  |  | SD taken for installation of insulation sleeve on the conductor to avoid tripping on hill side. | NRPC
[6 empty] | 2019-05-07 | 20:31 | 2019-05-07 | 20:53 |  |  |  | 0.015278 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault, FLR New Wanpoh12.44kM , 4.9kA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.35556 | 0 | 0 | 0 |  |  |  |  | NRPC | 98.85
79 | NR240078 | 400kV Hamirpur-Banala | 77 | NR2 | -- | 2019-05-05 | 10:56 | 2019-05-05 | 10:56 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | Line A/R on R-N fault .FLR Hamirpur: 76.58Km, 3.4kA & Banala: 0.72Km, 9.02kA | NRPC
[6 empty] | 2019-05-06 | 10:15 | 2019-05-06 | 20:03 |  |  |  | 0.40833 | 0 | 0 | 0 |  |  |  | SD taken for rectification of insulator at Loc No 3. | NRPC
[6 empty] | 2019-05-21 | 8:53 | 2019-05-21 | 8:53 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault. FLR Banala : 55.2kM , 4.32kA & Hamirpur : 22.2kM , 3.96kA. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.40833 | 0 | 0 | 0 |  |  |  |  | NRPC | 98.68
80 | NR240079 | 400KV Napthajhakri-Rampur-I | 20.519 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
81 | NR240080 | 400KV Rampur-Nalagarh-I | 126.481 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
82 | NR240082 | 400 KV (Koldam-Banala)- PGCIL portion | 0.884 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
83 | NR240083 | 400KV Napthajhakri-Rampur-II | 20.519 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
84 | NR240084 | 400KV Rampur-Nalagarh-II | 126.481 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
85 | NR240085 | 400 KV PANIPAT-PANCHKULLA LINE (LILO Portion) | 155 | NR2 | -- | 2019-05-20 | 14:49 | 2019-05-20 | 17:31 | -- | -- | -- | 0 | 0 | 0 | 0.1125 |  |  |  | Line SD taken by BBMB to attend hot spot on R-Phase of isolator at Panipat. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.1125 |  |  |  |  | NRPC | 100
86 | NR240086 | 400 KV DEHAR-PANCHKULLA LINE (LILO Portion) | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
87 | NR240089 | 400KV MOGA-HISAR-II | 206 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
88 | NR240090 | 400KV MOGA-HISAR-III | 206 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
89 | NR240095 | 400KV Abdullapur-Kurukshetra-I | 51.65 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
90 | NR240096 | 400KV Abdullapur-Kurukshetra-II | 51.65 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
91 | NR240097 | 400KV Kurukshetra-Sonipat-I | 124.66 | NR2 | -- | 2019-05-17 | 21:25 | 2019-05-18 | 15:25 | -- | -- | -- | 0 | 0 | 0 | 0.75 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.75 |  |  |  |  | NRPC | 100
92 | NR240098 | 400KV Kurukshetra-Sonipat-II | 124.66 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
93 | NR240099 | 400KV Kurukshetra-Jalandhar | 267 | NR2 | -- | 2019-05-16 | 7:18 | 2019-05-16 | 14:54 | -- | -- | -- | 0 | 0 | 0 | 0.31667 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=425KV | NRPC
[6 empty] | 2019-05-17 | 12:49 | 2019-05-17 | 12:49 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault. FLR Jalandhar: 139.55kM, 3.53kA & Kurukshetra: 134.1 kM, 3.261kA | NRPC
[6 empty] | 2019-05-17 | 21:11 | 2019-05-18 | 15:17 |  |  |  | 0 | 0 | 0 | 0.75417 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1899-12-31 01:42 |  |  |  |  | NRPC | 100
94 | NR240100 | 400KV Jalandhar-Nakodar | 234 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
95 | NR240101 | 400KV Kurukshetra-Nakodar | 42 | NR2 | -- | 2019-05-01 | 9:43 | 2019-05-01 | 21:09 | -- | -- | -- | 0.47639 | 0 | 0 | 0 |  |  |  | SD take for installment of Pilot insulator strings. | NRPC
[6 empty] | 2019-05-04 | 15:56 | 2019-05-04 | 22:11 |  |  |  | 0 | 0 | 0 | 0.26042 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=421KV | NRPC
[6 empty] | 2019-05-05 | 12:47 | 2019-05-06 | 21:58 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:11 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV | NRPC
[6 empty] | 2019-05-17 | 21:14 | 2019-05-18 | 15:19 |  |  |  | 0 | 0 | 0 | 0.75347 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV | NRPC
[6 empty] | 2019-05-24 | 7:15 | 2019-05-27 | 9:01 |  |  |  | 0 | 0 | 0 | 1900-01-02 01:46 |  |  |  | Line hand tripped for voltage regulation. Kurukshetra=428KV | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.47639 | 0 | 0 | 1900-01-04 11:17 |  |  |  |  | NRPC | 98.46
96 | NR240104 | 400KV Kaithal-Bagpat-I | 153.672 | NR2 | -- | 2019-05-02 | 18:43 | 2019-05-02 | 20:07 | -- | -- | -- | 0 | 0.058333 | 0 | 0 |  |  |  | Line tripped on Y-N fault caused by swinging of OPGW of undercrossing 220 kV Baraut Muradnagar line of UPPTCL. Later on UPTCL took SD for removal of OPGC on 12.05.19, their mail request attached. FLR Kaithal-153.6 Km,4.74 KA & Baghpat FLR:- 2.2 Km,18.77 KA | NRPC
[6 empty] | 2019-05-10 | 21:16 | 2019-05-10 | 22:25 |  |  |  | 0 | 0.047917 | 0 | 0 |  |  |  | Line tripped on Y-N fault caused by swinging of OPGW of undercrossing 220 kV Baraut Muradnagar line of UPPTCL. Later on UPTCL took SD for removal of OPGC on 12.05.19, their mail request attached.FLR Kaithal-153.6 Km,4.6 KA & Baghpat FLR:- 2.2 Km,17.2 KA. | NRPC
[6 empty] | 2019-05-12 | 11:20 | 2019-05-12 | 14:25 |  |  |  | 0 | 0 | 0 | 0.12847 |  |  |  | SD taken to remove earth wire/OPGW of 220 KV Baraut-Muradnagar line of UPPTCL. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.10625 | 0 | 0.12847 |  |  |  |  | NRPC | 100
97 | NR240105 | 400 KV Kaithal-Baghpat-II | 153.672 | NR2 | -- | 2019-05-02 | 18:43 | 2019-05-02 | 20:08 | -- | -- | -- | 0 | 0.059028 | 0 | 0 |  |  |  | Line tripped on Y-N fault caused by swinging of OPGW of undercrossing 220 kV Baraut Muradnagar line of UPPTCL. Later on UPTCL took SD for removal of OPGC on 12.05.19, their mail request attached. FLR Kaithal-153.6 Km,4.429 KA & Baghpat FLR:- 2.3 Km,16.22 KA. | NRPC
[6 empty] | 2019-05-12 | 11:21 | 2019-05-12 | 14:25 |  |  |  | 0 | 0 | 0 | 0.12778 |  |  |  | SD taken to remove earth wire/OPGW of 220 KV Baraut-Muradnagar line of UPPTCL. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.059028 | 0 | 0.12778 |  |  |  |  | NRPC | 100
98 | NR240106 | 400 KV Patiala- Panchkula-I | 65.5 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
99 | NR240107 | 400 KV Patiala- Panchkula-II | 65.5 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
100 | NR240108 | 400 KV Patiala- Patran-I | 78.837 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
101 | NR240109 | 400 KV Patiala- Patran-II | 78.837 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
102 | NR240110 | 400 KV Kaithal- Patran-I | 47.363 | NR2 | -- | 2019-05-09 | 9:31 | 2019-05-09 | 19:22 | -- | -- | -- | 0.41042 | 0 | 0 | 0 |  |  |  | SD taken for AMP works. | NRPC
[6 empty] | 2019-05-11 | 10:46 | 2019-05-11 | 15:26 |  |  |  | 0.19444 | 0 | 0 | 0 |  |  |  | SD taken to rectify bended hanger bolt of Rph at Loc 53. | NRPC
103 | [5 empty] | Sub Total --> | [6 empty] | 0.60486 | 0 | 0 | 0 |  |  |  |  | NRPC | 98.04
| NR240111 | 400 KV Kaithal- Patran-II | 47.363 | NR2 | -- | 2019-05-10 | 10:01 | 2019-05-10 | 18:13 | -- | -- | -- | 0.34167 | 0 | 0 | 0 |  |  |  | SD taken for AMP works. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.34167 | 0 | 0 | 0 |  |  |  |  | NRPC | 98.89
104 | NR240112 | 400KV DEHAR (BBMB) - RAJPURA (PSTCL) LILO PORTION | 14.4 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
105 | NR240113 | 400KV BHIWANI (BBMB) - RAJPURA (PSTCL) LILO PORTION | 14.4 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
106 | NR240114 | 400 KV Amritsar Jalandhar-II | 71.4 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
107 | NR240115 | 400KV Jalandhar Hamirpur | 135 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
108 | NR240116 | 400 KV Kaithal Malerkotla | 213 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
109 | NR240117 | 400KV Dadri-Kaithal | 135 | NR2 | -- | 2019-05-01 | 5:32 | 2019-05-01 | 5:32 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault .FLR Kaithal: 103.4Km, 3.4kA | NRPC
[6 empty] | 2019-05-15 | 5:15 | 2019-05-15 | 5:15 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault.FLR Kaithal: :2.49 KA | NRPC
[6 empty] | 2019-05-29 | 4:53 | 2019-05-29 | 4:53 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault .FLR Kaithal: 118.76Km, 3.086kA. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
110 | NR240118 | 400KV Parbati2-Banala LILO portion | 14.35 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
111 | NR240119 | 400KV PARBATI 3 (NHPC) - SAINJ (HPSEB) LILO PORTION | 9.403 | NR2 | -- | 2019-05-01 | 10:25 | 2019-05-01 | 14:56 | -- | -- | -- | 0 | 0 | 0 | 0.18819 |  |  |  | SD taken by Parbati-3 for replacing faulty R-Phase CB Pole of Unit # 4 with spare one. | NRPC
[6 empty] | 2019-05-03 | 10:35 | 2019-05-03 | 20:46 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | SD taken by HPSEB for CB retrifitting at Sainj. | NRPC
[6 empty] | 2019-05-06 | 12:03 | 2019-05-06 | 13:15 |  |  |  | 0 | 0 | 0 | 0.05 |  |  |  | SD taken by HPSEB for CB checking of unit-4 at Sainj. | NRPC
[6 empty] | 2019-05-25 | 11:25 | 2019-05-25 | 18:40 |  |  |  | 0 | 0 | 0 | 0.30208 |  |  |  | SD taken by HPSEB for carrying out feeder protection Relay testng at Sainj. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.96458 |  |  |  |  | NRPC | 100
112 | NR240120 | 400KV Kishenpur- New Wanpoh-III | 135 | NR2 | -- | 2019-05-20 | 0:42 | 2019-05-20 | 0:42 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | Line A/R on Y-N fault, FLR Kishenpur: 98.56kM, Iy=3.925kA & New Wanpoh: 39.94kM, Iy=5.401kA | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
113 | NR240121 | 400KV Kishenpur- New Wanpoh-IV | 135 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
114 | NR240122 | 400KV KURUKSHETRA - JIND - I | 103.6 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
115 | NR240123 | 400KV KURUKSHETRA - JIND - II | 103.6 | NR2 | -- | 2019-05-02 | 17:05 | 2019-05-02 | 19:11 | -- | -- | -- | 0.0875 | 0 | 0 | 0 |  |  |  | Line tripped on Y-B ph fault caused by heavy thunderstorm and cyclonic wind. FLR K'shtera:-12 Km,IY-20 KA,IB-21 KA. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.0875 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.71
116 | NR240124 | 400KV URI 1 - AMARGARH - I | 119.44 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
117 | NR240125 | 400KV AMARGARH - WAGOORA- I | 61.95 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
118 | NR240126 | 400KV URI 1 - AMARGARH - II | 39.34 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
119 | NR240127 | 400KV AMARGARH - WAGOORA - II | 61.95 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
120 | NR240128 | 400KV DULHASTI-KISHENPUR-II | 39.34 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
121 | NR276504 | 765 KV MEERUT-MOGA | 337.5 | NR2 | -- | 2019-05-01 | 12:09 | 2019-05-01 | 21:26 | -- | -- | -- | 0.38681 | 0 | 0 | 0 |  |  |  | SD taken for attend the hot spot in Line isolator at Moga end. | NRPC
[6 empty] | 2019-05-05 | 11:13 | 2019-05-05 | 19:11 |  |  |  | 0 | 0 | 0 | 0.33194 |  |  |  | Line hand tripped for voltage regulation. Moga=789KV | NRPC
[6 empty] | 2019-05-08 | 12:43 | 2019-05-08 | 20:49 |  |  |  | 0.3375 | 0 | 0 | 0 |  |  |  | SD taken to attend hot spot on polymer insulator at Loc. No. 367. | NRPC
[6 empty] | 2019-05-13 | 22:09 | 2019-05-14 | 9:28 |  |  |  | 0 | 0 | 0 | 0.47153 |  |  |  | Line hand tripped for voltage regulation. Moga=790KV | NRPC
[6 empty] | 2019-05-15 | 8:35 | 2019-05-15 | 15:12 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV | NRPC
[6 empty] | 2019-05-16 | 8:30 | 2019-05-16 | 9:26 |  |  |  | 0.038889 | 0 | 0 | 0 |  |  |  | Line trippped on B-N fault. FLR Moga:- 278.6, 2.5kA & Meerut:-21km, 10kA. | NRPC
[6 empty] | 2019-05-17 | 19:00 | 2019-05-18 | 16:28 |  |  |  | 0 | 0 | 0 | 0.89444 |  |  |  | Line hand tripped for voltage regulation. Moga=796KV | NRPC
[6 empty] | 2019-05-19 | 7:56 | 2019-05-19 | 23:21 |  |  |  | 0 | 0 | 0 | 0.64236 |  |  |  | Line hand tripped for voltage regulation. Moga=794KV | NRPC
[6 empty] | 2019-05-29 | 8:38 | 2019-05-29 | 19:39 |  |  |  | 0.45903 | 0 | 0 | 0 |  |  |  | SD taken for polymer insulator string replacment due to hot spot creation. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 1899-12-31 05:20 | 0 | 0 | 1900-01-01 14:47 |  |  |  |  | NRPC | 96.05
122 | NR2BRT01 | ABDULLAPUR 50MVAR BUS REACTOR | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
123 | NR2BRT02 | Fatehabad 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
124 | NR2BRT04 | KISHENPUR 63MVAR BUS REACTOR | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
125 | NR2BRT05 | MALERKOTLA 50MVAR BUS REACTOR | 50 | NR2 | -- | 2019-05-06 | 16:12 | 2019-05-07 | 8:00 | -- | -- | -- | 0 | 0.65833 | 0 | 0 |  |  |  | Reactor tripped on differential protection operation caused by external falshover on the bushing due to heavy smoke spread over the area generated by burning of agricilture waste in the surrounding fields of the station.. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.65833 | 0 | 0 |  |  |  |  | NRPC | 100
126 | NR2BRT06 | MOGA 50MVAR BUS REACTOR | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
127 | NR2BRT07 | NALAGARH 50MVAR BUS REACTOR | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
128 | NR2BRT08 | Wagoora 50 MVAR Bus Reactor-I | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
129 | NR2BRT09 | Ludhiana 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
130 | NR2BRT10 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -I | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
131 | NR2BRT11 | 50 MVAR Kaithal Switchable L/R on on Kaithal - Bagpat Line -II | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
132 | NR2BRT12 | Abdullapur 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
133 | NR2BRT14 | Kaithal 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
134 | NR2BRT15 | Patiala 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
135 | NR2BRT16 | Chamba 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
136 | NR2BRT17 | 125 MVAR Bus Reactor at Panchkula | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
137 | NR2BRT18 | 50 MVAR Panchkula Switchable L/R on on Panchkula - NJTL -I | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
138 | NR2BRT19 | 50 MVAR Panchkula Switchable L/R on Panchkula - NJTL -II | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
139 | NR2BRT20 | Amritsar 80 MVAR Bus Reactor | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
140 | NR2BRT21 | Jalandhar 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
141 | NR2BRT23 | 125 MVAR Bus Reactor at Nalagarh | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
142 | NR2BRT24 | 80MVAR Bus Reactor at Kishenpur | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
143 | NR2BRT25 | Moga 240 MVAR Bus Reactor -I | 240 | NR2 | -- | 2019-05-29 | 15:58 | 2019-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 08:02 |  |  |  | B/R Hand tripped for voltage regulation.Moga=750KV | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1900-01-01 08:02 |  |  |  |  | NRPC | 100
144 | NR2BRT26 | Moga 240 MVAR Bus Reactor -II | 240 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
145 | NR2BRT30 | 240 MVAR Moga Switchable L/R on Moga-Bhiwani | 240 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
146 | NR2BRT31 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -I | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
147 | NR2BRT32 | 50 MVAR Jallandhar Switchable L/R on Jal-Chamba -II | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
148 | NR2BRT33 | 80 MVAR Bus Reactor at Samba | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
149 | NR2BRT34 | 80 MVAR Bus Reactor at Banala | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
150 | NR2BRT36 | 80 Mvar bus reactor at Hamirpur | 80 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
151 | NR2BRT37 | 50 MVAR Hamirpur Switchable L/R on Amritsar-Hamirpur | 50 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
152 | NR2BRT38 | New Wanpoh 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
153 | NR2BRT39 | 240 MVAR Moga Switchable L/R on Moga-Meerut | 240 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
154 | NR2BRT40 | Kurukshetra 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
155 | NR2BRT41 | Panchkula 125 MVAR Bus Reactor - II | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
156 | NR2BRT42 | Kaithal 125 MVAR Bus Reactor | 125 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
157 | NR2BRT43 | Dehar 63 MVAR Bus Reactor-I | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
158 | NR2BRT44 | Dehar 63 MVAR Bus Reactor-II | 63 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
159 | NR2ICT01 | ABDULLAPUR 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
160 | NR2ICT02 | ABDULLAPUR 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
161 | NR2ICT03 | ABDULLAPUR 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
162 | NR2ICT04 | AMRITSAR 315 MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
163 | NR2ICT05 | Amritsar 315 MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
164 | NR2ICT06 | Fatehabad 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
165 | NR2ICT07 | Fatehabad 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
166 | NR2ICT11 | JALANDHAR 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
167 | NR2ICT12 | JALANDHAR 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
168 | NR2ICT13 | KAITHAL 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
169 | NR2ICT14 | KAITHAL 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
170 | NR2ICT15 | KISHENPUR 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
171 | NR2ICT16 | KISHENPUR 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
172 | NR2ICT17 | MALERKOTLA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
173 | NR2ICT18 | MALERKOTLA 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
174 | NR2ICT61 | MOGA 500MVA ICT-I | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
175 | NR2ICT20 | MOGA 250MVA ICT-II | 250 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
176 | NR2ICT64 | MOGA 500MVA ICT-III | 500 | NR2 | -- | 2019-05-22 | 10:16 | 2019-05-22 | 12:15 | -- | -- | -- | 0.082639 | 0 | 0 | 0 |  |  |  | SD taken to attend oil leakage from OLTC surge relay. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.082639 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.73
177 | NR2ICT22 | MOGA 315MVA ICT-IV | 315 | NR2 | -- | 2019-05-06 | 9:34 | 2019-05-15 | 19:37 | -- | -- | -- | 1900-01-08 10:03 | 0 | 0 | 0 |  |  |  | SD taken for degassing of transformer in order to arrest high hydrogen value in DGA. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 1900-01-08 10:03 | 0 | 0 | 0 |  |  |  |  | NRPC | 69.61
178 | NR2ICT23 | NALAGARH 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
179 | NR2ICT24 | NALAGARH 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
180 | NR2ICT25 | PANIPAT 450MVA ICT-II | 450 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
181 | NR2ICT26 | PATIALA 315MVA ICT-I | 315 | NR2 | -- | 2019-05-14 | 9:25 | 2019-05-14 | 18:43 | -- | -- | -- | 0.3875 | 0 | 0 | 0 |  |  |  | SD taken for AMP works. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.3875 | 0 | 0 | 0 |  |  |  |  | NRPC | 98.75
182 | NR2ICT27 | PATIALA 315MVA ICT-II | 315 | NR2 | -- | 2019-05-15 | 9:19 | 2019-05-20 | 14:14 | -- | -- | -- | 1900-01-04 04:55 | 0 | 0 | 0 |  |  |  | SD taken for AMP works. | NRPC
[6 empty] | 2019-05-23 | 17:02 | 2019-05-23 | 18:25 |  |  |  | 0.057639 | 0 | 0 | 0 |  |  |  | ICT tripped due to OSR relay operation of B-Phase OLTC caused by ingession of moisture. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 1900-01-04 06:18 | 0 | 0 | 0 |  |  |  |  | NRPC | 83.02
183 | NR2ICT28 | WAGOORA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
184 | NR2ICT29 | WAGOORA 315MVA ICT-II | 315 | NR2 | -- | 2019-05-09 | 9:13 | 2019-05-09 | 17:24 | -- | -- | -- | 0.34097 | 0 | 0 | 0 |  |  |  | SD taken for AMP works | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.34097 | 0 | 0 | 0 |  |  |  |  | NRPC | 98.9
185 | NR2ICT30 | WAGOORA 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
186 | NR2ICT31 | LUDHIANA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
187 | NR2ICT32 | LUDHIANA 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
188 | NR2ICT33 | LUDHIANA 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
189 | NR2ICT37 | WAGOORA 315MVA ICT-IV | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
190 | NR2ICT38 | Patiala 500 MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
191 | NR2ICT39 | Malerkotla 500 MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
192 | NR2ICT40 | Chamba 315 MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
193 | NR2ICT41 | Chamba 315 MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
194 | NR2ICT43 | 315 MVA ICT-I at Panchkula | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
195 | NR2ICT44 | 315 MVA ICT-II at Panchkula | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
196 | NR2ICT45 | Moga 1500MVA ICT-II | 1500 | NR2 | -- | 2019-05-24 | 9:31 | 2019-05-24 | 16:47 | -- | -- | -- | 0.30278 | 0 | 0 | 0 |  |  |  | SD taken for AMP works. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.30278 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.02
197 | NR2ICT47 | Moga 1500MVA ICT-I | 1500 | NR2 | -- | 2019-05-23 | 9:47 | 2019-05-23 | 16:47 | -- | -- | -- | 0.29167 | 0 | 0 | 0 |  |  |  | SD taken for AMP works. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.29167 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.05
198 | NR2ICT51 | Samba 315MVA ICT-I | 315 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:01 | -- | -- | -- | 0.023611 | 0 | 0 | 0 |  |  |  | Line tripped at Samba on tripping of 220 kV bus-2 caused by droping of bird nest. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.023611 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.92
199 | NR2ICT52 | Samba 315MVA ICT-II | 315 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:01 | -- | -- | -- | 0.023611 | 0 | 0 | 0 |  |  |  | Line tripped at Samba on tripping of 220 kV bus-2 caused by droping of bird nest. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.023611 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.92
200 | NR2ICT55 | Wanpoh 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
201 | NR2ICT56 | Amritsar 500 Mva ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
202 | NR2ICT57 | ABDULLAPUR 315MVA ICT-IV | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
203 | NR2ICT58 | NALAGARH 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
204 | NR2ICT59 | Hamirpur 315MVA ICT-1 | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
205 | NR2ICT60 | KISHENPUR 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
206 | NR2ICT62 | 315MVA ICT-II at Hamirpur S/S | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
207 | NR2ICT63 | 500MVA ICT-IV at Ludhiana S/S | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
208 | NR2ICT65 | 315MVA ICT-II at New Wanpoh S/S | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
209 | NR2ICT66 | Panchkula 500MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
210 | NR2ICT67 | JALANDHAR 500 MVA ICT-III | 500 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
211 | NR2ICT68 | SAMBA 315 MVA ICT-III | 315 | NR2 | -- | 2019-05-07 | 10:27 | 2019-05-07 | 11:04 | -- | -- | -- | 0.025694 | 0 | 0 | 0 |  |  |  | Line tripped at Samba on tripping of 220 kV bus-2 caused by droping of bird nest. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.025694 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.91
212 | NR2ICT69 | DEHAR 315 MVA ICT IV | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
213 | NR2ICT73 | KAITHAL 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
214 | NR2ICT76 | FATEHABAD 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
215 | NR2ICT77 | HAMIRPUR 315MVA ICT-III | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
216 | NR2ICT78 | BANALA 315MVA ICT-I | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
217 | NR2ICT79 | BANALA 315MVA ICT-II | 315 | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
218 | NR2SVC01 | Ludhiana -400/+600 MVAR SVC |  | NR2 | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC | 100
219 | NR2SVC02 | NEW WANPOH -200/+300 MVAR SVC |  | NR2 | -- | 2019-05-08 | 10:12 | 2019-05-08 | 14:02 | -- | -- | -- | 0.15972 | 0 | 0 | 0 |  |  |  | SVC handtripped to avoid consequential damage due to heavy sparking observed at R-PH isolator of coupling transformer. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.15972 | 0 | 0 | 0 |  |  |  |  | NRPC | 99.48
220 | NR2STCOM01 | NALAGARH -200/+200 MVAR STATCOM |  |  | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | NRPC
221 | NRWRDCP01 | 800KV HVDC Kurukshetra-Champa Pole - I |  | NR2 | -- | 2019-05-03 | 8:19 | 2019-05-04 | 17:00 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:41 |  |  |  | SD taken for Updation for software in Bipole-1 (Pole-1 & 2) for parallel operation of Pole-3 under construction. | NRPC
[6 empty] | 2019-05-05 | 9:33 | 2019-05-06 | 22:52 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:19 |  |  |  | SD taken for online load testing of Pole-3 with Pole -1 and 2 under construction. | NRPC
[6 empty] | 2019-05-05 | 14:24 | 2019-05-05 | 15:10 |  |  |  | 0.031944 | 0 | 0 | 0 |  |  |  | Pole Blocked due to cooling fauilure at Champa. | NRPC
[6 empty] | 2019-05-05 | 15:42 | 2019-05-05 | 16:57 |  |  |  | 0 | 0 | 0 | 0.052083 |  |  |  | SD taken for online load testing of Pole-3 with Pole -1 and 2 under construction. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.031944 | 0 | 0 | 1900-01-01 23:15 |  |  |  |  | NRPC | 99.89
222 | NRWRDCP02 | 800KV HVDC Kurukshetra-Champa Pole - II |  | NR2 | -- | 2019-05-03 | 8:38 | 2019-05-05 | 10:47 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 02:09 |  |  |  | SD taken for Updation for software in Bipole-1 (Pole-1 & 2) for parallel operation of Pole-3 under construction. | NRPC
[6 empty] | 2019-05-05 | 17:41 | 2019-05-06 | 23:15 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:34 |  |  |  | SD taken for online load testing of Pole-3 with Pole -1 and 2 under construction. | NRPC
[6 empty] | 2019-05-30 | 15:33 | 2019-05-30 | 16:18 |  |  |  | 0.03125 | 0 | 0 | 0 |  |  |  | Pole blocked due to WTI trip on B-ph Conveter transformer. | NRPC
[6 empty] | Sub Total --> | [6 empty] | 0.03125 | 0 | 0 | 1900-01-02 07:43 |  |  |  |  | NRPC | 99.9
Formulas:
ISTS Licensee = IF(RIGHT(T14)="T",(+[Date]-[Date]),0)
ISTS Licensee = SUM([ISTS Licensee, row above])
OTHERS = IF(RIGHT(T14)="U",(+[Date]-[Date]),0)
OTHERS = SUM([OTHERS, row above])
Deemed Available = IF(RIGHT(T14)="D",(+[Date]-[Date]),0)