## SOP DATA NR3 March-17
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-III
Availability calculation for the Period : From 01.07.2017 to 31.07.2017
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [24 empty] | 0
1 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 744
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1327 | 148.034 | 196441.118 | 196441.118 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2017-07-01 | 2017-07-01 20:39 |  |  |  | 0 | 0 | 0 | 0.86042 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=782kV
[6 empty] | 2017-07-02 02:36 | 2017-07-02 19:54 |  |  |  | 0 | 0 | 0 | 0.72083 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=787kV
[6 empty] | 2017-07-04 06:51 | 2017-07-04 20:57 |  |  |  | 0 | 0 | 0 | 0.5875 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=800kV
[6 empty] | 2017-07-05 01:39 | 2017-07-05 21:43 |  |  |  | 0 | 0 | 0 | 0.83611 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=801kV
[6 empty] | 2017-07-06 05:09 | 2017-07-06 14:55 |  |  |  | 0 | 0 | 0 | 0.40694 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Fatehpur=435kV
[6 empty] | 2017-07-12 03:45 | 2017-07-13 14:26 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:41 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=791kV
[6 empty] | 2017-07-20 08:01 | 2017-07-20 21:40 |  |  |  | 0 | 0 | 0 | 0.56875 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Agra=799kV
[6 empty] | 2017-07-23 16:35 | 2017-07-23 21:01 |  |  |  | 0 | 0 | 0 | 0.18472 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
[6 empty] | 2017-07-24 03:32 | 2017-07-24 12:08 |  |  |  | 0 | 0 | 0 | 0.35833 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2017-07-30 06:53 | 2017-07-31 10:57 |  |  |  | 0 | 0 | 0 | 1899-12-31 04:04 |  |  |  | LVRD | Line Hand tripped on Voltage regulation as per NRLDC instruction. Agra= 790KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 03:19 | [6 empty] | 744 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2017-07-03 06:48 | 2017-07-04 11:49 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:01 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=793kV
[6 empty] | 2017-07-05 21:30 | 2017-07-05 22:34 |  |  |  | 0.044444 | 0 | 0 | 0 |  |  |  | OSFT | Emergengy S/D taken due to sparking on loose jumper of NGR LA at FTP end
[6 empty] | 2017-07-09 18:43 | 2017-07-10 14:30 |  |  |  | 0 | 0 | 0 | 0.82431 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=788kV
[6 empty] | 2017-07-11 03:17 | 2017-07-11 23:03 |  |  |  | 0 | 0 | 0 | 0.82361 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=791kV
[6 empty] | 2017-07-25 07:24 | 2017-07-25 14:57 |  |  |  | 0 | 0 | 0 | 0.31458 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.044444 | 0 | 0 | 1900-01-02 04:07 | [6 empty] | 744 | 1210 | 334.8 | 405108 | 404527.2 | 99.8566
4 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | 2017-07-09 08:41 | 2017-07-09 11:38 |  |  |  | 0.12292 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.12292 | 0 | 0 | 0 | [6 empty] | 744 | 1374 | 318.919 | 438194.706 | 436457.2404 | 99.6035
5 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | 2017-07-24 12:19 | 2017-07-24 16:31 |  |  |  | 0.175 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for tightening of bolt in sag adjustment plate at Loc No. 324
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.175 | 0 | 0 | 0 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 254946.2635 | 99.4355
6 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | 2017-07-09 08:41 | 2017-07-09 10:48 |  |  |  | 0.088194 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.088194 | 0 | 0 | 0 | [6 empty] | 744 | 1419 | 165.98 | 235525.62 | 234855.5538 | 99.7155
7 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | 2017-07-05 12:12 | 2017-07-05 12:50 |  |  |  | 0.026389 | 0 | 0 | 0 |  |  |  | SRMT | Tripped due to Main bay R-phase CT SF-6 low alarm at Fatehpur & DT received at Varanasi.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.026389 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 223 | 310639 | 310374.5672 | 99.9149
8 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR3 | -- | 2017-07-02 06:44 | 2017-07-02 14:10 |  |  |  | 0 | 0 | 0 | 0.30972 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.KNP=808kV
[6 empty] | 2017-07-15 15:58 | 2017-07-15 17:58 |  |  |  | 0.083333 | 0 | 0 | 0 |  |  |  | OSPT | Emergency S/D taken for trimming/cutting of infringing line corridor
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.083333 | 0 | 0 | 0.30972 | [6 empty] | 744 | 1440 | 465.8 | 670752 | 668948.9032 | 99.7312
9 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
10 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | 2017-07-18 08:02 | 2017-07-18 10:00 |  |  |  | 0 | 0 | 0.081944 | 0 |  |  |  | LNCC | Tripped due to R-Phase PRD of Line Reactor-II operated at Kanpur(GIS) end and DT received at Varanasi end, due to heavy rain.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.081944 | 0 | [6 empty] | 742.0333 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
B |  | 400 KV TRANS LINES |  |  | --
1 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 29.982 | NR3 | -- | 2017-07-20 00:36 | 2017-07-20 01:25 | -- | -- |  | 0.034028 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault at Agra end only ,F.C.=2.03KA.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.034028 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15423.7812 | 99.8902
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2017-07-01 | 2017-07-01 20:49 | -- | -- | -- | 0 | 0 | 0 | 0.86736 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=435kV
[6 empty] | 2017-07-02 07:11 | 2017-07-06 18:37 |  |  |  | 0 | 0 | 0 | 1900-01-03 11:26 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=438kV
[6 empty] | 2017-07-11 04:14 | 2017-07-11 22:37 |  |  |  | 0 | 0 | 0 | 0.76597 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=434kV
[6 empty] | 2017-07-15 07:38 | 2017-07-15 20:10 |  |  |  | 0 | 0 | 0 | 0.52222 |  |  |  | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
[6 empty] | 2017-07-16 07:42 | 2017-07-16 20:20 |  |  |  | 0 | 0 | 0 | 0.52639 |  |  |  | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
[6 empty] | 2017-07-17 12:02 | 2017-07-17 19:30 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
[6 empty] | 2017-07-24 05:21 | 2017-07-26 21:12 |  |  |  | 0 | 0 | 0 | 1900-01-01 15:51 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=436kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 03:07 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2017-07-15 07:38 | 2017-07-15 20:15 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
[6 empty] | 2017-07-16 07:42 | 2017-07-16 20:22 |  |  |  | 0 | 0 | 0 | 1900-01-01 15:51 |  |  |  | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
[6 empty] | 2017-07-17 12:02 | 2017-07-17 19:32 |  |  |  | 0 | 0 | 0 | 0.3125 |  |  |  | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 06:49 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- | 2017-07-03 08:12 | 2017-07-04 15:58 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:46 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=435kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:46 | [6 empty] | 744 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2017-07-01 | 2017-07-01 14:57 | -- | -- | -- | 0 | 0 | 0 | 0.62292 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=427kV
[6 empty] | 2017-07-02 01:21 | 2017-07-02 20:02 |  |  |  | 0 | 0 | 0 | 0.77847 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=424kV
[6 empty] | 2017-07-03 03:21 | 2017-07-04 20:58 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:37 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
[6 empty] | 2017-07-05 01:44 | 2017-07-05 12:57 |  |  |  | 0 | 0 | 0 | 0.46736 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
[6 empty] | 2017-07-06 04:13 | 2017-07-07 14:59 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:46 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
[6 empty] | 2017-07-08 07:11 | 2017-07-08 21:18 |  |  |  | 0 | 0 | 0 | 0.58819 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=436kV
[6 empty] | 2017-07-11 03:19 | 2017-07-11 21:38 |  |  |  | 0 | 0 | 0 | 0.76319 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=435kV
[6 empty] | 2017-07-12 03:25 | 2017-07-13 16:12 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:47 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
[6 empty] | 2017-07-14 07:45 | 2017-07-14 09:26 |  |  |  | 0 | 0 | 0 | 0.070139 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=430kV
[6 empty] | 2017-07-14 09:26 | 2017-07-14 14:26 |  |  |  | 0.20833 | 0 | 0 | 0 |  |  |  | OSFT | S/D taken for replacement of Y-phase punctured LA at Agra end
[6 empty] | 2017-07-18 04:16 | 2017-07-18 14:45 |  |  |  | 0 | 0 | 0 | 0.43681 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=434kV
[6 empty] | 2017-07-20 08:06 | 2017-07-21 21:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:21 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Agra=435kV
[6 empty] | 2017-07-23 03:01 | 2017-07-24 11:56 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:55 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=426kV
[6 empty] | 2017-07-30 19:12 | 2017-08-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 04:48 |  |  |  | LVRD | Line Hand tripped on Voltage regulation as per NRLDC instruction. Agra= 421KV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.20833 | 0 | 0 | 1900-01-11 13:41 | [6 empty] | 744 | 515 | 209.51 | 107897.65 | 107172.5314 | 99.328
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
10 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
11 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 155.932 | 80304.98 | 80304.98 | 100
12 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 224 | 115360 | 115360 | 100
13 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.792 | 50877.88 | 50877.88 | 100
14 | NR140016 | 400KV ALLD-SASARAM | 212 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 369 | 212 | 78228 | 78228 | 100
15 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- | 2017-07-09 08:41 | 2017-07-09 10:43 | -- | -- |  | 0.084722 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.084722 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 13 | 6695 | 6676.7027 | 99.7267
16 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- | 2017-07-09 08:41 | 2017-07-09 10:51 | -- | -- | -- | 0.090278 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.090278 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 13 | 6695 | 6675.5029 | 99.7088
17 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | 2017-07-09 08:41 | 2017-07-09 09:49 |  |  |  | 0.047222 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.047222 | 0 | 0 | 0 | [6 empty] | 744 | 227 | 229.163 | 52020.001 | 51940.7591 | 99.8477
18 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | 2017-07-08 12:31 | 2017-07-08 12:36 |  |  |  | 0.0034722 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for taking L/R in service at Sohawal end which was out of service due to PRV malfunctioning.
[5 empty] | -- | 2017-07-09 08:41 | 2017-07-09 09:52 |  |  |  | 0.049306 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.052778 | 0 | 0 | 0 | [6 empty] | 744 | 227 | 229.163 | 52020.001 | 51931.4365 | 99.8297
19 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
20 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
21 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 9.2 | 4738 | 4738 | 100
22 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 9.2 | 4738 | 4738 | 100
23 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- | 2017-07-04 16:08 | 2017-07-04 16:42 | -- | -- | -- | 0.023611 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken to take L/R in service at Bareilly which was out of service due to oil leakage in Reactor tank.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.023611 | 0 | 0 | 0 | [6 empty] | 744 | 331 | 278.76 | 92269.56 | 92199.283 | 99.9238
24 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
25 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
26 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR3
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
27 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 115.926 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
28 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 | 100
29 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 |  | 2017-07-01 11:54 | 2017-07-01 12:28 |  |  |  | 0.023611 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault,F.D.=13.52km from Bareily, F.C.=13.77KA.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.023611 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69911.4784 | 99.9238
30 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 |  | 2017-07-08 13:01 | 2017-07-08 13:01 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully due to B-N fault. F.D.= 8.098KM from Bareilly, F.C.= 16.03KAmp at Bareilly
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
31 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2017-07-02 07:18 | 2017-07-02 15:23 | -- | -- | -- | 0 | 0 | 0 | 0.33681 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
[6 empty] | 2017-07-03 06:52 | 2017-07-03 09:47 |  |  |  | 0 | 0 | 0 | 0.12153 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=432kV
[6 empty] | 2017-07-04 06:10 | 2017-07-04 09:32 |  |  |  | 0 | 0 | 0 | 0.14028 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
[6 empty] | 2017-07-05 01:47 | 2017-07-05 13:15 |  |  |  | 0 | 0 | 0 | 0.47778 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 01:50 | [6 empty] | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
32 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- | 2017-07-16 16:56 | 2017-07-16 17:11 | -- | -- |  | 0.010417 | 0 | 0 | 0 |  |  |  | SPLT | Tripped from Mainpuri end only on DT received at Mainpuri due to PLCC mal-operation
[6 empty] | 2017-07-30 06:40 | 2017-07-31 14:23 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:43 |  |  |  | LVRD | Line Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri= 428KV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.010417 | 0 | 0 | 1899-12-31 07:43 | [6 empty] | 744 | 515 | 235.952 | 121515.28 | 121474.4483 | 99.9664
33 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2017-07-03 03:48 | 2017-07-03 11:23 | -- | -- | -- | 0 | 0 | 0 | 0.31597 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =430kV
[6 empty] | 2017-07-04 06:09 | 2017-07-04 09:25 |  |  |  | 0 | 0 | 0 | 0.13611 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =430kV
[6 empty] | 2017-07-06 07:47 | 2017-07-06 21:50 |  |  |  | 0 | 0 | 0 | 0.58542 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction Fatehpur =434kV
[5 empty] | -- | 2017-07-11 03:13 | 2017-07-11 21:42 | -- | -- | -- | 0 | 0 | 0 | 0.77014 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNPR=427kV
[6 empty] | 2017-07-24 05:25 | 2017-07-24 15:23 |  |  |  | 0 | 0 | 0 | 0.41528 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=790kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 05:21 | [6 empty] | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
34 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- | 2017-07-01 | 2017-07-01 11:03 | -- | -- | -- | 0 | 0 | 0 | 0.46042 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =436kV
[6 empty] | 2017-07-01 18:09 | 2017-07-02 15:35 |  |  |  | 0 | 0 | 0 | 0.89306 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =430kV
[6 empty] | 2017-07-05 01:41 | 2017-07-05 13:09 |  |  |  | 0 | 0 | 0 | 0.47778 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
[6 empty] | 2017-07-12 03:20 | 2017-07-13 15:51 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:31 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNPR=424kV
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 08:28 | [6 empty] | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
35 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
36 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | 2017-07-02 13:41 | 2017-07-02 14:22 |  |  |  | 0 | 0.028472 | 0 | 0 |  |  |  | OMSU | Tripped only from Gorakhpur(UPPCL) end due to unsuccessful A/R at UPPCL end caused by Y-N fault,F.D.=24.1km from GKP(PG), F.C.=8.62KA.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.028472 | 0 | 0 | [6 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
37 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | 2017-07-07 14:56 | 2017-07-07 18:18 |  |  |  | 0.14028 | 0 | 0 | 0 |  |  |  | OSFT | E/S/D availed for attending hot spot in Y-phase line main bay isolator at Kanpur
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.14028 | 0 | 0 | 0 | [6 empty] | 744 | 291 | 240 | 69840 | 69523.9677 | 99.5475
38 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 72.6 | 37389 | 37389 | 100
39 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 73.2 | 37698 | 37698 | 100
40 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2017-07-02 07:14 | 2017-07-02 15:16 | -- | -- |  | 0 | 0 | 0 | 0.33472 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.KNP=428kV
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.33472 | [6 empty] | 744 | 342 | 385.69 | 131905.98 | 131905.98 | 100
47 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- | 2017-07-06 07:52 | 2017-07-07 16:09 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:17 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction Kanpur =425/802kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:17 | [6 empty] | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
41 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- | 2017-07-03 08:10 | 2017-07-03 10:09 | -- | -- | -- | 0 | 0 | 0 | 0.082639 |  |  |  | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.KNP=425kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.082639 | [6 empty] | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
42 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 107.079 | 55145.685 | 55145.685 | 100
43 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 107.1 | 55156.5 | 55156.5 | 100
44 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | 2017-07-08 14:37 | 2017-07-08 17:26 |  |  |  | 0 | 0.11736 | 0 | 0 |  |  |  | OMSU | Tripped only from Panki(UP) end due to problem at UPPCL Panki end.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.11736 | 0 | 0 | [6 empty] | 744 | 515 | 5.922 | 3049.83 | 3049.83 | 100
45 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 5.86 | 3017.9 | 3017.9 | 100
46 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
47 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- | 2017-07-12 10:32 | 2017-07-12 10:47 | -- | -- | -- | 0.010417 | 0 | 0 | 0 |  |  |  | LEFT | Tripped only from Gorakhpur end due to unsuccessful A/R at GKP end caused by B-N fault,F.d.=155km from GKP,F.C.=2.03KA, F.d.=88.06km from LKO,F.C.=3.579KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.010417 | 0 | 0 | 0 | [6 empty] | 744 | 289 | 263.933 | 76276.637 | 76251.0064 | 99.9664
48 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
49 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
50 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | 2017-07-04 15:58 | 2017-07-04 17:13 |  |  |  | 0 | 0.052083 | 0 | 0 |  |  |  | OMSU | Tripped from Lucknow (PG) end only due to DT received from UPPTCL. Problem at uppcl end.
[6 empty] | 2017-07-06 14:47 | 2017-07-06 16:14 |  |  |  | 0 | 0 | 0 | 0.060417 |  |  |  | OSPD | S/D taken by UPPCL for maintenance work at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.052083 | 0 | 0.060417 | 0 | 0 | 0 |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
51 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 371 | 169.785 | 62990.235 | 62990.235 | 100
52 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 169.729 | 87410.435 | 87410.435 | 100
53 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
54 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
55 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
56 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
57 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 734.52 | 515 | 73.826 | 38020.39 | 38020.39 | 100
58 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 691 | 30.703 | 21215.773 | 21215.773 | 100
59 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 691 | 31.159 | 21530.869 | 21530.869 | 100
60 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR3 | -- | 2017-07-05 00:11 | 2017-07-05 00:11 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on Y-N fault. F.D.= 134.8KM from Bareilly & 118.5KM from Meerut, F.C.= 3.82KAmp at Bareilly & 3.6KAmp at Meerrut. The fault was in Powerlink juridiction.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
61 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR3 | -- | 2017-07-21 11:17 | 2017-07-21 11:36 | -- | -- | -- | 0 | 0.013194 | 0 | 0 |  |  |  | OMSU | Tripped due to R-B phase fault. F.D.= 137.9KM from Bareilly, Ir= 3.737KAmp & Ib= 3.948KAmp. The fault was in Powerlink juridiction.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.013194 | 0 | 0 | [6 empty] | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
62 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
63 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
64 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 332 | 224 | 74368 | 74368 | 100
65 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 306 | 202 | 61812 | 61812 | 100
66 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 25.057 | 12904.355 | 12904.355 | 100
67 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 236 | 330.953 | 78104.908 | 78104.908 | 100
68 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- | 2017-07-28 08:28 | 2017-07-28 09:17 | -- | -- |  | 0 | 0.034028 | 0 | 0 |  |  |  | OMSU | Tripped only from NTPC Singrauli end due to unsuccessful A/R at NTPC singrauli end(Problem at NTPC Singrauli) caused by B-N fault,F.D.=258.7km from LKO(UP).
[11 empty] | 0 | 0 | 0 | 0
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.034028 | 0 | 0 | [6 empty] | 744 | 337 | 408.6 | 137698.2 | 137698.2 | 100
69 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- | 2017-07-17 08:50 | 2017-07-18 23:39 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 14:49 |  |  |  | OSPD | S/D availed by NTPC for general maintenance work
[6 empty] | 2017-07-19 11:29 | 2017-07-19 19:59 |  |  |  | 0 | 0 | 0 | 0.35417 |  |  |  | OSPD | S/D taken by Chattisgarh WR transmission Ltd. for stringing (Power line crossing) of 400kV D/C Vindyachal 4&5 SSTPP Pool- Vindhya pool ( Line under construction by Chattisgarh WR transmission Ltd.)
[6 empty] | 2017-07-26 21:23 | 2017-07-26 22:57 |  |  |  | 0 | 0.065278 | 0 | 0 |  |  |  | OMSU | Tripped at Singrauli end only due to DT received at Singrauli.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 14:49 | [6 empty] | 744 | 515 | 42.026 | 21643.39 | 21643.39 | 100
70 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- | 2017-07-15 14:52 | 2017-07-15 14:52 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed successfully from both end due to B-N fault. FD: 13.4km from Rihand
[6 empty] | 2017-07-19 11:27 | 2017-07-20 21:18 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:51 |  |  |  | OSPD | S/D taken for Maintenance work by NTPC
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:51 | [6 empty] | 744 | 515 | 43.952 | 22635.28 | 22635.28 | 100
71 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 3.341 | 1720.615 | 1720.615 | 100
72 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 3.317 | 1708.255 | 1708.255 | 100
73 | NR140164 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | 2017-07-01 09:02 | 2017-07-01 21:09 |  |  |  | 0.50486 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for line maintenance work by Varanasi.
[6 empty] | 2017-07-04 09:17 | 2017-07-04 20:40 |  |  |  | 0.47431 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for line maintenance work by Varanasi.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.97917 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 69.677 | 35883.655 | 34750.2331 | 96.8414
74 | NR140165 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | 2017-07-01 13:16 | 2017-07-01 15:01 |  |  |  | 0 | 0.072917 | 0 | 0 |  |  |  | SRMU | Tripped from Sarnath(UPPCL) end only due to relay mal operation at Sarnath(UPPCL) end.
[6 empty] | 2017-07-03 09:35 | 2017-07-03 21:51 |  |  |  | 0.51111 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for line maintenance work by Varanasi.
[6 empty] | 2017-07-05 10:00 | 2017-07-05 19:13 |  |  |  | 0.38403 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for line maintenance work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.89514 | 0.072917 | 0 | 0 | [6 empty] | 744 | 515 | 69.677 | 35883.655 | 34847.4984 | 97.1125
75 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
76 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
77 | NR340008 | 400KV LKO(765)-KANPUR(GIS)-I | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 159.7 | 109713.9 | 109713.9 | 100
78 | NR340009 | 400KV LKO(765)-KANPUR(GIS)-II | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 159.7 | 109713.9 | 109713.9 | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- | 2017-07-01 20:07 | 2017-07-01 20:52 | -- | -- |  | 0.03125 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault,F.D.=201.7km from Bareily(UP), F.D.=18.63km from D'Ganga.
[6 empty] | 2017-07-21 15:30 | 2017-07-21 16:30 |  |  |  | 0 | 0 | 0.041667 | 0 |  |  |  | GOVC | Tripped due to over voltage at Dhauliganga(NHPC) end
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.03125 | 0 | 0.041667 | 0 | [6 empty] | 743 | 109 | 234.59 | 25570.31 | 25544.4988 | 99.8991
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- | 2017-07-21 15:30 | 2017-07-21 16:26 | -- | -- | -- | 0 | 0.038889 | 0 | 0 |  |  |  | OMSU | Tripped due to problem at Dhauliganga(NHPC) end & DT received at Pithoragarh.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.038889 | 0 | 0 | [6 empty] | 744 | 156 | 59.01 | 9205.56 | 9205.56 | 100
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- | 2017-07-22 10:05 | 2017-07-22 16:28 | -- | -- |  | 0 | 0 | 0 | 0.26597 |  |  |  | OSFD | S/D taken by UPPCL to attend hot spot in line isolator at Fatehpur(UP) end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.26597 | [6 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | 2017-07-15 12:03 | 2017-07-15 14:55 |  |  |  | 0 | 0 | 0 | 0.11944 |  |  |  | OSFD | S/D taken by UPPCL for attending CB problem at UPPCL end
[6 empty] | 2017-07-15 18:48 | 2017-07-15 21:54 |  |  |  | 0 | 0.12917 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault. FD: 19.06km from Fatehpur, FC: Fatehpur-5.67KA. Fault in UPPCL jurisdiction.
[6 empty] | 2017-07-28 19:53 | 2017-07-28 22:14 |  |  |  | 0 | 0 | 0 | 0.097917 |  |  |  | OSFD | Emergency S/D taken by UPPCL for attending sparking problem in conductor at UPPCL Naubasta end.
[6 empty] | 2017-07-29 16:24 | 2017-07-29 22:16 |  |  |  | 0 | 0 | 0 | 0.24444 |  |  |  | OSFD | Emergency S/D taken by UPPCL for attending damaged R- phase CT at UPPCL Naubasta end.
[6 empty] | 2017-07-31 15:38 | 2017-07-31 17:18 |  |  |  | 0 | 0.069444 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault. FD: 72.6km from Fatehpur, FC: 2.46KA. Fault in UPPCL jurisdiction
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.19861 | 0 | 0.46181 | [6 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
13 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- |  |  |  |  | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
14 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | 2017-07-28 15:33 | 2017-07-28 17:08 |  |  |  | 0 | 0 | 0 | 0.065972 |  |  |  | OSFD | Emergency S/D taken by UPPCL for attending some problem in UPPCL Naubasta end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.065972 | [6 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
15 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)-1 | 8.717 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 8.717 | 1141.927 | 1141.927 | 100
16 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- | 2017-07-05 00:58 | 2017-07-05 16:38 | -- | -- | -- | 0 | 0.65278 | 0 | 0 |  |  |  | OMSU | Tripped on B-N fault. F.D.= 22KM from Kanpur & 0.746KM from Panki(UP), F.C.= 5.6KAmp at Kanpur. The fault is in UPPCL juridiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.65278 | 0 | 0 | [6 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
17 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
18 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
19 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | 2017-07-03 08:34 | 2017-07-03 21:48 |  |  |  | 0 | 0 | 0 | 0.55139 |  |  |  | LCSD | S/D taken to facilitate rectification of theft conductor & cross arm of 220kv KNP-Unchahar-4 between loc no 397 to 399.
[6 empty] | 2017-07-04 11:21 | 2017-07-04 18:24 |  |  |  | 0 | 0 | 0 | 0.29375 |  |  |  | LCSD | S/D taken to facilitate rectification of theft conductor & cross arm of 220kv KNP-Unchahar-4 between loc no 397 to 399.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.84514 | [6 empty] | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
20 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | 2017-07-01 | 2017-07-04 18:32 |  |  |  | 0 | 0 | 1900-01-02 18:32 | 0 |  |  |  | LMAC | Tripped on R-N fault. F.D.= 15.93KM from Kanpur, F.C.= 8.56KAmp at Kanpur. During emergency patrolling it is found that conductor of bottom & middle phase cut & theft in between location nos. 396 to 399 and as a result 06 nos.cross-arms of middle & bottom phase at loc. no. 397, 398 & 399 are also damaged badly.
[5 empty] | -- | 2017-07-29 12:44 | 2017-07-29 13:15 |  |  |  | 0.021528 | 0 | 0 | 0 |  |  |  | LPPT | Tripped on R-Y fault. F.D.= 55KM from Kanpur & 85.9KM from Unchahar, F.C.: Ir=Iy= 4.1KAmp at Kanpur & Ir=Iy= 2KAmp at Unchahar
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.021528 | 0 | 1900-01-02 18:32 | 0 | [6 empty] | 653.4667 | 131 | 144.63 | 18946.53 | 18931.5498 | 99.9209
21 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | 2017-07-21 15:30 | 2017-07-21 15:57 |  |  |  | 0.01875 | 0 | 0 | 0 |  |  |  | SPLT | Tripped from Bareilly (UP) end only due to PLCC mal operation at Pithoragarh end .
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.01875 | 0 | 0 | 0 | [6 empty] | 744 | 156 | 177.88 | 27749.28 | 27732.4962 | 99.9395
22 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
23 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
24 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- | 2017-07-01 13:02 | 2017-07-01 14:02 | -- | -- | -- | 0 | 0.041667 | 0 | 0 |  |  |  | OMSU | Tripped due to some problem in Bareily (UPPCL) end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.041667 | 0 | 0 | [6 empty] | 744 | 132 | 105.72 | 13955.04 | 13955.04 | 100
25 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 106 | 13992 | 13992 | 100
26 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | 2017-07-01 13:02 | 2017-07-01 14:06 |  |  |  | 0 | 0.044444 | 0 | 0 |  |  |  | OMSU | Tripped from tanakpur end due to tripping of 220KV Sitarganj-Bareily(UP) line due to problem at Bareily (UPPCL) end
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.044444 | 0 | 0 | [6 empty] | 744 | 132 | 42.55 | 5616.6 | 5616.6 | 100
27 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
28 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
29 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 42.5 | 5610 | 5610 | 100
30 | NR320001 | 220KV KNP-RANIA | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 18.372 | 2425.104 | 2425.104 | 100
[5 empty] | -- | [17 empty] | 1829.706
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 | 58 | 2900 | 2900 | 100
119 | Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-02 05:05 | 1899-12-31 07:51 | 1900-01-02 21:30 | 1900-02-20 13:37 | [8 empty] | 16988.447 | 8451373.931 | 8441189.804 | 99.8795 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.8873 | % (AC) | 99.4525
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | 2017-07-09 08:41 | 2017-07-09 10:27 |  |  |  | 0.073611 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.073611 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1496.4382 | 99.7625
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | 2017-07-09 08:41 | 2017-07-09 10:41 |  |  |  | 0.083333 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia. |  | 744 | 1500 |  | 1500 | 1495.9677 | 99.7312
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
17 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
18 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
19 | NR3ICT701 | 765/400KV ICT-I Kanpur(GIS) | 1500 | NR3 |  | 2017-07-28 09:35 | 2017-07-28 18:27 |  |  |  | 0.36944 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.36944 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1482.1237 | 98.8082
20 | NR3ICT702 | 765/400KV ICT-II Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
F |  | 400/220 KV ICT'S |  | NR3 | --
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | 2017-07-28 09:26 | 2017-07-29 18:48 |  |  |  | 1899-12-31 09:22 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for replacement of B Ph bushing due to oil leakage and other maintainance work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 09:22 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 300.873 | 95.5152
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | 2017-07-26 11:55 | 2017-07-27 22:37 |  |  |  | 1899-12-31 10:42 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for replacement of 220kV R-phase bushing at Mainpuri.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-01 20:04 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 286.1815 | 90.8513
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR3 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | [15 empty] | 744 | 100 |  | 100 | 100 | 100
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
--
45 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 1900-01-07 00:46 | 0 | 0 | 0 | [7 empty] | 29425 |  | 29425 | 29356.584 | 99.7675 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2017-07-03 15:38 | 2017-07-03 15:38 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC transient Earth Fault,F.D.=784.1km from Rihand,F.D.=30.9km from Dadri(NR-1 jurisdiction)
[6 empty] | 2017-07-07 14:07 | 2017-07-13 18:38 |  |  |  | 0 | 0 | 0 | 1900-01-05 04:31 |  |  |  | LCSD | S/D availed for replacement of over aged snubber capacitors at HVDC Rihand under add. Cap.
[6 empty] | 2017-07-24 04:56 | 2017-07-24 04:56 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Dadri-1.94km, Rihand-813.06km.
[6 empty] | 2017-07-27 05:15 | 2017-07-27 05:15 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient Fault. FD=532.5kM from Rihand and 282.5kM from Dadri
[6 empty] | 2017-07-31 08:51 | 2017-07-31 08:51 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Rihand-744.9km, Dadri-70.1km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 04:31 | [6 empty] | 744 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2017-07-07 05:59 | 2017-07-07 05:59 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R Successfully on DC transient E/F. F.D.= 578.23KM from Rihand & 236.77KM from Dadri.
[6 empty] | 2017-07-09 04:05 | 2017-07-09 04:05 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on DC transient E/F. F.D.= 295.32KM from Rihand & 519.77KM from Dadri end.
[6 empty] | 2017-07-17 01:32 | 2017-07-17 01:32 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on DC transient E/F. FD: Rihand-295.29km, Dadri-519.71km
[6 empty] | 2017-07-17 16:20 | 2017-07-17 16:34 |  |  |  | 0.0097222 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to problem in newly installed converter module-A at Dadri end.
[6 empty] | 2017-07-23 23:42 | 2017-07-23 23:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Dadri-390.14km, Rihand-424.86km
[6 empty] | 2017-07-26 00:21 | 2017-07-26 00:21 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed operated successfully from both end on transient DC earth fault. FD= 295.7kM from Rihand end and 519.3kM from Dadri end.
[6 empty] | 2017-07-26 21:23 | 2017-07-27 00:04 |  |  |  | 0.11181 | 0 | 0 | 0 |  |  |  | SRMT | Tripped due to short circuit protection opearated at Rihand end.
[6 empty] | 2017-07-27 15:22 | 2017-07-27 15:50 |  |  |  | 0.019444 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for correcting the polarity of CT at Rihand end.
[6 empty] | 2017-07-28 10:03 | 2017-07-28 13:47 |  |  |  | 0.15556 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D taken for attending converter control changeover at Dadri end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.29653 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 605403.1418 | 99.0435
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | 2017-07-02 11:42 | 2017-07-02 11:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC transient Earth Fault,F.D.=330.044km from Balia,F.D.=456.746km from Bhiwadi,Tower No. 912
[6 empty] | 2017-07-09 08:41 | 2017-07-09 11:59 |  |  |  | 0.1375 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
[6 empty] | 2017-07-10 07:45 | 2017-07-10 07:45 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end on DC transient fault. FD= 118.983kM from Balia end and 607.80kM from Bhiwadi end. Tower No 325
[6 empty] | 2017-07-14 20:00 | 2017-07-14 20:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on DC transient fault. F.D.= 229.06KM from Balia & 560.71KM from Bhiwadi. Tower No.=627
[6 empty] | 2017-07-24 04:26 | 2017-07-24 04:26 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Ballia-584.81km, Tower No. 1597. Fault in NR-1 jurisdiction
[6 empty] | 2017-07-29 02:27 | 2017-07-29 02:27 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully due to DC transient earth fault, F.D.=489.45km from Balia,F.D.=300.340km from Bhiwadi,Tower no.-1338.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.1375 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 982853.6462 | 99.5565
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2017-07-01 17:14 | 2017-07-01 17:14 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC transient Earth Fault,F.D.=708.285km from Balia,F.D.=81.505km from Bhiwadi,Tower No. 1932(Fault in NR-1 Jurisdiction)
[6 empty] | 2017-07-07 02:18 | 2017-07-07 02:18 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R Successfully on DC transient E/F. F.D.= 253.80KM from Balia & 535.80KM from Bhiwadi. Tower No.=694
[6 empty] | 2017-07-07 05:08 | 2017-07-07 05:08 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R Successfully on DC transient E/F. F.D.= 253.789KM from Balia & 536.001KM from Bhiwadi. Tower No.=694
[6 empty] | 2017-07-09 08:41 | 2017-07-09 12:11 |  |  |  | 0.14583 | 0 | 0 | 0 |  |  |  | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
[6 empty] | 2017-07-11 06:03 | 2017-07-11 06:03 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end on DC transient fault. FD= 66.8kM from Balia end and 722.97kM from Bhiwadi end. Tower No 186
[6 empty] | 2017-07-22 04:43 | 2017-07-22 04:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on DC transient E/F. F.D.= 232.01KM from Balia & 557.78KM from Bhiwadi. Tower No.=635
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.14583 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 982588.2611 | 99.5296
4 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2017-07-17 08:18 | 2017-07-17 11:31 |  |  |  | 0.13403 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on DC transient earth fault. FD: 1763kM from Agra and 10kM from BNC end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.13403 | 0 | 0 | 0 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2580793.5484 | 99.5677
1 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | 2017-07-16 03:38 | 2017-07-16 04:39 |  |  |  | 0.042361 | 0 | 0 | 0 |  |  |  | SRMT | Tripped due to mal-operation of VESDA (fire trip) at BNC
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.042361 | 0 | 0 | 0 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2588458.0645 | 99.8634
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0.57986 | 0 | 0 | 1900-01-05 04:31 | [8 empty] | 3209.572 | 3196965 | 3182095.0491 | 99.5349 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2017-07-22 20:17 | 2017-07-23 06:53 |  |  |  | 0.44167 | 0 | 0 | 0 |  |  |  | SRMT | Tripped due to DC over current protection operated , due to transient disturbance in external feeder (400kV Korba-Vindhyachal-1)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.44167 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 246.4382 | 98.5753
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 0.44167 | 0 | 0 | 0 | [9 empty] | 500 | 496.4382 | 99.2876 | %
3 | NR1DCB02 | Sasaram HVDC B/B BLOCK-I | 250 | NR3 | -- | 2017-07-01 16:42 | 2017-07-01 18:17 |  |  |  | 0 | 0.065972 | 0 | 0 |  |  |  | OMSU | AS PER ERLDC INSTRUCTION HVDC BLOCKED FOR POWER REVERSAL AND DEBLOCKED WITH 200 MW NORTH TO EAST
[6 empty] | 2017-07-31 18:34 | 2017-07-31 19:25 |  |  |  | 0 | 0.035417 | 0 | 0 |  |  |  | OMSU | GOT BLOCKED DUE TO SYS FAIL ALARM DUE TO FAILURE OF AUX. SUPPLY.
[6 empty] | 2017-07-20 08:29 | 2017-07-20 09:35 |  |  |  | 0 | 0.045833 | 0 | 0 |  |  |  | OMSU | HVDC/SSRM GOT BLOCKED DUE TO SYS FAIL ALARM DUE TO FAILURE OF AUX. SUPPLY
[6 empty] | 2017-07-17 05:41 | 2017-07-17 06:38 |  |  |  | 0.039583 | 0 | 0 | 0 |  |  |  | OMST | BLOCKED DUE TO SYS FAIL ALARM
[5 empty] | -- | 2017-07-17 16:35 | 2017-07-17 17:34 |  |  |  | 0.040972 | 0 | 0 | 0 |  |  |  | OMST | BLOCKED DUE TO SYS FAIL ALARM
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.080556 | 0.14722 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 249.3504 | 99.7401
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 530 | 530 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- | 2017-07-20 21:37 | 2017-07-22 10:28 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:51 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=395kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 12:51 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- | 2017-07-01 | 2017-07-01 16:01 | -- | -- | -- | 0 | 0 | 0 | 0.66736 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=742kV
[6 empty] | 2017-07-07 20:15 | 2017-07-09 08:08 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:53 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=740kV
[6 empty] | 2017-07-14 20:05 | 2017-07-18 07:09 |  |  |  | 0 | 0 | 0 | 1900-01-02 11:04 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=747kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 14:58 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- | 2017-07-08 21:27 | 2017-07-10 06:55 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:28 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=752kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:28 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- | 2017-07-01 12:50 | 2017-07-02 06:35 | -- | -- |  | 0 | 0 | 0 | 0.73958 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=396kV
[6 empty] | 2017-07-09 23:34 | 2017-07-10 06:50 |  |  |  | 0 | 0 | 0 | 0.30278 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. BRLY=393kV
[6 empty] | 2017-07-16 14:42 | 2017-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-14 09:18 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=400kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-15 10:19 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 2X50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- | 2017-07-01 14:48 | 2017-07-02 06:13 | -- | -- |  | 0 | 0 | 0 | 0.64236 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=406kV
[6 empty] | 2017-07-02 19:58 | 2017-07-03 07:04 |  |  |  | 0 | 0 | 0 | 0.4625 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=396kV
[6 empty] | 2017-07-09 23:28 | 2017-07-10 06:50 |  |  |  | 0 | 0 | 0 | 0.30694 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. BRLY=391kV
[5 empty] | -- | 2017-07-11 23:57 | 2017-07-26 08:00 | -- | -- |  | 0 | 0 | 0 | 1900-01-13 08:03 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=397kV
[6 empty] | 2017-07-26 20:01 | 2017-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-04 03:59 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=389kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-19 21:55 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
15 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
16 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
17 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
18 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
19 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | 2017-07-08 23:52 | 2017-07-09 07:45 |  |  |  | 0 | 0 | 0 | 0.32847 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=393kV
[6 empty] | 2017-07-16 21:12 | 2017-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-14 02:48 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=389kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-14 10:41 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
20 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | 2017-07-08 23:49 | 2017-07-09 06:21 |  |  |  | 0 | 0 | 0 | 0.27222 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=390kV
[6 empty] | 2017-07-16 21:11 | 2017-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-14 02:49 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=389kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-14 09:21 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
21 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | 2017-07-20 23:44 | 2017-07-21 09:56 |  |  |  | 0 | 0 | 0 | 0.425 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=394kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.425 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
22 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
23 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
24 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | 2017-07-07 20:27 | 2017-07-08 06:17 |  |  |  | 0 | 0 | 0 | 0.40972 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=748kV
[6 empty] | 2017-07-08 21:35 | 2017-07-09 18:32 |  |  |  | 0 | 0 | 0 | 0.87292 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=755kV
[6 empty] | 2017-07-14 20:05 | 2017-07-16 08:31 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:26 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=751kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
25 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
26 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
27 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
28 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
29 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
30 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
31 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
32 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
33 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
34 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
35 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
36 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
37 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
38 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
39 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
40 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
41 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
42 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
43 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
44 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
45 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
46 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
47 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
48 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
49 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | 2017-07-01 12:58 | 2017-07-01 16:02 |  |  |  | 0 | 0 | 0 | 0.12778 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=766kV
[6 empty] | 2017-07-02 19:51 | 2017-07-03 07:03 |  |  |  | 0 | 0 | 0 | 0.46667 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=747kV
[6 empty] | 2017-07-13 20:45 | 2017-07-15 05:57 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:12 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=755kV
[6 empty] | 2017-07-16 21:10 | 2017-07-17 05:47 |  |  |  | 0 | 0 | 0 | 0.35903 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=754kV
[6 empty] | 2017-07-20 22:10 | 2017-07-21 04:05 |  |  |  | 0 | 0 | 0 | 0.24653 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=747kV
[6 empty] | 2017-07-29 00:21 | 2017-07-30 05:33 |  |  |  | 0 | 0 | 0 | 1899-12-31 05:12 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=740kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 19:12 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
50 | NR1BRT44 | 330MVAR B/Reactor-I VARANASI | 330 | NR3 | -- | 2017-07-08 21:38 | 2017-07-10 07:13 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:35 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=753kV
[6 empty] | 2017-07-14 20:06 | 2017-07-26 07:50 |  |  |  | 0 | 0 | 0 | 1900-01-10 11:44 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=756kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-11 21:19 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
51 | NR1BRT51 | 330MVAR B/Reactor-II VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
52 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | 2017-07-07 20:57 | 2017-07-08 07:04 |  |  |  | 0 | 0 | 0 | 0.42153 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=740kV
[6 empty] | 2017-07-08 21:38 | 2017-07-09 18:25 |  |  |  | 0 | 0 | 0 | 0.86597 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=751kV
[6 empty] | 2017-07-16 22:28 | 2017-07-18 07:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:46 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=750kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 15:40 | [6 empty] | 744 | 330 |  | 330 | 330 | 100 | %
53 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 125 | 125 | 100 | %
54 |  | 125MVAR B/Reactor-III KANPUR(GIS) | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 125 | 125 | 100 | %
|  | Total of Bus reactor | [8 empty] | 0 | 0 | 0 | 1900-07-13 19:05 | [9 empty] | 7943.4 | 7943.4 | 100 | %
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L11:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M11:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N11:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O11:[Deemed Available, row above])
Note on C11: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C42: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C46: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C50: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C54: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C169: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C172: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C331: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C334: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C456: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C528: DOC-15/06/14
Note on C529: DOC-26/09/14

## Sheet1
POWER GRID CORPORATION OF INDIA LTD.
CPCC, LUCKNOW
DOC No: NR-III-CPCC-
MONTH –July-2017 LINE- ICT OUTAGE DETAILS
CODE | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | NRLDC CODE | Classification- Category Code | REASON OF OUTAGE
|  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint- Natural calamity- Militancy | Deemed Available
|  |  |  | @ (T) | # (U) | & ( C ) | * (D)
|  |  |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min
| 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 11 | 12
NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I | 2017-07-17 08:18 | 2017-07-17 11:31 | 0.13403 | 0 | 0 | 0 | **** | LEFT | Tripped on DC transient earth fault. FD: 1763kM from Agra and 10kM from BNC end.
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2017-07-16 03:38 | 2017-07-16 04:39 | 0.042361 | 0 | 0 | 0 | **** | SRMT | Tripped due to mal-operation of VESDA (fire trip) at BNC
NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I | 2017-07-02 11:42 | 2017-07-02 11:42 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient Earth Fault,F.D.=330.044km from Balia,F.D.=456.746km from Bhiwadi,Tower No. 912
NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I | 2017-07-09 08:41 | 2017-07-09 11:59 | 0.1375 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I | 2017-07-10 07:45 | 2017-07-10 07:45 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end on DC transient fault. FD= 118.983kM from Balia end and 607.80kM from Bhiwadi end. Tower No 325
NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I | 2017-07-14 20:00 | 2017-07-14 20:00 | 0 | 0 | 0 | 0 |  | LART | A/R successfully on DC transient fault. F.D.= 229.06KM from Balia & 560.71KM from Bhiwadi. Tower No.=627
NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I | 2017-07-24 04:26 | 2017-07-24 04:26 | 0 | 0 | 0 | 0 |  | LART | Transient fault. FD: Ballia-584.81km, Tower No. 1597. Fault in NR-1 jurisdiction
NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I | 2017-07-29 02:27 | 2017-07-29 02:27 | 0 | 0 | 0 | 0 |  | LART | A/R operated successfully due to DC transient earth fault, F.D.=489.45km from Balia,F.D.=300.340km from Bhiwadi,Tower no.-1338.
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2017-07-01 17:14 | 2017-07-01 17:14 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient Earth Fault,F.D.=708.285km from Balia,F.D.=81.505km from Bhiwadi,Tower No. 1932(Fault in NR-1 Jurisdiction)
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2017-07-07 02:18 | 2017-07-07 02:18 | 0 | 0 | 0 | 0 | **** | LART | A/R Successfully on DC transient E/F. F.D.= 253.80KM from Balia & 535.80KM from Bhiwadi. Tower No.=694
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2017-07-07 05:08 | 2017-07-07 05:08 | 0 | 0 | 0 | 0 | **** | LART | A/R Successfully on DC transient E/F. F.D.= 253.789KM from Balia & 536.001KM from Bhiwadi. Tower No.=694
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2017-07-09 08:41 | 2017-07-09 12:11 | 0.14583 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2017-07-11 06:03 | 2017-07-11 06:03 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end on DC transient fault. FD= 66.8kM from Balia end and 722.97kM from Bhiwadi end. Tower No 186
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2017-07-22 04:43 | 2017-07-22 04:43 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on DC transient E/F. F.D.= 232.01KM from Balia & 557.78KM from Bhiwadi. Tower No.=635
NR1DCP01 | 500KV HVDC R-D POLE-I | 2017-07-03 15:38 | 2017-07-03 15:38 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient Earth Fault,F.D.=784.1km from Rihand,F.D.=30.9km from Dadri(NR-1 jurisdiction)
NR1DCP01 | 500KV HVDC R-D POLE-I | 2017-07-07 14:07 | 2017-07-13 18:38 | 0 | 0 | 0 | 1900-01-05 04:31 | N-577 | LCSD | S/D availed for replacement of over aged snubber capacitors at HVDC Rihand under add. Cap.
NR1DCP01 | 500KV HVDC R-D POLE-I | 2017-07-24 04:56 | 2017-07-24 04:56 | 0 | 0 | 0 | 0 |  | LART | Transient fault. FD: Dadri-1.94km, Rihand-813.06km.
NR1DCP01 | 500KV HVDC R-D POLE-I | 2017-07-27 05:15 | 2017-07-27 05:15 | 0 | 0 | 0 | 0 | **** | LART | Transient Fault. FD=532.5kM from Rihand and 282.5kM from Dadri
NR1DCP01 | 500KV HVDC R-D POLE-I | 2017-07-31 08:51 | 2017-07-31 08:51 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand-744.9km, Dadri-70.1km
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-07 05:59 | 2017-07-07 05:59 | 0 | 0 | 0 | 0 | **** | LART | A/R Successfully on DC transient E/F. F.D.= 578.23KM from Rihand & 236.77KM from Dadri.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-09 04:05 | 2017-07-09 04:05 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on DC transient E/F. F.D.= 295.32KM from Rihand & 519.77KM from Dadri end.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-17 01:32 | 2017-07-17 01:32 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on DC transient E/F. FD: Rihand-295.29km, Dadri-519.71km
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-17 16:20 | 2017-07-17 16:34 | 0.0097222 | 0 | 0 | 0 | **** | SEMT | Tripped due to problem in newly installed converter module-A at Dadri end.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-23 23:42 | 2017-07-23 23:42 | 0 | 0 | 0 | 0 |  | LART | Transient fault. FD: Dadri-390.14km, Rihand-424.86km
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-26 00:21 | 2017-07-26 00:21 | 0 | 0 | 0 | 0 | **** | LART | Auto reclosed operated successfully from both end on transient DC earth fault. FD= 295.7kM from Rihand end and 519.3kM from Dadri end.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-26 21:23 | 2017-07-27 00:04 | 0.11181 | 0 | 0 | 0 | **** | SRMT | Tripped due to short circuit protection opearated at Rihand end.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-27 15:22 | 2017-07-27 15:50 | 0.019444 | 0 | 0 | 0 | N-1975 | OSPT | S/D availed for correcting the polarity of CT at Rihand end.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2017-07-28 10:03 | 2017-07-28 13:47 | 0.15556 | 0 | 0 | 0 | N-2018 | OSFT | Emergency S/D taken for attending converter control changeover at Dadri end.
NR1DCB01 | VINDH HVDC B/B BLOCK-I | 2017-07-22 20:17 | 2017-07-23 06:53 | 0.44167 | 0 | 0 | 0 | **** | SRMT | Tripped due to DC over current protection operated , due to transient disturbance in external feeder (400kV Korba-Vindhyachal-1)
NEDCB01 | SASARAM-POLE1 | 2017-07-01 16:42 | 2017-07-01 18:17 | 0 | 0.065972 | 0 | 0 |  | OMSU | AS PER ERLDC INSTRUCTION HVDC BLOCKED FOR POWER REVERSAL AND DEBLOCKED WITH 200 MW NORTH TO EAST
NEDCB01 | SASARAM-POLE1 | 2017-07-31 18:34 | 2017-07-31 19:25 | 0 | 0.035417 | 0 | 0 |  | OMSU | GOT BLOCKED DUE TO SYS FAIL ALARM DUE TO FAILURE OF AUX. SUPPLY.
NEDCB01 | SASARAM-POLE1 | 2017-07-20 08:29 | 2017-07-20 09:35 | 0 | 0.045833 | 0 | 0 |  | OMSU | HVDC/SSRM GOT BLOCKED DUE TO SYS FAIL ALARM DUE TO FAILURE OF AUX. SUPPLY
NEDCB01 | SASARAM-POLE1 | 2017-07-17 05:41 | 2017-07-17 06:38 | 0.039583 | 0 | 0 | 0 |  | OMST | BLOCKED DUE TO SYS FAIL ALARM
NEDCB01 | SASARAM-POLE1 | 2017-07-17 16:35 | 2017-07-17 17:34 | 0.040972 | 0 | 0 | 0 |  | OMST | BLOCKED DUE TO SYS FAIL ALARM
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-01 | 2017-07-01 20:39 | 0 | 0 | 0 | 0.86042 | N-2551 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=782kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-02 02:36 | 2017-07-02 19:54 | 0 | 0 | 0 | 0.72083 | N-94 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=787kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-04 06:51 | 2017-07-04 20:57 | 0 | 0 | 0 | 0.5875 | N-248 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=800kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-05 01:39 | 2017-07-05 21:43 | 0 | 0 | 0 | 0.83611 | N-344 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=801kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-06 05:09 | 2017-07-06 14:55 | 0 | 0 | 0 | 0.40694 | N-447 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Fatehpur=435kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-12 03:45 | 2017-07-13 14:26 | 0 | 0 | 0 | 1899-12-31 10:41 | N-894 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=791kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-20 08:01 | 2017-07-20 21:40 | 0 | 0 | 0 | 0.56875 | N-1462 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Agra=799kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-23 16:35 | 2017-07-23 21:01 | 0 | 0 | 0 | 0.18472 | N-1726 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-24 03:32 | 2017-07-24 12:08 | 0 | 0 | 0 | 0.35833 | N-1758 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2017-07-30 06:53 | 2017-07-31 10:57 | 0 | 0 | 0 | 1899-12-31 04:04 | N-2144 | LVRD | Line Hand tripped on Voltage regulation as per NRLDC instruction. Agra= 790KV
NR176507 | 765KV AGRA-FATEHPUR-II | 2017-07-03 06:48 | 2017-07-04 11:49 | 0 | 0 | 0 | 1899-12-31 05:01 | N-163 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=793kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2017-07-05 21:30 | 2017-07-05 22:34 | 0.044444 | 0 | 0 | 0 | N-432 | OSFT | Emergengy S/D taken due to sparking on loose jumper of NGR LA at FTP end
NR176507 | 765KV AGRA-FATEHPUR-II | 2017-07-09 18:43 | 2017-07-10 14:30 | 0 | 0 | 0 | 0.82431 | N-748 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=788kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2017-07-11 03:17 | 2017-07-11 23:03 | 0 | 0 | 0 | 0.82361 | N-826 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=791kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2017-07-25 07:24 | 2017-07-25 14:57 | 0 | 0 | 0 | 0.31458 | N-1832 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-07-02 06:44 | 2017-07-02 14:10 | 0 | 0 | 0 | 0.30972 | N-108 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.KNP=808kV
NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-07-15 15:58 | 2017-07-15 17:58 | 0.083333 | 0 | 0 | 0 | N-1125 | OSPT | Emergency S/D taken for trimming/cutting of infringing line corridor
NR176501 | 765KV LUCKNOW-BALIA | 2017-07-09 08:41 | 2017-07-09 11:38 | 0.12292 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR176508 | 765KV LUCKNOW-BAREILLY | 2017-07-24 12:19 | 2017-07-24 16:31 | 0.175 | 0 | 0 | 0 | N-1777 | OSFT | Emergency S/D availed for tightening of bolt in sag adjustment plate at Loc No. 324
NR176512 | 765KV VARANASI-BALIA | 2017-07-09 08:41 | 2017-07-09 10:48 | 0.088194 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR176513 | 765KV VARANASI-FATEHPUR | 2017-07-05 12:12 | 2017-07-05 12:50 | 0.026389 | 0 | 0 | 0 | **** | SRMT | Tripped due to Main bay R-phase CT SF-6 low alarm at Fatehpur & DT received at Varanasi.
NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 2017-07-18 08:02 | 2017-07-18 10:00 | 0 | 0 | 0.081944 | 0 | **** | LNCC | Tripped due to R-Phase PRD of Line Reactor-II operated at Kanpur(GIS) end and DT received at Varanasi end, due to heavy rain.
NR140003 | 400KV AGRA-AURAIYA-I | 2017-07-01 | 2017-07-01 20:49 | 0 | 0 | 0 | 0.86736 | N-2457 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=435kV
NR140003 | 400KV AGRA-AURAIYA-I | 2017-07-02 07:11 | 2017-07-06 18:37 | 0 | 0 | 0 | 1900-01-03 11:26 | N-112 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=438kV
NR140003 | 400KV AGRA-AURAIYA-I | 2017-07-11 04:14 | 2017-07-11 22:37 | 0 | 0 | 0 | 0.76597 | N-828 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=434kV
NR140003 | 400KV AGRA-AURAIYA-I | 2017-07-15 07:38 | 2017-07-15 20:10 | 0 | 0 | 0 | 0.52222 | N-1090 | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
NR140003 | 400KV AGRA-AURAIYA-I | 2017-07-16 07:42 | 2017-07-16 20:20 | 0 | 0 | 0 | 0.52639 | N-1162 | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
NR140003 | 400KV AGRA-AURAIYA-I | 2017-07-17 12:02 | 2017-07-17 19:30 | 0 | 0 | 0 | 0.31111 | N-1240 | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
NR140003 | 400KV AGRA-AURAIYA-I | 2017-07-24 05:21 | 2017-07-26 21:12 | 0 | 0 | 0 | 1900-01-01 15:51 | N-1765 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=436kV
NR140004 | 400KV AGRA-AURAIYA-II | 2017-07-15 07:38 | 2017-07-15 20:15 | 0 | 0 | 0 | 0.52569 | N-1090 | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
NR140004 | 400KV AGRA-AURAIYA-II | 2017-07-16 07:42 | 2017-07-16 20:22 | 0 | 0 | 0 | 0.52778 | N-1162 | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
NR140004 | 400KV AGRA-AURAIYA-II | 2017-07-17 12:02 | 2017-07-17 19:32 | 0 | 0 | 0 | 0.3125 | N-1240 | LCSD | S/D taken for crossing work of 765KV Orai-Aligarh-D/C line
NR140005 | 400KV AGRA-BASSI-I | 2017-07-03 08:12 | 2017-07-04 15:58 | 0 | 0 | 0 | 1899-12-31 07:46 | N-174 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=435kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-01 | 2017-07-01 14:57 | 0 | 0 | 0 | 0.62292 | N-2425 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=427kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-02 01:21 | 2017-07-02 20:02 | 0 | 0 | 0 | 0.77847 | N-91 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=424kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-03 03:21 | 2017-07-04 20:58 | 0 | 0 | 0 | 1899-12-31 17:37 | N-158 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-05 01:44 | 2017-07-05 12:57 | 0 | 0 | 0 | 0.46736 | N-345 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-06 04:13 | 2017-07-07 14:59 | 0 | 0 | 0 | 1899-12-31 10:46 | N-445 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-08 07:11 | 2017-07-08 21:18 | 0 | 0 | 0 | 0.58819 | N-630 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=436kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-11 03:19 | 2017-07-11 21:38 | 0 | 0 | 0 | 0.76319 | N-824 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=435kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-12 03:25 | 2017-07-13 16:12 | 0 | 0 | 0 | 1899-12-31 12:47 | N-893 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=432kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-14 07:45 | 2017-07-14 09:26 | 0 | 0 | 0 | 0.070139 | N-1030 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=430kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-14 09:26 | 2017-07-14 14:26 | 0.20833 | 0 | 0 | 0 | N-1047 | OSFT | S/D taken for replacement of Y-phase punctured LA at Agra end
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-18 04:16 | 2017-07-18 14:45 | 0 | 0 | 0 | 0.43681 | N-1289 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.Agra=434kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-20 08:06 | 2017-07-21 21:27 | 0 | 0 | 0 | 1899-12-31 13:21 | N-1463 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Agra=435kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-23 03:01 | 2017-07-24 11:56 | 0 | 0 | 0 | 1899-12-31 08:55 | N-1698 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=426kV
NR140009 | 400KV AGRA-BHIWADI-II | 2017-07-30 19:12 | 2017-08-01 | 0 | 0 | 0 | 1899-12-31 04:48 | N-2190 | LVRD | Line Hand tripped on Voltage regulation as per NRLDC instruction. Agra= 421KV
NR340006 | 400KV AGRA-FATEHABD(UP)-I | 2017-07-20 00:36 | 2017-07-20 01:25 | 0.034028 | 0 | 0 | 0 | **** | LEFT | Tripped on B-N fault at Agra end only ,F.C.=2.03KA.
NR140019 | 400KV BALIA-MAU-I | 2017-07-09 08:41 | 2017-07-09 10:43 | 0.084722 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR140020 | 400KV BALIA-MAU-II | 2017-07-09 08:41 | 2017-07-09 10:51 | 0.090278 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR140140 | 400KV BALIA-SOHAWAL-I | 2017-07-09 08:41 | 2017-07-09 09:49 | 0.047222 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR140120 | 400KV BALIA-SOHAWAL-II | 2017-07-08 12:31 | 2017-07-08 12:36 | 0.0034722 | 0 | 0 | 0 | N-657 | OSPT | S/D taken for taking L/R in service at Sohawal end which was out of service due to PRV malfunctioning.
NR140120 | 400KV BALIA-SOHAWAL-II | 2017-07-09 08:41 | 2017-07-09 09:52 | 0.049306 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR140025 | 400KV BAREILLY-LKO(UP) | 2017-07-04 16:08 | 2017-07-04 16:42 | 0.023611 | 0 | 0 | 0 | N-300 | OSPT | S/D taken to take L/R in service at Bareilly which was out of service due to oil leakage in Reactor tank.
NR140158 | 400KV BARLY(765)-KASHIPUR-I | 2017-07-01 11:54 | 2017-07-01 12:28 | 0.023611 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault,F.D.=13.52km from Bareily, F.C.=13.77KA.
NR140159 | 400KV BARLY(765)-KASHIPUR-II | 2017-07-08 13:01 | 2017-07-08 13:01 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully due to B-N fault. F.D.= 8.098KM from Bareilly, F.C.= 16.03KAmp at Bareilly
NR140037 | 400KV BLBGRH-MAINPURI-I | 2017-07-02 07:18 | 2017-07-02 15:23 | 0 | 0 | 0 | 0.33681 | N-114 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2017-07-03 06:52 | 2017-07-03 09:47 | 0 | 0 | 0 | 0.12153 | N-162 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=432kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2017-07-04 06:10 | 2017-07-04 09:32 | 0 | 0 | 0 | 0.14028 | N-243 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2017-07-05 01:47 | 2017-07-05 13:15 | 0 | 0 | 0 | 0.47778 | N-346 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
NR140038 | 400KV BLBGRH-MAINPURI-II | 2017-07-16 16:56 | 2017-07-16 17:11 | 0.010417 | 0 | 0 | 0 | **** | SPLT | Tripped from Mainpuri end only on DT received at Mainpuri due to PLCC mal-operation
NR140038 | 400KV BLBGRH-MAINPURI-II | 2017-07-30 06:40 | 2017-07-31 14:23 | 0 | 0 | 0 | 1899-12-31 07:43 | N-2143 | LVRD | Line Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri= 428KV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2017-07-03 03:48 | 2017-07-03 11:23 | 0 | 0 | 0 | 0.31597 | N-159 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =430kV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2017-07-04 06:09 | 2017-07-04 09:25 | 0 | 0 | 0 | 0.13611 | N-243 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =430kV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2017-07-06 07:47 | 2017-07-06 21:50 | 0 | 0 | 0 | 0.58542 | N-459 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction Fatehpur =434kV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2017-07-11 03:13 | 2017-07-11 21:42 | 0 | 0 | 0 | 0.77014 | N-825 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNPR=427kV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2017-07-24 05:25 | 2017-07-24 15:23 | 0 | 0 | 0 | 0.41528 | N-1767 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=790kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2017-07-01 | 2017-07-01 11:03 | 0 | 0 | 0 | 0.46042 | N-2507 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =436kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2017-07-01 18:09 | 2017-07-02 15:35 | 0 | 0 | 0 | 0.89306 | N-65 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction. Mainpuri =430kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2017-07-05 01:41 | 2017-07-05 13:09 | 0 | 0 | 0 | 0.47778 | N-346 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNP=430kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2017-07-12 03:20 | 2017-07-13 15:51 | 0 | 0 | 0 | 1899-12-31 12:31 | N-893 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.MNPR=424kV
NR140047 | 400KV GORAKH-GORAKH-II | 2017-07-02 13:41 | 2017-07-02 14:22 | 0 | 0.028472 | 0 | 0 | **** | OMSU | Tripped only from Gorakhpur(UPPCL) end due to unsuccessful A/R at UPPCL end caused by Y-N fault,F.D.=24.1km from GKP(PG), F.C.=8.62KA.
NR140052 | 400KV KNP-AGRA | 2017-07-07 14:56 | 2017-07-07 18:18 | 0.14028 | 0 | 0 | 0 | N-581 | OSFT | E/S/D availed for attending hot spot in Y-phase line main bay isolator at Kanpur
NR140055 | 400KV KNP-BLBGARH-I | 2017-07-02 07:14 | 2017-07-02 15:16 | 0 | 0 | 0 | 0.33472 | N-114 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.KNP=428kV
NR140056 | 400KV KNP-BLBGARH-II | 2017-07-06 07:52 | 2017-07-07 16:09 | 0 | 0 | 0 | 1899-12-31 08:17 | N-462 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction Kanpur =425/802kV
NR140057 | 400KV KNP-BLBGARH-III | 2017-07-03 08:10 | 2017-07-03 10:09 | 0 | 0 | 0 | 0.082639 | N-173 | LVRD | Line hand tripped for Voltage regulation as per NRLDC instruction.KNP=425kV
NR140058 | 400KV KNP-PANKI-I | 2017-07-08 14:37 | 2017-07-08 17:26 | 0 | 0.11736 | 0 | 0 | **** | OMSU | Tripped only from Panki(UP) end due to problem at UPPCL Panki end.
NR140071 | 400KV LUCKNOW-GORAKH-IV | 2017-07-12 10:32 | 2017-07-12 10:47 | 0.010417 | 0 | 0 | 0 | **** | LEFT | Tripped only from Gorakhpur end due to unsuccessful A/R at GKP end caused by B-N fault,F.d.=155km from GKP,F.C.=2.03KA, F.d.=88.06km from LKO,F.C.=3.579KA.
NR140072 | 400KV LUCKNOW-LKO(UP) | 2017-07-04 15:58 | 2017-07-04 17:13 | 0 | 0.052083 | 0 | 0 | **** | OMSU | Tripped from Lucknow (PG) end only due to DT received from UPPTCL. Problem at uppcl end.
NR140072 | 400KV LUCKNOW-LKO(UP) | 2017-07-06 14:47 | 2017-07-06 16:14 | 0 | 0 | 0 | 0.060417 | N-494 | OSPD | S/D taken by UPPCL for maintenance work at their end.
NR140142 | 400KV MEERUT-BAREILLY-I | 2017-07-05 00:11 | 2017-07-05 00:11 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on Y-N fault. F.D.= 134.8KM from Bareilly & 118.5KM from Meerut, F.C.= 3.82KAmp at Bareilly & 3.6KAmp at Meerrut. The fault was in Powerlink juridiction.
NR140130 | 400KV MEERUT-BAREILLY-II | 2017-07-21 11:17 | 2017-07-21 11:36 | 0 | 0.013194 | 0 | 0 | **** | OMSU | Tripped due to R-B phase fault. F.D.= 137.9KM from Bareilly, Ir= 3.737KAmp & Ib= 3.948KAmp. The fault was in Powerlink juridiction.
NR140095 | 400KV SING-LKO(UP)-I | 2017-07-28 08:28 | 2017-07-28 09:17 | 0 | 0.034028 | 0 | 0 |  | OMSU | Tripped only from NTPC Singrauli end due to unsuccessful A/R at NTPC singrauli end(Problem at NTPC Singrauli) caused by B-N fault,F.D.=258.7km from LKO(UP).
NR140096 | 400KV SING-RIHAND-I | 2017-07-17 08:50 | 2017-07-18 23:39 | 0 | 0 | 0 | 1899-12-31 14:49 | N-1224 | OSPD | S/D availed by NTPC for general maintenance work
NR140096 | 400KV SING-RIHAND-I | 2017-07-19 11:29 | 2017-07-19 19:59 | 0 | 0 | 0 | 0.35417 | N-1389 | OSPD | S/D taken by Chattisgarh WR transmission Ltd. for stringing (Power line crossing) of 400kV D/C Vindyachal 4&5 SSTPP Pool- Vindhya pool ( Line under construction by Chattisgarh WR transmission Ltd.)
NR140096 | 400KV SING-RIHAND-I | 2017-07-26 21:23 | 2017-07-26 22:57 | 0 | 0.065278 | 0 | 0 | **** | OMSU | Tripped at Singrauli end only due to DT received at Singrauli.
NR140097 | 400KV SING-RIHAND-II | 2017-07-15 14:52 | 2017-07-15 14:52 | 0 | 0 | 0 | 0 | **** | LART | Auto reclosed successfully from both end due to B-N fault. FD: 13.4km from Rihand
NR140097 | 400KV SING-RIHAND-II | 2017-07-19 11:27 | 2017-07-20 21:18 | 0 | 0 | 0 | 1899-12-31 09:51 | N-1384 | OSPD | S/D taken for Maintenance work by NTPC
NR340004 | 400KV VARANASI-SARNATH-I | 2017-07-01 09:02 | 2017-07-01 21:09 | 0.50486 | 0 | 0 | 0 | N-11 | OSPT | S/D taken for line maintenance work by Varanasi.
NR340004 | 400KV VARANASI-SARNATH-I | 2017-07-04 09:17 | 2017-07-04 20:40 | 0.47431 | 0 | 0 | 0 | N-259 | OSPT | S/D taken for line maintenance work by Varanasi.
NR340005 | 400KV VARANASI-SARNATH-II | 2017-07-01 13:16 | 2017-07-01 15:01 | 0 | 0.072917 | 0 | 0 | **** | SRMU | Tripped from Sarnath(UPPCL) end only due to relay mal operation at Sarnath(UPPCL) end.
NR340005 | 400KV VARANASI-SARNATH-II | 2017-07-03 09:35 | 2017-07-03 21:51 | 0.51111 | 0 | 0 | 0 | N-182 | OSPT | S/D taken for line maintenance work by Varanasi.
NR340005 | 400KV VARANASI-SARNATH-II | 2017-07-05 10:00 | 2017-07-05 19:13 | 0.38403 | 0 | 0 | 0 | N-367 | OSPT | S/D taken for line maintenance work
| 400KV VARANASI-SARNATH-II | 2017-07-31 11:08 | 2017-07-31 11:50 | 0 | 0.029167 | 0 | 0 |  | OMSU | Tripped only from Sarnath end due to problem at their end
NR122012 | 220KV DGANGA-BLY(UP)-II | 2017-07-01 20:07 | 2017-07-01 20:52 | 0.03125 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault,F.D.=201.7km from Bareily(UP), F.D.=18.63km from D'Ganga.
NR122012 | 220KV DGANGA-BLY(UP)-II | 2017-07-21 15:30 | 2017-07-21 16:30 | 0 | 0 | 0.041667 | 0 | **** | GOVC | Tripped due to over voltage at Dhauliganga(NHPC) end
NR122013 | 220KV DGANGA-PITHORAGRH | 2017-07-21 15:30 | 2017-07-21 16:26 | 0 | 0.038889 | 0 | 0 | **** | OMSU | Tripped due to problem at Dhauliganga(NHPC) end & DT received at Pithoragarh.
NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 2017-07-22 10:05 | 2017-07-22 16:28 | 0 | 0 | 0 | 0.26597 | N-1632 | OSFD | S/D taken by UPPCL to attend hot spot in line isolator at Fatehpur(UP) end.
NR122041 | 220KV FATEHPUR-NAUBASTA | 2017-07-15 12:03 | 2017-07-15 14:55 | 0 | 0 | 0 | 0.11944 | N-1111 | OSFD | S/D taken by UPPCL for attending CB problem at UPPCL end
NR122041 | 220KV FATEHPUR-NAUBASTA | 2017-07-15 18:48 | 2017-07-15 21:54 | 0 | 0.12917 | 0 | 0 | **** | OMSU | Tripped due to R-N fault. FD: 19.06km from Fatehpur, FC: Fatehpur-5.67KA. Fault in UPPCL jurisdiction.
NR122041 | 220KV FATEHPUR-NAUBASTA | 2017-07-28 19:53 | 2017-07-28 22:14 | 0 | 0 | 0 | 0.097917 | N-2049 | OSFD | Emergency S/D taken by UPPCL for attending sparking problem in conductor at UPPCL Naubasta end.
NR122041 | 220KV FATEHPUR-NAUBASTA | 2017-07-29 16:24 | 2017-07-29 22:16 | 0 | 0 | 0 | 0.24444 | N-2049 | OSFD | Emergency S/D taken by UPPCL for attending damaged R- phase CT at UPPCL Naubasta end.
NR122041 | 220KV FATEHPUR-NAUBASTA | 2017-07-31 15:38 | 2017-07-31 17:18 | 0 | 0.069444 | 0 | 0 | **** | OMSU | Tripped due to R-N fault. FD: 72.6km from Fatehpur, FC: 2.46KA. Fault in UPPCL jurisdiction
NR122017 | 220KV KNP-NAUBASTA | 2017-07-28 15:33 | 2017-07-28 17:08 | 0 | 0 | 0 | 0.065972 | N-2036 | OSFD | Emergency S/D taken by UPPCL for attending some problem in UPPCL Naubasta end.
NR122019 | 220KV KNP-PANKI-II | 2017-07-05 00:58 | 2017-07-05 16:38 | 0 | 0.65278 | 0 | 0 | **** | OMSU | Tripped on B-N fault. F.D.= 22KM from Kanpur & 0.746KM from Panki(UP), F.C.= 5.6KAmp at Kanpur. The fault is in UPPCL juridiction.
NR122022 | 220KV KNP-UNCHR-III | 2017-07-03 08:34 | 2017-07-03 21:48 | 0 | 0 | 0 | 0.55139 | N-171 | LCSD | S/D taken to facilitate rectification of theft conductor & cross arm of 220kv KNP-Unchahar-4 between loc no 397 to 399.
NR122022 | 220KV KNP-UNCHR-III | 2017-07-04 11:21 | 2017-07-04 18:24 | 0 | 0 | 0 | 0.29375 | N-269 | LCSD | S/D taken to facilitate rectification of theft conductor & cross arm of 220kv KNP-Unchahar-4 between loc no 397 to 399.
NR122023 | 220KV KNP-UNCHR-IV | 2017-07-01 | 2017-07-04 18:32 | 0 | 0 | 1900-01-02 18:32 | 0 | **** | LMAC | Tripped on R-N fault. F.D.= 15.93KM from Kanpur, F.C.= 8.56KAmp at Kanpur. During emergency patrolling it is found that conductor of bottom & middle phase cut & theft in between location nos. 396 to 399 and as a result 06 nos.cross-arms of middle & bottom phase at loc. no. 397, 398 & 399 are also damaged badly.
NR122023 | 220KV KNP-UNCHR-IV | 2017-07-29 12:44 | 2017-07-29 13:15 | 0.021528 | 0 | 0 | 0 | **** | LPPT | Tripped on R-Y fault. F.D.= 55KM from Kanpur & 85.9KM from Unchahar, F.C.: Ir=Iy= 4.1KAmp at Kanpur & Ir=Iy= 2KAmp at Unchahar
NR122024 | 220KV PITHORAGRH-BRLY(UP) | 2017-07-21 15:30 | 2017-07-21 15:57 | 0.01875 | 0 | 0 | 0 | **** | SPLT | Tripped from Bareilly (UP) end only due to PLCC mal operation at Pithoragarh end .
NR122032 | 220KV SITARGANJ-BLY(UP) | 2017-07-01 13:02 | 2017-07-01 14:02 | 0 | 0.041667 | 0 | 0 | **** | OMSU | Tripped due to some problem in Bareily (UPPCL) end
| 220KV SITARGANJ-CB GANJ | 2017-07-04 18:21 | 2017-07-04 20:00 | 0 | 0 | 0 | 0.06875 | N-314 | OSPD | S/D taken by UPPCL to attend CB at CB Ganj.
NR122034 | 220KV TNKPR-SITARGANJ | 2017-07-01 13:02 | 2017-07-01 14:06 | 0 | 0.044444 | 0 | 0 | **** | OMSU | Tripped from tanakpur end due to tripping of 220KV Sitarganj-Bareily(UP) line due to problem at Bareily (UPPCL) end
NR1ICT701 | 765/400KV ICT-I BALIA | 2017-07-09 08:41 | 2017-07-09 10:27 | 0.073611 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR3ICT701 | 765/400KV ICT-I KANPUR(GIS) | 2017-07-28 09:35 | 2017-07-28 18:27 | 0.36944 | 0 | 0 | 0 | N-2015 | OSPT | S/D availed for AMP work
NR1ICT702 | 765/400KV ICT-II BALIA | 2017-07-09 08:41 | 2017-07-09 10:41 | 0.083333 | 0 | 0 | 0 | **** | SEMT | Tripped due to B-Phase pole discrepancy of Main Circuit Breaker problem of 400kV Balia-Patna-4 at Balia and during opening the line isolator, causing fault due to creation of heavy Arc.Resulting tripping of all associated line at Balia.
NR1ICT26 | 315MVA ICT-I MAINPURI | 2017-07-28 09:26 | 2017-07-29 18:48 | 1899-12-31 09:22 | 0 | 0 | 0 | N-2015 | OSPT | S/D availed for replacement of B Ph bushing due to oil leakage and other maintainance work
NR1ICT27 | 315MVA ICT-II MAINPURI | 2017-07-26 11:55 | 2017-07-27 22:37 | 1899-12-31 10:42 | 0 | 0 | 0 | N-1914 | OSPT | S/D availed for replacement of 220kV R-phase bushing at Mainpuri.
NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 2017-07-08 23:52 | 2017-07-09 07:45 | 0 | 0 | 0 | 0.32847 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=393kV
NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 2017-07-16 21:12 | 2017-08-01 | 0 | 0 | 0 | 1900-01-14 02:48 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=389kV
NR1BRT46 | 125MVAR B/Reactor-II Gorakhpur | 2017-07-08 23:49 | 2017-07-09 06:21 | 0 | 0 | 0 | 0.27222 | - | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=390kV
NR1BRT46 | 125MVAR B/Reactor-II Gorakhpur | 2017-07-16 21:11 | 2017-08-01 | 0 | 0 | 0 | 1900-01-14 02:49 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=389kV
NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 2017-07-20 21:37 | 2017-07-22 10:28 | 0 | 0 | 0 | 1899-12-31 12:51 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=395kV
NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 2017-07-01 | 2017-07-01 16:01 | 0 | 0 | 0 | 0.66736 | N-2638 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=742kV
NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 2017-07-07 20:15 | 2017-07-09 08:08 | 0 | 0 | 0 | 1899-12-31 11:53 | N-615 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=740kV
NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 2017-07-14 20:05 | 2017-07-18 07:09 | 0 | 0 | 0 | 1900-01-02 11:04 | N-1079 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=747kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2017-07-01 12:58 | 2017-07-01 16:02 | 0 | 0 | 0 | 0.12778 | N-30 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=766kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2017-07-02 19:51 | 2017-07-03 07:03 | 0 | 0 | 0 | 0.46667 | N-146 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=747kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2017-07-13 20:45 | 2017-07-15 05:57 | 0 | 0 | 0 | 1899-12-31 09:12 | N-1021 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=755kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2017-07-16 21:10 | 2017-07-17 05:47 | 0 | 0 | 0 | 0.35903 | N-1206 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=754kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2017-07-20 22:10 | 2017-07-21 04:05 | 0 | 0 | 0 | 0.24653 | N-1532 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=747kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2017-07-29 00:21 | 2017-07-30 05:33 | 0 | 0 | 0 | 1899-12-31 05:12 | N-2063 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=740kV
NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 2017-07-08 21:27 | 2017-07-10 06:55 | 0 | 0 | 0 | 1899-12-31 09:28 | N-687 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=752kV
NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2017-07-07 20:27 | 2017-07-08 06:17 | 0 | 0 | 0 | 0.40972 | N-616 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=748kV
NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2017-07-08 21:35 | 2017-07-09 18:32 | 0 | 0 | 0 | 0.87292 | N-689 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=755kV
NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2017-07-14 20:05 | 2017-07-16 08:31 | 0 | 0 | 0 | 1899-12-31 12:26 | N-1078 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=751kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2017-07-01 14:48 | 2017-07-02 06:13 | 0 | 0 | 0 | 0.64236 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=406kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2017-07-02 19:58 | 2017-07-03 07:04 | 0 | 0 | 0 | 0.4625 |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=396kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2017-07-09 23:28 | 2017-07-10 06:50 | 0 | 0 | 0 | 0.30694 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. BRLY=391kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2017-07-11 23:57 | 2017-07-26 08:00 | 0 | 0 | 0 | 1900-01-13 08:03 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=397kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2017-07-26 20:01 | 2017-08-01 | 0 | 0 | 0 | 1900-01-04 03:59 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=389kV
NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 2017-07-08 21:38 | 2017-07-10 07:13 | 0 | 0 | 0 | 1899-12-31 09:35 | N-691 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=753kV
NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 2017-07-14 20:06 | 2017-07-26 07:50 | 0 | 0 | 0 | 1900-01-10 11:44 | N-1080 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=756kV
NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765 | 2017-07-07 20:57 | 2017-07-08 07:04 | 0 | 0 | 0 | 0.42153 | N-617 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=740kV
NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765 | 2017-07-08 21:38 | 2017-07-09 18:25 | 0 | 0 | 0 | 0.86597 | N-690 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=751kV
NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765 | 2017-07-16 22:28 | 2017-07-18 07:14 | 0 | 0 | 0 | 1899-12-31 08:46 | N-1212 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=750kV
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2017-07-01 12:50 | 2017-07-02 06:35 | 0 | 0 | 0 | 0.73958 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=396kV
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2017-07-09 23:34 | 2017-07-10 06:50 | 0 | 0 | 0 | 0.30278 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. BRLY=393kV
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2017-07-16 14:42 | 2017-08-01 | 0 | 0 | 0 | 1900-01-14 09:18 | N-1184 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=400kV
NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 2017-07-20 23:44 | 2017-07-21 09:56 | 0 | 0 | 0 | 0.425 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=394kV
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="T",(+[RESTORATION]-[OUTAGE]),0))
OTHERS = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="U",(+[RESTORATION]-[OUTAGE]),0))
Hrs:Min = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="C",(+[RESTORATION]-[OUTAGE]),0))
Deemed Available = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="D",(+[RESTORATION]-[OUTAGE]),0))
Deemed Available = IF(OR([RESTORATION]="****",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="D",(+[RESTORATION]-[OUTAGE]),0))
Note on B64: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet3
400kv LINES |  |  |  | 220kv LINES |  | ICTs,HVDC & SVC. |  | OTHER LINES
400kv LINES NR-I |  | 400kv LINES NR-III |  | 220kv LINES & ICT & Reactor NR-I |  | 220kv LINES & ICT & Reactor NR-III
400KV AGRA-JAIPUR(S)-I | 1 | 400KV AGRA-FATEHABD(UP)-I | 1 | 220KV ANTA-BHIL-I | 1 | 220KV ALLD-JHUSI(UP) | RRVPNL | 220KV BASSI-KUKAS-I
400KV AGRA-JAIPUR(S)-II | 2 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2 | 220KV ANTA-BHIL-II | 2 | 220KV ALLD-REWA RD-I | RRVPNL | 220KV BASSI-KUNDA KI DHANI
400KV AGRA-SIKAR-I | 3 | 400KV AGRA-AGRA(UP)-II | 3 | 220KV ANTA-LALSOT | 3 | 220KV ALLD-REWA RD-II | RRVPNL | 220KV BHIWADI(PG)-BHIWADI
400KV AGRA-SIKAR-II | 4 | 400KV AGRA-AURAIYA-I | 4 | 220KV ANTA-RAPPC | 4 | 220KV AUR-SIKANDARA-I | RRVPNL | 220KV BHIWADI-KHUSHKHERA-I
400KV BASSI-BHIWADI-I | 5 | 400KV AGRA-AURAIYA-II | 5 | 220KV ANTA-S.MDHPR | 5 | 220KV AUR-SIKANDARA-II | RRVPNL | 220KV BHIWADI-KHUSHKHERA-II
400KV BASSI-HIRAPURA-I | 6 | 400KV AGRA-BASSI-I | 6 | 220KV BASSI-BAGRU | 6 | 220KV DGANGA-BLY(UP)-II | RRVPNL | 220KV BHIWADI-NIMRANA(RJ)
400KV BASSI-HIRAPURA-II | 7 | 400KV AGRA-BHIWADI-I | 7 | 220KV BASSI-DAUSA-I | 7 | 220KV DGANGA-PITHORAGRH | RRVPNL | 220KV BHINMAL-BHINMAL-I
400KV BASSI-JAIPUR(S)-I | 8 | 400KV AGRA-BHIWADI-II | 8 | 220KV BASSI-DAUSA-II | 8 | 220KV FATEHPUR-FTHPR(UP)-I | RRVPNL | 220KV BHINMAL-BHINMAL-II
400KV BASSI-JAIPUR(S)-II | 9 | 400KV AGRA-BLBGRH | 9 | 220KV BASSI-IG NAGAR | 9 | 220KV FATEHPUR-FTHPR(UP)-II | RRVPNL | 220KV BHINMAL-SANCHORE
400KV BASSI-KOTPUTLI | 10 | 400KV ALLD-FATEHPUR-I | 10 | 220KV FGPP-PALLA-I | 10 | 220KV FATEHPUR-KNP SOUTH | RRVPNL | 220KV BHINMAL-SIROHI
400KV BASSI-PHAGI-I | 11 | 400KV ALLD-FATEHPUR-II | 11 | 220KV FGPP-PALLA-II | 11 | 220KV FATEHPUR-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-CHAKSU-I |  | LEGENDS
400KV BASSI-PHAGI-II | 12 | 400KV ALLD-FATEHPUR-III | 12 | 220KV FGPP-SPUR-I | 12 | 220KV JHUSI(UP)-PHULPUR(UP) | RRVPNL | 220KV JAIPUR(S)-CHAKSU-II
400KV BHINMAL-ZERDA | 13 | 400KV ALLD-KNP-II | 13 | 220KV FGPP-SPUR-II | 13 | 220KV KNP-MAINPURI | RRVPNL | 220KV JAIPUR(S)-SEZ |  |  | Lines maintained by ER
400KV BHIWADI-GURGAON | 14 | 400KV ALLD-VARANASI | 14 | 220KV HIRAPURA-IG NAGAR | 14 | 220KV KNP-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-DOONI
400KV BHIWADI-HISAR-I | 15 | 400KV BALIA-MAU-I | 15 | 220KV HIRAPURA-SANGANER | 15 | 220 KV KANPUR(PG) - RANIYA( UP)-1 | RRVPNL | 220KV KANKROLI(PG)-BHILWARA
400KV BHIWADI-KOTPUTLI | 16 | 400KV BALIA-MAU-II | 16 | 220KV LALSOT-DAUSA | 16 | 220 KV RANIYA( UP) - PANKI (UP)-1 | RRVPNL | 220KV KANKROLI(PG)-KANK-I
400KV BHIWADI-NIMRANA-I | 17 | 400KV BALIA-SOHAWAL-I | 17 | 220KV MEERUT-MPURAM-I | 17 | 220KV KNP-PANKI-II | RRVPNL | 220KV KANKROLI(PG)-KANK-II
400KV BHIWADI-NIMRANA-II | 18 | 400KV BALIA-SOHAWAL-II | 18 | 220KV MEERUT-MPURAM-II | 18 | 220KV KNP-UNCHR-I | RRVPNL | 220KV KANKROLI-DEBARI |  |  | lines maintained by WR
400KV BLBGRH-GURGAON | 19 | 400KV BAREILLY-BRLY(765)-I | 19 | 220KV MEERUT-NARA | 19 | 220KV KNP-UNCHR-II | RRVPNL | 220KV KOTA-KTPS-1
400KV BLBGRH-MAHRANIBG | 20 | 400KV BAREILLY-BRLY(765)-II | 20 | 220KV MEERUT-SHTBDNGR | 20 | 220KV KNP-UNCHR-III | RRVPNL | 220KV KOTA-KTPS-2 |  |  | LILO portions only of POWERGRID
400KV BLBGRH-NAVADA(HVPN) | 21 | 400KV BAREILLY-BRLY(UP)-I | 21 | 220KV MEERUT-SIMBHOLI | 21 | 220KV KNP-UNCHR-IV | RRVPNL | 220KV KOTA-BHILWARA
400KV DAD-GR.NOIDA | 22 | 400KV BAREILLY-BRLY(UP)-II | 22 | 220KV RAPPB-CHITT-I | 22 | 220KV PITHORAGRH-BRLY(UP) | RRVPNL | 220KV KOTA-DHUNI |  |  | LILO portion maintained by constituents
400KV DAD-MAHRANIBG | 23 | 400KV BAREILLY-LKO(UP) | 23 | 220KV RAPPB-CHITT-II | 23 | 220KV RAIBRLY-CHINHAT | RRVPNL | 220KV KOTPUTLI-KOTPUTLI
400KV DAD-MANDOLA-I | 24 | 400KV BAREILLY-MBAD-I | 24 | 220KV RAPPB-RAPPC | 24 | 220KV RAIBRLY-LKO(UP) | RRVPNL | 220KV KOTPUTLI-MANOHARPUR
400KV DAD-MANDOLA-II | 25 | 400KV BAREILLY-MBAD-II | 25 | 220KV RAPPB-UDAIPUR | 25 | 220KV SITARGANJ-BLY(UP) | RRVPNL | 220KV NIMRANA-NIMRANA
400KV DAD-MURADNGR | 26 | 400KV BAREILLY-ROSA-I | 26 | 220KV S.MDHPR-DAUSA-I | 26 | 220KV TNKPR-BLY(UP) | RRVPNL | 220KV NIMRANA-KHUSHKHERA |  |  | Maintained by NR-1 & NR-II
400KV DAD-PANIPAT-I | 27 | 400KV BAREILLY-SHAHJHNPR-I | 27 | 220KV SIKAR-RATANGARH-I | 27 | 220KV TNKPR-SITARGANJ | HVPNL | 220KV BHIWADI-MAU
400KV DAD-PANIPAT-II | 28 | 400KV BAREILLY-SHAHJHNPR-II | 28 | 220KV SIKAR-RATANGARH-II | 28 | 220KV UNCHR-RAIBRLY-I | HVPNL | 220KV BHIWADI-REWARI-I
400KV GURGAON-MANESAR-I | 29 | 400KV BARLY(765)-KASHIPUR-I | 29 | 220KV SIKAR-SIKAR(RJ)-I | 29 | 220KV UNCHR-RAIBRLY-II | HVPNL | 220KV BHIWADI-REWARI-II
400KV GURGAON-MANESAR-II | 30 | 400KV BARLY(765)-KASHIPUR-II | 30 | 220KV SIKAR-SIKAR(RJ)-II | 30 | 220KV UNCHR-RAIBRLY-III | HVPNL | 220KV BHIWADI-BAWAL
400KV JHATIKALA-BAMNOLI-I | 31 | 400KV BLBGRH-MAINPURI-I | 31 | 220KV HISAR-HISAR I/A-I |  |  | HVPNL | 220KV GURGAON-GURGAON-I
400KV JHATIKALA-BAMNOLI-II | 32 | 400KV BLBGRH-MAINPURI-II | 32 | 220KV HISAR-HISAR I/A-II |  |  | HVPNL | 220KV GURGAON-GURGAON-II
400KV JHATIKALA-MUNDKA-I | 33 | 400KV FATEHPUR-MAINPURI-I |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-III
400KV JHATIKALA-MUNDKA-II | 34 | 400KV FATEHPUR-MAINPURI-II |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-IV
400KV KANKROLI-BHINMAL | 35 | 400KV GORAKH-GORAKH-I |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-I
400KV KANKROLI-JODHPUR | 36 | 400KV GORAKH-GORAKH-II |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-II
400KV KANKROLI-CHITTOR(RJ)-I | 37 | 400KV KNP-AGRA |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-I
400KV KANKROLI-RAPPC-II | 38 | 400KV KNP-AURAIYA-I |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-II
400KV KANKROLI-ZERDA-I | 39 | 400KV KNP-AURAIYA-II |  | 400KV & 220KV ICT NR-I |  |  | HVPNL | 220 KV MANESAR-BADSHAHPUR-I
400KV KOTA-BEAWAR | 40 | 400KV KNP-BLBGARH-I | 1 | 315MVA ICT-I BASSI |  | 400KV & 220KV ICT NR-III | HVPNL | 220 KV MANESAR-BADSHAHPUR-II
400KV KOTA-MERTA-I | 41 | 400KV KNP-BLBGARH-II | 2 | 315MVA ICT-II BASSI | 1 | 315MVA ICT-I AGRA | HVPNL | 220 KV MANESAR-MAU-I
400KV KOTA-RAPPC | 42 | 400KV KNP-BLBGARH-III | 3 | 500MVA ICT-III BASSI | 2 | 315MVA ICT-I ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-II
400KV KOTESHWR-KHEP-I | 43 | 400KV KNP-FATEHPUR-I | 4 | 315MVA ICT-III BAWANA | 3 | 315MVA ICT-II ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-III
400KV KOTESHWR-KHEP-II | 44 | 400KV KNP-FATEHPUR-II | 5 | 315MVA ICT-I BHINMAL | 4 | 315MVA ICT-III ALLAHABAD | HVPNL | 220 KV SONIPAT-MOHANA-I
400KV KOTESHWR-TEHRI-I | 45 | 400KV KNP-PANKI-I | 6 | 315MVA ICT-II BHINMAL | 5 | 315MVA ICT-I FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-I
400KV KOTESHWR-TEHRI-II | 46 | 400KV KNP-PANKI-II | 7 | 315MVA ICT-I BHIWADI | 6 | 315MVA ICT-II FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-II
400KV MBAD-MURADNGR | 47 | 400KV LUCKNOW-GORAKH-III | 8 | 315MVA ICT-II BHIWADI | 7 | 315MVA ICT-I GORAKHPR | HVPNL | 220KV HISAR-SRWL-I
400KV MEERUT-BAGPAT-I | 48 | 400KV LUCKNOW-GORAKH-IV | 9 | 315MVA ICT-III BHIWADI | 8 | 315MVA ICT-II GORAKHPR | HVPNL | 220KV HISAR-SRWL-II
400KV MEERUT-BAREILLY-I | 49 | 400KV LUCKNOW-LKO(765)-I | 10 | 500MVA ICT-I BLBGARH | 9 | 315MVA ICT-I KANPUR | HVPNL | 220KV HISAR-FATEHABAD-I
400KV MEERUT-BAREILLY-II | 50 | 400KV LUCKNOW-LKO(765)-II | 11 | 315MVA ICT-II BLBGARH | 10 | 315MVA ICT-II KANPUR | HVPNL | 220KV HISAR-FATEHABAD-II
400KV MEERUT-KOTESHWR-I | 51 | 400KV LUCKNOW-LKO(UP) | 12 | 315MVA ICT-III BLBGARH | 11 | 315MVA ICT-I LUCKNOW | NTPC | 132KV SING-VINDH-RIH
400KV MEERUT-KOTESHWR-II | 52 | 400KV LUCKNOW-ROSA-I | 13 | 315MVA ICT-IV BLBGARH | 12 | 500MVA ICT-II LUCKNOW | NTPC | 132KV SING-RENUSAGAR-PIPRI
400KV MEERUT-MND-I | 53 | 400KV LUCKNOW-SHAHJHNPR-I | 14 | 315MVA ICT-I GURGAON | 13 | 315MVA ICT-I MAINPURI | DTL | 400KV B'GARH-BAMNOLI-I
400KV MEERUT-MND-II | 54 | 400KV LUCKNOW-SHAHJHNPR-II | 15 | 315MVA ICT-II GURGAON | 14 | 315MVA ICT-II MAINPURI | DTL | 400KV B'GARH-BAMNOLI-II
400KV MEERUT-MND-III | 55 | 400KV LUCKNOW-SOHAWAL-I | 16 | 500MVA ICT-I JAIPUR(S) | 15 | 100MVA ICT-I PITHORAGRH | DTL | 400KV MND-BAWANA-I
400KV MEERUT-MND-IV | 56 | 400KV LUCKNOW-SOHAWAL-II | 17 | 500MVA ICT-II JAIPUR(S) | 16 | 100MVA ICT-II PITHORAGRH | DTL | 400KV MND-BAWANA-II
400KV MEERUT-MUZFRNGR | 57 | 400KV LUCKNOW-SULTANPR | 18 | 315MVA ICT-I KANKROLI | 17 | 100MVA ICT-I RAIBAREILLY | DTL | 220KV MND-S.WZRBD-I
400KV MERTA-BEAWAR | 58 | 400KV LUCKNOW-UNNAO-I | 19 | 315MVA ICT-II KANKROLI | 18 | 100MVA ICT-II RAIBAREILLY | DTL | 220KV MND-S.WZRBD-II
400KV NAVADA(HVPN)-GR.NOIDA | 59 | 400KV LUCKNOW-UNNAO-II | 20 | 315MVA ICT-III KANKROLI | 19 | 100MVA ICT-III RAIBAREILLY | DTL | 220KV MND-S.WZRBD-III
400KV NIMRANA-MANESAR-I | 60 | 400KV MEERUT-BAREILLY-I | 21 | 315MVA ICT-I KOTA | 20 | 500MVA ICT-I SHAHJHNPR | DTL | 220KV MND-S.WZRBD-IV
400KV NIMRANA-MANESAR-II | 61 | 400KV MEERUT-BAREILLY-II | 22 | 315MVA ICT-II KOTA | 21 | 500MVA ICT-II SHAHJHNPR | DTL | 220KV MND-NARELA-I
400KV NIMRANA-SIKAR-I | 62 | 400KV RIHAND-ALLD-I | 23 | 315MVA ICT-I KOTPUTLI | 22 | 100MVA ICT-I SITARGANJ | DTL | 220KV MND-NARELA-II
400KV NIMRANA-SIKAR-II | 63 | 400KV RIHAND-ALLD-II | 24 | 315MVA ICT-II KOTPUTLI | 23 | 100MVA ICT-II SITARGANJ | DTL | 220KV MND-GOPALPUR-I
400KV ROORKI-KASHIPUR-I | 64 | 400KV RIHAND3-VINDH(Pool)-I | 25 | 315MVA ICT-I MAHRANIBAG | 24 | 315MVA ICT-I SOHAWAL | DTL | 220KV MND-GOPALPUR-II
400KV ROORKI-KASHIPUR-II | 65 | 400KV RIHAND3-VINDH(Pool)-II | 26 | 315MVA ICT-II MAHRANIBAG | 25 | 315MVA ICT-II SOHAWAL | DTL | 220KV MBAG-SARITAVIHAR
400KV ROORKI-MUZFRNGR | 66 | 400KV SING-ALLD-I | 27 | 500MVA ICT-III MAHRANIBAG | 26 |  | DTL | 220KV MBAG-LODHIROAD-I
400KV ROORKI-RISHIKESH | 67 | 400KV SING-ALLD-II | 28 | 500MVA ICT-IV MAHRANIBAG | 27 |  | DTL | 220KV MBAG-LODHIROAD-II
400KV SIKAR-RATANGARH-I | 68 | 400KV SING(NTPC)-ANPARA(UP) | 29 | 500MVA ICT-I MANDOLA | 28 |  | DTL | 220KV MBAG-I P EXTN
400KV SIKAR-RATANGARH-II | 69 | 400KV SING-FATEHPUR | 30 | 500MVA ICT-II MANDOLA | 29 |  | UPPCL | 220KV AGRA-SHAMSABD-I
400KV MEERUT-BAGPAT-II | 70 | 400KV SING-LKO(UP)-I | 31 | 500MVA ICT-III MANDOLA | 30 |  | UPPCL | 220KV AGRA-FEROZABAD
400KV ROORKI-SAHARANPUR-I | 71 | 400KV SING-RIHAND-I | 32 | 500MVA ICT-IV MANDOLA |  |  | UPPCL | 220KV BAGHPAT(PG)-BAGHPAT(UP)
400KV ROORKI-SAHARANPUR-II | 72 | 400KV SING-RIHAND-II | 33 | 500MVA ICT-I MANESAR |  |  | UPPCL | 220KV BAGHPAT-MURADNGR
400KV RAPPC-CHITTOR(RJ)-I | 73 | 400KV SING-VINDH-I | 34 | 500MVA ICT-II MANESAR |  |  | UPPCL | 220KV BAGHPAT-SHAMLI
| 74 | 400KV SING-VINDH-II | 35 | 315MVA ICT-I MEERUT |  |  | UPPCL | 220KV GORAKH-BARHUA
| 75 | 400KV KANPUR-KANPUR(GIS)-I | 36 | 315MVA ICT-II MEERUT |  | 765KV ICT NR-III | UPPCL | 220KV GORAKH-BASTI
| 76 | 400KV KANPUR-KANPUR(GIS)-II | 37 | 315MVA ICT-III MEERUT | 1 | 765/400KV ICT-I BALIA | UPPCL | 220KV LKO(PG)-Bakhsi Ka Talab
| 77 | 400KV VARANASI-SASARAM(ER) | 38 | 500MVA ICT-IV MEERUT | 2 | 765/400KV ICT-II BALIA | UPPCL | 220KV LKO(PG)-CHINHAT
400KV BAHADURGRH-BAWANA | 78 | 400KV VARANASI-SARNATH-I | 39 | 315MVA ICT-III MUZFRNGR | 3 | 765/400KV ICT-I LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-I
400KV BAHADURGRH-SONIPAT-I | 79 | 400KV VARANASI-SARNATH-II | 40 | 315MVA ICT-II NIMRANA | 4 | 765/400KV ICT-II LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-II
400KV BAHADURGRH-SONIPAT-II | 80 | 400KV ALLAHABAD-MEJA(NTPC)-I | 41 | 315MVA ICT-I ROORKI | 5 | 765/400KV ICT-I FATEHPUR | UPPCL | 220KV M'PURI-ETAH
400KV BHIWANI-BAWANA | 81 | 400KV BALIA-BIHARSHRF-I | 42 | 315MVA ICT-II ROORKI | 6 | 765/400KV ICT-II FATEHPUR | UPPCL | 220KV M'PURI-SIRSAGANJ-I
400KV BHIWANI-BHIWANI(BBMB) | 82 | 400KV BALIA-BIHARSHRF-II | 43 | 315MVA ICT-I SIKAR | 7 | 765/400KV ICT-I AGRA | UPPCL | 220KV M'PURI-M'PURI(UP)-II
400KV BHIWANI-HISAR-I | 83 | 400KV ALLD-SASARAM | 44 | 315MVA ICT-II SIKAR | 8 | 765/400KV ICT-II AGRA | UPPCL | 220KV M'PURI-FEROZBD
400KV BHIWANI-HISAR-II | 84 | 400KV BALIA-PATNA-I | 45 | 500MVA ICT-I BAGPAT | 9 | 765/400KV ICT-I BAREILLY | UPPCL | 400KV M'PURI-ORAI-I
400KV BHIWANI-HISAR-III | 85 | 400KV BALIA-PATNA-II | 46 | 500MVA ICT-II BAGPAT | 10 | 765/400KV ICT-II BAREILLY | UPPCL | 400KV M'PURI-PARICHA-II
400KV BHIWANI-JIND-I | 86 | 400KV BALIA-PATNA-III | 47 | 315MVA ICT-I SAHARANPUR | 11 | 765/400KV ICT-I VARANASI | UPPCL | 220KV MEERUT-GAJRAULA
400KV BHIWANI-JIND-II | 87 | 400KV BALIA-PATNA-IV | 48 | 315MVA ICT-II SAHARANPUR | 12 | 765/400KV ICT-II VARANASI | UPPCL | 220KV MEERUT-NEHTAUR
400KV FATEHABAD-HISAR | 88 | 400KV LKO(765)-KANPUR(GIS)-I |  |  | 13 | 765/400KV ICT-I KANPUR(GIS) | UPPCL | 220KV ORAI-KANPUR
400KV BHIWADI-HISAR-II | 89 | 400KV LKO(765)-KANPUR(GIS)-II |  |  | 14 | 765/400KV ICT-II KANPUR(GIS) | UPPCL | 400KV PANKI-MURADNGR
400KV BHIWADI-HISAR-III | [6 empty] | UPPCL | 220KV SHAHJHNP-HARDOI
400KV HISAR-BHIWANI(BBMB) | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-I | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-II |  | 400kv LINES of ER-1 in NR-III Availability |  | NR-I Additional ICT from NR-II |  |  | UPPCL | 220KV SOHAWAL(PG) - SOHAWAL(UP)
400KV KABULPR-BAHADURGRH | 1 | 400KV SASARAM-BIHARSHRF-I | 1 | 315MVA ICT-I BAHADURGARH |  | NR-III HVDC SYSTEM / SVC | UPPCL | 220KV UNCHR-RBRLY-I
400KV KABULPR-BHIWANI | 2 | 400KV SASARAM-BIHARSHRF-II | 2 | 500MVA ICT-II BAHADURGARH | 1 | 500KV HVDC R-D POLE-I | UPPCL | 220KV UNCHR-RBRLY-II
|  |  | 3 | 315MVA ICT-I HISAR | 2 | 500KV HVDC R-D POLE-II | PTCUL | 220KV ROORKI-HARDWAR
|  |  | 4 | 315MVA ICT-II HISAR | 3 | 500KV HVDC BALIA-BHWD POLE-I | PTCUL | 220KV ROORKI--RAMNAGAR
|  | 765 KV TRANS LINES NR-III | 5 | 315MVA ICT-III HISAR | 4 | 500KV HVDC BALIA-BHWD POLE-II | PTCUL | 132KV SITARGNJ(PG)-SITARGNJ(PTCUL)
765 KV TRANS LINES NR-I | 1 | 765KV AGRA-FATEHPUR-I | 6 | 315MVA ICT-I SONIPAT | 5 | 800KV HVDC AGRA-BNC POLE-I | PTCUL | 132KV PITHORAGRH-CHANDOK
765KV AGRA-JHATIKALA | 2 | 765KV AGRA-FATEHPUR-II | 7 | 315MVA ICT-II SONIPAT | 6 | 800KV HVDC AGRA-BNC POLE-II | PTCUL | 132KV PITHORAGRH-ALMORA
765KV BHIWANI-PHAGI(JPR)-I | 3 | 765KV AGRA-GR.NOIDA | 8 | 315MVA ICT-I BHIWANI | 7 | VINDH HVDC B/B BLOCK-I | PTCUL | 132KV PTRGRH-PTRGRH(PTCUL)
765KV MEERUT-GR.NOIDA | 4 | 765KV FATEHPUR-SASARAM | 9 | 315MVA ICT-II BHIWANI | 8 | VINDH HVDC B/B BLOCK-II | POWERLINK
765KV MOGA-BHIWANI | 5 | 765KV LUCKNOW-BALIA | 10 | 500MVA ICT-I JIND | 9 | SASARAM HVDC B/B | PLINK | 400KV LUCKNOW-GORAKH-I (PL)
765KV JHATIKALA-BHIWANI | 6 | 765KV LUCKNOW-BAREILLY | 11 | 500MVA ICT-II JIND | 10 | +/-140MVAR SVC-I KANPUR | PLINK | 400KV LUCKNOW-GORAKH-II (PL)
765KV MEERUT-BHIWANI | 7 | 765KV VARANASI-BALIA |  |  | 11 | +/-140MVAR SVC-II KANPUR | PLINK | 400KV GRKHPR-MZFRPR-I (PL)
765KV BHIWANI-PHAGI(JPR)-II | 8 | 765KV VARANASI-FATEHPUR |  |  |  |  | PLINK | 400KV GRKHPR-MZFRPR-II (PL)
| 9 | 765KV VARANASI-GAYA-I |  | 765KV ICT NR-I
| 10 | 765KV VARANASI-KANPUR(GIS)-I | 1 | 765/400KV ICT-I JHATIKALA
BUS REACTORS NR-I | 11 | 765KV VARANASI-KANPUR(GIS)-II | 2 | 765/400KV ICT-II JHATIKALA |  | SWITCABLE LINE REACTORS NR-III | NR-II | 400KV DAD-M'KOTLA
125MVAR B/Reactor-I BAGPAT | 12 | 765KV KANPUR(GIS)-JHATIKRA-I | 3 | 765/400KV ICT-III JHATIKALA | 1 | AGRA 240MVAR S/R FATEHPR line | NR-II | 400KV BAGHPAT-KAITHAL-I
50MVAR B/Reactor-I BASSI |  |  | 4 | 765/400KV ICT-IV JHATIKALA | 2 | AGRA 50MVAR S/R BHIWADI-I LINE | NR-II | 400KV BAGHPAT-KAITHAL-II
50MVAR B/Reactor-II BASSI |  |  | 5 | 765/400KV ICT-I MEERUT | 3 | ALLHBD 50MVAR S/R MNPR-I LINE | NR-II | 765KV MEERUT-MOGA
50MVAR B/Reactor-III BASSI |  | BUS REACTORS NR-III | 6 | 765/400KV ICT-II MEERUT | 4 | ALLHBD 50MVAR S/R MNPR-II LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-I | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
125MVAR B/Reactor-IV BASSI | 1 | 125MVAR B/Reactor-I AGRA | 7 | 765/400KV ICT-I BHIWANI | 5 | BARLLY 50MVAR S/R MND-I LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-II | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
80MVAR B/Reactor BHINMAL | 2 | 125MVAR B/Reactor-II AGRA | 8 | 765/400KV ICT-II BHIWANI | 6 | BARLLY 50MVAR S/R MND-II LINE | NR-II | 400KV HISAR-MOGA-I
80MVAR B/Reactor BHIWADI | 3 | 240MVAR B/Reactor-II AGRA-765 |  |  | 7 | BALIA 240MVAR S/R LUCKNW Ckt-I | NR-II | 400KV HISAR-MOGA-II
80MVAR B/Reactor BLBGARH | 4 | 240MVAR B/Reactor-1 AGRA-765 |  |  | 8 | BALIA 240MVAR S/R GAYA Line | NR-II | 400KV HISAR-MOGA-III
125MVAR B/Reactor-I JAIPUR(S) | 5 | 80MVAR B/Reactor ALLAHABAD |  |  | 9 | FATEHPR 330MVAR S/R AGRA line
125MVAR B/Reactor-II JAIPUR(S) | 6 | 125MVAR B/Reactor-II ALLAHABAD |  |  | 10 | GORAKH 50MVAR S/R LKO-I LINE
240MVAR B/Reactor-I JHATIKALA-765 | 7 | 80MVAR B/Reactor-I BALIA |  |  | 11 | GORAKH 50MVAR S/R LKO-II LINE
240MVAR B/Reactor-II JHATIKALA-765 | 8 | 125MVAR B/Reactor-II BALIA |  |  | 12 | GORAKH 63MVAR S/R LKO-III LINE
50MVAR B/Reactor KANKROLI | 9 | 125MVAR B/Reactor-III BALIA |  | SWITCABLE LINE REACTORS NR-I | 13 | GORAKH 63MVAR S/R LKO-IV LINE | ER-I | 400KV BALIA-SASARAM
125MVAR B/Reactor-II KANKROLI | 10 | 125MVAR B/Reactor-IV BALIA | 1 | BHINML 50MVAR S/R KANKROLI | 14 | GORAKH 80MVAR S/R Barh-I line | ER-I | 765KV BALIA-GAYA
80MVAR B/Reactor-I KOTA | 11 | 240MVAR B/Reactor-I BALIA-765 | 2 | MEERUT 50MVAR S/R Kotesh-I LINE | 15 | GORAKH 80MVAR S/R Barh-II line | ER-I | 400KV BARH- GRKHPR-I
50MVAR B/Reactor-II KOTA | 12 | 240MVAR B/Reactor-II BALIA-765 | 3 | MEERUT 50MVAR S/R Kotesh-II LINE | 16 | LUCKNW 240MVAR S/R BRLY Line | ER-I | 400KV BARH- GRKHPR-II
80MVAR B/Reactor-I KOTPUTLI | 13 | 80MVAR B/Reactor BAREILLY | 4 | JHATIKALA 240MVAR S/R AGRA Line | 17 | LUCKNW 63MVAR S/R GKP-III LINE | ER-I | 765KV VARANASI-GAYA-II
50MVAR B/Reactor MANDOLA | 14 | 2x50MVAR B/Reactor BAREILLY | 5 | MEERUT 240MVAR S/R AGRA line | 18 | LUCKNW 63MVAR S/R GKP-IV LINE | ER-I | 400KV VARANASI-BIHARSHRF-I
240MVAR B/Reactor-I MEERUT-765 | 15 | 240MVAR B/Reactor-I BAREILLY-765 | 6 | SIKAR 50MVAR S/R AGRA Ckt-I | 19 | LUCKNW 240MVAR S/R BALIA Ckt-I | ER-I | 400KV VARANASI-BIHARSHRF-II
125MVAR B/Reactor MANESAR | 16 | 80MVAR B/Reactor BIHARSHRF | 7 | SIKAR 50MVAR S/R AGRA Ckt-II | 20 | VARANASI 240MVAR S/R KNP(GIS) ckt-1
50MVAR B/Reactor MURADNGR | 17 | 125MVAR B/Reactor-I FATEHPUR | 8 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | 21 | VARANASI 240MVAR S/R KNP(GIS) ckt-2
80MVAR B/Reactor NIMRANA | 18 | 125MVAR B/Reactor-II FATEHPUR | 9 | BHIWANI 240MVAR S/R MEERUT line | 22 | KNP(GIS) 330MVAR S/R JHATIKRA ckt-1 | WR | 765KV AGRA-GWALIOR-I
240MVAR B/Reactor-I PHAGI(JPR)-765 | 19 | 330MVAR B/Reactor-III FTHPR-765 | 10 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line |  |  | WR | 765KV AGRA-GWALIOR-II
125MVAR B/Reactor ROORKEE | 20 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | WR | 765KV GWALIOR-PHAGI-I
125MVAR B/Reactor-I RATANGRH(RJ) | 21 | 125MVAR B/Reactor-II LUCKNOW |  | SVC NR-I |  |  | WR | 765KV GWALIOR-PHAGI-II
80MVAR B/Reactor SIKAR | 22 | 125MVAR B/Reactor-III LUCKNOW | 1 | +400/-300MVAR SVC KANKROLI
50MVAR B/Reactor-I SAHARANPUR | 23 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-I
50MVAR B/Reactor-II SAHARANPUR | 24 | 125MVAR B/Reactor-I VINDH |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-II
125MVAR B/Reactor-II SONIPAT | 25 | 125MVAR B/Reactor-II VINDH
| 26 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - I
BUS REACTORS NR-I From NR2 | 27 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - II
240MVAR B/Reactor-I BHIWANI | 28 | 125MVAR B/Reactor-1 Mainpuri
240MVAR B/Reactor-II BHIWANI | 29 | 125MVAR B/Reactor Gorakhpur-I
50MVAR B/Reactor HISAR | 30 | 125MVAR B/Reactor-II Gorakhpur
125MVAR B/Reactor HISAR | 31 | 125MVAR B/Reactor-I SHAHJHNPR
125MVAR Bus/eactor JIND | 32 | 240MVAR B/Reactor-I KANPUR(GIS)
125MVAR B/Reactor SONIPAT | 33 | 240MVAR B/Reactor-II KANPUR(GIS)
| 34 | 125MVAR B/Reactor-III KANPUR(GIS)
| 35 | 125MVAR B/Reactor-I VARANASI
| 36 | 330MVAR B/Reactor-I VARANASI
| 37 | 330MVAR B/Reactor-II VARANASI
| 38 | 125MVAR B/Reactor KANPUR
Note on E50: a: DOC-01.04.12
Note on I83: 220KV M'PURI-M'PURI(UP)-I LILO at SIRSAGANJ
Note on E84: a: DOC-01.04.12
Note on I86: '400KV M'PURI-PARICHA-I LILO at URI
Note on A96: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on A97: Total-45.6km, PG-26.64km, HVPN-19km.
Note on I98: DELL: 220KV ROORKI-SIDKUL
Note on C108: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C109: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on I112: LILO of 400KV MEERUT-KAITHAL-I at Baghpat
Note on I113: LILO of 400KV MEERUT-KAITHAL-II at Baghpat
Note on I128: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet4
SL.NO. | ELEMENT | Element Name
ID
A |  | 765 KV TRANS LINES
1 | NR176502 | 765KV AGRA-FATEHPUR-I
2 | NR176507 | 765KV AGRA-FATEHPUR-II
3 | NR176510 | 765KV AGRA-GR.NOIDA
4 | NR176506 | 765KV FATEHPUR-SASARAM
5 | NR176501 | 765KV LUCKNOW-BALIA
6 | NR176508 | 765KV LUCKNOW-BAREILLY
7 | NR176512 | 765KV VARANASI-BALIA
8 | NR176513 | 765KV VARANASI-FATEHPUR
9 | NR176514 | 765KV VARANASI-GAYA-I
10 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I
11 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I
B |  | 400 KV TRANS LINES
1 | NR140002 | 400KV AGRA-AGRA(UP)-II | 400KV AGRA-AGRA(UP)-II | 400KV AGRA-FATEHABD(UP)-I
2 | NR140003 | 400KV AGRA-AURAIYA-I | 400KV AGRA-AURAIYA-I
3 | NR140004 | 400KV AGRA-AURAIYA-II | 400KV AGRA-AURAIYA-II
4 | NR140005 | 400KV AGRA-BASSI-I | 400KV AGRA-BASSI-I
5 | NR140008 | 400KV AGRA-BHIWADI-I | 400KV AGRA-BHIWADI-I
6 | NR140009 | 400KV AGRA-BHIWADI-II | 400KV AGRA-BHIWADI-II
7 | NR140010 | 400KV AGRA-BLBGRH | 400KV AGRA-BLBGRH
8 | NR140122 | 400KV ALLD-FATEHPUR-I | 400KV ALLD-FATEHPUR-I
9 | NR140123 | 400KV ALLD-FATEHPUR-II | 400KV ALLD-FATEHPUR-II
10 | NR140104 | 400KV ALLD-FATEHPUR-III | 400KV ALLD-FATEHPUR-III
11 | NR140012 | 400KV ALLD-KNP-II | 400KV ALLD-KNP-II
12 | NR140163 | 400KV ALLD-VARANASI | 400KV ALLD-VARANASI
13 | NR140016 | 400KV ALLD-SASARAM | 400KV ALLD-SASARAM
14 | NR140017 | 400KV BALIA-BIHARSHRF-I | 400KV BALIA-BIHARSHRF-I
15 | NR140018 | 400KV BALIA-BIHARSHRF-II | 400KV BALIA-BIHARSHRF-II
16 | NR140019 | 400KV BALIA-MAU-I | 400KV BALIA-MAU-I
17 | NR140020 | 400KV BALIA-MAU-II | 400KV BALIA-MAU-II
18 | NR140021 | 400KV BALIA-PATNA-I | 400KV BALIA-PATNA-I
19 | NR140022 | 400KV BALIA-PATNA-II | 400KV BALIA-PATNA-II
20 | NR140136 | 400KV BALIA-PATNA-III | 400KV BALIA-PATNA-III
21 | NR140137 | 400KV BALIA-PATNA-IV | 400KV BALIA-PATNA-IV
22 | NR140140 | 400KV BALIA-SOHAWAL-I | 400KV BALIA-SOHAWAL-I
23 | NR140120 | 400KV BALIA-SOHAWAL-II | 400KV BALIA-SOHAWAL-II
24 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 400KV BAREILLY-BAREILLY(765)-I
25 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 400KV BAREILLY-BAREILLY(765)-II
26 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 400KV BAREILLY-BRLY(UP)-I
27 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 400KV BAREILLY-BRLY(UP)-II
28 | NR140025 | 400KV BAREILLY-LKO(UP) | 400KV BAREILLY-LKO(UP)
29 | NR140026 | 400KV BAREILLY-MBAD-I | 400KV BAREILLY-MBAD-I
30 | NR140027 | 400KV BAREILLY-MBAD-II | 400KV BAREILLY-MBAD-II
31 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 400KV BAREILLY-SHAHJHNPR-I
32 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 400KV BAREILLY-SHAHJHNPR-II | 400KV BAREILLY-ROSA-I
33 | NR140158 | 400KV BARLY(765)-KASHIPUR-I | 400KV BRLY(765)-KASHIPUR-I
34 | NR140159 | 400KV BARLY(765)-KASHIPUR-II | 400KV BRLY(765)-KASHIPUR-II
35 | NR140037 | 400KV BLBGRH-MAINPURI-I | 400KV BLBGRH-MAINPURI-I
36 | NR140038 | 400KV BLBGRH-MAINPURI-II | 400KV BLBGRH-MAINPURI-II
37 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 400KV FATEHPUR-MAINPURI-I
38 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 400KV FATEHPUR-MAINPURI-II
39 | NR140046 | 400KV GORAKH-GORAKH-I | 400KV GORAKH-GORAKH-I
40 | NR140047 | 400KV GORAKH-GORAKH-II | 400KV GORKH-GORAKH-II
41 | NR140052 | 400KV KNP-AGRA | 400KV KNP-AGRA
42 | NR140053 | 400KV KNP-AURAIYA-I | 400KV KNP-AURAIYA-I
43 | NR140054 | 400KV KNP-AURAIYA-II | 400KV KNP-AURAIYA-II
44 | NR140055 | 400KV KNP-BLBGARH-I | 400KV KNP-BLBGARH-I
45 | NR140056 | 400KV KNP-BLBGARH-II | 400KV KNP-BLBGARH-II
46 | NR140057 | 400KV KNP-BLBGARH-III | 400KV KNP-BLBGARH-III
47 | NR140110 | 400KV KNP-FATEHPUR-I | 400KV KNP-FATEHPUR-I
48 | NR140105 | 400KV KNP-FATEHPUR-II | 400KV KNP-FATEHPUR-II
49 | NR140058 | 400KV KNP-PANKI-I | 400KV KNP-PANKI-I
50 | NR140059 | 400KV KNP-PANKI-II | 400KV KNP-PANKI-II
51 | NR140070 | 400KV LUCKNOW-GORAKH-III | 400KV LUCKNOW-GORAKH-III
52 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 400KV LUCKNOW-GORAKH-IV
53 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 400KV LUCKNOW-LKO(765)-I
54 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 400KV LUCKNOW-LKO(765)-II
55 | NR140072 | 400KV LUCKNOW-LKO(UP) | 400KV LUCKNOW-LKO(UP)
56 | NR140114 | 400KV LUCKNOW-ROSA-I | 400KV LUCKNOW-ROSA-I
57 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 400KV LUCKNOW-SHAHJHNPR-II
58 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 400KV LUCKNOW-SOHAWAL-I
59 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 400KV LUCKNOW-SOHAWAL-II
60 | NR140073 | 400KV LUCKNOW-SULTANPR | 400KV LUCKNOW-SULTANPR
61 | NR140074 | 400KV LUCKNOW-UNNAO-I | 400KV LUCKNOW-UNNAO-I
62 | NR140075 | 400KV LUCKNOW-UNNAO-II | 400KV LUCKNOW-UNNAO-II
63 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 400KV RIHAND3-VINDH(Pool)-I
64 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 400KV RIHAND3-VINDH(Pool)-II
65 | NR140084 | 400KV RIHAND-ALLD-I | 400KV RIHAND-ALLD-I
66 | NR140085 | 400KV RIHAND-ALLD-II | 400KV RIHAND-ALLD-II
67 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 400KV SASARAM-BIHARSHRF-I
68 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 400KV SASARAM-BIHARSHRF-II
69 | NR140090 | 400KV SASARAM-SARNATH | 400KV SASARAM-SARNATH
70 | NR140091 | 400KV SING-ALLD-I | 400KV SING-ALLD-I
71 | NR140092 | 400KV SING-ALLD-II | 400KV SING-ALLD-II
72 | NR140093 | 400KV SING-ANPARA | 400KV SING-ANPARA
73 | NR140111 | 400KV SING-FATEHPUR | 400KV SING-FATEHPUR
74 | NR140095 | 400KV SING-LKO(UP)-I | 400KV SING-LKO(UP)
75 | NR140096 | 400KV SING-RIHAND-I | 400KV SING-RIHAND-I
76 | NR140097 | 400KV SING-RIHAND-II | 400KV SING-RIHAND-II
77 | N-W40001 | 400KV SING-VINDH-I | 400KV SING-VINDH-I
78 | N-W40002 | 400KV SING-VINDH-II | 400KV SING-VINDH-II
79 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 400KV KANPUR-KANPUR(GIS)-I
80 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 400KV KANPUR-KANPUR(GIS)-II
81 | NR340003 | 400KV VARANASI-SASARAM(ER)
82 | NR340004 | 400KV VARANASI-SARNATH-I | 400KV VARANASI-SARNATH-I
83 | NR340005 | 400KV VARANASI-SARNATH-II | 400KV VARANASI-SARNATH-II
84 | NR340006 | 400KV AGRA-FATEHABD(UP)-I
85 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II
86 | NR340008 | 400KV LKO(765)-KANPUR(GIS)-I | 400KV LKO(765)-KANPUR(GIS)-I
87 | NR340009 | 400KV LKO(765)-KANPUR(GIS)-II | 400KV LKO(765)-KANPUR(GIS)-II
88 | NR140142 | 400KV MEERUT-BAREILLY-I
89 | NR140130 | 400KV MEERUT-BAREILLY-II
90 | NR340010 | 400KV ALLAHABAD-MEJA(NTPC)-I
C |  | 220 KV TRANS LINES
1 | BILUP2209 | 220KV ALLD-JHUSI(UP)
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP)
3 | BILUP2202 | 220KV ALLD-REWA RD-I
4 | BILUP2203 | 220KV ALLD-REWA RD-II
5 | NR122006 | 220KV AUR-SIKANDARA-I
6 | NR122007 | 220KV AUR-SIKANDARA-II
7 | NR122012 | 220KV DGANGA-BLY(UP)-II
8 | NR122013 | 220KV DGANGA-PITHORAGRH
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH
12 | NR122041 | 220KV FATEHPUR-NAUBASTA
13 | NR122016 | 220KV KNP-MAINPURI
14 | NR122017 | 220KV KNP-NAUBASTA
15 | NR122019 | 220KV KNP-PANKI-II
16 | NR122020 | 220KV KNP-UNCHR-I
17 | NR122021 | 220KV KNP-UNCHR-II
18 | NR122022 | 220KV KNP-UNCHR-III
19 | NR122023 | 220KV KNP-UNCHR-IV
20 | NR122024 | 220KV PITHORAGRH-BRLY(UP)
21 | NR122025 | 220KV RAIBRLY-CHINHAT
22 | NR122026 | 220KV RAIBRLY-LKO(UP)
23 | NR122032 | 220KV SITARGANJ-BLY(UP)
24 | NR122033 | 220KV TNKPR-BLY(UP)
25 | NR122034 | 220KV TNKPR-SITARGANJ
26 | NR122035 | 220KV UNCHR-RAIBRLY-I
27 | NR122036 | 220KV UNCHR-RAIBRLY-II
28 | NR122037 | 220KV UNCHR-RAIBRLY-III
29 | NR320001 | 220KV KNP-RANIA
30 | NR320002 | 220KV RANIA-PANKI
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA
#REF! | Lines | TOTAL FOR T/LS
OVERALL SYSTEM AVAILABILITY=
E |  | 765/400 KV ICT'S
1 | NR1ICT707 | 765/400KV ICT-I AGRA
2 | NR1ICT708 | 765/400KV ICT-II AGRA
3 | NR1ICT701 | 765/400KV ICT-I BALIA
4 | NR1ICT702 | 765/400KV ICT-II BALIA
5 | NR1ICT715 | 765/400KV ICT-I BAREILLY
6 | NR1ICT716 | 765/400KV ICT-II BAREILLY
7 | NR1ICT705 | 765/400KV ICT-I FATEHPUR
8 | NR1ICT706 | 765/400KV ICT-II FATEHPUR
9 | NR1ICT703 | 765/400KV ICT-I LUCKNOW
10 | NR1ICT704 | 765/400KV ICT-II LUCKNOW
11 | NR1ICT717 | 765/400KV ICT-I VARANASI
12 | NR1ICT718 | 765/400KV ICT-II VARANASI
13 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS)
14 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS)
F |  | 400/220 KV ICT'S
1 | NR1ICT70 | 315MVA ICT-I AGRA
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR
9 | NR1ICT19 | 315MVA ICT-I KANPUR
10 | NR1ICT20 | 315MVA ICT-II KANPUR
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW
13 | NR1ICT26 | 315MVA ICT-I MAINPURI
14 | NR1ICT27 | 315MVA ICT-II MAINPURI
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 100MVA ICT-I PITHORAGRH
2 | NR1ICT44 | 100MVA ICT-II PITHORAGRH
3 | NR1ICT47 | 100MVA ICT-I RAIBAREILLY
4 | NR1ICT38 | 100MVA ICT-II RAIBAREILLY
5 | NR1ICT39 | 100MVA ICT-III RAIBAREILLY
6 | NR1ICT40 | 100MVA ICT-I SITARGANJ
7 | NR1ICT41 | 100MVA ICT-II SITARGANJ
39 |  | TOTAL FOR ICTs
H |  | HVDC RIHAND-DADRI
1 | NR1DCP01 | 500KV HVDC R-D POLE-I
2 | NR1DCP02 | 500KV HVDC R-D POLE-II
3 | NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I
4 | NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II
TOTAL FOR HVDC line
J |  | HVDC AGRA-BNC
1 | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I
2 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II
TOTAL of HVDC POLE-I
K |  | HVDC BTB VINDHYACHAL
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II
TOTAL FOR HVDC VINDHYACHAL
L |  | HVDC BTB SASARAM
1 | NEDCB01 | +/-500MW HVDC B/B SASARAM
TOTAL FOR HVDC SASARAM
M |  | SVC, KANPUR
1 | NR1SVC01 | +/-140MVAR SVC-I KANPUR
2 | NR1SVC02 | +/-140MVAR SVC-II KANPUR
TOTAL FOR SVC
N |  | Bus & Switch Line Reactor
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD
6 | NR1BRT33 | 125MVAR B/Reactor-II ALLAHABAD
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY
14 | NR1BRT44 | 2x50MVAR B/Reactor- BAREILLY
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR
20 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI
28 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR
29 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W
30 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N
31 | NR1BRT42 | 125MVAR B/Reactor-I VINDH
32 | NR1BRT43 | 125MVAR B/Reactor-II VINDH
| NR1BRT55 | 330MVAR B/Reactor-I VARANASI
33 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI
34 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I
35 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line
36 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I
37 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II
38 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line
39 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I
40 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I
41 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II
42 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line
43 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I
44 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II
45 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE
46 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE
47 | NR1SRT24 | GORAKH 80MVAR S/R Barh-I line
48 | NR1SRT25 | GORAKH 80MVAR S/R Barh-II line
49 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE
50 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE
51 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I
52 | NR1SRT26 | LUCKNW 240MVAR S/R Bareilly Line
53 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS)
54 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS)
55 | NR3SRT01 | VARANASI 240MVAR S/R KNP(GIS)-1
56 | NR3SRT02 | VARANASI 240MVAR S/R KNP(GIS)-2
57 | NR3SRT03 | KNP(GIS) 330MVAR S/R JHATIKRA-1
58 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS)
59 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI
TOTAL FOR BUS REACTORS
TOTAL
Note on C7: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C12: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C13: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C29: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16
Note on D48: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on D49: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C74: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C86: Line Re-configured as 400kv Varanasi-Sasaram(ER) on 30-09-16.
Note on D99: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on D100: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C101: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C102: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C143: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C144: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C239: DOC-26/05/2014

## Sheet5
220KV ALLD-JHUSI(UP)
220KV JHUSI(UP)-PHULPUR(UP)
220KV ALLD-REWA RD-I
220KV ALLD-REWA RD-II
220KV AUR-SIKANDARA-I
220KV AUR-SIKANDARA-II
220KV DGANGA-BLY(UP)-II
220KV DGANGA-PITHORAGRH
220KV FATEHPUR-FTHPR(UP)-I
220KV FATEHPUR-FTHPR(UP)-II
220KV FATEHPUR-KNP SOUTH
220KV FATEHPUR-NAUBASTA
220KV KNP-MAINPURI
220KV KNP-NAUBASTA
220KV KNP-PANKI-I
220KV KNP-PANKI-II
220KV KNP-UNCHR-I
220KV KNP-UNCHR-II
220KV KNP-UNCHR-III
220KV KNP-UNCHR-IV
220KV PITHORAGRH-BRLY(UP)
220KV RAIBRLY-CHINHAT
220KV RAIBRLY-LKO(UP)
220KV SITARGANJ-BLY(UP)
220KV TNKPR-BLY(UP)
220KV TNKPR-SITARGANJ
220KV UNCHR-RAIBRLY-I
220KV UNCHR-RAIBRLY-II
220KV UNCHR-RAIBRLY-III
220KV KNP-RANIA
132 KV TRANS LINES
Note on A31: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Sheet2 (hidden)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
125MVAR B/Reactor-1 Mainpuri | 2017-05-27 22:42 | 2017-05-28 06:46 | 0 | 0 | 0 | 0.33611 | N-2790 | SVRD | H-T for voltage regulation as per NRLDC instruction. Mainpuri=386KV
125MVAR B/Reactor-I GORAKHPUR | 2017-05-22 21:55 | 2017-06-01 | 0 | 0 | 0 | 1900-01-08 02:05 | N-2235 | SVRD | H-T for voltage regulation as per NRLDC instruction. Gorakhpur=393KV
125MVAR B/Reactor-III KANPUR(GIS) | 2017-05-25 23:46 | 2017-05-26 06:58 | 0 | 0 | 0 | 0.3 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. Kanpur=395KV
240MVAR B/Reactor-I BALIA-765 | 2017-05-13 21:25 | 2017-05-27 01:23 | 0 | 0 | 0 | 1900-01-12 03:58 | N-1003 | SVRD | H-T for voltage regulation as per NRLDC instruction. Ballia=744KV
240MVAR B/Reactor-I BAREILLY-765 | 2017-05-25 09:56 | 2017-05-28 05:20 | 0 | 0 | 0 | 1900-01-01 19:24 | N-2455 | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-13 21:24 | 2017-05-14 06:52 | 0 | 0 | 0 | 0.39444 | N-1002 | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-16 20:01 | 2017-05-17 07:40 | 0 | 0 | 0 | 0.48542 | N-1534 | SVRD | H-T for voltage regulation as per NRLDC instruction. Lucknow=749KV
330MVAR B/Reactor-II VARANASI | 2017-05-19 15:05 | 2017-05-19 22:00 | 0 | 0 | 0 | 0.28819 | N-1850 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=751KV
330MVAR B/Reactor-II VARANASI | 2017-05-22 21:34 | 2017-05-24 06:25 | 0 | 0 | 0 | 1899-12-31 08:51 | N-2234 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=761KV
80MVAR B/Reactor BAREILLY | 2017-05-25 23:41 | 2017-05-26 07:02 | 0 | 0 | 0 | 0.30625 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=395KV
80MVAR B/Reactor LUCKNOW | 2017-05-25 23:35 | 2017-05-26 06:53 | 0 | 0 | 0 | 0.30417 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=396KV
Note on A9: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1
Note on A10: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1