## SOP DATA NR3 November-17
Standard of Performance data for the month of DECEMBER - 2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., NORTHERN REGION - III
Annexure-A
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Restoration Time as per Regulation 5(b) (2) |  | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME |  |  |  | @ (T) | # (U) | & ( C ) | * (D) | [15 empty] | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  |  | Code |  |  |  |  | Z | ( E) | ( F) | G=E x F |  |  | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 |  |  | Hrs | E | F | G | H
A |  | 765 KV TRANS LINES | [20 empty] | NRPC | [6 empty] | 0
1 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR3 | -- | 2017-12-01 09:52 | 2017-12-01 15:23 |  |  |  | 0 | 0 | 0 | 0.22986 |  |  |  |  | LCSD |  |  | S/D availed for completing the pending work related for stringing(Powerline crossing) of 765kv Orai-Aligarh D/C | [7 empty] | 744
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.22986 | [9 empty] | 744 | 1327 | 148.034 | 196441.118 | 196441.118 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2017-12-01 | 2017-12-01 09:12 |  |  |  | 0 | 0 | 0 | 0.38333 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=785kV
[6 empty] | 2017-12-04 09:20 | 2017-12-04 19:06 |  |  |  | 0.40694 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | For insulator cleaning work & pre winter maintenance work
[6 empty] | 2017-12-04 19:06 | 2017-12-05 07:24 |  |  |  | 0 | 0 | 0 | 0.5125 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2017-12-05 20:50 | 2017-12-06 07:50 |  |  |  | 0 | 0 | 0 | 0.45833 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2017-12-07 19:37 | 2017-12-08 07:41 |  |  |  | 0 | 0 | 0 | 0.50278 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2017-12-10 00:38 | 2017-12-11 08:16 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:38 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
[6 empty] | 2017-12-12 01:37 | 2017-12-12 10:51 |  |  |  | 0 | 0 | 0 | 0.38472 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
[6 empty] | 2017-12-12 20:15 | 2017-12-13 07:08 |  |  |  | 0 | 0 | 0 | 0.45347 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
[6 empty] | 2017-12-13 19:52 | 2017-12-14 09:30 |  |  |  | 0 | 0 | 0 | 0.56806 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2017-12-16 19:44 | 2017-12-17 09:00 |  |  |  | 0 | 0 | 0 | 0.55278 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
[6 empty] | 2017-12-17 20:07 | 2017-12-18 06:45 |  |  |  | 0 | 0 | 0 | 0.44306 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2017-12-19 01:13 | 2017-12-19 07:10 |  |  |  | 0 | 0 | 0 | 0.24792 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
[6 empty] | 2017-12-21 19:36 | 2017-12-22 07:23 |  |  |  | 0 | 0 | 0 | 0.49097 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
[6 empty] | 2017-12-22 21:37 | 2017-12-23 06:43 |  |  |  | 0 | 0 | 0 | 0.37917 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
[6 empty] | 2017-12-25 23:53 | 2017-12-26 09:53 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2017-12-28 13:07 | 2017-12-29 06:34 |  |  |  | 0 | 0 | 0 | 0.72708 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
[6 empty] | 2017-12-29 20:54 | 2017-12-30 10:18 |  |  |  | 0 | 0 | 0 | 0.55833 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=793kV
[6 empty] | 2017-12-30 20:45 | 2017-12-31 09:55 |  |  |  | 0 | 0 | 0 | 0.54861 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[6 empty] | 2017-12-31 20:58 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 0.12639 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.40694 | 0 | 0 | 1900-01-08 01:44 | [9 empty] | 744 | 1216 | 334.52 | 406776.32 | 401436.4696 | 98.6873
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2017-12-01 19:12 | 2017-12-02 09:06 |  |  |  | 0 | 0 | 0 | 0.57917 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
[6 empty] | 2017-12-02 21:05 | 2017-12-04 09:06 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:01 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2017-12-05 07:57 | 2017-12-05 18:23 |  |  |  | 0.43472 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | For insulator cleaning work & pre winter maintenance work
[6 empty] | 2017-12-06 01:10 | 2017-12-06 06:12 |  |  |  | 0 | 0 | 0 | 0.20972 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2017-12-06 20:02 | 2017-12-07 07:08 |  |  |  | 0 | 0 | 0 | 0.4625 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[6 empty] | 2017-12-08 19:15 | 2017-12-09 07:15 |  |  |  | 0 | 0 | 0 | 0.5 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
[6 empty] | 2017-12-11 19:33 | 2017-12-12 07:00 |  |  |  | 0 | 0 | 0 | 0.47708 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=797kV
[6 empty] | 2017-12-14 20:01 | 2017-12-15 08:00 |  |  |  | 0 | 0 | 0 | 0.49931 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
[6 empty] | 2017-12-15 20:01 | 2017-12-16 08:29 |  |  |  | 0 | 0 | 0 | 0.51944 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2017-12-18 01:14 | 2017-12-18 08:32 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
[6 empty] | 2017-12-18 22:02 | 2017-12-19 10:03 |  |  |  | 0 | 0 | 0 | 0.50069 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
[6 empty] | 2017-12-19 22:06 | 2017-12-20 08:45 |  |  |  | 0 | 0 | 0 | 0.44375 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2017-12-21 00:13 | 2017-12-21 06:57 |  |  |  | 0 | 0 | 0 | 0.28056 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
[6 empty] | 2017-12-23 17:12 | 2017-12-25 10:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:15 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
[6 empty] | 2017-12-26 01:14 | 2017-12-26 06:44 |  |  |  | 0 | 0 | 0 | 0.22917 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2017-12-27 00:04 | 2017-12-28 08:56 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:52 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.43472 | 0 | 0 | 1900-01-08 14:16 | [9 empty] | 744 | 1210 | 334.8 | 405108 | 399427.05 | 98.5977
4 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | 2017-12-19 03:36 | 2017-12-19 15:05 |  |  |  | 0 | 0 | 0.47847 | 0 |  |  |  |  | LNCC |  |  | Tripped due to B-N fault,F.D.=146.734km from LKO(Lucknow jurisdiction),F.C.=2.781KA,F.D.=73.33km from Balia(Azamgarh jurisdiction) caused by dense fog
[6 empty] | 2017-12-23 09:34 | 2017-12-23 19:38 |  |  |  | 0.41944 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Taken under S/D for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-24 04:13 | 2017-12-24 08:35 |  |  |  | 0 | 0 | 0.18194 | 0 |  |  |  |  | LNCC |  |  | Tripped due to B-N fault. FD- 270.3 km from Ballia. FC- Ballia-2.48km. Dense fog reported.
[6 empty] | 2017-12-24 08:35 | 2017-12-24 21:06 |  |  |  | 0.52153 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Taken under S/D for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-25 02:30 | 2017-12-25 02:30 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R successfully at both end on B-N fault (Main bay at Balia tripped and Tie bay remain closed at Balia). FD: 273kM from Balia end and 25.92kM from Lucknow. FC: 2.445kA at Balia. Fault in Lucknow T/L group jurisdiction.
[6 empty] | 2017-12-25 07:01 | 2017-12-25 08:30 |  |  |  | 0 | 0 | 0.061806 | 0 |  |  |  |  | LNCC |  |  | Tripped due to B-N fault due to heavy fog. FD- 274.9 km from Ballia. FC- Ballia-2.421km. Fault in Lucknow T/L group jurisdiction.
[6 empty] | 2017-12-25 08:30 | 2017-12-25 19:03 |  |  |  | 0.43958 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Taken under S/D for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-26 09:56 | 2017-12-26 18:58 |  |  |  | 0.37639 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-28 06:21 | 2017-12-28 06:21 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R operated successfully due to B-N Fault, M1:F.D.=86.93km from Balia,F.C.=5.619KA, M2:F.D.=87.2km from Balia,F.C.=5.466KA,F.D.=206.3km from LKO (Azamgarh jurisdiction)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 18:10 | 0 | 0.72222 | 0 | [9 empty] | 726.6667 | 1374 | 318.919 | 438194.706 | 412767.3526 | 94.1972
5 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | 2017-12-01 09:48 | 2017-12-01 19:08 |  |  |  | 0.38889 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for insulator cleaning due to upcoming dense fog
[6 empty] | 2017-12-02 09:12 | 2017-12-02 18:42 |  |  |  | 0.39583 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-03 09:21 | 2017-12-03 18:43 |  |  |  | 0.39028 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for insulator cleaning work for winter season preparation.
[5 empty] | -- | 2017-12-04 08:45 | 2017-12-04 18:18 |  |  |  | 0.39792 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | For insulator cleaning work for winter preparation
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 13:45 | 0 | 0 | 0 | [9 empty] | 744 | 1019 | 251.613 | 256393.647 | 243384.4263 | 94.9261
6 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | 2017-12-27 13:38 | 2017-12-27 18:29 |  |  |  | 0.20208 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for removal spare reactor unit at Varanasi end
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.20208 | 0 | 0 | 0 | [9 empty] | 744 | 1419 | 165.98 | 235525.62 | 233990.2715 | 99.3481
7 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1393 | 223 | 310639 | 310639 | 100
8 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR3 | -- | 2017-12-04 00:50 | 2017-12-04 05:44 |  |  |  | 0 | 0 | 0 | 0.20417 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP GIS=797kV
[6 empty] | 2017-12-11 01:54 | 2017-12-11 06:37 |  |  |  | 0 | 0 | 0 | 0.19653 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP GIS=787kV
[6 empty] | 2017-12-11 20:14 | 2017-12-12 07:31 |  |  |  | 0 | 0 | 0 | 0.47014 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP GIS=787kV
[6 empty] | 2017-12-14 01:04 | 2017-12-14 09:01 |  |  |  | 0 | 0 | 0 | 0.33125 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur GIS=788kV
[6 empty] | 2017-12-16 00:50 | 2017-12-16 08:45 |  |  |  | 0 | 0 | 0 | 0.32986 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur GIS=797kV
[6 empty] | 2017-12-16 23:51 | 2017-12-17 06:44 |  |  |  | 0 | 0 | 0 | 0.28681 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur GIS=796kV
[6 empty] | 2017-12-22 02:53 | 2017-12-22 06:07 |  |  |  | 0 | 0 | 0 | 0.13472 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=797kV
[6 empty] | 2017-12-23 02:04 | 2017-12-23 06:39 |  |  |  | 0 | 0 | 0 | 0.19097 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=791kV
[6 empty] | 2017-12-24 02:13 | 2017-12-24 06:48 |  |  |  | 0 | 0 | 0 | 0.19097 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-433KV
[6 empty] | 2017-12-25 00:09 | 2017-12-25 07:37 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=796kV
[6 empty] | 2017-12-30 03:12 | 2017-12-30 07:18 |  |  |  | 0 | 0 | 0 | 0.17083 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=793kV
[6 empty] | 2017-12-31 01:12 | 2017-12-31 09:19 |  |  |  | 0 | 0 | 0 | 0.33819 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=801kV
[6 empty] | 2017-12-31 21:05 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 0.12153 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=798kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 06:39 | [9 empty] | 744 | 1440 | 465.8 | 670752 | 670752 | 100
9 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | 2017-12-27 01:38 | 2017-12-27 03:02 |  |  |  | 0.058333 | 0 | 0 | 0 |  |  |  |  | OMST |  |  | H/T on emergency basis from Varanasi end due to fire in B Ph L/R of 765KV Varanasi-Kanpur-2 at Varanasi end.
[6 empty] | 2017-12-31 11:31 | 2017-12-31 14:54 |  |  |  | 0.14097 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Emergency S/D availed for replacement of failed NGR LA at Kanpur GIS
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.19931 | 0 | 0 | 0 | [9 empty] | 744 | 1447 | 326.172 | 471970.884 | 468936.4834 | 99.3571
10 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | Winding Failure | 2017-12-27 01:38 | 2017-12-27 07:41 |  |  |  | 0.25208 | 0 | 0 | 0 |  |  |  |  | SEFT |  |  | Tripped due to fire in its B Ph L/R at Varanasi end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.25208 | 0 | 0 | 0 | [9 empty] | 744 | 1447 | 326.172 | 471970.884 | 468132.9487 | 99.1868
B |  | 400 KV TRANS LINES |  |  | --
1 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 29.982 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2017-12-13 20:52 | 2017-12-14 08:56 | -- | -- | -- | 0 | 0 | 0 | 0.50278 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-19 01:15 | 2017-12-19 09:39 |  |  |  | 0 | 0 | 0 | 0.35 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2017-12-22 00:44 | 2017-12-22 09:48 |  |  |  | 0 | 0 | 0 | 0.37778 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
[6 empty] | 2017-12-23 00:20 | 2017-12-23 09:52 |  |  |  | 0 | 0 | 0 | 0.39722 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-23 17:02 | 2017-12-26 13:18 |  |  |  | 0 | 0 | 0 | 1900-01-01 20:16 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 11:20 | [9 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2017-12-01 | 2017-12-04 11:01 |  |  |  | 0 | 0 | 0 | 1900-01-02 11:01 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=436kV
[6 empty] | 2017-12-05 22:09 | 2017-12-13 11:58 |  |  |  | 0 | 0 | 0 | 1900-01-06 13:49 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2017-12-14 21:01 | 2017-12-18 11:38 |  |  |  | 0 | 0 | 0 | 1900-01-02 14:37 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
[6 empty] | 2017-12-20 01:29 | 2017-12-21 09:03 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:34 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-27 00:02 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 1900-01-03 23:58 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-19 22:59 | [9 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- | 2017-12-27 08:27 | 2017-12-27 19:18 | -- | -- | -- | 0 | 0 | 0 | 0.45208 |  |  |  |  | LCSD |  |  | S/D availed for replacement of Porcelain insulator with Polymer
[6 empty] | 2017-12-28 08:30 | 2017-12-28 19:24 |  |  |  | 0 | 0 | 0 | 0.45417 |  |  |  |  | LCSD |  |  | S/D availed for replacement of Porcelain insulator with Polymer
[6 empty] | 2017-12-29 10:04 | 2017-12-29 19:26 |  |  |  | 0 | 0 | 0 | 0.39028 |  |  |  |  | LCSD |  |  | S/D availed for replacement of Porcelain insulator with Polymer
[6 empty] | 2017-12-30 08:30 | 2017-12-30 19:32 |  |  |  | 0 | 0 | 0 | 0.45972 |  |  |  |  | LCSD |  |  | S/D availed for replacement of Porcelain insulator with Polymer
[6 empty] | 2017-12-31 08:35 | 2017-12-31 19:15 |  |  |  | 0 | 0 | 0 | 0.44444 |  |  |  |  | LCSD |  |  | S/D availed for replacement of Porcelain insulator with Polymer
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 04:49 | [9 empty] | 744 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2017-12-01 | 2017-12-02 09:28 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 09:28 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-07 19:55 | 2017-12-09 07:26 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:31 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
[6 empty] | 2017-12-13 20:08 | 2017-12-14 10:42 |  |  |  | 0 | 0 | 0 | 0.60694 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-22 20:16 | 2017-12-23 09:51 |  |  |  | 0 | 0 | 0 | 0.56597 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-23 21:49 | 2017-12-25 09:43 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:54 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 13:02 | [9 empty] | 744 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2017-12-02 16:47 | 2017-12-03 10:10 | -- | -- | -- | 0 | 0 | 0 | 0.72431 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-03 19:54 | 2017-12-04 09:44 |  |  |  | 0 | 0 | 0 | 0.57639 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-04 18:46 | 2017-12-05 09:13 |  |  |  | 0 | 0 | 0 | 0.60208 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
[6 empty] | 2017-12-05 19:19 | 2017-12-06 09:30 |  |  |  | 0 | 0 | 0 | 0.59097 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
[6 empty] | 2017-12-06 21:01 | 2017-12-07 08:46 |  |  |  | 0 | 0 | 0 | 0.48958 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=436kV
[6 empty] | 2017-12-09 13:11 | 2017-12-10 08:31 |  |  |  | 0 | 0 | 0 | 0.80556 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-10 18:46 | 2017-12-11 07:17 |  |  |  | 0 | 0 | 0 | 0.52153 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-11 18:54 | 2017-12-13 10:24 |  |  |  | 0 | 0 | 0 | 1899-12-31 15:30 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2017-12-14 20:24 | 2017-12-15 08:04 |  |  |  | 0 | 0 | 0 | 0.48611 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
[6 empty] | 2017-12-15 20:19 | 2017-12-18 06:41 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:22 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-18 19:56 | 2017-12-19 07:42 |  |  |  | 0 | 0 | 0 | 0.49028 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-19 21:08 | 2017-12-20 06:28 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2017-12-20 19:15 | 2017-12-21 07:42 |  |  |  | 0 | 0 | 0 | 0.51875 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-21 23:42 | 2017-12-22 06:43 |  |  |  | 0 | 0 | 0 | 0.29236 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-25 20:54 | 2017-12-26 06:41 |  |  |  | 0 | 0 | 0 | 0.40764 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-26 20:27 | 2017-12-27 06:25 |  |  |  | 0 | 0 | 0 | 0.41528 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=427kV
[6 empty] | 2017-12-27 20:07 | 2017-12-28 08:49 |  |  |  | 0 | 0 | 0 | 0.52917 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-29 01:30 | 2017-12-29 09:32 |  |  |  | 0 | 0 | 0 | 0.33472 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2017-12-29 19:59 | 2017-12-31 10:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 14:15 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2017-12-31 19:24 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 0.19167 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-13 00:53 | [9 empty] | 744 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | 2017-12-18 01:14 | 2017-12-18 11:00 |  |  |  | 0 | 0 | 0 | 0.40694 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=431kV
[6 empty] | 2017-12-19 08:42 | 2017-12-19 19:22 |  |  |  | 0.44444 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for insulator cleaning work for winter season preparation
[6 empty] | 2017-12-20 09:23 | 2017-12-20 18:28 |  |  |  | 0.37847 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D taken for insulator cleaning work for pre winter preparation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.82292 | 0 | 0 | 0.40694 | [9 empty] | 744 | 332 | 139.73 | 46390.36 | 45158.8955 | 97.3454
10 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | 2017-12-21 09:19 | 2017-12-21 18:55 |  |  |  | 0.4 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D taken for insulator cleaning work for pre winter preparation.
[6 empty] | 2017-12-22 08:25 | 2017-12-22 19:09 |  |  |  | 0.44722 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Taken under S/D for insulator cleaning work
[6 empty] | 2017-12-30 03:05 | 2017-12-30 21:54 |  |  |  | 0 | 0 | 0.78403 | 0 |  |  |  |  | LNCC |  |  | Tripped due to heavy fog on Y-B fault,F.D.=140km from Allahabad, F.C.=4.68KA, (Kanpur TL Jurisdiction). Decapped insulator restored at loc no 205
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.84722 | 0 | 0.78403 | 0 | [9 empty] | 725.1833 | 332 | 139.73 | 46390.36 | 45089.626 | 97.1961
11 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 155.932 | 80304.98 | 80304.98 | 100
12 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 224 | 115360 | 115360 | 100
13 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- | 2017-12-29 06:09 | 2017-12-29 06:09 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R successfully at both end on R-N fault. FD: 55.62kM from VNS. FC: 5.4(Allahabad jurisdiction)
[6 empty] | 2017-12-30 01:06 | 2017-12-30 01:06 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R successfully on R-N fault. FD: 52.06kM from Allhabad. FC: 7.61kA(Mirzapur jurisdiction)
[6 empty] | 2017-12-31 11:01 | 2017-12-31 21:12 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for stringing work of 765 KV Anpara D -Jhunsi line
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.42431 | [9 empty] | 744 | 515 | 98.792 | 50877.88 | 50877.88 | 100
14 | NR140016 | 400KV ALLD-SASARAM | 212 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 05:21 | 0 | 0 | 0.40694 | [9 empty] | 744 | 369 | 212 | 78228 | 75141.9895 | 96.0551
15 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- | 2017-12-14 16:55 | 2017-12-14 19:00 | -- | -- |  | 0 | 0 | 0 | 0.086806 |  |  |  |  | OSFD |  |  | E/S/D availed by UPPCL for attending hot spot at UPPCL/Mau end.
[6 empty] | 2017-12-16 15:22 | 2017-12-16 19:16 |  |  |  | 0 | 0 | 0 | 0.1625 |  |  |  |  | OSFD |  |  | E/S/D availed by UPPCL for attending hot spot at Mau(UPPCL) end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.24931 | [9 empty] | 744 | 515 | 13 | 6695 | 6695 | 100
16 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 13 | 6695 | 6695 | 100
17 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 227 | 229.163 | 52020.001 | 52020.001 | 100
18 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 227 | 229.163 | 52020.001 | 52020.001 | 100
19 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
20 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
21 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 9.2 | 4738 | 4738 | 100
22 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 9.2 | 4738 | 4738 | 100
23 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- | 2017-12-25 17:23 | 2017-12-25 18:32 | -- | -- | -- | 0 | 0.047917 | 0 | 0 |  |  |  |  | SBBU |  |  | Tripped due to Bus Bar protection operated at Lucknow(UP) (Sarojininagar).
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.047917 | 0 | 0 | [9 empty] | 744 | 331 | 278.76 | 92269.56 | 92269.56 | 100
24 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
25 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
26 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR3
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
27 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 115.926 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
28 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 | 100
29 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
30 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
31 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2017-12-01 | 2017-12-01 09:41 | -- | -- | -- | 0 | 0 | 0 | 0.40347 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=424kV
[6 empty] | 2017-12-01 19:08 | 2017-12-02 09:23 |  |  |  | 0 | 0 | 0 | 0.59375 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
[6 empty] | 2017-12-02 16:39 | 2017-12-04 09:56 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:17 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=432kV
[6 empty] | 2017-12-04 18:51 | 2017-12-06 06:54 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:03 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
[6 empty] | 2017-12-06 21:05 | 2017-12-07 12:58 |  |  |  | 0 | 0 | 0 | 0.66181 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
[6 empty] | 2017-12-07 21:04 | 2017-12-08 08:22 |  |  |  | 0 | 0 | 0 | 0.47083 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
[6 empty] | 2017-12-08 09:18 | 2017-12-08 10:00 |  |  |  | 0 | 0 | 0.029167 | 0 |  |  |  |  | LNCC |  |  | Tripped only from BLB end due to heavy fog at BLB end
[6 empty] | 2017-12-12 22:17 | 2017-12-13 12:16 |  |  |  | 0 | 0 | 0 | 0.58264 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-13 20:54 | 2017-12-14 08:53 |  |  |  | 0 | 0 | 0 | 0.49931 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[6 empty] | 2017-12-14 20:50 | 2017-12-15 08:59 |  |  |  | 0 | 0 | 0 | 0.50625 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-15 22:19 | 2017-12-16 09:44 |  |  |  | 0 | 0 | 0 | 0.47569 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-16 21:20 | 2017-12-17 10:14 |  |  |  | 0 | 0 | 0 | 0.5375 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
[6 empty] | 2017-12-17 20:07 | 2017-12-18 09:38 |  |  |  | 0 | 0 | 0 | 0.56319 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
[6 empty] | 2017-12-18 20:05 | 2017-12-20 07:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:09 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
[6 empty] | 2017-12-21 00:55 | 2017-12-21 06:08 |  |  |  | 0 | 0 | 0 | 0.21736 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-21 23:46 | 2017-12-22 06:49 |  |  |  | 0 | 0 | 0 | 0.29375 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
[6 empty] | 2017-12-23 00:25 | 2017-12-23 07:25 |  |  |  | 0 | 0 | 0 | 0.29167 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[6 empty] | 2017-12-23 22:28 | 2017-12-24 07:35 |  |  |  | 0 | 0 | 0 | 0.37986 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=421kV
[6 empty] | 2017-12-25 00:05 | 2017-12-25 10:00 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2017-12-26 02:45 | 2017-12-26 08:40 |  |  |  | 0 | 0 | 0 | 0.24653 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2017-12-26 23:04 | 2017-12-27 12:35 |  |  |  | 0 | 0 | 0 | 0.56319 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2017-12-28 00:53 | 2017-12-28 10:21 |  |  |  | 0 | 0 | 0 | 0.39444 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2017-12-28 23:24 | 2017-12-29 07:25 |  |  |  | 0 | 0 | 0 | 0.33403 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2017-12-29 20:59 | 2017-12-30 10:41 |  |  |  | 0 | 0 | 0 | 0.57083 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2017-12-30 20:48 | 2017-12-31 09:38 |  |  |  | 0 | 0 | 0 | 0.53472 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-31 19:27 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 0.18958 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.029167 | 1900-01-13 09:51 | [9 empty] | 743.3 | 515 | 235.952 | 121515.28 | 121515.28 | 100
32 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- | 2017-12-08 20:34 | 2017-12-09 11:59 | -- | -- |  | 0 | 0 | 0 | 0.64236 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
[6 empty] | 2017-12-09 13:07 | 2017-12-12 12:01 |  |  |  | 0 | 0 | 0 | 1900-01-01 22:54 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 14:19 | [9 empty] | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
33 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2017-12-12 12:05 | 2017-12-13 12:15 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 00:10 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2017-12-16 21:20 | 2017-12-17 09:44 |  |  |  | 0 | 0 | 0 | 0.51667 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
[6 empty] | 2017-12-29 21:00 | 2017-12-30 10:38 |  |  |  | 0 | 0 | 0 | 0.56806 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2017-12-30 20:49 | 2017-12-31 09:00 |  |  |  | 0 | 0 | 0 | 0.50764 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-31 19:28 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 0.18889 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 18:55 | [9 empty] | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
34 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- | 2017-12-01 | 2017-12-01 09:37 | -- | -- | -- | 0 | 0 | 0 | 0.40069 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=424kV
[6 empty] | 2017-12-01 19:05 | 2017-12-02 09:22 |  |  |  | 0 | 0 | 0 | 0.59514 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
[6 empty] | 2017-12-02 16:36 | 2017-12-03 10:52 |  |  |  | 0 | 0 | 0 | 0.76111 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=432kV
[6 empty] | 2017-12-03 19:49 | 2017-12-04 09:56 |  |  |  | 0 | 0 | 0 | 0.58819 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=429kV
[6 empty] | 2017-12-04 18:49 | 2017-12-06 07:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:11 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
[6 empty] | 2017-12-06 15:10 | 2017-12-07 08:05 |  |  |  | 0 | 0 | 0 | 0.70486 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction.
[6 empty] | 2017-12-07 21:05 | 2017-12-08 07:33 |  |  |  | 0 | 0 | 0 | 0.43611 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
[6 empty] | 2017-12-08 20:35 | 2017-12-09 11:59 |  |  |  | 0 | 0 | 0 | 0.64167 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
[6 empty] | 2017-12-09 13:06 | 2017-12-12 07:02 |  |  |  | 0 | 0 | 0 | 1900-01-01 17:56 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2017-12-13 20:55 | 2017-12-14 08:50 |  |  |  | 0 | 0 | 0 | 0.49653 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[6 empty] | 2017-12-14 20:54 | 2017-12-15 09:07 |  |  |  | 0 | 0 | 0 | 0.50903 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-15 22:17 | 2017-12-16 09:43 |  |  |  | 0 | 0 | 0 | 0.47639 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-17 20:07 | 2017-12-18 09:19 |  |  |  | 0 | 0 | 0 | 0.55 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
[6 empty] | 2017-12-18 20:05 | 2017-12-20 09:08 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:03 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
[6 empty] | 2017-12-21 00:55 | 2017-12-21 06:07 |  |  |  | 0 | 0 | 0 | 0.21667 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2017-12-21 23:46 | 2017-12-22 06:48 |  |  |  | 0 | 0 | 0 | 0.29306 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
[6 empty] | 2017-12-23 00:24 | 2017-12-23 07:29 |  |  |  | 0 | 0 | 0 | 0.29514 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[6 empty] | 2017-12-23 22:28 | 2017-12-24 07:10 |  |  |  | 0 | 0 | 0 | 0.3625 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=421kV
[6 empty] | 2017-12-25 00:05 | 2017-12-25 09:48 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2017-12-26 02:47 | 2017-12-26 08:38 |  |  |  | 0 | 0 | 0 | 0.24375 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2017-12-26 23:01 | 2017-12-27 06:29 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2017-12-28 00:52 | 2017-12-28 09:13 |  |  |  | 0 | 0 | 0 | 0.34792 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[5 empty] | -- | 2017-12-28 23:24 | 2017-12-29 07:32 | -- | -- | -- | 0 | 0 | 0 | 0.33889 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-13 18:32 | [9 empty] | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
35 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
36 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
37 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | 2017-12-18 11:03 | 2017-12-18 11:40 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OSFT |  |  | H/T on emergency basis to attend heavy hot spot in line isolator at Agra end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 291 | 240 | 69840 | 69840 | 100
38 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 72.6 | 37389 | 37389 | 100
39 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 73.2 | 37698 | 37698 | 100
40 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2017-12-01 12:01 | 2017-12-01 17:19 | -- | -- |  | 0.22083 | 0 | 0 | 0 |  |  |  |  | OSFT |  |  | E/S/D availed for attending hot spot in Y ph line isolator at Kanpur
[6 empty] | 2017-12-02 01:02 | 2017-12-02 07:23 |  |  |  | 0 | 0 | 0 | 0.26458 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=420kV
[6 empty] | 2017-12-02 12:08 | 2017-12-02 12:38 |  |  |  | 0.020833 | 0 | 0 | 0 |  |  |  |  | OSFT |  |  | Hand tripped on emergency after heavy sparking observed in Y-phase Line isolator at Kanpur.
[6 empty] | 2017-12-03 19:13 | 2017-12-03 19:13 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R operated successfully from both end due to Y-N fault, F.D.=21.89km from KNP,F.C.=13.13KA, F.D.=370.5km from BLB,F.C.=1.239KA (Kanpur jurisdiction)
[6 empty] | 2017-12-07 04:05 | 2017-12-07 06:49 |  |  |  | 0 | 0 | 0 | 0.11389 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=437kV
[6 empty] | 2017-12-10 22:06 | 2017-12-10 22:06 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R operated successfully from both end due to Y-N fault,F.D.=88.47 KM from Kanpur,F.C.=4.29KA, F.D.=253.5km from BLB,F.C.=1.826KA .
[6 empty] | 2017-12-12 00:44 | 2017-12-12 12:00 |  |  |  | 0 | 0 | 0 | 0.46944 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP =425kV
[6 empty] | 2017-12-16 23:52 | 2017-12-17 09:48 |  |  |  | 0 | 0 | 0 | 0.41389 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=420kV
[6 empty] | 2017-12-20 01:26 | 2017-12-20 07:20 |  |  |  | 0 | 0 | 0 | 0.24583 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-420KV
[6 empty] | 2017-12-21 00:56 | 2017-12-21 06:13 |  |  |  | 0 | 0 | 0 | 0.22014 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-420KV
[6 empty] | 2017-12-28 23:24 | 2017-12-29 06:57 |  |  |  | 0 | 0 | 0 | 0.31458 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=424kV
[6 empty] | 2017-12-29 14:51 | 2017-12-29 14:51 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R successfully on R-N fault,F.D.=219.1km from Kanpur, F.C.=1.7KA, and F.D.=143km from Ballabhgarh, F.C.=2.6KA (Mainpuri TL Jurisdiction)
[5 empty] | -- | 2017-12-31 19:24 | 2018-01-01 | -- | -- |  | 0 | 0 | 0 | 0.19167 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=426kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.24167 | 0 | 0 | 1900-01-01 05:37 | [9 empty] | 744 | 342 | 385.69 | 131905.98 | 130877.6807 | 99.2204
47 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- | 2017-12-05 22:08 | 2017-12-06 07:00 | -- | -- |  | 0 | 0 | 0 | 0.36944 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=421kV
[6 empty] | 2017-12-13 20:53 | 2017-12-14 08:52 |  |  |  | 0 | 0 | 0 | 0.49931 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=423kV
[6 empty] | 2017-12-14 20:58 | 2017-12-15 09:03 |  |  |  | 0 | 0 | 0 | 0.50347 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=420kV
[6 empty] | 2017-12-23 00:20 | 2017-12-23 07:18 |  |  |  | 0 | 0 | 0 | 0.29028 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-28 00:56 | 2017-12-28 09:16 |  |  |  | 0 | 0 | 0 | 0.34722 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=420kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 00:14 | [9 empty] | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
41 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- | 2017-12-12 21:41 | 2017-12-13 18:48 | -- | -- | -- | 0 | 0 | 0 | 0.87986 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=422kV
[6 empty] | 2017-12-17 20:12 | 2017-12-18 09:38 |  |  |  | 0 | 0 | 0 | 0.55972 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction.
[6 empty] | 2017-12-21 23:48 | 2017-12-22 07:46 |  |  |  | 0 | 0 | 0 | 0.33194 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-421KV
[6 empty] | 2017-12-29 21:02 | 2017-12-30 10:32 |  |  |  | 0 | 0 | 0 | 0.5625 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=419kV
[6 empty] | 2017-12-30 20:44 | 2017-12-31 09:02 |  |  |  | 0 | 0 | 0 | 0.5125 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=416kV
[6 empty] | 2017-12-31 12:21 | 2017-12-31 15:58 |  |  |  | 0.15069 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Emergency S/D availed for rectification of melted jumper at location no 561.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.15069 | 0 | 0 | 1900-01-01 20:19 | [9 empty] | 744 | 361 | 370.772 | 133848.692 | 133198.0386 | 99.5139
42 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- | 2017-12-02 07:04 | 2017-12-06 15:24 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 08:20 |  |  |  |  | LCSD |  |  | S/D taken for diversion of line between loc no 1115 to 1119 due to DFCC on continious basis.
[5 empty] | -- | 2017-12-12 07:39 | 2017-12-16 18:21 | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 10:42 |  |  |  |  | LCSD |  |  | S/D taken for Diversion of line due to DFCC work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 19:02 | [9 empty] | 744 | 515 | 107.079 | 55145.685 | 55145.685 | 100
43 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 107.1 | 55156.5 | 55156.5 | 100
44 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | 2017-12-13 15:01 | 2017-12-13 19:46 |  |  |  | 0.19792 | 0 | 0 | 0 |  |  |  |  | OSFT |  |  | S/D taken to attend hot spot in line isolator at Kanpur
[6 empty] | 2017-12-21 11:28 | 2017-12-21 16:34 |  |  |  | 0.2125 | 0 | 0 | 0 |  |  |  |  | OSFT |  |  | S/D taken for attending problem of sparking & abnormal sound in R-phase wave trap at Kanpur.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.41042 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 5.922 | 3049.83 | 3009.4525 | 98.6761
45 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 5.86 | 3017.9 | 3017.9 | 100
46 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
47 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
48 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
49 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
50 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | 2017-12-19 04:06 | 2017-12-19 05:08 |  |  |  | 0 | 0 | 0.043056 | 0 |  |  |  |  | GOVC |  |  | Tripped due to Over Voltage at Lucknow(PG) end. D/T received at Lucknow(UP) end.
[6 empty] | 2017-12-25 17:23 | 2017-12-25 18:26 |  |  |  | 0 | 0.04375 | 0 | 0 |  |  |  |  | SBBU |  |  | Tripped due to Bus Bar protection operated at Lucknow(UP) (Sarojininagar).
[6 empty] | 2017-12-26 02:00 | 2017-12-26 08:52 |  |  |  | 0 | 0.28611 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped due to R-N fault due to heavy fog. FD: 42.44kM from Lucknow, FC: 8.25kA at Lucknow. Fault in UPPCL jurisdiction.
[6 empty] | 2017-12-26 08:52 | 2017-12-26 17:28 |  |  |  | 0 | 0 | 0 | 0.35833 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for restoration work of damaged insulator string at location no. 351.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.32986 | 0.043056 | 0.35833 | [9 empty] | 742.9667 | 515 | 41.743 | 21497.645 | 21497.645 | 100
51 | NR140114 | 400KV LUCKNOW-SHAHJHNPR-I | 169.785 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 371 | 169.785 | 62990.235 | 62990.235 | 100
52 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 169.729 | 87410.435 | 87410.435 | 100
53 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
54 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
55 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
56 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
57 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 734.52 | 515 | 73.826 | 38020.39 | 38020.39 | 100
58 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 691 | 30.703 | 21215.773 | 21215.773 | 100
59 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 691 | 31.159 | 21530.869 | 21530.869 | 100
60 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR3 | -- | 2017-12-19 08:32 | 2017-12-19 16:55 |  |  |  | 0 | 0 | 0 | 0.34931 |  |  |  |  | OSPD |  |  | S/D availed by Powerlink for insulator cleaning & other maintenanance work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.34931 | [9 empty] | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
61 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR3 | -- | 2017-12-20 08:07 | 2017-12-20 17:54 | -- | -- | -- | 0.40764 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D taken by Powerlink for insulator cleaning work for pre winter preparation.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.40764 | 0 | 0 | 0 | [9 empty] | 744 | 616 | 66.009 | 40661.544 | 40126.8593 | 98.685
62 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
63 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
64 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | 2017-12-28 09:13 | 2017-12-28 19:34 |  |  |  | 0.43125 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for Insulator cleaning work for winter season preparation.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.43125 | 0 | 0 | 0 | [9 empty] | 744 | 332 | 224 | 74368 | 73333.4452 | 98.6089
65 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | 2017-12-25 09:02 | 2017-12-25 19:19 |  |  |  | 0.42847 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Taken under S/D for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-26 08:47 | 2017-12-26 19:31 |  |  |  | 0.44722 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for insulator cleaning work for winter season preparation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.87569 | 0 | 0 | 0 | [9 empty] | 744 | 306 | 202 | 61812 | 60065.9218 | 97.1752
66 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 25.057 | 12904.355 | 12904.355 | 100
67 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | 2017-12-23 09:06 | 2017-12-23 22:01 |  |  |  | 0.53819 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Taken under S/D for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-24 09:14 | 2017-12-24 19:39 |  |  |  | 0.43403 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Taken under S/D for insulator cleaning work for winter season preparation.
[6 empty] | 2017-12-31 02:28 | 2017-12-31 17:03 |  |  |  | 0 | 0 | 0.60764 | 0 |  |  |  |  | LNCC |  |  | Tripped due to heavy fog on R-Y fault. FD: FTP-302.8km, FC: FTP- R Ph-1.73KA, Y Ph-2.12KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.97222 | 0 | 0.60764 | 0 | [9 empty] | 729.4167 | 236 | 330.953 | 78104.908 | 75606.4076 | 96.8011
68 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- | 2017-12-07 09:08 | 2017-12-09 22:35 | -- | -- |  | 0 | 0 | 0 | 1900-01-01 13:27 |  |  |  |  | LCSD |  |  | S/D taken for transferring of line from ERS to normal tower
[6 empty] | 2017-12-25 17:23 | 2017-12-25 18:30 |  |  |  | 0 | 0.046528 | 0 | 0 |  |  |  |  | SBBU |  |  | Tripped due to Bus Bar protection operated at Lucknow(UP) (Sarojininagar).
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.046528 | 0 | 1900-01-01 13:27 | [9 empty] | 744 | 337 | 408.6 | 137698.2 | 137698.2 | 100
69 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 42.026 | 21643.39 | 21643.39 | 100
70 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 43.952 | 22635.28 | 22635.28 | 100
71 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 3.341 | 1720.615 | 1720.615 | 100
72 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 515 | 3.317 | 1708.255 | 1708.255 | 100
73 | NR140164 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | 2017-12-17 08:08 | 2017-12-17 17:37 |  |  |  | 0 | 0 | 0 | 0.39514 |  |  |  |  | OSPD |  |  | S/D taken by UPPCL for general maintenance work at UPPCL end
[6 empty] | 2017-12-27 01:38 | 2017-12-27 02:35 |  |  |  | 0 | 0.039583 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped only from UPPCL Sarnath end due to problem at their end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.039583 | 0 | 0.39514 | [9 empty] | 744 | 515 | 69.677 | 35883.655 | 35883.655 | 100
74 | NR140165 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | 2017-12-16 08:34 | 2017-12-16 18:05 |  |  |  | 0 | 0 | 0 | 0.39653 |  |  |  |  | OSPD |  |  | S/D availed for general maintenanace work by UPPCL
[6 empty] | 2017-12-27 01:38 | 2017-12-27 02:35 |  |  |  | 0 | 0.039583 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped only from UPPCL Sarnath end due to problem at their end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.039583 | 0 | 0.39653 | [9 empty] | 744 | 515 | 69.677 | 35883.655 | 35883.655 | 100
75 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
76 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
77 | NR340008 | 400KV LKO(765)-KANPUR(GIS)-I | 159.7 | NR3 | -- | 2017-12-18 02:55 | 2017-12-18 10:08 |  |  |  | 0 | 0 | 0 | 0.30069 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=427kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.30069 | [9 empty] | 744 | 687 | 159.7 | 109713.9 | 109713.9 | 100
78 | NR340009 | 400KV LKO(765)-KANPUR(GIS)-II | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 687 | 159.7 | 109713.9 | 109713.9 | 100
79 | NR340010 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR3 | -- | 2017-12-03 08:49 | 2017-12-03 19:57 |  |  |  | 0 | 0 | 0 | 0.46389 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for construction related work
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.46389 | [9 empty] | 744 | 687 | 28.19 | 19366.53 | 19366.53 | 100
80 | NR340011 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR3 | -- | 2017-12-01 | 2017-12-03 08:49 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:49 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=422kV
[6 empty] | 2017-12-03 08:49 | 2017-12-03 20:02 |  |  |  | 0 | 0 | 0 | 0.46736 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for construction related work
[6 empty] | 2017-12-09 17:17 | 2017-12-09 22:00 |  |  |  | 0 | 0.19653 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped due to some problem at Meja (NTPC) end & DT received at Allahabad.
[5 empty] | -- | 2017-12-11 10:30 | 2017-12-11 11:27 | -- | -- |  | 0 | 0.039583 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped due to D/T received at Allahabad end due to PLCC problem at NTPC Meja end |  | 744 | 687 | 28.19 | 19366.53 | 19366.53 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.23611 | 0 | 0 | [9 empty] | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) |  |  |  | 2017-12-29 23:09 | 2017-12-30 01:34 |  |  |  | 0 | 0.10069 | 0 | 0 |  |  |  |  | OMSU |  |  | Line tripped Due to E/F at Jhusi (UPPTCL ) switchyard because of heavy fog.
|  |  | 21.879 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.10069 | 0 | 0 | [9 empty] | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | 2017-12-30 15:16 | 2017-12-30 17:24 |  |  |  | 0 | 0 | 0 | 0.088889 |  |  |  |  | OSFD |  |  | Emergency S/D availed by UPPCL to attend hot spot at their end
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.088889 | [9 empty] | 744 | 132 | 3 | 396 | 396 | 100
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- | 2017-12-12 01:54 | 2017-12-12 02:08 | -- | -- |  | 0 | 0 | 0.0097222 | 0 |  |  |  |  | GOVC |  |  | Tripped due to D/T received at Bareily(UP) end due to O/V at Dhauliganga. D'Ganga=239KV
[6 empty] | 2017-12-12 02:08 | 2017-12-12 06:22 |  |  |  | 0 | 0 | 0 | 0.17639 |  |  |  |  | LVRD |  |  | Kept open for Voltage regulation as per NRLDC instruction. P'garh=239kV
[6 empty] | 2017-12-16 09:19 | 2017-12-16 18:19 |  |  |  | 0.375 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for AMP work by PGCIL
[6 empty] | 2017-12-23 11:20 | 2017-12-23 15:32 |  |  |  | 0 | 0 | 0 | 0.175 |  |  |  |  | OSPD |  |  | Taken under S/D by NHPC for testing work at their end
[5 empty] | -- | 2017-12-24 23:11 | 2017-12-25 04:24 | -- | -- |  | 0 | 0 | 0.21736 | 0 |  |  |  |  | GOVC |  |  | Tripped due to O/V protection operated
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.375 | 0 | 0.22708 | 0.35139 | [9 empty] | 738.55 | 109 | 234.59 | 25570.31 | 25258.7092 | 98.7814
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- | 2017-12-12 01:54 | 2017-12-12 02:08 | -- | -- | -- | 0 | 0 | 0.21736 | 0 |  |  |  |  | GOVC |  |  | Tripped due to D/T received at Pithoragarh end due to O/V at Dhauliganga. D'Ganga=239KV
[6 empty] | 2017-12-12 02:08 | 2017-12-12 07:14 |  |  |  | 0 | 0 | 0 | 0.2125 |  |  |  |  | LVRD |  |  | Kept open for Voltage regulation as per NRLDC instruction. Bareily(UP)=239kV
[5 empty] | -- | 2017-12-25 03:03 | 2017-12-25 08:47 | -- | -- | -- | 0 | 0 | 0.23889 | 0 |  |  |  |  | GOVC |  |  | Tripped due to O/V protection operated
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.45625 | 0.2125 | [9 empty] | 733.05 | 156 | 59.01 | 9205.56 | 9205.56 | 100
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
13 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- | 2017-12-16 12:58 | 2017-12-26 22:11 |  |  | -- | 0 | 0 | 0 | 1900-01-09 09:13 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for line Diversion due to upcoming NTPC project at Billhaur
[6 empty] | 2017-12-16 12:58 | 2017-12-26 22:11 |  |  |  | 0 | 0 | 0 | 1900-01-09 09:13 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for line Diversion due to upcoming NTPC project at Billhaur
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-19 18:26 | [9 empty] | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
14 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
15 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)-1 | 8.717 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 131 | 8.717 | 1141.927 | 1141.927 | 100
16 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
17 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | 2017-12-06 08:37 | 2017-12-09 16:25 |  |  |  | 0 | 0 | 0 | 1900-01-02 07:48 |  |  |  |  | LCSD |  |  | S/D taken for diversion of line due to DFCC
[6 empty] | 2017-12-09 16:25 | 2017-12-10 17:06 |  |  |  | 0 | 0 | 1899-12-31 00:41 | 0 |  |  |  |  | LMAC |  |  | Middle phase conductor theft at LOC. No. 401 to 403 and cross arm bent at Loc. No. 401 & 402
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1899-12-31 00:41 | 1900-01-02 07:48 | [9 empty] | 719.3167 | 131 | 143.553 | 18805.443 | 18805.443 | 100
18 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- | 2017-12-06 08:37 | 2017-12-09 16:48 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 08:11 |  |  |  |  | LCSD |  |  | S/D taken for diversion of line due to DFCC
[5 empty] | -- | 2017-12-10 10:22 | 2017-12-10 17:05 | -- | -- | -- | 0 | 0 | 0 | 0.27986 |  |  |  |  | LCSD |  |  | S/D taken for facilitating restoration of 220KV KNP-Unchahar-1. Line-1 was out due to conductor theft between loc no 401 to 403 during s/d for diversion of line due to DFCC on continious basis
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-02 14:54 | [9 empty] | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
19 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | 2017-12-13 08:07 | 2017-12-17 20:46 |  |  |  | 0 | 0 | 0 | 1900-01-03 12:39 |  |  |  |  | LCSD |  |  | S/D taken for Diversion of line due to DFCC work.
[6 empty] | 2017-12-28 09:26 | 2017-12-28 19:36 |  |  |  | 0 | 0 | 0 | 0.42361 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for powerline crossing work
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 22:49 | [9 empty] | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
20 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | 2017-12-13 08:07 | 2017-12-16 18:16 |  |  |  | 0 | 0 | 0 | 1900-01-02 10:09 |  |  |  |  | LCSD |  |  | S/D taken for Diversion of line due to DFCC work.
[5 empty] | -- | 2017-12-28 09:26 | 2017-12-28 19:40 |  |  |  | 0 | 0 | 0 | 0.42639 |  |  |  |  | OSPD |  |  | S/D availed by UPPCL for powerline crossing work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-02 20:23 | [9 empty] | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
21 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | 2017-12-24 22:58 | 2017-12-25 00:15 |  |  |  | 0 | 0 | 0.053472 | 0 |  |  |  |  | GOVC |  |  | Tripped due to O/V protection operated
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.053472 | 0 | [9 empty] | 742.7167 | 156 | 177.88 | 27749.28 | 27749.28 | 100
22 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR3 | -- | 2017-12-27 09:51 | 2017-12-27 16:48 | -- | -- | -- | 0 | 0 | 0 | 0.28958 |  |  |  |  | OSFD |  |  | E/S/D availed by UPPCL for attending oil leakage from B phase C.T. stud at UPPCL Chinhat end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.28958 | [9 empty] | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
23 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
24 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 105.72 | 13955.04 | 13955.04 | 100
25 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | 2017-12-29 11:43 | 2017-12-29 15:28 |  |  |  | 0.15625 | 0 | 0 | 0 |  |  |  |  | OSFT |  |  | E/S/D taken by POWERGRID to attend Hotspot in B-Ph line side CT connector at BLY(UP)
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.15625 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 106 | 13992 | 13921.4758 | 99.496
26 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 42.55 | 5616.6 | 5616.6 | 100
27 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
28 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
29 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 42.5 | 5610 | 5610 | 100
30 | NR320001 | 220KV KNP-RANIA | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 132 | 18.372 | 2425.104 | 2425.104 | 100
[5 empty] | -- | [20 empty] | 1851.585
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 | 58 | 2900 | 2900 | 100
121 | Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-10 03:03 | 0.84028 | 1900-01-02 22:50 | 1900-06-13 19:36 | [11 empty] | 17118.567 | 8508435.749 | 8437037.2078 | 99.1608 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.5411 | % (HVDC) | 89.7328
E |  | 765/400 KV ICT'S |  |  | -- | [19 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
17 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
18 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
19 | NR3ICT701 | 765/400KV ICT-I Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
20 | NR3ICT702 | 765/400KV ICT-II Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
F |  | 400/220 KV ICT'S |  | NR3 | --
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 500 |  | 500 | 500 | 100
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 |  | 2017-12-08 10:02 | 2017-12-08 15:29 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for AMP work. |  | 744 | 500 |  | 500 | 500 | 100
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 500 |  | 500 | 500 | 100
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR3 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | 2017-12-12 03:04 | 2017-12-12 03:10 |  |  |  | 0 | 0 | 0.0041667 | 0 |  |  |  |  | GOFC |  |  | Tripped due to operation of over flux, P'garh=239KV
[6 empty] | 2017-12-12 03:10 | 2017-12-12 07:31 |  |  |  | 0 | 0 | 0 | 0.18125 |  |  |  |  | SPRD |  |  | Kept open for Voltage regulation as per NRLDC instruction. P'garh=239kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.0041667 | 0.18125 | [9 empty] | 743.9 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | 2017-12-12 02:57 | 2017-12-12 03:10 |  |  |  | 0 | 0 | 0.0090278 | 0 |  |  |  |  | GOFC |  |  | Tripped due to operation of over flux, P'garh=239KV |  | 743.7833 | 100 |  | 100 | 100 | 100
[6 empty] | 2017-12-12 03:10 | 2017-12-12 07:52 |  |  |  | 0 | 0 | 0 | 0.19583 |  |  |  |  | SPRD |  |  | Kept open for Voltage regulation as per NRLDC instruction. P'garh=239kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.0090278 | 0.19583
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.018056 | 0.39167 | [9 empty] | 743.5667 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR3 | -- | 2017-12-03 01:36 | 2017-12-03 18:13 |  |  |  | 0.69236 | 0 | 0 | 0 |  |  |  |  | SRET |  |  | Tripped due to REF protection operated
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.69236 | 0 | 0 | 0 | [9 empty] | 744 | 100 |  | 100 | 97.7666 | 97.7666
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 100 |  | 100 | 100 | 100
--
45 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 0.69236 | 0 | 0.022222 | 0.57292 | [10 empty] | 29425 |  | 29425 | 29422.7666 | 99.9924 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [19 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2017-12-09 17:29 | 2017-12-09 19:44 |  |  |  | 0 | 0.09375 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped due to AC supply failure at Dadri (NTPC) end.
[6 empty] | 2017-12-29 17:30 | 2017-12-29 17:30 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R operated successfully due to DC Transient earth fault, F.D. -149.60kM from Rihand and 665.40kM from dadri (Mirzapur TL jurisdiction)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.09375 | 0 | 0 | [9 empty] | 744 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2017-12-01 | 2017-12-03 20:25 |  |  |  | 1900-01-01 20:25 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D availed for various maintenance work at Rihand HVDC
[6 empty] | 2017-12-07 10:39 | 2017-12-07 18:01 |  |  |  | 0.30694 | 0 | 0 | 0 |  |  |  |  | OMST |  |  | Emergency S/D taken for inspection of valve hall for any leakage of fine water & rectification at Rihand
[6 empty] | 2017-12-09 17:29 | 2017-12-09 19:53 |  |  |  | 0 | 0.1 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped due to AC supply failure at Dadri (NTPC) end.
[6 empty] | 2017-12-10 16:42 | 2017-12-10 16:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R operated successfully from both end due to DC transient earth fault, F.D.=377.8km from Rihand,F.D.=437.2km from Dadri (Kanpur Jurisdiction)
[6 empty] | 2017-12-10 19:47 | 2017-12-10 19:47 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | A/R operated successfully from both end due to DC transient earth fault, F.D.=324.8km from Rihand,F.D.=490.2km from Dadri (Allahabad Jurisdiction)
[6 empty] | 2017-12-14 09:35 | 2017-12-14 09:58 |  |  |  | 0.015972 | 0 | 0 | 0 |  |  |  |  | OMST |  |  | Tripped due to Protective Block received on Rh due to malfunctioning of Convertor fire control at Dadri end(NR-1)
[6 empty] | 2017-12-19 19:15 | 2017-12-19 19:48 |  |  |  | 0 | 0 | 0.022917 | 0 |  |  |  |  | LNCC |  |  | Tripped due to heavy fog at Dadri end
[6 empty] | 2017-12-21 04:17 | 2017-12-21 05:02 |  |  |  | 0 | 0 | 0.03125 | 0 |  |  |  |  | LNCC |  |  | Tripped due to heavy fog at Dadri
[6 empty] | 2017-12-21 11:00 | 2017-12-21 13:30 |  |  |  | 0.10417 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | S/D taken for analysing convertor control sequence system at Dadri end.
[6 empty] | 2017-12-23 01:08 | 2017-12-23 01:08 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | LART |  |  | Transient fault. FD: Rihand-149.66km, Dadri-665.34km.
[6 empty] | 2017-12-29 22:26 | 2017-12-29 23:09 |  |  |  | 0.029861 | 0 | 0 | 0 |  |  |  |  | OMST |  |  | Tripped on reciept of Protection block from Dadri end
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-02 07:23 | 0.1 | 0.054167 | 0 | [9 empty] | 742.7 | 750 | 815 | 611250 | 545916.6723 | 89.3115
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | 2017-12-13 03:57 | 2017-12-13 04:16 |  |  |  | 0 | 0 | 0.013194 | 0 |  |  |  |  | LNCC |  |  | Tripped due to DC line E/F. F.D.= 637.37KM from Balia & 152.5KM from Bhiwadi. The fault was in NR-I juridiction.
[6 empty] | 2017-12-21 00:38 | 2017-12-21 15:19 |  |  |  | 0.61181 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Tripped due to SF 6 gas leakage from Pole 1 valve hall A.C Bushing due to external pipe nearby manometer gauge of bushing have got damaged during inclement weather at Bhiwadi
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.61181 | 0 | 0.013194 | 0 | [9 empty] | 743.6833 | 1250 | 789.786 | 987232.5 | 967740.5157 | 98.0256
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2017-12-13 03:57 | 2017-12-13 04:16 |  |  |  | 0 | 0 | 0.013194 | 0 |  |  |  |  | LNCC |  |  | Tripped due to DC line E/F. F.D.= 637.37KM from Balia & 152.5KM from Bhiwadi. The fault was in NR-I juridiction.
[6 empty] | 2017-12-21 00:38 | 2017-12-21 02:17 |  |  |  | 0.06875 | 0 | 0 | 0 |  |  |  |  | OSPT |  |  | Tripped due to SF 6 gas leakage from Pole 1 valve hall A.C Bushing due to external pipe nearby manometer gauge of bushing have got damaged during inclement weather at Bhiwadi
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.06875 | 0 | 0.013194 | 0 | [9 empty] | 743.6833 | 1250 | 789.786 | 987232.5 | 985042.1408 | 99.7781
5 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2017-12-22 11:04 | 2017-12-23 13:09 |  |  |  | 1899-12-31 02:05 | 0 | 0 | 0 |  |  |  |  | OMST |  |  | Taken under Emergency S/D to attend leakage in valve hall
[6 empty] | 2017-12-29 17:55 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:05 |  |  |  |  | LVRD |  |  | Blocked on voltage regulation as per NLDC instruction
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 02:05 | 0 | 0 | 1900-01-01 06:05 | [9 empty] | 744 | 1500 | 1728 | 2592000 | 2501129.0323 | 96.4942
6 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | 2017-12-12 02:06 | 2017-12-12 07:14 |  |  |  | 0 | 0 | 0 | 0.21389 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
[6 empty] | 2017-12-22 17:16 | 2018-01-01 |  |  |  | 0 | 0 | 0 | 1900-01-08 06:44 |  |  |  |  | LVRD |  |  | Blocked on voltage regulation as per NLDC instruction
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 11:52 | [9 empty] | 744 | 1500 | 1728 | 2592000 | 2592000 | 100
7 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-III | 789.786 | NR3 | -- | 2017-12-01 | 2017-12-01 06:45 |  |  |  | 0 | 0 | 0 | 0.28125 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NLDC instruction due to Voltage problem at APD.
[6 empty] | 2017-12-01 13:30 | 2017-12-03 06:50 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:20 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NLDC instruction due to Voltage problem at APD.
[6 empty] | 2017-12-04 23:23 | 2017-12-09 09:00 |  |  |  | 0 | 0 | 0 | 1900-01-03 09:37 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2017-12-09 11:43 | 2017-12-14 10:38 |  |  |  | 0 | 0 | 0 | 1900-01-03 22:55 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2017-12-14 21:40 | 2017-12-22 10:50 |  |  |  | 0 | 0 | 0 | 1900-01-06 13:10 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2017-12-14 21:40 | 2017-12-22 10:50 |  |  |  | 0 | 0 | 0 | 1900-01-06 13:10 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2017-12-22 21:43 | 2017-12-28 07:35 |  |  |  | 0 | 0 | 0 | 1900-01-04 09:52 |  |  |  |  | LVRD |  |  | Blocked on voltage regulation as per NRLDC instruction
[6 empty] | 2017-12-28 13:03 | 2017-12-29 07:32 |  |  |  | 0 | 0 | 0 | 0.77014 |  |  |  |  | LVRD |  |  | Blocked on voltage regulation as per NRLDC instruction
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-31 15:18 | [9 empty] | 744 | 1500 | 1728 | 2592000 | 2592000 | 100
8 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-IV | 789.786 | NR3 | -- | 2017-12-01 | 2017-12-03 09:14 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:14 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction.
[6 empty] | 2017-12-03 19:18 | 2017-12-05 06:50 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:32 |  |  |  |  | LVRD |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2017-12-06 21:03 | 2017-12-07 07:01 |  |  |  | 0 | 0 | 0 | 0.41528 |  |  |  |  | LVRD |  |  | Blocked on Voltage regulation as per NRLDC instruction
[6 empty] | 2017-12-07 12:39 | 2017-12-08 07:12 |  |  |  | 0 | 0 | 0 | 0.77292 |  |  |  |  | LVRD |  |  | Blocked on voltage regulation as per NRLDC instruction
[6 empty] | 2017-12-08 21:56 | 2017-12-11 06:34 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:38 |  |  |  |  | LVRD |  |  | Blocked on voltage regulation as per NRLDC instruction due to APD end
[6 empty] | 2017-12-11 20:13 | 2017-12-21 11:14 |  |  |  | 0 | 0 | 0 | 1900-01-08 15:01 |  |  |  |  | LVRD |  |  | Blocked on voltage regulation as per NLDC instruction .Agra-798KV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-16 00:56 | [9 empty] | 744 | 1500 | 1728 | 2592000 | 2592000 | 100
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 1900-01-04 01:48 | 0.19375 | 0.080556 | 1900-02-12 09:15 | [11 empty] | 10121.572 | 13564965 | 13387078.361 | 98.6886 | %
J |  | HVDC BTB VINDH |  |  | -- | [19 empty] | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2017-12-09 02:30 | 2017-12-09 20:43 |  |  |  | 0.75903 | 0 | 0 | 0 |  |  |  |  | OMST |  |  | Blocked for changing power flow direction from W->N to N->W at 02:30 Hrs. of 09.12.2017 as per NLDC instruction. But RFS (Ready for start) for Block#1 was not obtained due to Thyristor Failure Level 2 alarm at Vindyachal
[6 empty] | 2017-12-27 03:06 | 2017-12-27 05:07 |  |  |  | 0 | 0.084028 | 0 | 0 |  |  |  |  | OMSU |  |  | Tripped due to operation of DC over current protection caused by fault in external agency
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.75903 | 0.084028 | 0 | 0 | [9 empty] | 744 | 250 |  | 250 | 243.8788 | 97.5515
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | 2017-12-01 | 2018-01-01 |  |  |  | 1900-01-30 | 0 | 0 | 0 |  |  |  |  | OMST |  |  | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-30 | 0 | 0 | 0 | [9 empty] | 744 | 250 |  | 250 | 0 | 0
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-30 18:13 | 0.084028 | 0 | 0 | [12 empty] | 500 | 243.8788 | 48.7758 | %
3 | NR1DCB02 | Sasaram HVDC B/B BLOCK-I | 250 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 250 |  | 250 | 250 | 100
|  | HVDC BTB TOTAL |  |  | -- | [5 empty] | 1900-01-30 18:13 | 0.084028 | 0 | 0 | [10 empty] | RC
L |  | SVC, KANPUR |  |  | -- | [19 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 530 | 530 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [19 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | [10 empty] | 744 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 2X50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 100 |  | 100 | 100 | 100
15 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 |  | 50 | 50 | 100
16 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
17 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
18 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 330 |  | 330 | 330 | 100
19 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
20 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
21 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 80 |  | 80 | 80 | 100
22 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
23 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
24 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
25 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
26 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
27 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 80 |  | 80 | 80 | 100
28 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
29 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
30 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
31 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
32 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
33 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
34 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
35 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
36 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 330 |  | 330 | 330 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
37 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
38 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
39 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
40 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
41 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
42 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
43 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
44 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
45 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
46 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
47 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 125 |  | 125 | 125 | 100
48 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 744 | 50 |  | 50 | 50 | 100
49 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 240 |  | 240 | 240 | 100
50 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 330 |  | 330 | 330 | 100
51 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 330 |  | 330 | 330 | 100
52 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 330 |  | 330 | 330 | 100 | %
53 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 330 |  | 125 | 125 | 100 | %
54 |  | 125MVAR B/Reactor-III KANPUR(GIS) | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [9 empty] | 744 | 330 |  | 125 | 125 | 100 | %
|  | TOTAL FOR B/Rs |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [10 empty] | 1931-01-30 09:36 |  | 1929-12-16 09:36 | 1929-12-16 09:36 | 100 | %
Formulas:
Hrs:Min = IF(RIGHT([Code])="T",(+H9-G9),0)
Hrs:Min = IF(RIGHT([Code])="U",(+H9-G9),0)
RC = SUM(Z824:[RC, row above])
G=E x F = SUM(AB824:[G=E x F, row above])
THMxMVARxMF = SUM(AC824:[THMxMVARxMF, row above])
Note on C9: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C73: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C77: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C91: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C100: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C232: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C235: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C469: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C472: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C610: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C685: DOC-15/06/14
Note on C686: DOC-26/09/14

## Sheet1
POWER GRID CORPORATION OF INDIA LTD.
CPCC, LUCKNOW
DOC No: NR-III-CPCC-
MONTH –December LINE- ICT OUTAGE DETAILS
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | NRLDC CODE | Classification- Category Code | REASON OF OUTAGE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint- Natural calamity- Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  | Code
[5 empty] | 1900-02-16 07:05 | 1899-12-31 02:50 | 1900-01-03 08:22 | 1900-08-05 10:45
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 11 | 12
NRNEDCP03 | 311245 | 800KV HVDC AGRA-APD POLE-III | 2017-12-01 | 2017-12-01 06:45 | 0 | 0 | 0 | 0.28125 | NL-1788 | LVRD | Hand tripped on Voltage regulation as per NLDC instruction due to Voltage problem at APD.
NRNEDCP03 | 312004 | 800KV HVDC AGRA-APD POLE-III | 2017-12-01 13:30 | 2017-12-03 06:50 | 0 | 0 | 0 | 1899-12-31 17:20 | NL-26 | LVRD | Hand tripped on Voltage regulation as per NLDC instruction due to Voltage problem at APD.
NRNEDCP03 | 312027 | 800KV HVDC AGRA-APD POLE-III | 2017-12-04 23:23 | 2017-12-09 09:00 | 0 | 0 | 0 | 1900-01-03 09:37 | N217 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NRNEDCP03 | 312056 | 800KV HVDC AGRA-APD POLE-III | 2017-12-09 11:43 | 2017-12-14 10:38 | 0 | 0 | 0 | 1900-01-03 22:55 | N-856 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NRNEDCP03 | 312112 | 800KV HVDC AGRA-APD POLE-III | 2017-12-14 21:40 | 2017-12-22 10:50 | 0 | 0 | 0 | 1900-01-06 13:10 | N-1516 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NRNEDCP03 | 312112 | 800KV HVDC AGRA-APD POLE-III | 2017-12-14 21:40 | 2017-12-22 10:50 | 0 | 0 | 0 | 1900-01-06 13:10 | N-1516 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NRNEDCP03 | 312176 | 800KV HVDC AGRA-APD POLE-III | 2017-12-22 21:43 | 2017-12-28 07:35 | 0 | 0 | 0 | 1900-01-04 09:52 | N-2449 | LVRD | Blocked on voltage regulation as per NRLDC instruction
NRNEDCP03 | 312240 | 800KV HVDC AGRA-APD POLE-III | 2017-12-28 13:03 | 2017-12-29 07:32 | 0 | 0 | 0 | 0.77014 | N-3037 | LVRD | Blocked on voltage regulation as per NRLDC instruction
NRNEDCP04 | 311237 | 800KV HVDC AGRA-APD POLE-IV | 2017-12-01 | 2017-12-03 09:14 | 0 | 0 | 0 | 1900-01-01 09:14 | N-3329 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
NRNEDCP04 | 312020A | 800KV HVDC AGRA-APD POLE-IV | 2017-12-03 19:18 | 2017-12-05 06:50 | 0 | 0 | 0 | 1899-12-31 11:32 | N-274 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NRNEDCP04 | 312040 | 800KV HVDC AGRA-APD POLE-IV | 2017-12-06 21:03 | 2017-12-07 07:01 | 0 | 0 | 0 | 0.41528 | N-586 | LVRD | Blocked on Voltage regulation as per NRLDC instruction
NRNEDCP04 | 312044 | 800KV HVDC AGRA-APD POLE-IV | 2017-12-07 12:39 | 2017-12-08 07:12 | 0 | 0 | 0 | 0.77292 | N-652 | LVRD | Blocked on voltage regulation as per NRLDC instruction
NRNEDCP04 | 312054 | 800KV HVDC AGRA-APD POLE-IV | 2017-12-08 21:56 | 2017-12-11 06:34 | 0 | 0 | 0 | 1900-01-01 08:38 | N-822 | LVRD | Blocked on voltage regulation as per NRLDC instruction due to APD end
NRNEDCP04 | 312074 | 800KV HVDC AGRA-APD POLE-IV | 2017-12-11 20:13 | 2017-12-21 11:14 | 0 | 0 | 0 | 1900-01-08 15:01 | NL-573 | LVRD | Blocked on voltage regulation as per NLDC instruction .Agra-798KV
NRNEDCP01 | 312172 | 800KV HVDC AGRA-BNC POLE-I | 2017-12-22 11:04 | 2017-12-23 13:09 | 1899-12-31 02:05 | 0 | 0 | 0 | N-2372 | OMST | Taken under Emergency S/D to attend leakage in valve hall
NRNEDCP01 | 312249 | 800KV HVDC AGRA-BNC POLE-I | 2017-12-29 17:55 | 2018-01-01 | 0 | 0 | 0 | 1900-01-01 06:05 | NL-1675 | LVRD | Blocked on voltage regulation as per NLDC instruction
NRNEDCP02 | 312078 | 800KV HVDC AGRA-BNC POLE-II | 2017-12-12 02:06 | 2017-12-12 07:14 | 0 | 0 | 0 | 0.21389 | N-1111 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
NRNEDCP02 | 312173 | 800KV HVDC AGRA-BNC POLE-II | 2017-12-22 17:16 | 2018-01-01 | 0 | 0 | 0 | 1900-01-08 06:44 | NL-1239 | LVRD | Blocked on voltage regulation as per NLDC instruction
NR1DCP03 | 312092 | 500KV HVDC BALIA-BHWD POLE-I | 2017-12-13 03:57 | 2017-12-13 04:16 | 0 | 0 | 0.013194 | 0 | **** | LNCC | Tripped due to DC line E/F. F.D.= 637.37KM from Balia & 152.5KM from Bhiwadi. The fault was in NR-I juridiction.
NR1DCP03 | 312158 | 500KV HVDC BALIA-BHWD POLE-I | 2017-12-21 00:38 | 2017-12-21 15:19 | 0.61181 | 0 | 0 | 0 | **** | OSPT | Tripped due to SF 6 gas leakage from Pole 1 valve hall A.C Bushing due to external pipe nearby manometer gauge of bushing have got damaged during inclement weather at Bhiwadi
NR1DCP04 | 312093 | 500KV HVDC BALIA-BHWD POLE-II | 2017-12-13 03:57 | 2017-12-13 04:16 | 0 | 0 | 0.013194 | 0 | **** | LNCC | Tripped due to DC line E/F. F.D.= 637.37KM from Balia & 152.5KM from Bhiwadi. The fault was in NR-I juridiction.
NR1DCP04 | 312159 | 500KV HVDC BALIA-BHWD POLE-II | 2017-12-21 00:38 | 2017-12-21 02:17 | 0.06875 | 0 | 0 | 0 | **** | OSPT | Tripped due to SF 6 gas leakage from Pole 1 valve hall A.C Bushing due to external pipe nearby manometer gauge of bushing have got damaged during inclement weather at Bhiwadi
NR1DCP01 | 312062 | 500KV HVDC R-D POLE-I | 2017-12-09 17:29 | 2017-12-09 19:44 | 0 | 0.09375 | 0 | 0 | **** | OMSU | Tripped due to AC supply failure at Dadri (NTPC) end.
NR1DCP01 | 312255 | 500KV HVDC R-D POLE-I | 2017-12-29 17:30 | 2017-12-29 17:30 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully due to DC Transient earth fault, F.D. -149.60kM from Rihand and 665.40kM from dadri (Mirzapur TL jurisdiction)
NR1DCP02 | 311210 | 500KV HVDC R-D POLE-II | 2017-12-01 | 2017-12-03 20:25 | 1900-01-01 20:25 | 0 | 0 | 0 | N-2978 | OSPT | S/D availed for various maintenance work at Rihand HVDC
NR1DCP02 | 312043 | 500KV HVDC R-D POLE-II | 2017-12-07 10:39 | 2017-12-07 18:01 | 0.30694 | 0 | 0 | 0 | N-637 | OMST | Emergency S/D taken for inspection of valve hall for any leakage of fine water & rectification at Rihand
NR1DCP02 | 312063 | 500KV HVDC R-D POLE-II | 2017-12-09 17:29 | 2017-12-09 19:53 | 0 | 0.1 | 0 | 0 | **** | OMSU | Tripped due to AC supply failure at Dadri (NTPC) end.
NR1DCP02 | 312067 | 500KV HVDC R-D POLE-II | 2017-12-10 16:42 | 2017-12-10 16:42 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient earth fault, F.D.=377.8km from Rihand,F.D.=437.2km from Dadri (Kanpur Jurisdiction)
NR1DCP02 | 312068 | 500KV HVDC R-D POLE-II | 2017-12-10 19:47 | 2017-12-10 19:47 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient earth fault, F.D.=324.8km from Rihand,F.D.=490.2km from Dadri (Allahabad Jurisdiction)
NR1DCP02 | 312111 | 500KV HVDC R-D POLE-II | 2017-12-14 09:35 | 2017-12-14 09:58 | 0.015972 | 0 | 0 | 0 | **** | OMST | Tripped due to Protective Block received on Rh due to malfunctioning of Convertor fire control at Dadri end(NR-1)
NR1DCP02 | 312148 | 500KV HVDC R-D POLE-II | 2017-12-19 19:15 | 2017-12-19 19:48 | 0 | 0 | 0.022917 | 0 | **** | LNCC | Tripped due to heavy fog at Dadri end
NR1DCP02 | 312160 | 500KV HVDC R-D POLE-II | 2017-12-21 04:17 | 2017-12-21 05:02 | 0 | 0 | 0.03125 | 0 | **** | LNCC | Tripped due to heavy fog at Dadri
NR1DCP02 | 312162 | 500KV HVDC R-D POLE-II | 2017-12-21 11:00 | 2017-12-21 13:30 | 0.10417 | 0 | 0 | 0 | N-2245 | OSPT | S/D taken for analysing convertor control sequence system at Dadri end.
NR1DCP02 | 312181 | 500KV HVDC R-D POLE-II | 2017-12-23 01:08 | 2017-12-23 01:08 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand-149.66km, Dadri-665.34km.
NR1DCP02 | 312256 | 500KV HVDC R-D POLE-II | 2017-12-29 22:26 | 2017-12-29 23:09 | 0.029861 | 0 | 0 | 0 | N-4119 | OMST | Tripped on reciept of Protection block from Dadri end
NR1DCB01 | 312055 | VINDH HVDC B/B BLOCK-I | 2017-12-09 02:30 | 2017-12-09 20:43 | 0.75903 | 0 | 0 | 0 | NL-115 | OMST | Blocked for changing power flow direction from W->N to N->W at 02:30 Hrs. of 09.12.2017 as per NLDC instruction. But RFS (Ready for start) for Block#1 was not obtained due to Thyristor Failure Level 2 alarm at Vindyachal
NR1DCB01 | 312226 | VINDH HVDC B/B BLOCK-I | 2017-12-27 03:06 | 2017-12-27 05:07 | 0 | 0.084028 | 0 | 0 | **** | OMSU | Tripped due to operation of DC over current protection caused by fault in external agency
NR1DCB02 | 311198 | VINDH HVDC B/B BLOCK-II | 2017-12-01 | 2018-01-01 | 1900-01-30 | 0 | 0 | 0 | **** | OMST | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL
NR176502 | 311243 | 765KV AGRA-FATEHPUR-I | 2017-12-01 | 2017-12-01 09:12 | 0 | 0 | 0 | 0.38333 | N-3437 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=785kV
NR176502 | 312025 | 765KV AGRA-FATEHPUR-I | 2017-12-04 09:20 | 2017-12-04 19:06 | 0.40694 | 0 | 0 | 0 | N-316 | OSPT | For insulator cleaning work & pre winter maintenance work
NR176502 | 312026 | 765KV AGRA-FATEHPUR-I | 2017-12-04 19:06 | 2017-12-05 07:24 | 0 | 0 | 0 | 0.5125 | N-373 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176502 | 312030 | 765KV AGRA-FATEHPUR-I | 2017-12-05 20:50 | 2017-12-06 07:50 | 0 | 0 | 0 | 0.45833 | N-485 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176502 | 312045 | 765KV AGRA-FATEHPUR-I | 2017-12-07 19:37 | 2017-12-08 07:41 | 0 | 0 | 0 | 0.50278 | N-699 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176502 | 312064 | 765KV AGRA-FATEHPUR-I | 2017-12-10 00:38 | 2017-12-11 08:16 | 0 | 0 | 0 | 1899-12-31 07:38 | N-927 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
NR176502 | 312077 | 765KV AGRA-FATEHPUR-I | 2017-12-12 01:37 | 2017-12-12 10:51 | 0 | 0 | 0 | 0.38472 | N-1108 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
NR176502 | 312089 | 765KV AGRA-FATEHPUR-I | 2017-12-12 20:15 | 2017-12-13 07:08 | 0 | 0 | 0 | 0.45347 | N-1261 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
NR176502 | 312097 | 765KV AGRA-FATEHPUR-I | 2017-12-13 19:52 | 2017-12-14 09:30 | 0 | 0 | 0 | 0.56806 | N-1376 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176502 | 312122 | 765KV AGRA-FATEHPUR-I | 2017-12-16 19:44 | 2017-12-17 09:00 | 0 | 0 | 0 | 0.55278 | N-1737 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
NR176502 | 312128 | 765KV AGRA-FATEHPUR-I | 2017-12-17 20:07 | 2017-12-18 06:45 | 0 | 0 | 0 | 0.44306 | N-1827 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176502 | 312140 | 765KV AGRA-FATEHPUR-I | 2017-12-19 01:13 | 2017-12-19 07:10 | 0 | 0 | 0 | 0.24792 | N-1952 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
NR176502 | 312164 | 765KV AGRA-FATEHPUR-I | 2017-12-21 19:36 | 2017-12-22 07:23 | 0 | 0 | 0 | 0.49097 | N-2302 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
NR176502 | 312175 | 765KV AGRA-FATEHPUR-I | 2017-12-22 21:37 | 2017-12-23 06:43 | 0 | 0 | 0 | 0.37917 | N-2441 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
NR176502 | 312209 | 765KV AGRA-FATEHPUR-I | 2017-12-25 23:53 | 2017-12-26 09:53 | 0 | 0 | 0 | 0.41667 | N-2752 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176502 | 312239 | 765KV AGRA-FATEHPUR-I | 2017-12-28 13:07 | 2017-12-29 06:34 | 0 | 0 | 0 | 0.72708 | N-3038 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
NR176502 | 312254 | 765KV AGRA-FATEHPUR-I | 2017-12-29 20:54 | 2017-12-30 10:18 | 0 | 0 | 0 | 0.55833 | N-4109 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=793kV
NR176502 | 312266 | 765KV AGRA-FATEHPUR-I | 2017-12-30 20:45 | 2017-12-31 09:55 | 0 | 0 | 0 | 0.54861 | N-4233 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR176502 | 312279 | 765KV AGRA-FATEHPUR-I | 2017-12-31 20:58 | 2018-01-01 | 0 | 0 | 0 | 0.12639 | N-4310 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
NR176507 | 312007 | 765KV AGRA-FATEHPUR-II | 2017-12-01 19:12 | 2017-12-02 09:06 | 0 | 0 | 0 | 0.57917 | N-123 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
NR176507 | 312015 | 765KV AGRA-FATEHPUR-II | 2017-12-02 21:05 | 2017-12-04 09:06 | 0 | 0 | 0 | 1899-12-31 12:01 | N-212 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176507 | 312028 | 765KV AGRA-FATEHPUR-II | 2017-12-05 07:57 | 2017-12-05 18:23 | 0.43472 | 0 | 0 | 0 | N-400 | OSPT | For insulator cleaning work & pre winter maintenance work
NR176507 | 312033 | 765KV AGRA-FATEHPUR-II | 2017-12-06 01:10 | 2017-12-06 06:12 | 0 | 0 | 0 | 0.20972 | N-497 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176507 | 312037 | 765KV AGRA-FATEHPUR-II | 2017-12-06 20:02 | 2017-12-07 07:08 | 0 | 0 | 0 | 0.4625 | N-583 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR176507 | 312051 | 765KV AGRA-FATEHPUR-II | 2017-12-08 19:15 | 2017-12-09 07:15 | 0 | 0 | 0 | 0.5 | N-810 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
NR176507 | 312073 | 765KV AGRA-FATEHPUR-II | 2017-12-11 19:33 | 2017-12-12 07:00 | 0 | 0 | 0 | 0.47708 | N-1071 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=797kV
NR176507 | 312105 | 765KV AGRA-FATEHPUR-II | 2017-12-14 20:01 | 2017-12-15 08:00 | 0 | 0 | 0 | 0.49931 | N-1511 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
NR176507 | 312113 | 765KV AGRA-FATEHPUR-II | 2017-12-15 20:01 | 2017-12-16 08:29 | 0 | 0 | 0 | 0.51944 | N-1626 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176507 | 312132 | 765KV AGRA-FATEHPUR-II | 2017-12-18 01:14 | 2017-12-18 08:32 | 0 | 0 | 0 | 0.30417 | N-1839 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
NR176507 | 312139 | 765KV AGRA-FATEHPUR-II | 2017-12-18 22:02 | 2017-12-19 10:03 | 0 | 0 | 0 | 0.50069 | N-1949 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
NR176507 | 312147 | 765KV AGRA-FATEHPUR-II | 2017-12-19 22:06 | 2017-12-20 08:45 | 0 | 0 | 0 | 0.44375 | N-2068 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176507 | 312154 | 765KV AGRA-FATEHPUR-II | 2017-12-21 00:13 | 2017-12-21 06:57 | 0 | 0 | 0 | 0.28056 | N-2192 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
NR176507 | 312187 | 765KV AGRA-FATEHPUR-II | 2017-12-23 17:12 | 2017-12-25 10:27 | 0 | 0 | 0 | 1899-12-31 17:15 | N-2534 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
NR176507 | 312210 | 765KV AGRA-FATEHPUR-II | 2017-12-26 01:14 | 2017-12-26 06:44 | 0 | 0 | 0 | 0.22917 | N-2754 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176507 | 312221 | 765KV AGRA-FATEHPUR-II | 2017-12-27 00:04 | 2017-12-28 08:56 | 0 | 0 | 0 | 1899-12-31 08:52 | N-2865 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR176510 | 312001 | 765KV AGRA-GR.NOIDA | 2017-12-01 09:52 | 2017-12-01 15:23 | 0 | 0 | 0 | 0.22986 | N-42 | LCSD | S/D availed for completing the pending work related for stringing(Powerline crossing) of 765kv Orai-Aligarh D/C
NR176506 | 312245 | 765kV FATEHPUR-SASARAM | 2017-12-29 04:14 | 2017-12-29 16:30 | 0 | 0 | 0.51111 | 0 | N-4064 | LNCC | Tripped due to heavy fog on R-N fault,F.D.=250km from Fatehpur, F.C.=2.34KA, (Varanasi Jurisdiction)
NR376503 | 312023 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-04 00:50 | 2017-12-04 05:44 | 0 | 0 | 0 | 0.20417 | N-290 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP GIS=797kV
NR376503 | 312070 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-11 01:54 | 2017-12-11 06:37 | 0 | 0 | 0 | 0.19653 | N-988 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP GIS=787kV
NR376503 | 312075 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-11 20:14 | 2017-12-12 07:31 | 0 | 0 | 0 | 0.47014 | N-1077 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP GIS=787kV
NR376503 | 312103 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-14 01:04 | 2017-12-14 09:01 | 0 | 0 | 0 | 0.33125 | N-1393 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur GIS=788kV
NR376503 | 312117 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-16 00:50 | 2017-12-16 08:45 | 0 | 0 | 0 | 0.32986 | N-1636 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur GIS=797kV
NR376503 | 312125 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-16 23:51 | 2017-12-17 06:44 | 0 | 0 | 0 | 0.28681 | N-1748 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur GIS=796kV
NR376503 | 312170 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-22 02:53 | 2017-12-22 06:07 | 0 | 0 | 0 | 0.13472 | N-2320 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=797kV
NR376503 | 312182 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-23 02:04 | 2017-12-23 06:39 | 0 | 0 | 0 | 0.19097 | N-2456 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=791kV
NR376503 | 312191 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-24 02:13 | 2017-12-24 06:48 | 0 | 0 | 0 | 0.19097 | N-2576 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-433KV
NR376503 | 312199 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-25 00:09 | 2017-12-25 07:37 | 0 | 0 | 0 | 0.31111 | N-2648 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=796kV
NR376503 | 312260 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-30 03:12 | 2017-12-30 07:18 | 0 | 0 | 0 | 0.17083 | N-4163 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=793kV
NR376503 | 312269 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-31 01:12 | 2017-12-31 09:19 | 0 | 0 | 0 | 0.33819 | N-4240 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=801kV
NR376503 | 312280 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-12-31 21:05 | 2018-01-01 | 0 | 0 | 0 | 0.12153 | N-4313 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=798kV
NR176501 | 312142 | 765KV LUCKNOW-BALIA | 2017-12-19 03:36 | 2017-12-19 15:05 | 0 | 0 | 0.47847 | 0 | **** | LNCC | Tripped due to B-N fault,F.D.=146.734km from LKO(Lucknow jurisdiction),F.C.=2.781KA,F.D.=73.33km from Balia(Azamgarh jurisdiction) caused by dense fog
NR176501 | 312184 | 765KV LUCKNOW-BALIA | 2017-12-23 09:34 | 2017-12-23 19:38 | 0.41944 | 0 | 0 | 0 | N-2484 | OSPT | Taken under S/D for insulator cleaning work for winter season preparation.
NR176501 | 312192 | 765KV LUCKNOW-BALIA | 2017-12-24 04:13 | 2017-12-24 08:35 | 0 | 0 | 0.18194 | 0 | **** | LNCC | Tripped due to B-N fault. FD- 270.3 km from Ballia. FC- Ballia-2.48km. Dense fog reported.
NR176501 | 312193 | 765KV LUCKNOW-BALIA | 2017-12-24 08:35 | 2017-12-24 21:06 | 0.52153 | 0 | 0 | 0 | N-2598 | OSPT | Taken under S/D for insulator cleaning work for winter season preparation.
NR176501 | 312200 | 765KV LUCKNOW-BALIA | 2017-12-25 02:30 | 2017-12-25 02:30 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully at both end on B-N fault (Main bay at Balia tripped and Tie bay remain closed at Balia). FD: 273kM from Balia end and 25.92kM from Lucknow. FC: 2.445kA at Balia. Fault in Lucknow T/L group jurisdiction.
NR176501 | 312202 | 765KV LUCKNOW-BALIA | 2017-12-25 07:01 | 2017-12-25 08:30 | 0 | 0 | 0.061806 | 0 | **** | LNCC | Tripped due to B-N fault due to heavy fog. FD- 274.9 km from Ballia. FC- Ballia-2.421km. Fault in Lucknow T/L group jurisdiction.
NR176501 | 312203 | 765KV LUCKNOW-BALIA | 2017-12-25 08:30 | 2017-12-25 19:03 | 0.43958 | 0 | 0 | 0 | N-2689 | OSPT | Taken under S/D for insulator cleaning work for winter season preparation.
NR176501 | 312216 | 765KV LUCKNOW-BALIA | 2017-12-26 09:56 | 2017-12-26 18:58 | 0.37639 | 0 | 0 | 0 | N-2792 | OSPT | S/D availed for insulator cleaning work for winter season preparation.
NR176501 | 312234 | 765KV LUCKNOW-BALIA | 2017-12-28 06:21 | 2017-12-28 06:21 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully due to B-N Fault, M1:F.D.=86.93km from Balia,F.C.=5.619KA, M2:F.D.=87.2km from Balia,F.C.=5.466KA,F.D.=206.3km from LKO (Azamgarh jurisdiction)
NR176508 | 312002 | 765KV LUCKNOW-BAREILLY | 2017-12-01 09:48 | 2017-12-01 19:08 | 0.38889 | 0 | 0 | 0 | N-30 | OSPT | S/D availed for insulator cleaning due to upcoming dense fog
NR176508 | 312010 | 765KV LUCKNOW-BAREILLY | 2017-12-02 09:12 | 2017-12-02 18:42 | 0.39583 | 0 | 0 | 0 | N-159 | OSPT | S/D availed for insulator cleaning work for winter season preparation.
NR176508 | 312020 | 765KV LUCKNOW-BAREILLY | 2017-12-03 09:21 | 2017-12-03 18:43 | 0.39028 | 0 | 0 | 0 | N-245 | OSPT | S/D availed for insulator cleaning work for winter season preparation.
NR176508 | 312024 | 765KV LUCKNOW-BAREILLY | 2017-12-04 08:45 | 2017-12-04 18:18 | 0.39792 | 0 | 0 | 0 | N-310 | OSPT | For insulator cleaning work for winter preparation
NR176512 | 312229 | 765KV VARANASI-BALIA | 2017-12-27 13:38 | 2017-12-27 18:29 | 0.20208 | 0 | 0 | 0 | N-2919 | OSPT | S/D availed for removal spare reactor unit at Varanasi end
NR376501 | 312222 | 765KV VARANASI-KANPUR(GIS)-I | 2017-12-27 01:38 | 2017-12-27 03:02 | 0.058333 | 0 | 0 | 0 | **** | OMST | H/T on emergency basis from Varanasi end due to fire in B Ph L/R of 765KV Varanasi-Kanpur-2 at Varanasi end.
NR376501 | 312273 | 765KV VARANASI-KANPUR(GIS)-I | 2017-12-31 11:31 | 2017-12-31 14:54 | 0.14097 | 0 | 0 | 0 | N-4277 | OSPT | Emergency S/D availed for replacement of failed NGR LA at Kanpur GIS
NR376502 | 312223 | 765KV VARANASI-KANPUR(GIS)-II | 2017-12-27 01:38 | 2017-12-27 07:41 | 0.25208 | 0 | 0 | 0 | **** | SEFT | Tripped due to fire in its B Ph L/R at Varanasi end
NR140003 | 312099 | 400KV AGRA-AURAIYA-I | 2017-12-13 20:52 | 2017-12-14 08:56 | 0 | 0 | 0 | 0.50278 | N-1382 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140003 | 312141 | 400KV AGRA-AURAIYA-I | 2017-12-19 01:15 | 2017-12-19 09:39 | 0 | 0 | 0 | 0.35 | N-1953 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140003 | 312169 | 400KV AGRA-AURAIYA-I | 2017-12-22 00:44 | 2017-12-22 09:48 | 0 | 0 | 0 | 0.37778 | N-2315 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
NR140003 | 312177 | 400KV AGRA-AURAIYA-I | 2017-12-23 00:20 | 2017-12-23 09:52 | 0 | 0 | 0 | 0.39722 | N-2453 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140003 | 312186 | 400KV AGRA-AURAIYA-I | 2017-12-23 17:02 | 2017-12-26 13:18 | 0 | 0 | 0 | 1900-01-01 20:16 | N-2529 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140004 | 311066 | 400KV AGRA-AURAIYA-II | 2017-12-01 | 2017-12-04 11:01 | 0 | 0 | 0 | 1900-01-02 11:01 | N-1263 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=436kV
NR140004 | 312032 | 400KV AGRA-AURAIYA-II | 2017-12-05 22:09 | 2017-12-13 11:58 | 0 | 0 | 0 | 1900-01-06 13:49 | N-492 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140004 | 312107 | 400KV AGRA-AURAIYA-II | 2017-12-14 21:01 | 2017-12-18 11:38 | 0 | 0 | 0 | 1900-01-02 14:37 | N-1513 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
NR140004 | 312150 | 400KV AGRA-AURAIYA-II | 2017-12-20 01:29 | 2017-12-21 09:03 | 0 | 0 | 0 | 1899-12-31 07:34 | N-2071 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140004 | 312220 | 400KV AGRA-AURAIYA-II | 2017-12-27 00:02 | 2018-01-01 | 0 | 0 | 0 | 1900-01-03 23:58 | N-2864 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140005 | 312227 | 400KV AGRA-BASSI-I | 2017-12-27 08:27 | 2017-12-27 19:18 | 0 | 0 | 0 | 0.45208 | N-2891 | LCSD | S/D availed for replacement of Porcelain insulator with Polymer
NR140005 | 312235 | 400KV AGRA-BASSI-I | 2017-12-28 08:30 | 2017-12-28 19:24 | 0 | 0 | 0 | 0.45417 | N-3003 | LCSD | S/D availed for replacement of Porcelain insulator with Polymer
NR140005 | 312247 | 400KV AGRA-BASSI-I | 2017-12-29 10:04 | 2017-12-29 19:26 | 0 | 0 | 0 | 0.39028 | N-4029 | LCSD | S/D availed for replacement of Porcelain insulator with Polymer
NR140005 | 312263 | 400KV AGRA-BASSI-I | 2017-12-30 08:30 | 2017-12-30 19:32 | 0 | 0 | 0 | 0.45972 | N-4158 | LCSD | S/D availed for replacement of Porcelain insulator with Polymer
NR140005 | 312271 | 400KV AGRA-BASSI-I | 2017-12-31 08:35 | 2017-12-31 19:15 | 0 | 0 | 0 | 0.44444 | N-4263 | LCSD | S/D availed for replacement of Porcelain insulator with Polymer
NR140008 | 311244 | 400KV AGRA-BHIWADI-I | 2017-12-01 | 2017-12-02 09:28 | 0 | 0 | 0 | 1899-12-31 09:28 | N-3436 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140008 | 312046 | 400KV AGRA-BHIWADI-I | 2017-12-07 19:55 | 2017-12-09 07:26 | 0 | 0 | 0 | 1899-12-31 11:31 | N-700 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
NR140008 | 312098 | 400KV AGRA-BHIWADI-I | 2017-12-13 20:08 | 2017-12-14 10:42 | 0 | 0 | 0 | 0.60694 | N-1378 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140008 | 312174 | 400KV AGRA-BHIWADI-I | 2017-12-22 20:16 | 2017-12-23 09:51 | 0 | 0 | 0 | 0.56597 | N-2440 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140008 | 312188 | 400KV AGRA-BHIWADI-I | 2017-12-23 21:49 | 2017-12-25 09:43 | 0 | 0 | 0 | 1899-12-31 11:54 | N-2569 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
NR140009 | 312014 | 400KV AGRA-BHIWADI-II | 2017-12-02 16:47 | 2017-12-03 10:10 | 0 | 0 | 0 | 0.72431 | N-186 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140009 | 312022 | 400KV AGRA-BHIWADI-II | 2017-12-03 19:54 | 2017-12-04 09:44 | 0 | 0 | 0 | 0.57639 | N-277 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140009 | 312026 | 400KV AGRA-BHIWADI-II | 2017-12-04 18:46 | 2017-12-05 09:13 | 0 | 0 | 0 | 0.60208 | N-369 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
NR140009 | 312029 | 400KV AGRA-BHIWADI-II | 2017-12-05 19:19 | 2017-12-06 09:30 | 0 | 0 | 0 | 0.59097 | N-479 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
NR140009 | 312038 | 400KV AGRA-BHIWADI-II | 2017-12-06 21:01 | 2017-12-07 08:46 | 0 | 0 | 0 | 0.48958 | N-587 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=436kV
NR140009 | 312059 | 400KV AGRA-BHIWADI-II | 2017-12-09 13:11 | 2017-12-10 08:31 | 0 | 0 | 0 | 0.80556 | N-867 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140009 | 312066 | 400KV AGRA-BHIWADI-II | 2017-12-10 18:46 | 2017-12-11 07:17 | 0 | 0 | 0 | 0.52153 | N-974 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140009 | 312072 | 400KV AGRA-BHIWADI-II | 2017-12-11 18:54 | 2017-12-13 10:24 | 0 | 0 | 0 | 1899-12-31 15:30 | N-1067 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140009 | 312106 | 400KV AGRA-BHIWADI-II | 2017-12-14 20:24 | 2017-12-15 08:04 | 0 | 0 | 0 | 0.48611 | N-1513 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
NR140009 | 312114 | 400KV AGRA-BHIWADI-II | 2017-12-15 20:19 | 2017-12-18 06:41 | 0 | 0 | 0 | 1900-01-01 10:22 | N-1627 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140009 | 312136 | 400KV AGRA-BHIWADI-II | 2017-12-18 19:56 | 2017-12-19 07:42 | 0 | 0 | 0 | 0.49028 | N-1940 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140009 | 312146 | 400KV AGRA-BHIWADI-II | 2017-12-19 21:08 | 2017-12-20 06:28 | 0 | 0 | 0 | 0.38889 | N-2066 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140009 | 312153 | 400KV AGRA-BHIWADI-II | 2017-12-20 19:15 | 2017-12-21 07:42 | 0 | 0 | 0 | 0.51875 | N-2174 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140009 | 312165 | 400KV AGRA-BHIWADI-II | 2017-12-21 23:42 | 2017-12-22 06:43 | 0 | 0 | 0 | 0.29236 | N-2315 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140009 | 312208 | 400KV AGRA-BHIWADI-II | 2017-12-25 20:54 | 2017-12-26 06:41 | 0 | 0 | 0 | 0.40764 | N-2747 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140009 | 312217 | 400KV AGRA-BHIWADI-II | 2017-12-26 20:27 | 2017-12-27 06:25 | 0 | 0 | 0 | 0.41528 | N-2852 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=427kV
NR140009 | 312230 | 400KV AGRA-BHIWADI-II | 2017-12-27 20:07 | 2017-12-28 08:49 | 0 | 0 | 0 | 0.52917 | N-2971 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140009 | 312244 | 400KV AGRA-BHIWADI-II | 2017-12-29 01:30 | 2017-12-29 09:32 | 0 | 0 | 0 | 0.33472 | N-3093 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140009 | 312250 | 400KV AGRA-BHIWADI-II | 2017-12-29 19:59 | 2017-12-31 10:14 | 0 | 0 | 0 | 1899-12-31 14:15 | N-4100 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140009 | 312275 | 400KV AGRA-BHIWADI-II | 2017-12-31 19:24 | 2018-01-01 | 0 | 0 | 0 | 0.19167 | N-4302 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR340008 | 312017 | 400KV ALLAHABAD-MEJA(NTPC)-I | 2017-12-03 08:49 | 2017-12-03 19:57 | 0 | 0 | 0 | 0.46389 | N-234 | OSPD | S/D availed by UPPCL for construction related work
NR340009 | 311127 | 400KV ALLAHABAD-MEJA(NTPC)-II | 2017-12-01 | 2017-12-03 08:49 | 0 | 0 | 0 | 1900-01-01 08:49 | N-2124 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=422kV
NR340009 | 312018 | 400KV ALLAHABAD-MEJA(NTPC)-II | 2017-12-03 08:49 | 2017-12-03 20:02 | 0 | 0 | 0 | 0.46736 | N-235 | OSPD | S/D availed by UPPCL for construction related work
NR340009 | 312061 | 400KV ALLAHABAD-MEJA(NTPC)-II | 2017-12-09 17:17 | 2017-12-09 22:00 | 0 | 0.19653 | 0 | 0 | **** | OMSU | Tripped due to some problem at Meja (NTPC) end & DT received at Allahabad.
NR340009 | 312071 | 400KV ALLAHABAD-MEJA(NTPC)-II | 2017-12-11 10:30 | 2017-12-11 11:27 | 0 | 0.039583 | 0 | 0 | **** | OMSU | Tripped due to D/T received at Allahabad end due to PLCC problem at NTPC Meja end
NR140122 | 312133 | 400KV ALLD-FATEHPUR-I | 2017-12-18 01:14 | 2017-12-18 11:00 | 0 | 0 | 0 | 0.40694 | N-1840 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=431kV
NR140122 | 312144 | 400KV ALLD-FATEHPUR-I | 2017-12-19 08:42 | 2017-12-19 19:22 | 0.44444 | 0 | 0 | 0 | N-1969 | OSPT | S/D availed for insulator cleaning work for winter season preparation
NR140122 | 312152 | 400KV ALLD-FATEHPUR-I | 2017-12-20 09:23 | 2017-12-20 18:28 | 0.37847 | 0 | 0 | 0 | N-2094 | OSPT | S/D taken for insulator cleaning work for pre winter preparation.
NR140123 | 312161 | 400KV ALLD-FATEHPUR-II | 2017-12-21 09:19 | 2017-12-21 18:55 | 0.4 | 0 | 0 | 0 | N-2227 | OSPT | S/D taken for insulator cleaning work for pre winter preparation.
NR140123 | 312171 | 400KV ALLD-FATEHPUR-II | 2017-12-22 08:25 | 2017-12-22 19:09 | 0.44722 | 0 | 0 | 0 | N-2342 | OSPT | Taken under S/D for insulator cleaning work
NR140123 | 312262 | 400KV ALLD-FATEHPUR-II | 2017-12-30 03:05 | 2017-12-30 21:54 | 0 | 0 | 0.78403 | 0 | **** | LNCC | Tripped due to heavy fog on Y-B fault,F.D.=140km from Allahabad, F.C.=4.68KA, (Kanpur TL Jurisdiction). Decapped insulator restored at loc no 205
NR140163 | 312246 | 400KV ALLD-VARANASI | 2017-12-29 06:09 | 2017-12-29 06:09 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully at both end on R-N fault. FD: 55.62kM from VNS. FC: 5.4(Allahabad jurisdiction)
NR140163 | 312259 | 400KV ALLD-VARANASI | 2017-12-30 01:06 | 2017-12-30 01:06 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on R-N fault. FD: 52.06kM from Allhabad. FC: 7.61kA(Mirzapur jurisdiction)
NR140163 | 312272 | 400KV ALLD-VARANASI | 2017-12-31 11:01 | 2017-12-31 21:12 | 0 | 0 | 0 | 0.42431 | N-4274 | OSPD | S/D availed by UPPCL for stringing work of 765 KV Anpara D -Jhunsi line
NR140019 | 312104 | 400KV BALIA-MAU-I | 2017-12-14 16:55 | 2017-12-14 19:00 | 0 | 0 | 0 | 0.086806 | N-1479 | OSFD | E/S/D availed by UPPCL for attending hot spot at UPPCL/Mau end.
NR140019 | 312121 | 400KV BALIA-MAU-I | 2017-12-16 15:22 | 2017-12-16 19:16 | 0 | 0 | 0 | 0.1625 | N-1704 | OSFD | E/S/D availed by UPPCL for attending hot spot at Mau(UPPCL) end
NR140025 | 312206 | 400KV BAREILLY-LKO(UP) | 2017-12-25 17:23 | 2017-12-25 18:32 | 0 | 0.047917 | 0 | 0 | **** | SBBU | Tripped due to Bus Bar protection operated at Lucknow(UP) (Sarojininagar).
NR140037 | 311235 | 400KV BLBGRH-MAINPURI-I | 2017-12-01 | 2017-12-01 09:41 | 0 | 0 | 0 | 0.40347 | N-3312 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=424kV
NR140037 | 312006 | 400KV BLBGRH-MAINPURI-I | 2017-12-01 19:08 | 2017-12-02 09:23 | 0 | 0 | 0 | 0.59375 | N-121 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
NR140037 | 312013 | 400KV BLBGRH-MAINPURI-I | 2017-12-02 16:39 | 2017-12-04 09:56 | 0 | 0 | 0 | 1899-12-31 17:17 | N-185 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=432kV
NR140037 | 312026 | 400KV BLBGRH-MAINPURI-I | 2017-12-04 18:51 | 2017-12-06 06:54 | 0 | 0 | 0 | 1899-12-31 12:03 | N-369 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
NR140037 | 312039 | 400KV BLBGRH-MAINPURI-I | 2017-12-06 21:05 | 2017-12-07 12:58 | 0 | 0 | 0 | 0.66181 | N-590 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
NR140037 | 312047 | 400KV BLBGRH-MAINPURI-I | 2017-12-07 21:04 | 2017-12-08 08:22 | 0 | 0 | 0 | 0.47083 | N-712 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
NR140037 | 312050 | 400KV BLBGRH-MAINPURI-I | 2017-12-08 09:18 | 2017-12-08 10:00 | 0 | 0 | 0.029167 | 0 |  | LNCC | Tripped only from BLB end due to heavy fog at BLB end
NR140037 | 312091 | 400KV BLBGRH-MAINPURI-I | 2017-12-12 22:17 | 2017-12-13 12:16 | 0 | 0 | 0 | 0.58264 | N-1268 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 312101 | 400KV BLBGRH-MAINPURI-I | 2017-12-13 20:54 | 2017-12-14 08:53 | 0 | 0 | 0 | 0.49931 | N-1382 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140037 | 312108 | 400KV BLBGRH-MAINPURI-I | 2017-12-14 20:50 | 2017-12-15 08:59 | 0 | 0 | 0 | 0.50625 | N-1513 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 312116 | 400KV BLBGRH-MAINPURI-I | 2017-12-15 22:19 | 2017-12-16 09:44 | 0 | 0 | 0 | 0.47569 | N-1633 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 312123 | 400KV BLBGRH-MAINPURI-I | 2017-12-16 21:20 | 2017-12-17 10:14 | 0 | 0 | 0 | 0.5375 | N-1744 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
NR140037 | 312130 | 400KV BLBGRH-MAINPURI-I | 2017-12-17 20:07 | 2017-12-18 09:38 | 0 | 0 | 0 | 0.56319 | N-1828 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
NR140037 | 312137 | 400KV BLBGRH-MAINPURI-I | 2017-12-18 20:05 | 2017-12-20 07:14 | 0 | 0 | 0 | 1899-12-31 11:09 | N-1942 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
NR140037 | 312156 | 400KV BLBGRH-MAINPURI-I | 2017-12-21 00:55 | 2017-12-21 06:08 | 0 | 0 | 0 | 0.21736 | N-2195 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 312167 | 400KV BLBGRH-MAINPURI-I | 2017-12-21 23:46 | 2017-12-22 06:49 | 0 | 0 | 0 | 0.29375 | N-2316 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
NR140037 | 312180 | 400KV BLBGRH-MAINPURI-I | 2017-12-23 00:25 | 2017-12-23 07:25 | 0 | 0 | 0 | 0.29167 | N-2453 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140037 | 312190 | 400KV BLBGRH-MAINPURI-I | 2017-12-23 22:28 | 2017-12-24 07:35 | 0 | 0 | 0 | 0.37986 | N-2571 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=421kV
NR140037 | 312198 | 400KV BLBGRH-MAINPURI-I | 2017-12-25 00:05 | 2017-12-25 10:00 | 0 | 0 | 0 | 0.41319 | N-2647 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140037 | 312211 | 400KV BLBGRH-MAINPURI-I | 2017-12-26 02:45 | 2017-12-26 08:40 | 0 | 0 | 0 | 0.24653 | N-2758 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140037 | 312218 | 400KV BLBGRH-MAINPURI-I | 2017-12-26 23:04 | 2017-12-27 12:35 | 0 | 0 | 0 | 0.56319 | N-2863 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140037 | 312232 | 400KV BLBGRH-MAINPURI-I | 2017-12-28 00:53 | 2017-12-28 10:21 | 0 | 0 | 0 | 0.39444 | N-2982 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140037 | 312242 | 400KV BLBGRH-MAINPURI-I | 2017-12-28 23:24 | 2017-12-29 07:25 | 0 | 0 | 0 | 0.33403 | N-3085 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140037 | 312251 | 400KV BLBGRH-MAINPURI-I | 2017-12-29 20:59 | 2017-12-30 10:41 | 0 | 0 | 0 | 0.57083 | N-4108 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140037 | 312267 | 400KV BLBGRH-MAINPURI-I | 2017-12-30 20:48 | 2017-12-31 09:38 | 0 | 0 | 0 | 0.53472 | N-4232 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 312277 | 400KV BLBGRH-MAINPURI-I | 2017-12-31 19:27 | 2018-01-01 | 0 | 0 | 0 | 0.18958 | N-4303 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140038 | 312052 | 400KV BLBGRH-MAINPURI-II | 2017-12-08 20:34 | 2017-12-09 11:59 | 0 | 0 | 0 | 0.64236 | N-816 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
NR140038 | 312058 | 400KV BLBGRH-MAINPURI-II | 2017-12-09 13:07 | 2017-12-12 12:01 | 0 | 0 | 0 | 1900-01-01 22:54 | N-867 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140124 | 312088 | 400KV FATEHPUR-MAINPURI-I | 2017-12-12 12:05 | 2017-12-13 12:15 | 0 | 0 | 0 | 1899-12-31 00:10 | N-1207 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140124 | 312124 | 400KV FATEHPUR-MAINPURI-I | 2017-12-16 21:20 | 2017-12-17 09:44 | 0 | 0 | 0 | 0.51667 | N-1744 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
NR140124 | 312252 | 400KV FATEHPUR-MAINPURI-I | 2017-12-29 21:00 | 2017-12-30 10:38 | 0 | 0 | 0 | 0.56806 | N-4108 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140124 | 312268 | 400KV FATEHPUR-MAINPURI-I | 2017-12-30 20:49 | 2017-12-31 09:00 | 0 | 0 | 0 | 0.50764 | N-4232 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140124 | 312278 | 400KV FATEHPUR-MAINPURI-I | 2017-12-31 19:28 | 2018-01-01 | 0 | 0 | 0 | 0.18889 | N-4303 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140125 | 311234 | 400KV FATEHPUR-MAINPURI-II | 2017-12-01 | 2017-12-01 09:37 | 0 | 0 | 0 | 0.40069 | N-3312 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=424kV
NR140125 | 312005 | 400KV FATEHPUR-MAINPURI-II | 2017-12-01 19:05 | 2017-12-02 09:22 | 0 | 0 | 0 | 0.59514 | N-121 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
NR140125 | 312012 | 400KV FATEHPUR-MAINPURI-II | 2017-12-02 16:36 | 2017-12-03 10:52 | 0 | 0 | 0 | 0.76111 | N-185 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=432kV
NR140125 | 312021 | 400KV FATEHPUR-MAINPURI-II | 2017-12-03 19:49 | 2017-12-04 09:56 | 0 | 0 | 0 | 0.58819 | N-278 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=429kV
NR140125 | 312026 | 400KV FATEHPUR-MAINPURI-II | 2017-12-04 18:49 | 2017-12-06 07:00 | 0 | 0 | 0 | 1899-12-31 12:11 | N-369 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
NR140125 | 312036 | 400KV FATEHPUR-MAINPURI-II | 2017-12-06 15:10 | 2017-12-07 08:05 | 0 | 0 | 0 | 0.70486 | N-552 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
NR140125 | 312048 | 400KV FATEHPUR-MAINPURI-II | 2017-12-07 21:05 | 2017-12-08 07:33 | 0 | 0 | 0 | 0.43611 | N-712 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
NR140125 | 312053 | 400KV FATEHPUR-MAINPURI-II | 2017-12-08 20:35 | 2017-12-09 11:59 | 0 | 0 | 0 | 0.64167 | N-816 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=434kV
NR140125 | 312057 | 400KV FATEHPUR-MAINPURI-II | 2017-12-09 13:06 | 2017-12-12 07:02 | 0 | 0 | 0 | 1900-01-01 17:56 | N-867 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140125 | 312102 | 400KV FATEHPUR-MAINPURI-II | 2017-12-13 20:55 | 2017-12-14 08:50 | 0 | 0 | 0 | 0.49653 | N-1382 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140125 | 312109 | 400KV FATEHPUR-MAINPURI-II | 2017-12-14 20:54 | 2017-12-15 09:07 | 0 | 0 | 0 | 0.50903 | N-1513 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140125 | 312115 | 400KV FATEHPUR-MAINPURI-II | 2017-12-15 22:17 | 2017-12-16 09:43 | 0 | 0 | 0 | 0.47639 | N-1633 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140125 | 312129 | 400KV FATEHPUR-MAINPURI-II | 2017-12-17 20:07 | 2017-12-18 09:19 | 0 | 0 | 0 | 0.55 | N-1828 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
NR140125 | 312138 | 400KV FATEHPUR-MAINPURI-II | 2017-12-18 20:05 | 2017-12-20 09:08 | 0 | 0 | 0 | 1899-12-31 13:03 | N-1942 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
NR140125 | 312155 | 400KV FATEHPUR-MAINPURI-II | 2017-12-21 00:55 | 2017-12-21 06:07 | 0 | 0 | 0 | 0.21667 | N-2195 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140125 | 312166 | 400KV FATEHPUR-MAINPURI-II | 2017-12-21 23:46 | 2017-12-22 06:48 | 0 | 0 | 0 | 0.29306 | N-2316 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=423kV
NR140125 | 312179 | 400KV FATEHPUR-MAINPURI-II | 2017-12-23 00:24 | 2017-12-23 07:29 | 0 | 0 | 0 | 0.29514 | N-2453 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140125 | 312189 | 400KV FATEHPUR-MAINPURI-II | 2017-12-23 22:28 | 2017-12-24 07:10 | 0 | 0 | 0 | 0.3625 | N-2571 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=421kV
NR140125 | 312197 | 400KV FATEHPUR-MAINPURI-II | 2017-12-25 00:05 | 2017-12-25 09:48 | 0 | 0 | 0 | 0.40486 | N-2647 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140125 | 312212 | 400KV FATEHPUR-MAINPURI-II | 2017-12-26 02:47 | 2017-12-26 08:38 | 0 | 0 | 0 | 0.24375 | N-2759 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140125 | 312219 | 400KV FATEHPUR-MAINPURI-II | 2017-12-26 23:01 | 2017-12-27 06:29 | 0 | 0 | 0 | 0.31111 | N-2863 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140125 | 312231 | 400KV FATEHPUR-MAINPURI-II | 2017-12-28 00:52 | 2017-12-28 09:13 | 0 | 0 | 0 | 0.34792 | N-2982 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140125 | 312241 | 400KV FATEHPUR-MAINPURI-II | 2017-12-28 23:24 | 2017-12-29 07:32 | 0 | 0 | 0 | 0.33889 | N-3085 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140052 | 312135 | 400KV KNP-AGRA | 2017-12-18 11:03 | 2017-12-18 11:40 | 0.025694 | 0 | 0 | 0 | **** | OSFT | H/T on emergency basis to attend heavy hot spot in line isolator at Agra end
NR140055 | 312003 | 400KV KNP-BLBGARH-I | 2017-12-01 12:01 | 2017-12-01 17:19 | 0.22083 | 0 | 0 | 0 | N-63 | OSFT | E/S/D availed for attending hot spot in Y ph line isolator at Kanpur
NR140055 | 312008 | 400KV KNP-BLBGARH-I | 2017-12-02 01:02 | 2017-12-02 07:23 | 0 | 0 | 0 | 0.26458 | N-136 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=420kV
NR140055 | 312011 | 400KV KNP-BLBGARH-I | 2017-12-02 12:08 | 2017-12-02 12:38 | 0.020833 | 0 | 0 | 0 | **** | OSFT | Hand tripped on emergency after heavy sparking observed in Y-phase Line isolator at Kanpur.
NR140055 | 312019 | 400KV KNP-BLBGARH-I | 2017-12-03 19:13 | 2017-12-03 19:13 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to Y-N fault, F.D.=21.89km from KNP,F.C.=13.13KA, F.D.=370.5km from BLB,F.C.=1.239KA (Kanpur jurisdiction)
NR140055 | 312041 | 400KV KNP-BLBGARH-I | 2017-12-07 04:05 | 2017-12-07 06:49 | 0 | 0 | 0 | 0.11389 | N-594 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=437kV
NR140055 | 312069 | 400KV KNP-BLBGARH-I | 2017-12-10 22:06 | 2017-12-10 22:06 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to Y-N fault,F.D.=88.47 KM from Kanpur,F.C.=4.29KA, F.D.=253.5km from BLB,F.C.=1.826KA .
NR140055 | 312076 | 400KV KNP-BLBGARH-I | 2017-12-12 00:44 | 2017-12-12 12:00 | 0 | 0 | 0 | 0.46944 | N-1103 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP =425kV
NR140055 | 312126 | 400KV KNP-BLBGARH-I | 2017-12-16 23:52 | 2017-12-17 09:48 | 0 | 0 | 0 | 0.41389 | N-1749 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=420kV
NR140055 | 312149 | 400KV KNP-BLBGARH-I | 2017-12-20 01:26 | 2017-12-20 07:20 | 0 | 0 | 0 | 0.24583 | N-2071 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-420KV
NR140055 | 312157 | 400KV KNP-BLBGARH-I | 2017-12-21 00:56 | 2017-12-21 06:13 | 0 | 0 | 0 | 0.22014 | N-2195 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-420KV
NR140055 | 312243 | 400KV KNP-BLBGARH-I | 2017-12-28 23:24 | 2017-12-29 06:57 | 0 | 0 | 0 | 0.31458 | N-3085 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=424kV
NR140055 | 312248 | 400KV KNP-BLBGARH-I | 2017-12-29 14:51 | 2017-12-29 14:51 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on R-N fault,F.D.=219.1km from Kanpur, F.C.=1.7KA, and F.D.=143km from Ballabhgarh, F.C.=2.6KA (Mainpuri TL Jurisdiction)
NR140055 | 312276 | 400KV KNP-BLBGARH-I | 2017-12-31 19:24 | 2018-01-01 | 0 | 0 | 0 | 0.19167 | N-4303 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=426kV
NR140056 | 312031 | 400KV KNP-BLBGARH-II | 2017-12-05 22:08 | 2017-12-06 07:00 | 0 | 0 | 0 | 0.36944 | N-492 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=421kV
NR140056 | 312100 | 400KV KNP-BLBGARH-II | 2017-12-13 20:53 | 2017-12-14 08:52 | 0 | 0 | 0 | 0.49931 | N-1382 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=423kV
NR140056 | 312110 | 400KV KNP-BLBGARH-II | 2017-12-14 20:58 | 2017-12-15 09:03 | 0 | 0 | 0 | 0.50347 | N-1513 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=420kV
NR140056 | 312178 | 400KV KNP-BLBGARH-II | 2017-12-23 00:20 | 2017-12-23 07:18 | 0 | 0 | 0 | 0.29028 | N-2453 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140056 | 312233 | 400KV KNP-BLBGARH-II | 2017-12-28 00:56 | 2017-12-28 09:16 | 0 | 0 | 0 | 0.34722 | N-2982 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=420kV
NR140057 | 312090 | 400KV KNP-BLBGARH-III | 2017-12-12 21:41 | 2017-12-13 18:48 | 0 | 0 | 0 | 0.87986 | N-1266 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=422kV
NR140057 | 312131 | 400KV KNP-BLBGARH-III | 2017-12-17 20:12 | 2017-12-18 09:38 | 0 | 0 | 0 | 0.55972 | N-1828 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
NR140057 | 312168 | 400KV KNP-BLBGARH-III | 2017-12-21 23:48 | 2017-12-22 07:46 | 0 | 0 | 0 | 0.33194 | N-2316 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-421KV
NR140057 | 312253 | 400KV KNP-BLBGARH-III | 2017-12-29 21:02 | 2017-12-30 10:32 | 0 | 0 | 0 | 0.5625 | N-4108 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=419kV
NR140057 | 312265 | 400KV KNP-BLBGARH-III | 2017-12-30 20:44 | 2017-12-31 09:02 | 0 | 0 | 0 | 0.5125 | N-4232 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP=416kV
NR140057 | 312274 | 400KV KNP-BLBGARH-III | 2017-12-31 12:21 | 2017-12-31 15:58 | 0.15069 | 0 | 0 | 0 | N-4281 | OSPT | Emergency S/D availed for rectification of melted jumper at location no 561.
NR140110 | 312009 | 400KV KNP-FATEHPUR-I | 2017-12-02 07:04 | 2017-12-06 15:24 | 0 | 0 | 0 | 1900-01-03 08:20 | N-147 | LCSD | S/D taken for diversion of line between loc no 1115 to 1119 due to DFCC on continious basis.
NR140110 | 312087 | 400KV KNP-FATEHPUR-I | 2017-12-12 07:39 | 2017-12-16 18:21 | 0 | 0 | 0 | 1900-01-03 10:42 | N-1143 | LCSD | S/D taken for Diversion of line due to DFCC work.
NR140058 | 312096 | 400KV KNP-PANKI-I | 2017-12-13 15:01 | 2017-12-13 19:46 | 0.19792 | 0 | 0 | 0 | N-1337 | OSFT | S/D taken to attend hot spot in line isolator at Kanpur
NR140058 | 312163 | 400KV KNP-PANKI-I | 2017-12-21 11:28 | 2017-12-21 16:34 | 0.2125 | 0 | 0 | 0 | N-2249 | OSFT | S/D taken for attending problem of sparking & abnormal sound in R-phase wave trap at Kanpur.
NR340010 | 312134 | 400KV LKO(765)-KANPUR(GIS)-I | 2017-12-18 02:55 | 2017-12-18 10:08 | 0 | 0 | 0 | 0.30069 | N-1842 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=427kV
NR140072 | 312143 | 400KV LUCKNOW-LKO(UP) | 2017-12-19 04:06 | 2017-12-19 05:08 | 0 | 0 | 0.043056 | 0 | **** | GOVC | Tripped due to Over Voltage at Lucknow(PG) end. D/T received at Lucknow(UP) end.
NR140072 | 312205 | 400KV LUCKNOW-LKO(UP) | 2017-12-25 17:23 | 2017-12-25 18:26 | 0 | 0.04375 | 0 | 0 | **** | SBBU | Tripped due to Bus Bar protection operated at Lucknow(UP) (Sarojininagar).
NR140072 | 312213 | 400KV LUCKNOW-LKO(UP) | 2017-12-26 02:00 | 2017-12-26 08:52 | 0 | 0.28611 | 0 | 0 | **** | OMSU | Tripped due to R-N fault due to heavy fog. FD: 42.44kM from Lucknow, FC: 8.25kA at Lucknow. Fault in UPPCL jurisdiction.
NR140072 | 312215 | 400KV LUCKNOW-LKO(UP) | 2017-12-26 08:52 | 2017-12-26 17:28 | 0 | 0 | 0 | 0.35833 | N-2775 | OSPD | S/D availed by UPPCL for restoration work of damaged insulator string at location no. 351.
NR140142 | 312145 | 400KV MEERUT-BAREILLY-I | 2017-12-19 08:32 | 2017-12-19 16:55 | 0 | 0 | 0 | 0.34931 | N-1971 | OSPD | S/D availed by Powerlink for insulator cleaning & other maintenanance work
NR140130 | 312151 | 400KV MEERUT-BAREILLY-II | 2017-12-20 08:07 | 2017-12-20 17:54 | 0.40764 | 0 | 0 | 0 | N-2085 | OSPT | S/D taken by Powerlink for insulator cleaning work for pre winter preparation.
NR140091 | 312236 | 400KV SING-ALLD-I | 2017-12-28 09:13 | 2017-12-28 19:34 | 0.43125 | 0 | 0 | 0 | N-3004 | OSPT | S/D availed for Insulator cleaning work for winter season preparation.
NR140092 | 312204 | 400KV SING-ALLD-II | 2017-12-25 09:02 | 2017-12-25 19:19 | 0.42847 | 0 | 0 | 0 | N-2698 | OSPT | Taken under S/D for insulator cleaning work for winter season preparation.
NR140092 | 312214 | 400KV SING-ALLD-II | 2017-12-26 08:47 | 2017-12-26 19:31 | 0.44722 | 0 | 0 | 0 | N-2779 | OSPT | S/D availed for insulator cleaning work for winter season preparation.
NR140111 | 312183 | 400KV SING-FATEHPUR | 2017-12-23 09:06 | 2017-12-23 22:01 | 0.53819 | 0 | 0 | 0 | N-2479 | OSPT | Taken under S/D for insulator cleaning work for winter season preparation.
NR140111 | 312194 | 400KV SING-FATEHPUR | 2017-12-24 09:14 | 2017-12-24 19:39 | 0.43403 | 0 | 0 | 0 | N-2600 | OSPT | Taken under S/D for insulator cleaning work for winter season preparation.
NR140111 | 312270 | 400KV SING-FATEHPUR | 2017-12-31 02:28 | 2017-12-31 17:03 | 0 | 0 | 0.60764 | 0 | **** | LNCC | Tripped due to heavy fog on R-Y fault. FD: FTP-302.8km, FC: FTP- R Ph-1.73KA, Y Ph-2.12KA.
NR140095 | 312042 | 400KV SING-LKO(UP)-I | 2017-12-07 09:08 | 2017-12-09 22:35 | 0 | 0 | 0 | 1900-01-01 13:27 | N-607 | LCSD | S/D taken for transferring of line from ERS to normal tower
NR140095 | 312207 | 400KV SING-LKO(UP)-I | 2017-12-25 17:23 | 2017-12-25 18:30 | 0 | 0.046528 | 0 | 0 | **** | SBBU | Tripped due to Bus Bar protection operated at Lucknow(UP) (Sarojininagar).
NR340004 | 312127 | 400KV VARANASI-SARNATH-I | 2017-12-17 08:08 | 2017-12-17 17:37 | 0 | 0 | 0 | 0.39514 | N-1766 | OSPD | S/D taken by UPPCL for general maintenance work at UPPCL end
NR340004 | 312224 | 400KV VARANASI-SARNATH-I | 2017-12-27 01:38 | 2017-12-27 02:35 | 0 | 0.039583 | 0 | 0 | **** | OMSU | Tripped only from UPPCL Sarnath end due to problem at their end
NR340005 | 312118 | 400KV VARANASI-SARNATH-II | 2017-12-16 08:34 | 2017-12-16 18:05 | 0 | 0 | 0 | 0.39653 | N-1651 | OSPD | S/D availed for general maintenanace work by UPPCL
NR340005 | 312225 | 400KV VARANASI-SARNATH-II | 2017-12-27 01:38 | 2017-12-27 02:35 | 0 | 0.039583 | 0 | 0 | **** | OMSU | Tripped only from UPPCL Sarnath end due to problem at their end
BILUP2209 | 312257 | 220KV ALLD-JHUSI(UP) | 2017-12-29 23:09 | 2017-12-30 01:34 | 0 | 0.10069 | 0 | 0 | N-4127 | OMSU | Line tripped Due to E/F at Jhusi (UPPTCL ) switchyard because of heavy fog.
BILUP2203 | 312264 | 220KV ALLD-REWA RD-II | 2017-12-30 15:16 | 2017-12-30 17:24 | 0 | 0 | 0 | 0.088889 | N-4197 | OSFD | Emergency S/D availed by UPPCL to attend hot spot at their end
NR122012 | 312079 | 220KV DGANGA-BLY(UP)-II | 2017-12-12 01:54 | 2017-12-12 02:08 | 0 | 0 | 0.0097222 | 0 | **** | GOVC | Tripped due to D/T received at Bareily(UP) end due to O/V at Dhauliganga. D'Ganga=239KV
NR122012 | 312083 | 220KV DGANGA-BLY(UP)-II | 2017-12-12 02:08 | 2017-12-12 06:22 | 0 | 0 | 0 | 0.17639 | N-1115 | LVRD | Kept open for Voltage regulation as per NRLDC instruction. P'garh=239kV
NR122012 | 312119 | 220KV DGANGA-BLY(UP)-II | 2017-12-16 09:19 | 2017-12-16 18:19 | 0.375 | 0 | 0 | 0 | N-1657 | OSPT | S/D availed for AMP work by PGCIL
NR122012 | 312185 | 220KV DGANGA-BLY(UP)-II | 2017-12-23 11:20 | 2017-12-23 15:32 | 0 | 0 | 0 | 0.175 | N-2499 | OSPD | Taken under S/D by NHPC for testing work at their end
NR122012 | 312196 | 220KV DGANGA-BLY(UP)-II | 2017-12-24 23:11 | 2017-12-25 04:24 | 0 | 0 | 0.21736 | 0 | **** | GOVC | Tripped due to O/V protection operated
NR122013 | 312080 | 220KV DGANGA-PITHORAGRH | 2017-12-12 01:54 | 2017-12-12 02:08 | 0 | 0 | 0.0097222 | 0 | **** | GOVC | Tripped due to D/T received at Pithoragarh end due to O/V at Dhauliganga. D'Ganga=239KV
NR122013 | 312084 | 220KV DGANGA-PITHORAGRH | 2017-12-12 02:08 | 2017-12-12 07:14 | 0 | 0 | 0 | 0.2125 | N-1115 | LVRD | Kept open for Voltage regulation as per NRLDC instruction. Bareily(UP)=239kV
NR122013 | 312201 | 220KV DGANGA-PITHORAGRH | 2017-12-25 03:03 | 2017-12-25 08:47 | 0 | 0 | 0.23889 | 0 | **** | GOVC | Tripped due to O/V protection operated
NR122016 | 312120 | 220KV KNP-MAINPURI | 2017-12-16 12:58 | 2017-12-26 22:11 | 0 | 0 | 0 | 1900-01-09 09:13 | N-1688 | OSPD | S/D availed by UPPCL for line Diversion due to upcoming NTPC project at Billhaur
NR122020 | 312034 | 220KV KNP-UNCHR-I | 2017-12-06 08:37 | 2017-12-09 16:25 | 0 | 0 | 0 | 1900-01-02 07:48 | N-514 | LCSD | S/D taken for diversion of line due to DFCC
NR122020 | 312060 | 220KV KNP-UNCHR-I | 2017-12-09 16:25 | 2017-12-10 17:06 | 0 | 0 | 1899-12-31 00:41 | 0 | **** | LMAC | Middle phase conductor theft at LOC. No. 401 to 403 and cross arm bent at Loc. No. 401 & 402
NR122021 | 312035 | 220KV KNP-UNCHR-II | 2017-12-06 08:37 | 2017-12-09 16:48 | 0 | 0 | 0 | 1900-01-02 08:11 | N-514 | LCSD | S/D taken for diversion of line due to DFCC
NR122021 | 312065 | 220KV KNP-UNCHR-II | 2017-12-10 10:22 | 2017-12-10 17:05 | 0 | 0 | 0 | 0.27986 | N-954 | LCSD | S/D taken for facilitating restoration of 220KV KNP-Unchahar-1. Line-1 was out due to conductor theft between loc no 401 to 403 during s/d for diversion of line due to DFCC on continious basis
NR122022 | 312094 | 220KV KNP-UNCHR-III | 2017-12-13 08:07 | 2017-12-17 20:46 | 0 | 0 | 0 | 1900-01-03 12:39 | N-1294 | LCSD | S/D taken for Diversion of line due to DFCC work.
NR122022 | 312237 | 220KV KNP-UNCHR-III | 2017-12-28 09:26 | 2017-12-28 19:36 | 0 | 0 | 0 | 0.42361 | N-3000 | OSPD | S/D availed by UPPCL for powerline crossing work
NR122023 | 312095 | 220KV KNP-UNCHR-IV | 2017-12-13 08:07 | 2017-12-16 18:16 | 0 | 0 | 0 | 1900-01-02 10:09 | N-1294 | LCSD | S/D taken for Diversion of line due to DFCC work.
NR122023 | 312238 | 220KV KNP-UNCHR-IV | 2017-12-28 09:26 | 2017-12-28 19:40 | 0 | 0 | 0 | 0.42639 | N-3000 | OSPD | S/D availed by UPPCL for powerline crossing work
NR122024 | 312195 | 220KV PITHORAGRH-BRLY(UP) | 2017-12-24 22:58 | 2017-12-25 00:15 | 0 | 0 | 0.053472 | 0 | **** | GOVC | Tripped due to O/V protection operated
NR122025 | 312228 | 220KV RAIBRLY-CHINHAT | 2017-12-27 09:51 | 2017-12-27 16:48 | 0 | 0 | 0 | 0.28958 | N-2898 | OSFD | E/S/D availed by UPPCL for attending oil leakage from B phase C.T. stud at UPPCL Chinhat end
NR122033 | 312261 | 220KV TNKPR-BLY(UP) | 2017-12-29 11:43 | 2017-12-29 15:28 | 0.15625 | 0 | 0 | 0 | N-4037 | OSFT | E/S/D taken by POWERGRID to attend Hotspot in B-Ph line side CT connector at BLY(UP)
NR1ICT65 | 312049 | 500MVA ICT-I SHAHJHNPR | 2017-12-08 10:02 | 2017-12-08 15:29 | 0.22708 | 0 | 0 | 0 | N-750 | OSPT | S/D availed for AMP work.
NR1ICT43 | 312081 | 100MVA ICT-I PITHORAGRH | 2017-12-12 03:04 | 2017-12-12 03:10 | 0 | 0 | 0.0041667 | 0 | **** | GOFC | Tripped due to operation of over flux, P'garh=239KV
NR1ICT43 | 312085 | 100MVA ICT-I PITHORAGRH | 2017-12-12 03:10 | 2017-12-12 07:31 | 0 | 0 | 0 | 0.18125 | N-1119 | SPRD | Kept open for Voltage regulation as per NRLDC instruction. P'garh=239kV
NR1ICT44 | 312082 | 100MVA ICT-II PITHORAGRH | 2017-12-12 02:57 | 2017-12-12 03:10 | 0 | 0 | 0.0090278 | 0 | **** | GOFC | Tripped due to operation of over flux, P'garh=239KV
NR1ICT44 | 312086 | 100MVA ICT-II PITHORAGRH | 2017-12-12 03:10 | 2017-12-12 07:52 | 0 | 0 | 0 | 0.19583 | N-1119 | SPRD | Kept open for Voltage regulation as per NRLDC instruction. P'garh=239kV
NR1ICT39 | 312016 | 200MVA ICT-III RAIBAREILLY | 2017-12-03 01:36 | 2017-12-03 18:13 | 0.69236 | 0 | 0 | 0 | **** | SRET | Tripped due to REF protection operated
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="T",(+[RESTORATION]-[OUTAGE]),0))
OTHERS = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="U",(+[RESTORATION]-[OUTAGE]),0))
Hrs:Min = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="C",(+[RESTORATION]-[OUTAGE]),0))
Deemed Available = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="D",(+[RESTORATION]-[OUTAGE]),0))
Note on C167: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16

## Sheet3
400kv LINES |  |  |  | 220kv LINES |  | ICTs,HVDC & SVC. |  | OTHER LINES
400kv LINES NR-I |  | 400kv LINES NR-III |  | 220kv LINES & ICT & Reactor NR-I |  | 220kv LINES & ICT & Reactor NR-III
400KV AGRA-JAIPUR(S)-I | 1 | 400KV AGRA-FATEHABD(UP)-I | 1 | 220KV ANTA-BHIL-I | 1 | 220KV ALLD-JHUSI(UP) | RRVPNL | 220KV BASSI-KUKAS-I
400KV AGRA-JAIPUR(S)-II | 2 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2 | 220KV ANTA-BHIL-II | 2 | 220KV ALLD-REWA RD-I | RRVPNL | 220KV BASSI-KUNDA KI DHANI
400KV AGRA-SIKAR-I | 3 | 400KV AGRA-AGRA(UP)-II | 3 | 220KV ANTA-LALSOT | 3 | 220KV ALLD-REWA RD-II | RRVPNL | 220KV BHIWADI(PG)-BHIWADI
400KV AGRA-SIKAR-II | 4 | 400KV AGRA-AURAIYA-I | 4 | 220KV ANTA-RAPPC | 4 | 220KV AUR-SIKANDARA-I | RRVPNL | 220KV BHIWADI-KHUSHKHERA-I
400KV BASSI-BHIWADI-I | 5 | 400KV AGRA-AURAIYA-II | 5 | 220KV ANTA-S.MDHPR | 5 | 220KV AUR-SIKANDARA-II | RRVPNL | 220KV BHIWADI-KHUSHKHERA-II
400KV BASSI-HIRAPURA-I | 6 | 400KV AGRA-BASSI-I | 6 | 220KV BASSI-BAGRU | 6 | 220KV DGANGA-BLY(UP)-II | RRVPNL | 220KV BHIWADI-NIMRANA(RJ)
400KV BASSI-HIRAPURA-II | 7 | 400KV AGRA-BHIWADI-I | 7 | 220KV BASSI-DAUSA-I | 7 | 220KV DGANGA-PITHORAGRH | RRVPNL | 220KV BHINMAL-BHINMAL-I
400KV BASSI-JAIPUR(S)-I | 8 | 400KV AGRA-BHIWADI-II | 8 | 220KV BASSI-DAUSA-II | 8 | 220KV FATEHPUR-FTHPR(UP)-I | RRVPNL | 220KV BHINMAL-BHINMAL-II
400KV BASSI-JAIPUR(S)-II | 9 | 400KV AGRA-BLBGRH | 9 | 220KV BASSI-IG NAGAR | 9 | 220KV FATEHPUR-FTHPR(UP)-II | RRVPNL | 220KV BHINMAL-SANCHORE
400KV BASSI-KOTPUTLI | 10 | 400KV ALLD-FATEHPUR-I | 10 | 220KV FGPP-PALLA-I | 10 | 220KV FATEHPUR-KNP SOUTH | RRVPNL | 220KV BHINMAL-SIROHI
400KV BASSI-PHAGI-I | 11 | 400KV ALLD-FATEHPUR-II | 11 | 220KV FGPP-PALLA-II | 11 | 220KV FATEHPUR-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-CHAKSU-I |  | LEGENDS
400KV BASSI-PHAGI-II | 12 | 400KV ALLD-FATEHPUR-III | 12 | 220KV FGPP-SPUR-I | 12 | 220KV JHUSI(UP)-PHULPUR(UP) | RRVPNL | 220KV JAIPUR(S)-CHAKSU-II
400KV BHINMAL-ZERDA | 13 | 400KV ALLD-KNP-II | 13 | 220KV FGPP-SPUR-II | 13 | 220KV KNP-MAINPURI | RRVPNL | 220KV JAIPUR(S)-SEZ |  |  | Lines maintained by ER
400KV BHIWADI-GURGAON | 14 | 400KV ALLD-VARANASI | 14 | 220KV HIRAPURA-IG NAGAR | 14 | 220KV KNP-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-DOONI
400KV BHIWADI-HISAR-I | 15 | 400KV BALIA-MAU-I | 15 | 220KV HIRAPURA-SANGANER | 15 | 220 KV KANPUR(PG) - RANIYA( UP)-1 | RRVPNL | 220KV KANKROLI(PG)-BHILWARA
400KV BHIWADI-KOTPUTLI | 16 | 400KV BALIA-MAU-II | 16 | 220KV LALSOT-DAUSA | 16 | 220 KV RANIYA( UP) - PANKI (UP)-1 | RRVPNL | 220KV KANKROLI(PG)-KANK-I
400KV BHIWADI-NIMRANA-I | 17 | 400KV BALIA-SOHAWAL-I | 17 | 220KV MEERUT-MPURAM-I | 17 | 220KV KNP-PANKI-II | RRVPNL | 220KV KANKROLI(PG)-KANK-II
400KV BHIWADI-NIMRANA-II | 18 | 400KV BALIA-SOHAWAL-II | 18 | 220KV MEERUT-MPURAM-II | 18 | 220KV KNP-UNCHR-I | RRVPNL | 220KV KANKROLI-DEBARI |  |  | lines maintained by WR
400KV BLBGRH-GURGAON | 19 | 400KV BAREILLY-BRLY(765)-I | 19 | 220KV MEERUT-NARA | 19 | 220KV KNP-UNCHR-II | RRVPNL | 220KV KOTA-KTPS-1
400KV BLBGRH-MAHRANIBG | 20 | 400KV BAREILLY-BRLY(765)-II | 20 | 220KV MEERUT-SHTBDNGR | 20 | 220KV KNP-UNCHR-III | RRVPNL | 220KV KOTA-KTPS-2 |  |  | LILO portions only of POWERGRID
400KV BLBGRH-NAVADA(HVPN) | 21 | 400KV BAREILLY-BRLY(UP)-I | 21 | 220KV MEERUT-SIMBHOLI | 21 | 220KV KNP-UNCHR-IV | RRVPNL | 220KV KOTA-BHILWARA
400KV DAD-GR.NOIDA | 22 | 400KV BAREILLY-BRLY(UP)-II | 22 | 220KV RAPPB-CHITT-I | 22 | 220KV PITHORAGRH-BRLY(UP) | RRVPNL | 220KV KOTA-DHUNI |  |  | LILO portion maintained by constituents
400KV DAD-MAHRANIBG | 23 | 400KV BAREILLY-LKO(UP) | 23 | 220KV RAPPB-CHITT-II | 23 | 220KV RAIBRLY-CHINHAT | RRVPNL | 220KV KOTPUTLI-KOTPUTLI
400KV DAD-MANDOLA-I | 24 | 400KV BAREILLY-MBAD-I | 24 | 220KV RAPPB-RAPPC | 24 | 220KV RAIBRLY-LKO(UP) | RRVPNL | 220KV KOTPUTLI-MANOHARPUR
400KV DAD-MANDOLA-II | 25 | 400KV BAREILLY-MBAD-II | 25 | 220KV RAPPB-UDAIPUR | 25 | 220KV SITARGANJ-BLY(UP) | RRVPNL | 220KV NIMRANA-NIMRANA
400KV DAD-MURADNGR | 26 | 400KV BAREILLY-ROSA-I | 26 | 220KV S.MDHPR-DAUSA-I | 26 | 220KV TNKPR-BLY(UP) | RRVPNL | 220KV NIMRANA-KHUSHKHERA |  |  | Maintained by NR-1 & NR-II
400KV DAD-PANIPAT-I | 27 | 400KV BAREILLY-SHAHJHNPR-I | 27 | 220KV SIKAR-RATANGARH-I | 27 | 220KV TNKPR-SITARGANJ | HVPNL | 220KV BHIWADI-MAU
400KV DAD-PANIPAT-II | 28 | 400KV BAREILLY-SHAHJHNPR-II | 28 | 220KV SIKAR-RATANGARH-II | 28 | 220KV UNCHR-RAIBRLY-I | HVPNL | 220KV BHIWADI-REWARI-I
400KV GURGAON-MANESAR-I | 29 | 400KV BARLY(765)-KASHIPUR-I | 29 | 220KV SIKAR-SIKAR(RJ)-I | 29 | 220KV UNCHR-RAIBRLY-II | HVPNL | 220KV BHIWADI-REWARI-II
400KV GURGAON-MANESAR-II | 30 | 400KV BARLY(765)-KASHIPUR-II | 30 | 220KV SIKAR-SIKAR(RJ)-II | 30 | 220KV UNCHR-RAIBRLY-III | HVPNL | 220KV BHIWADI-BAWAL
400KV JHATIKALA-BAMNOLI-I | 31 | 400KV BLBGRH-MAINPURI-I | 31 | 220KV HISAR-HISAR I/A-I |  |  | HVPNL | 220KV GURGAON-GURGAON-I
400KV JHATIKALA-BAMNOLI-II | 32 | 400KV BLBGRH-MAINPURI-II | 32 | 220KV HISAR-HISAR I/A-II |  |  | HVPNL | 220KV GURGAON-GURGAON-II
400KV JHATIKALA-MUNDKA-I | 33 | 400KV FATEHPUR-MAINPURI-I |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-III
400KV JHATIKALA-MUNDKA-II | 34 | 400KV FATEHPUR-MAINPURI-II |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-IV
400KV KANKROLI-BHINMAL | 35 | 400KV GORAKH-GORAKH-I |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-I
400KV KANKROLI-JODHPUR | 36 | 400KV GORAKH-GORAKH-II |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-II
400KV KANKROLI-CHITTOR(RJ)-I | 37 | 400KV KNP-AGRA |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-I
400KV KANKROLI-RAPPC-II | 38 | 400KV KNP-AURAIYA-I |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-II
400KV KANKROLI-ZERDA-I | 39 | 400KV KNP-AURAIYA-II |  | 400KV & 220KV ICT NR-I |  |  | HVPNL | 220 KV MANESAR-BADSHAHPUR-I
400KV KOTA-BEAWAR | 40 | 400KV KNP-BLBGARH-I | 1 | 315MVA ICT-I BASSI |  | 400KV & 220KV ICT NR-III | HVPNL | 220 KV MANESAR-BADSHAHPUR-II
400KV KOTA-MERTA-I | 41 | 400KV KNP-BLBGARH-II | 2 | 315MVA ICT-II BASSI | 1 | 315MVA ICT-I AGRA | HVPNL | 220 KV MANESAR-MAU-I
400KV KOTA-RAPPC | 42 | 400KV KNP-BLBGARH-III | 3 | 500MVA ICT-III BASSI | 2 | 315MVA ICT-I ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-II
400KV KOTESHWR-KHEP-I | 43 | 400KV KNP-FATEHPUR-I | 4 | 315MVA ICT-III BAWANA | 3 | 315MVA ICT-II ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-III
400KV KOTESHWR-KHEP-II | 44 | 400KV KNP-FATEHPUR-II | 5 | 315MVA ICT-I BHINMAL | 4 | 315MVA ICT-III ALLAHABAD | HVPNL | 220 KV SONIPAT-MOHANA-I
400KV KOTESHWR-TEHRI-I | 45 | 400KV KNP-PANKI-I | 6 | 315MVA ICT-II BHINMAL | 5 | 315MVA ICT-I FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-I
400KV KOTESHWR-TEHRI-II | 46 | 400KV KNP-PANKI-II | 7 | 315MVA ICT-I BHIWADI | 6 | 315MVA ICT-II FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-II
400KV MBAD-MURADNGR | 47 | 400KV LUCKNOW-GORAKH-III | 8 | 315MVA ICT-II BHIWADI | 7 | 315MVA ICT-I GORAKHPR | HVPNL | 220KV HISAR-SRWL-I
400KV MEERUT-BAGPAT-I | 48 | 400KV LUCKNOW-GORAKH-IV | 9 | 315MVA ICT-III BHIWADI | 8 | 315MVA ICT-II GORAKHPR | HVPNL | 220KV HISAR-SRWL-II
400KV MEERUT-BAREILLY-I | 49 | 400KV LUCKNOW-LKO(765)-I | 10 | 500MVA ICT-I BLBGARH | 9 | 315MVA ICT-I KANPUR | HVPNL | 220KV HISAR-FATEHABAD-I
400KV MEERUT-BAREILLY-II | 50 | 400KV LUCKNOW-LKO(765)-II | 11 | 315MVA ICT-II BLBGARH | 10 | 315MVA ICT-II KANPUR | HVPNL | 220KV HISAR-FATEHABAD-II
400KV MEERUT-KOTESHWR-I | 51 | 400KV LUCKNOW-LKO(UP) | 12 | 315MVA ICT-III BLBGARH | 11 | 315MVA ICT-I LUCKNOW | NTPC | 132KV SING-VINDH-RIH
400KV MEERUT-KOTESHWR-II | 52 | 400KV LUCKNOW-ROSA-I | 13 | 315MVA ICT-IV BLBGARH | 12 | 500MVA ICT-II LUCKNOW | NTPC | 132KV SING-RENUSAGAR-PIPRI
400KV MEERUT-MND-I | 53 | 400KV LUCKNOW-SHAHJHNPR-I | 14 | 315MVA ICT-I GURGAON | 13 | 315MVA ICT-I MAINPURI | DTL | 400KV B'GARH-BAMNOLI-I
400KV MEERUT-MND-II | 54 | 400KV LUCKNOW-SHAHJHNPR-II | 15 | 315MVA ICT-II GURGAON | 14 | 315MVA ICT-II MAINPURI | DTL | 400KV B'GARH-BAMNOLI-II
400KV MEERUT-MND-III | 55 | 400KV LUCKNOW-SOHAWAL-I | 16 | 500MVA ICT-I JAIPUR(S) | 15 | 100MVA ICT-I PITHORAGRH | DTL | 400KV MND-BAWANA-I
400KV MEERUT-MND-IV | 56 | 400KV LUCKNOW-SOHAWAL-II | 17 | 500MVA ICT-II JAIPUR(S) | 16 | 100MVA ICT-II PITHORAGRH | DTL | 400KV MND-BAWANA-II
400KV MEERUT-MUZFRNGR | 57 | 400KV LUCKNOW-SULTANPR | 18 | 315MVA ICT-I KANKROLI | 17 | 100MVA ICT-I RAIBAREILLY | DTL | 220KV MND-S.WZRBD-I
400KV MERTA-BEAWAR | 58 | 400KV LUCKNOW-UNNAO-I | 19 | 315MVA ICT-II KANKROLI | 18 | 100MVA ICT-II RAIBAREILLY | DTL | 220KV MND-S.WZRBD-II
400KV NAVADA(HVPN)-GR.NOIDA | 59 | 400KV LUCKNOW-UNNAO-II | 20 | 315MVA ICT-III KANKROLI | 19 | 100MVA ICT-III RAIBAREILLY | DTL | 220KV MND-S.WZRBD-III
400KV NIMRANA-MANESAR-I | 60 | 400KV MEERUT-BAREILLY-I | 21 | 315MVA ICT-I KOTA | 20 | 500MVA ICT-I SHAHJHNPR | DTL | 220KV MND-S.WZRBD-IV
400KV NIMRANA-MANESAR-II | 61 | 400KV MEERUT-BAREILLY-II | 22 | 315MVA ICT-II KOTA | 21 | 500MVA ICT-II SHAHJHNPR | DTL | 220KV MND-NARELA-I
400KV NIMRANA-SIKAR-I | 62 | 400KV RIHAND-ALLD-I | 23 | 315MVA ICT-I KOTPUTLI | 22 | 100MVA ICT-I SITARGANJ | DTL | 220KV MND-NARELA-II
400KV NIMRANA-SIKAR-II | 63 | 400KV RIHAND-ALLD-II | 24 | 315MVA ICT-II KOTPUTLI | 23 | 100MVA ICT-II SITARGANJ | DTL | 220KV MND-GOPALPUR-I
400KV ROORKI-KASHIPUR-I | 64 | 400KV RIHAND3-VINDH(Pool)-I | 25 | 315MVA ICT-I MAHRANIBAG | 24 | 315MVA ICT-I SOHAWAL | DTL | 220KV MND-GOPALPUR-II
400KV ROORKI-KASHIPUR-II | 65 | 400KV RIHAND3-VINDH(Pool)-II | 26 | 315MVA ICT-II MAHRANIBAG | 25 | 315MVA ICT-II SOHAWAL | DTL | 220KV MBAG-SARITAVIHAR
400KV ROORKI-MUZFRNGR | 66 | 400KV SING-ALLD-I | 27 | 500MVA ICT-III MAHRANIBAG | 26 |  | DTL | 220KV MBAG-LODHIROAD-I
400KV ROORKI-RISHIKESH | 67 | 400KV SING-ALLD-II | 28 | 500MVA ICT-IV MAHRANIBAG | 27 |  | DTL | 220KV MBAG-LODHIROAD-II
400KV SIKAR-RATANGARH-I | 68 | 400KV SING(NTPC)-ANPARA(UP) | 29 | 500MVA ICT-I MANDOLA | 28 |  | DTL | 220KV MBAG-I P EXTN
400KV SIKAR-RATANGARH-II | 69 | 400KV SING-FATEHPUR | 30 | 500MVA ICT-II MANDOLA | 29 |  | UPPCL | 220KV AGRA-SHAMSABD-I
400KV MEERUT-BAGPAT-II | 70 | 400KV SING-LKO(UP)-I | 31 | 500MVA ICT-III MANDOLA | 30 |  | UPPCL | 220KV AGRA-FEROZABAD
400KV ROORKI-SAHARANPUR-I | 71 | 400KV SING-RIHAND-I | 32 | 500MVA ICT-IV MANDOLA |  |  | UPPCL | 220KV BAGHPAT(PG)-BAGHPAT(UP)
400KV ROORKI-SAHARANPUR-II | 72 | 400KV SING-RIHAND-II | 33 | 500MVA ICT-I MANESAR |  |  | UPPCL | 220KV BAGHPAT-MURADNGR
400KV RAPPC-CHITTOR(RJ)-I | 73 | 400KV SING-VINDH-I | 34 | 500MVA ICT-II MANESAR |  |  | UPPCL | 220KV BAGHPAT-SHAMLI
| 74 | 400KV SING-VINDH-II | 35 | 315MVA ICT-I MEERUT |  |  | UPPCL | 220KV GORAKH-BARHUA
| 75 | 400KV KANPUR-KANPUR(GIS)-I | 36 | 315MVA ICT-II MEERUT |  | 765KV ICT NR-III | UPPCL | 220KV GORAKH-BASTI
| 76 | 400KV KANPUR-KANPUR(GIS)-II | 37 | 315MVA ICT-III MEERUT | 1 | 765/400KV ICT-I BALIA | UPPCL | 220KV LKO(PG)-Bakhsi Ka Talab
| 77 | 400KV VARANASI-SASARAM(ER) | 38 | 500MVA ICT-IV MEERUT | 2 | 765/400KV ICT-II BALIA | UPPCL | 220KV LKO(PG)-CHINHAT
400KV BAHADURGRH-BAWANA | 78 | 400KV VARANASI-SARNATH-I | 39 | 315MVA ICT-III MUZFRNGR | 3 | 765/400KV ICT-I LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-I
400KV BAHADURGRH-SONIPAT-I | 79 | 400KV VARANASI-SARNATH-II | 40 | 315MVA ICT-II NIMRANA | 4 | 765/400KV ICT-II LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-II
400KV BAHADURGRH-SONIPAT-II | 80 | 400KV ALLAHABAD-MEJA(NTPC)-I | 41 | 315MVA ICT-I ROORKI | 5 | 765/400KV ICT-I FATEHPUR | UPPCL | 220KV M'PURI-ETAH
400KV BHIWANI-BAWANA | 81 | 400KV BALIA-BIHARSHRF-I | 42 | 315MVA ICT-II ROORKI | 6 | 765/400KV ICT-II FATEHPUR | UPPCL | 220KV M'PURI-SIRSAGANJ-I
400KV BHIWANI-BHIWANI(BBMB) | 82 | 400KV BALIA-BIHARSHRF-II | 43 | 315MVA ICT-I SIKAR | 7 | 765/400KV ICT-I AGRA | UPPCL | 220KV M'PURI-M'PURI(UP)-II
400KV BHIWANI-HISAR-I | 83 | 400KV ALLD-SASARAM | 44 | 315MVA ICT-II SIKAR | 8 | 765/400KV ICT-II AGRA | UPPCL | 220KV M'PURI-FEROZBD
400KV BHIWANI-HISAR-II | 84 | 400KV BALIA-PATNA-I | 45 | 500MVA ICT-I BAGPAT | 9 | 765/400KV ICT-I BAREILLY | UPPCL | 400KV M'PURI-ORAI-I
400KV BHIWANI-HISAR-III | 85 | 400KV BALIA-PATNA-II | 46 | 500MVA ICT-II BAGPAT | 10 | 765/400KV ICT-II BAREILLY | UPPCL | 400KV M'PURI-PARICHA-II
400KV BHIWANI-JIND-I | 86 | 400KV BALIA-PATNA-III | 47 | 315MVA ICT-I SAHARANPUR | 11 | 765/400KV ICT-I VARANASI | UPPCL | 220KV MEERUT-GAJRAULA
400KV BHIWANI-JIND-II | 87 | 400KV BALIA-PATNA-IV | 48 | 315MVA ICT-II SAHARANPUR | 12 | 765/400KV ICT-II VARANASI | UPPCL | 220KV MEERUT-NEHTAUR
400KV FATEHABAD-HISAR | 88 | 400KV LKO(765)-KANPUR(GIS)-I |  |  | 13 | 765/400KV ICT-I KANPUR(GIS) | UPPCL | 220KV ORAI-KANPUR
400KV BHIWADI-HISAR-II | 89 | 400KV LKO(765)-KANPUR(GIS)-II |  |  | 14 | 765/400KV ICT-II KANPUR(GIS) | UPPCL | 400KV PANKI-MURADNGR
400KV BHIWADI-HISAR-III | [6 empty] | UPPCL | 220KV SHAHJHNP-HARDOI
400KV HISAR-BHIWANI(BBMB) | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-I | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-II |  | 400kv LINES of ER-1 in NR-III Availability |  | NR-I Additional ICT from NR-II |  |  | UPPCL | 220KV SOHAWAL(PG) - SOHAWAL(UP)
400KV KABULPR-BAHADURGRH | 1 | 400KV SASARAM-BIHARSHRF-I | 1 | 315MVA ICT-I BAHADURGARH |  | NR-III HVDC SYSTEM / SVC | UPPCL | 220KV UNCHR-RBRLY-I
400KV KABULPR-BHIWANI | 2 | 400KV SASARAM-BIHARSHRF-II | 2 | 500MVA ICT-II BAHADURGARH | 1 | 500KV HVDC R-D POLE-I | UPPCL | 220KV UNCHR-RBRLY-II
|  |  | 3 | 315MVA ICT-I HISAR | 2 | 500KV HVDC R-D POLE-II | PTCUL | 220KV ROORKI-HARDWAR
|  |  | 4 | 315MVA ICT-II HISAR | 3 | 500KV HVDC BALIA-BHWD POLE-I | PTCUL | 220KV ROORKI--RAMNAGAR
|  | 765 KV TRANS LINES NR-III | 5 | 315MVA ICT-III HISAR | 4 | 500KV HVDC BALIA-BHWD POLE-II | PTCUL | 132KV SITARGNJ(PG)-SITARGNJ(PTCUL)
765 KV TRANS LINES NR-I | 1 | 765KV AGRA-FATEHPUR-I | 6 | 315MVA ICT-I SONIPAT | 5 | 800KV HVDC AGRA-BNC POLE-I | PTCUL | 132KV PITHORAGRH-CHANDOK
765KV AGRA-JHATIKALA | 2 | 765KV AGRA-FATEHPUR-II | 7 | 315MVA ICT-II SONIPAT | 6 | 800KV HVDC AGRA-BNC POLE-II | PTCUL | 132KV PITHORAGRH-ALMORA
765KV BHIWANI-PHAGI(JPR)-I | 3 | 765KV AGRA-GR.NOIDA | 8 | 315MVA ICT-I BHIWANI | 7 | VINDH HVDC B/B BLOCK-I | PTCUL | 132KV PTRGRH-PTRGRH(PTCUL)
765KV MEERUT-GR.NOIDA | 4 | 765KV FATEHPUR-SASARAM | 9 | 315MVA ICT-II BHIWANI | 8 | VINDH HVDC B/B BLOCK-II | POWERLINK
765KV MOGA-BHIWANI | 5 | 765KV LUCKNOW-BALIA | 10 | 500MVA ICT-I JIND | 9 | SASARAM HVDC B/B | PLINK | 400KV LUCKNOW-GORAKH-I (PL)
765KV JHATIKALA-BHIWANI | 6 | 765KV LUCKNOW-BAREILLY | 11 | 500MVA ICT-II JIND | 10 | +/-140MVAR SVC-I KANPUR | PLINK | 400KV LUCKNOW-GORAKH-II (PL)
765KV MEERUT-BHIWANI | 7 | 765KV VARANASI-BALIA |  |  | 11 | +/-140MVAR SVC-II KANPUR | PLINK | 400KV GRKHPR-MZFRPR-I (PL)
765KV BHIWANI-PHAGI(JPR)-II | 8 | 765KV VARANASI-FATEHPUR |  |  |  |  | PLINK | 400KV GRKHPR-MZFRPR-II (PL)
| 9 | 765KV VARANASI-GAYA-I |  | 765KV ICT NR-I
| 10 | 765KV VARANASI-KANPUR(GIS)-I | 1 | 765/400KV ICT-I JHATIKALA
BUS REACTORS NR-I | 11 | 765KV VARANASI-KANPUR(GIS)-II | 2 | 765/400KV ICT-II JHATIKALA |  | SWITCABLE LINE REACTORS NR-III | NR-II | 400KV DAD-M'KOTLA
125MVAR B/Reactor-I BAGPAT | 12 | 765KV KANPUR(GIS)-JHATIKRA-I | 3 | 765/400KV ICT-III JHATIKALA | 1 | AGRA 240MVAR S/R FATEHPR line | NR-II | 400KV BAGHPAT-KAITHAL-I
50MVAR B/Reactor-I BASSI |  |  | 4 | 765/400KV ICT-IV JHATIKALA | 2 | AGRA 50MVAR S/R BHIWADI-I LINE | NR-II | 400KV BAGHPAT-KAITHAL-II
50MVAR B/Reactor-II BASSI |  |  | 5 | 765/400KV ICT-I MEERUT | 3 | ALLHBD 50MVAR S/R MNPR-I LINE | NR-II | 765KV MEERUT-MOGA
50MVAR B/Reactor-III BASSI |  | BUS REACTORS NR-III | 6 | 765/400KV ICT-II MEERUT | 4 | ALLHBD 50MVAR S/R MNPR-II LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-I | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
125MVAR B/Reactor-IV BASSI | 1 | 125MVAR B/Reactor-I AGRA | 7 | 765/400KV ICT-I BHIWANI | 5 | BARLLY 50MVAR S/R MND-I LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-II | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
80MVAR B/Reactor BHINMAL | 2 | 125MVAR B/Reactor-II AGRA | 8 | 765/400KV ICT-II BHIWANI | 6 | BARLLY 50MVAR S/R MND-II LINE | NR-II | 400KV HISAR-MOGA-I
80MVAR B/Reactor BHIWADI | 3 | 240MVAR B/Reactor-II AGRA-765 |  |  | 7 | BALIA 240MVAR S/R LUCKNW Ckt-I | NR-II | 400KV HISAR-MOGA-II
80MVAR B/Reactor BLBGARH | 4 | 240MVAR B/Reactor-1 AGRA-765 |  |  | 8 | BALIA 240MVAR S/R GAYA Line | NR-II | 400KV HISAR-MOGA-III
125MVAR B/Reactor-I JAIPUR(S) | 5 | 80MVAR B/Reactor ALLAHABAD |  |  | 9 | FATEHPR 330MVAR S/R AGRA line
125MVAR B/Reactor-II JAIPUR(S) | 6 | 125MVAR B/Reactor-II ALLAHABAD |  |  | 10 | GORAKH 50MVAR S/R LKO-I LINE
240MVAR B/Reactor-I JHATIKALA-765 | 7 | 80MVAR B/Reactor-I BALIA |  |  | 11 | GORAKH 50MVAR S/R LKO-II LINE
240MVAR B/Reactor-II JHATIKALA-765 | 8 | 125MVAR B/Reactor-II BALIA |  |  | 12 | GORAKH 63MVAR S/R LKO-III LINE
50MVAR B/Reactor KANKROLI | 9 | 125MVAR B/Reactor-III BALIA |  | SWITCABLE LINE REACTORS NR-I | 13 | GORAKH 63MVAR S/R LKO-IV LINE | ER-I | 400KV BALIA-SASARAM
125MVAR B/Reactor-II KANKROLI | 10 | 125MVAR B/Reactor-IV BALIA | 1 | BHINML 50MVAR S/R KANKROLI | 14 | GORAKH 80MVAR S/R Barh-I line | ER-I | 765KV BALIA-GAYA
80MVAR B/Reactor-I KOTA | 11 | 240MVAR B/Reactor-I BALIA-765 | 2 | MEERUT 50MVAR S/R Kotesh-I LINE | 15 | GORAKH 80MVAR S/R Barh-II line | ER-I | 400KV BARH- GRKHPR-I
50MVAR B/Reactor-II KOTA | 12 | 240MVAR B/Reactor-II BALIA-765 | 3 | MEERUT 50MVAR S/R Kotesh-II LINE | 16 | LUCKNW 240MVAR S/R BRLY Line | ER-I | 400KV BARH- GRKHPR-II
80MVAR B/Reactor-I KOTPUTLI | 13 | 80MVAR B/Reactor BAREILLY | 4 | JHATIKALA 240MVAR S/R AGRA Line | 17 | LUCKNW 63MVAR S/R GKP-III LINE | ER-I | 765KV VARANASI-GAYA-II
50MVAR B/Reactor MANDOLA | 14 | 2x50MVAR B/Reactor BAREILLY | 5 | MEERUT 240MVAR S/R AGRA line | 18 | LUCKNW 63MVAR S/R GKP-IV LINE | ER-I | 400KV VARANASI-BIHARSHRF-I
240MVAR B/Reactor-I MEERUT-765 | 15 | 240MVAR B/Reactor-I BAREILLY-765 | 6 | SIKAR 50MVAR S/R AGRA Ckt-I | 19 | LUCKNW 240MVAR S/R BALIA Ckt-I | ER-I | 400KV VARANASI-BIHARSHRF-II
125MVAR B/Reactor MANESAR | 16 | 80MVAR B/Reactor BIHARSHRF | 7 | SIKAR 50MVAR S/R AGRA Ckt-II | 20 | VARANASI 240MVAR S/R KNP(GIS) ckt-1
50MVAR B/Reactor MURADNGR | 17 | 125MVAR B/Reactor-I FATEHPUR | 8 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | 21 | VARANASI 240MVAR S/R KNP(GIS) ckt-2
80MVAR B/Reactor NIMRANA | 18 | 125MVAR B/Reactor-II FATEHPUR | 9 | BHIWANI 240MVAR S/R MEERUT line | 22 | KNP(GIS) 330MVAR S/R JHATIKRA ckt-1 | WR | 765KV AGRA-GWALIOR-I
240MVAR B/Reactor-I PHAGI(JPR)-765 | 19 | 330MVAR B/Reactor-III FTHPR-765 | 10 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line |  |  | WR | 765KV AGRA-GWALIOR-II
125MVAR B/Reactor ROORKEE | 20 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | WR | 765KV GWALIOR-PHAGI-I
125MVAR B/Reactor-I RATANGRH(RJ) | 21 | 125MVAR B/Reactor-II LUCKNOW |  | SVC NR-I |  |  | WR | 765KV GWALIOR-PHAGI-II
80MVAR B/Reactor SIKAR | 22 | 125MVAR B/Reactor-III LUCKNOW | 1 | +400/-300MVAR SVC KANKROLI
50MVAR B/Reactor-I SAHARANPUR | 23 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-I
50MVAR B/Reactor-II SAHARANPUR | 24 | 125MVAR B/Reactor-I VINDH |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-II
125MVAR B/Reactor-II SONIPAT | 25 | 125MVAR B/Reactor-II VINDH
| 26 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - I
BUS REACTORS NR-I From NR2 | 27 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - II
240MVAR B/Reactor-I BHIWANI | 28 | 125MVAR B/Reactor-1 Mainpuri
240MVAR B/Reactor-II BHIWANI | 29 | 125MVAR B/Reactor Gorakhpur-I
50MVAR B/Reactor HISAR | 30 | 125MVAR B/Reactor-II Gorakhpur
125MVAR B/Reactor HISAR | 31 | 125MVAR B/Reactor-I SHAHJHNPR
125MVAR Bus/eactor JIND | 32 | 240MVAR B/Reactor-I KANPUR(GIS)
125MVAR B/Reactor SONIPAT | 33 | 240MVAR B/Reactor-II KANPUR(GIS)
| 34 | 125MVAR B/Reactor-III KANPUR(GIS)
| 35 | 125MVAR B/Reactor-I VARANASI
| 36 | 330MVAR B/Reactor-I VARANASI
| 37 | 330MVAR B/Reactor-II VARANASI
| 38 | 125MVAR B/Reactor KANPUR
Note on E50: a: DOC-01.04.12
Note on I83: 220KV M'PURI-M'PURI(UP)-I LILO at SIRSAGANJ
Note on E84: a: DOC-01.04.12
Note on I86: '400KV M'PURI-PARICHA-I LILO at URI
Note on A96: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on A97: Total-45.6km, PG-26.64km, HVPN-19km.
Note on I98: DELL: 220KV ROORKI-SIDKUL
Note on C108: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C109: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on I112: LILO of 400KV MEERUT-KAITHAL-I at Baghpat
Note on I113: LILO of 400KV MEERUT-KAITHAL-II at Baghpat
Note on I128: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet4
SL.NO. | ELEMENT | Element Name
ID
A |  | 765 KV TRANS LINES
1 | NR176502 | 765KV AGRA-FATEHPUR-I
2 | NR176507 | 765KV AGRA-FATEHPUR-II
3 | NR176510 | 765KV AGRA-GR.NOIDA
4 | NR176506 | 765KV FATEHPUR-SASARAM
5 | NR176501 | 765KV LUCKNOW-BALIA
6 | NR176508 | 765KV LUCKNOW-BAREILLY
7 | NR176512 | 765KV VARANASI-BALIA
8 | NR176513 | 765KV VARANASI-FATEHPUR
9 | NR176514 | 765KV VARANASI-GAYA-I
10 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I
11 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I
B |  | 400 KV TRANS LINES
1 | NR140002 | 400KV AGRA-AGRA(UP)-II | 400KV AGRA-AGRA(UP)-II | 400KV AGRA-FATEHABD(UP)-I
2 | NR140003 | 400KV AGRA-AURAIYA-I | 400KV AGRA-AURAIYA-I
3 | NR140004 | 400KV AGRA-AURAIYA-II | 400KV AGRA-AURAIYA-II
4 | NR140005 | 400KV AGRA-BASSI-I | 400KV AGRA-BASSI-I
5 | NR140008 | 400KV AGRA-BHIWADI-I | 400KV AGRA-BHIWADI-I
6 | NR140009 | 400KV AGRA-BHIWADI-II | 400KV AGRA-BHIWADI-II
7 | NR140010 | 400KV AGRA-BLBGRH | 400KV AGRA-BLBGRH
8 | NR140122 | 400KV ALLD-FATEHPUR-I | 400KV ALLD-FATEHPUR-I
9 | NR140123 | 400KV ALLD-FATEHPUR-II | 400KV ALLD-FATEHPUR-II
10 | NR140104 | 400KV ALLD-FATEHPUR-III | 400KV ALLD-FATEHPUR-III
11 | NR140012 | 400KV ALLD-KNP-II | 400KV ALLD-KNP-II
12 | NR140163 | 400KV ALLD-VARANASI | 400KV ALLD-VARANASI
13 | NR140016 | 400KV ALLD-SASARAM | 400KV ALLD-SASARAM
14 | NR140017 | 400KV BALIA-BIHARSHRF-I | 400KV BALIA-BIHARSHRF-I
15 | NR140018 | 400KV BALIA-BIHARSHRF-II | 400KV BALIA-BIHARSHRF-II
16 | NR140019 | 400KV BALIA-MAU-I | 400KV BALIA-MAU-I
17 | NR140020 | 400KV BALIA-MAU-II | 400KV BALIA-MAU-II
18 | NR140021 | 400KV BALIA-PATNA-I | 400KV BALIA-PATNA-I
19 | NR140022 | 400KV BALIA-PATNA-II | 400KV BALIA-PATNA-II
20 | NR140136 | 400KV BALIA-PATNA-III | 400KV BALIA-PATNA-III
21 | NR140137 | 400KV BALIA-PATNA-IV | 400KV BALIA-PATNA-IV
22 | NR140140 | 400KV BALIA-SOHAWAL-I | 400KV BALIA-SOHAWAL-I
23 | NR140120 | 400KV BALIA-SOHAWAL-II | 400KV BALIA-SOHAWAL-II
24 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 400KV BAREILLY-BAREILLY(765)-I
25 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 400KV BAREILLY-BAREILLY(765)-II
26 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 400KV BAREILLY-BRLY(UP)-I
27 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 400KV BAREILLY-BRLY(UP)-II
28 | NR140025 | 400KV BAREILLY-LKO(UP) | 400KV BAREILLY-LKO(UP)
29 | NR140026 | 400KV BAREILLY-MBAD-I | 400KV BAREILLY-MBAD-I
30 | NR140027 | 400KV BAREILLY-MBAD-II | 400KV BAREILLY-MBAD-II
31 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 400KV BAREILLY-SHAHJHNPR-I
32 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 400KV BAREILLY-SHAHJHNPR-II | 400KV BAREILLY-ROSA-I
33 | NR140158 | 400KV BARLY(765)-KASHIPUR-I | 400KV BRLY(765)-KASHIPUR-I
34 | NR140159 | 400KV BARLY(765)-KASHIPUR-II | 400KV BRLY(765)-KASHIPUR-II
35 | NR140037 | 400KV BLBGRH-MAINPURI-I | 400KV BLBGRH-MAINPURI-I
36 | NR140038 | 400KV BLBGRH-MAINPURI-II | 400KV BLBGRH-MAINPURI-II
37 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 400KV FATEHPUR-MAINPURI-I
38 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 400KV FATEHPUR-MAINPURI-II
39 | NR140046 | 400KV GORAKH-GORAKH-I | 400KV GORAKH-GORAKH-I
40 | NR140047 | 400KV GORAKH-GORAKH-II | 400KV GORKH-GORAKH-II
41 | NR140052 | 400KV KNP-AGRA | 400KV KNP-AGRA
42 | NR140053 | 400KV KNP-AURAIYA-I | 400KV KNP-AURAIYA-I
43 | NR140054 | 400KV KNP-AURAIYA-II | 400KV KNP-AURAIYA-II
44 | NR140055 | 400KV KNP-BLBGARH-I | 400KV KNP-BLBGARH-I
45 | NR140056 | 400KV KNP-BLBGARH-II | 400KV KNP-BLBGARH-II
46 | NR140057 | 400KV KNP-BLBGARH-III | 400KV KNP-BLBGARH-III
47 | NR140110 | 400KV KNP-FATEHPUR-I | 400KV KNP-FATEHPUR-I
48 | NR140105 | 400KV KNP-FATEHPUR-II | 400KV KNP-FATEHPUR-II
49 | NR140058 | 400KV KNP-PANKI-I | 400KV KNP-PANKI-I
50 | NR140059 | 400KV KNP-PANKI-II | 400KV KNP-PANKI-II
51 | NR140070 | 400KV LUCKNOW-GORAKH-III | 400KV LUCKNOW-GORAKH-III
52 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 400KV LUCKNOW-GORAKH-IV
53 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 400KV LUCKNOW-LKO(765)-I
54 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 400KV LUCKNOW-LKO(765)-II
55 | NR140072 | 400KV LUCKNOW-LKO(UP) | 400KV LUCKNOW-LKO(UP)
56 | NR140114 | 400KV LUCKNOW-ROSA-I | 400KV LUCKNOW-ROSA-I
57 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 400KV LUCKNOW-SHAHJHNPR-II
58 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 400KV LUCKNOW-SOHAWAL-I
59 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 400KV LUCKNOW-SOHAWAL-II
60 | NR140073 | 400KV LUCKNOW-SULTANPR | 400KV LUCKNOW-SULTANPR
61 | NR140074 | 400KV LUCKNOW-UNNAO-I | 400KV LUCKNOW-UNNAO-I
62 | NR140075 | 400KV LUCKNOW-UNNAO-II | 400KV LUCKNOW-UNNAO-II
63 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 400KV RIHAND3-VINDH(Pool)-I
64 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 400KV RIHAND3-VINDH(Pool)-II
65 | NR140084 | 400KV RIHAND-ALLD-I | 400KV RIHAND-ALLD-I
66 | NR140085 | 400KV RIHAND-ALLD-II | 400KV RIHAND-ALLD-II
67 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 400KV SASARAM-BIHARSHRF-I
68 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 400KV SASARAM-BIHARSHRF-II
69 | NR140090 | 400KV SASARAM-SARNATH | 400KV SASARAM-SARNATH
70 | NR140091 | 400KV SING-ALLD-I | 400KV SING-ALLD-I
71 | NR140092 | 400KV SING-ALLD-II | 400KV SING-ALLD-II
72 | NR140093 | 400KV SING-ANPARA | 400KV SING-ANPARA
73 | NR140111 | 400KV SING-FATEHPUR | 400KV SING-FATEHPUR
74 | NR140095 | 400KV SING-LKO(UP)-I | 400KV SING-LKO(UP)
75 | NR140096 | 400KV SING-RIHAND-I | 400KV SING-RIHAND-I
76 | NR140097 | 400KV SING-RIHAND-II | 400KV SING-RIHAND-II
77 | N-W40001 | 400KV SING-VINDH-I | 400KV SING-VINDH-I
78 | N-W40002 | 400KV SING-VINDH-II | 400KV SING-VINDH-II
79 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 400KV KANPUR-KANPUR(GIS)-I
80 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 400KV KANPUR-KANPUR(GIS)-II
81 | NR340003 | 400KV VARANASI-SASARAM(ER)
82 | NR340004 | 400KV VARANASI-SARNATH-I | 400KV VARANASI-SARNATH-I
83 | NR340005 | 400KV VARANASI-SARNATH-II | 400KV VARANASI-SARNATH-II
84 | NR340006 | 400KV AGRA-FATEHABD(UP)-I
85 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II
86 | NR340008 | 400KV LKO(765)-KANPUR(GIS)-I | 400KV LKO(765)-KANPUR(GIS)-I
87 | NR340009 | 400KV LKO(765)-KANPUR(GIS)-II | 400KV LKO(765)-KANPUR(GIS)-II
88 | NR140142 | 400KV MEERUT-BAREILLY-I
89 | NR140130 | 400KV MEERUT-BAREILLY-II
90 | NR340010 | 400KV ALLAHABAD-MEJA(NTPC)-I
C |  | 220 KV TRANS LINES
1 | BILUP2209 | 220KV ALLD-JHUSI(UP)
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP)
3 | BILUP2202 | 220KV ALLD-REWA RD-I
4 | BILUP2203 | 220KV ALLD-REWA RD-II
5 | NR122006 | 220KV AUR-SIKANDARA-I
6 | NR122007 | 220KV AUR-SIKANDARA-II
7 | NR122012 | 220KV DGANGA-BLY(UP)-II
8 | NR122013 | 220KV DGANGA-PITHORAGRH
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH
12 | NR122041 | 220KV FATEHPUR-NAUBASTA
13 | NR122016 | 220KV KNP-MAINPURI
14 | NR122017 | 220KV KNP-NAUBASTA
15 | NR122019 | 220KV KNP-PANKI-II
16 | NR122020 | 220KV KNP-UNCHR-I
17 | NR122021 | 220KV KNP-UNCHR-II
18 | NR122022 | 220KV KNP-UNCHR-III
19 | NR122023 | 220KV KNP-UNCHR-IV
20 | NR122024 | 220KV PITHORAGRH-BRLY(UP)
21 | NR122025 | 220KV RAIBRLY-CHINHAT
22 | NR122026 | 220KV RAIBRLY-LKO(UP)
23 | NR122032 | 220KV SITARGANJ-BLY(UP)
24 | NR122033 | 220KV TNKPR-BLY(UP)
25 | NR122034 | 220KV TNKPR-SITARGANJ
26 | NR122035 | 220KV UNCHR-RAIBRLY-I
27 | NR122036 | 220KV UNCHR-RAIBRLY-II
28 | NR122037 | 220KV UNCHR-RAIBRLY-III
29 | NR320001 | 220KV KNP-RANIA
30 | NR320002 | 220KV RANIA-PANKI
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA
#REF! | Lines | TOTAL FOR T/LS
OVERALL SYSTEM AVAILABILITY=
E |  | 765/400 KV ICT'S
1 | NR1ICT707 | 765/400KV ICT-I AGRA
2 | NR1ICT708 | 765/400KV ICT-II AGRA
3 | NR1ICT701 | 765/400KV ICT-I BALIA
4 | NR1ICT702 | 765/400KV ICT-II BALIA
5 | NR1ICT715 | 765/400KV ICT-I BAREILLY
6 | NR1ICT716 | 765/400KV ICT-II BAREILLY
7 | NR1ICT705 | 765/400KV ICT-I FATEHPUR
8 | NR1ICT706 | 765/400KV ICT-II FATEHPUR
9 | NR1ICT703 | 765/400KV ICT-I LUCKNOW
10 | NR1ICT704 | 765/400KV ICT-II LUCKNOW
11 | NR1ICT717 | 765/400KV ICT-I VARANASI
12 | NR1ICT718 | 765/400KV ICT-II VARANASI
13 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS)
14 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS)
F |  | 400/220 KV ICT'S
1 | NR1ICT70 | 315MVA ICT-I AGRA
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR
9 | NR1ICT19 | 315MVA ICT-I KANPUR
10 | NR1ICT20 | 315MVA ICT-II KANPUR
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW
13 | NR1ICT26 | 315MVA ICT-I MAINPURI
14 | NR1ICT27 | 315MVA ICT-II MAINPURI
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 100MVA ICT-I PITHORAGRH
2 | NR1ICT44 | 100MVA ICT-II PITHORAGRH
3 | NR1ICT47 | 100MVA ICT-I RAIBAREILLY
4 | NR1ICT38 | 100MVA ICT-II RAIBAREILLY
5 | NR1ICT39 | 100MVA ICT-III RAIBAREILLY
6 | NR1ICT40 | 100MVA ICT-I SITARGANJ
7 | NR1ICT41 | 100MVA ICT-II SITARGANJ
39 |  | TOTAL FOR ICTs
H |  | HVDC RIHAND-DADRI
1 | NR1DCP01 | 500KV HVDC R-D POLE-I
2 | NR1DCP02 | 500KV HVDC R-D POLE-II
3 | NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I
4 | NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II
TOTAL FOR HVDC line
J |  | HVDC AGRA-BNC
1 | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I
2 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II
TOTAL of HVDC POLE-I
K |  | HVDC BTB VINDHYACHAL
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II
TOTAL FOR HVDC VINDHYACHAL
L |  | HVDC BTB SASARAM
1 | NEDCB01 | +/-500MW HVDC B/B SASARAM
TOTAL FOR HVDC SASARAM
M |  | SVC, KANPUR
1 | NR1SVC01 | +/-140MVAR SVC-I KANPUR
2 | NR1SVC02 | +/-140MVAR SVC-II KANPUR
TOTAL FOR SVC
N |  | Bus & Switch Line Reactor
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD
6 | NR1BRT33 | 125MVAR B/Reactor-II ALLAHABAD
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY
14 | NR1BRT44 | 2x50MVAR B/Reactor- BAREILLY
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR
20 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI
28 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR
29 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W
30 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N
31 | NR1BRT42 | 125MVAR B/Reactor-I VINDH
32 | NR1BRT43 | 125MVAR B/Reactor-II VINDH
| NR1BRT55 | 330MVAR B/Reactor-I VARANASI
33 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI
34 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I
35 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line
36 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I
37 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II
38 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line
39 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I
40 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I
41 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II
42 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line
43 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I
44 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II
45 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE
46 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE
47 | NR1SRT24 | GORAKH 80MVAR S/R Barh-I line
48 | NR1SRT25 | GORAKH 80MVAR S/R Barh-II line
49 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE
50 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE
51 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I
52 | NR1SRT26 | LUCKNW 240MVAR S/R Bareilly Line
53 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS)
54 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS)
55 | NR3SRT01 | VARANASI 240MVAR S/R KNP(GIS)-1
56 | NR3SRT02 | VARANASI 240MVAR S/R KNP(GIS)-2
57 | NR3SRT03 | KNP(GIS) 330MVAR S/R JHATIKRA-1
58 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS)
59 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI
TOTAL FOR BUS REACTORS
TOTAL
Note on C7: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C12: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C13: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C29: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16
Note on D48: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on D49: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C74: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C86: Line Re-configured as 400kv Varanasi-Sasaram(ER) on 30-09-16.
Note on D99: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on D100: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C101: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C102: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C143: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C144: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C239: DOC-26/05/2014

## Sheet5
220KV ALLD-JHUSI(UP)
220KV JHUSI(UP)-PHULPUR(UP)
220KV ALLD-REWA RD-I
220KV ALLD-REWA RD-II
220KV AUR-SIKANDARA-I
220KV AUR-SIKANDARA-II
220KV DGANGA-BLY(UP)-II
220KV DGANGA-PITHORAGRH
220KV FATEHPUR-FTHPR(UP)-I
220KV FATEHPUR-FTHPR(UP)-II
220KV FATEHPUR-KNP SOUTH
220KV FATEHPUR-NAUBASTA
220KV KNP-MAINPURI
220KV KNP-NAUBASTA
220KV KNP-PANKI-I
220KV KNP-PANKI-II
220KV KNP-UNCHR-I
220KV KNP-UNCHR-II
220KV KNP-UNCHR-III
220KV KNP-UNCHR-IV
220KV PITHORAGRH-BRLY(UP)
220KV RAIBRLY-CHINHAT
220KV RAIBRLY-LKO(UP)
220KV SITARGANJ-BLY(UP)
220KV TNKPR-BLY(UP)
220KV TNKPR-SITARGANJ
220KV UNCHR-RAIBRLY-I
220KV UNCHR-RAIBRLY-II
220KV UNCHR-RAIBRLY-III
220KV KNP-RANIA
132 KV TRANS LINES
Note on A31: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Sheet2 (hidden)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
125MVAR B/Reactor-1 Mainpuri | 2017-05-27 22:42 | 2017-05-28 06:46 | 0 | 0 | 0 | 0.33611 | N-2790 | SVRD | H-T for voltage regulation as per NRLDC instruction. Mainpuri=386KV
125MVAR B/Reactor-I GORAKHPUR | 2017-05-22 21:55 | 2017-06-01 | 0 | 0 | 0 | 1900-01-08 02:05 | N-2235 | SVRD | H-T for voltage regulation as per NRLDC instruction. Gorakhpur=393KV
125MVAR B/Reactor-III KANPUR(GIS) | 2017-05-25 23:46 | 2017-05-26 06:58 | 0 | 0 | 0 | 0.3 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. Kanpur=395KV
240MVAR B/Reactor-I BALIA-765 | 2017-05-13 21:25 | 2017-05-27 01:23 | 0 | 0 | 0 | 1900-01-12 03:58 | N-1003 | SVRD | H-T for voltage regulation as per NRLDC instruction. Ballia=744KV
240MVAR B/Reactor-I BAREILLY-765 | 2017-05-25 09:56 | 2017-05-28 05:20 | 0 | 0 | 0 | 1900-01-01 19:24 | N-2455 | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-13 21:24 | 2017-05-14 06:52 | 0 | 0 | 0 | 0.39444 | N-1002 | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-16 20:01 | 2017-05-17 07:40 | 0 | 0 | 0 | 0.48542 | N-1534 | SVRD | H-T for voltage regulation as per NRLDC instruction. Lucknow=749KV
330MVAR B/Reactor-II VARANASI | 2017-05-19 15:05 | 2017-05-19 22:00 | 0 | 0 | 0 | 0.28819 | N-1850 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=751KV
330MVAR B/Reactor-II VARANASI | 2017-05-22 21:34 | 2017-05-24 06:25 | 0 | 0 | 0 | 1899-12-31 08:51 | N-2234 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=761KV
80MVAR B/Reactor BAREILLY | 2017-05-25 23:41 | 2017-05-26 07:02 | 0 | 0 | 0 | 0.30625 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=395KV
80MVAR B/Reactor LUCKNOW | 2017-05-25 23:35 | 2017-05-26 06:53 | 0 | 0 | 0 | 0.30417 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=396KV
Note on A9: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1
Note on A10: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1