## SOP DATA NR3 January-17
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-III
Availability calculation for the Period : From 01.01.2017 to 31.01.2017
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [24 empty] | 0
1 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 744
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1327 | 148.034 | 196441.118 | 196441.118 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2017-01-02 23:44 | 2017-01-03 08:30 |  |  |  | 0 | 0 | 0 | 0.36528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV
[6 empty] | 2017-01-10 01:12 | 2017-01-10 06:49 |  |  |  | 0 | 0 | 0 | 0.23403 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789 kV
[6 empty] | 2017-01-12 00:25 | 2017-01-12 06:12 |  |  |  | 0 | 0 | 0 | 0.24097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-12 21:09 | 2017-01-13 06:29 |  |  |  | 0 | 0 | 0 | 0.38889 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-14 00:16 | 2017-01-14 07:37 |  |  |  | 0 | 0 | 0 | 0.30625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-17 01:32 | 2017-01-17 08:16 |  |  |  | 0 | 0 | 0 | 0.28056 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ftpr-802kV
[6 empty] | 2017-01-24 01:04 | 2017-01-24 06:59 |  |  |  | 0 | 0 | 0 | 0.24653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-781 kV
[6 empty] | 2017-01-26 01:38 | 2017-01-27 05:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:36 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-793kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 05:06 | [6 empty] | 744 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2017-01-01 01:21 | 2017-01-01 07:29 |  |  |  | 0 | 0 | 0 | 0.25556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-798 kV
[6 empty] | 2017-01-01 23:40 | 2017-01-02 07:30 |  |  |  | 0 | 0 | 0 | 0.32639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV
[6 empty] | 2017-01-03 21:37 | 2017-01-04 08:12 |  |  |  | 0 | 0 | 0 | 0.44097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV
[6 empty] | 2017-01-05 00:05 | 2017-01-05 06:42 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV
[6 empty] | 2017-01-07 04:41 | 2017-01-07 09:18 |  |  |  | 0 | 0 | 0 | 0.19236 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-795 kV
[6 empty] | 2017-01-07 23:14 | 2017-01-08 06:08 |  |  |  | 0 | 0 | 0 | 0.2875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-782kV
[6 empty] | 2017-01-08 15:08 | 2017-01-09 07:16 |  |  |  | 0 | 0 | 0 | 0.67222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790kV
[6 empty] | 2017-01-11 00:11 | 2017-01-11 07:25 |  |  |  | 0 | 0 | 0 | 0.30139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-15 00:02 | 2017-01-15 07:16 |  |  |  | 0 | 0 | 0 | 0.30139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-16 00:06 | 2017-01-16 08:15 |  |  |  | 0 | 0 | 0 | 0.33958 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-798 kV
[6 empty] | 2017-01-17 22:05 | 2017-01-18 06:14 |  |  |  | 0 | 0 | 0 | 0.33958 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-786kV
[6 empty] | 2017-01-18 23:45 | 2017-01-19 06:49 |  |  |  | 0 | 0 | 0 | 0.29444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-429 kV
[6 empty] | 2017-01-19 20:50 | 2017-01-20 06:26 |  |  |  | 0 | 0 | 0 | 0.4 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-20 20:59 | 2017-01-21 05:59 |  |  |  | 0 | 0 | 0 | 0.375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-21 23:54 | 2017-01-22 07:16 |  |  |  | 0 | 0 | 0 | 0.30694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV
[6 empty] | 2017-01-22 23:27 | 2017-01-23 06:56 |  |  |  | 0 | 0 | 0 | 0.31181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-781 kV
[6 empty] | 2017-01-25 01:11 | 2017-01-25 08:23 |  |  |  | 0 | 0 | 0 | 0.3 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-781 kV
[6 empty] | 2017-01-25 22:10 | 2017-01-26 06:36 |  |  |  | 0 | 0 | 0 | 0.35139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789 kV
[6 empty] | 2017-01-26 21:57 | 2017-01-27 07:41 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-787kV
[6 empty] | 2017-01-27 22:25 | 2017-01-28 09:33 |  |  |  | 0 | 0 | 0 | 0.46389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-787kV
[6 empty] | 2017-01-28 23:15 | 2017-01-29 07:03 |  |  |  | 0 | 0 | 0 | 0.325 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-787kV
[6 empty] | 2017-01-29 21:07 | 2017-01-30 06:51 |  |  |  | 0 | 0 | 0 | 0.40556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-787kV
[6 empty] | 2017-01-30 22:43 | 2017-01-31 07:26 |  |  |  | 0 | 0 | 0 | 0.36319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-784 kV
[6 empty] | 2017-01-31 21:19 | 2017-02-01 |  |  |  | 0 | 0 | 0 | 0.11181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-784 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 03:32 | [6 empty] | 744 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
5 | NR176503 | 765KV FATEHPUR-GAYA | 484.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1070 | 484.6 | 518522 | 518522 | 100
6 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1067 | 355.008 | 378793.536 | 378793.536 | 100
7 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | 2017-01-23 03:03 | 2017-01-23 09:51 |  |  |  | 0 | 0 | 0 | 0.28333 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Lko-805 kV
[6 empty] | 2017-01-27 02:00 | 2017-01-27 11:40 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Lko-804 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.68611 | [6 empty] | 744 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
8 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | 2017-01-20 16:07 | 2017-01-20 16:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/R on Y-N fault, FLR-Brly-53.63Km, If-4.4KA.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 256393.647 | 100
9 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | 2017-01-17 09:49 | 2017-01-17 19:29 |  |  |  | 0.40278 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP work at Varanasi.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.40278 | 0 | 0 | 0 | [6 empty] | 744 | 1419 | 165.98 | 235525.62 | 232465.4753 | 98.7007
10 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | 2017-01-07 14:44 | 2017-01-07 20:35 |  |  |  | 0.24375 | 0 | 0 | 0 |  |  |  | LPPT | Line tripped on R-Y fault. FLR:VNS-50.2 km, If- 9.3kAmp
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.24375 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 223 | 310639 | 308196.4756 | 99.2137
11 | NR176514 | 765KV VARANASI-GAYA-I | 264 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1108 | 264 | 292512 | 292512 | 100
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR3 | -- | 2017-01-01 23:48 | 2017-01-02 08:25 |  |  |  | 0 | 0 | 0 | 0.35903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhat-805 kV
[6 empty] | 2017-01-03 01:07 | 2017-01-03 10:11 |  |  |  | 0 | 0 | 0 | 0.37778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhatkr-806 kV
[6 empty] | 2017-01-04 03:00 | 2017-01-04 07:39 |  |  |  | 0 | 0 | 0 | 0.19375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhatkr-806 kV
[6 empty] | 2017-01-06 23:32 | 2017-01-07 06:58 |  |  |  | 0 | 0 | 0 | 0.30972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhatkr-806 kV
[6 empty] | 2017-01-08 01:30 | 2017-01-08 07:29 |  |  |  | 0 | 0 | 0 | 0.24931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhatkr-804 kV
[6 empty] | 2017-01-10 01:09 | 2017-01-10 08:17 |  |  |  | 0 | 0 | 0 | 0.29722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. JHTR-807kV
[6 empty] | 2017-01-11 00:13 | 2017-01-11 07:45 |  |  |  | 0 | 0 | 0 | 0.31389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. JHTR-802kV
[6 empty] | 2017-01-15 01:49 | 2017-01-15 05:55 |  |  |  | 0 | 0 | 0 | 0.17083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. JHTR-807kV
[6 empty] | 2017-01-18 02:26 | 2017-01-18 06:47 |  |  |  | 0 | 0 | 0 | 0.18125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV
[6 empty] | 2017-01-19 00:48 | 2017-01-19 06:41 |  |  |  | 0 | 0 | 0 | 0.24514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-801 kV
[6 empty] | 2017-01-22 01:19 | 2017-01-22 07:07 |  |  |  | 0 | 0 | 0 | 0.24167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-801 kV
[6 empty] | 2017-01-22 23:25 | 2017-01-23 08:06 |  |  |  | 0 | 0 | 0 | 0.36181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-800 kV
[6 empty] | 2017-01-25 23:22 | 2017-01-26 09:49 |  |  |  | 0 | 0 | 0 | 0.43542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV
[6 empty] | 2017-01-26 13:05 | 2017-01-27 07:26 |  |  |  | 0 | 0 | 0 | 0.76458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV
[6 empty] | 2017-01-28 00:43 | 2017-01-28 07:36 |  |  |  | 0 | 0 | 0 | 0.28681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV
[6 empty] | 2017-01-29 00:15 | 2017-01-29 06:44 |  |  |  | 0 | 0 | 0 | 0.27014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV
[6 empty] | 2017-01-29 23:33 | 2017-01-30 10:09 |  |  |  | 0 | 0 | 0 | 0.44167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV
[6 empty] | 2017-01-30 22:45 | 2017-01-31 07:38 |  |  |  | 0 | 0 | 0 | 0.37014 |  |  |  | LVRD | Line hand tripped for Voltage regulation Jhat-784 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 20:53 | [6 empty] | 744 | 1440 | 465.8 | 670752 | 670752 | 100
13 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | 2017-01-21 06:36 | 2017-01-21 18:41 |  |  |  | 0 | 0 | 0.50347 | 0 |  |  |  | LNCC | Line tripped on B-N fault, FLR-Knp-56.4Km, Vns-255.8Km If-6.2KA, Charging attempt fail & SOTF optd.during dense fog.
[6 empty] | 2017-01-25 05:06 | 2017-01-25 18:25 |  |  |  | 0 | 0 | 0.55486 | 0 |  |  |  | LNCC | Tripped due to severe fog on B-N fault. FLR- KNP- 54.0 km, If-6.17 kAmp, VNS- 258.4 km. Jumper snapped found at loc-46/0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1899-12-31 01:24 | 0 | [6 empty] | 718.6 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
14 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | 2017-01-09 19:44 | 2017-01-09 22:23 |  |  |  | 0.11042 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on R-N fault, FLR:Knp-0.2km, Vrns-397km, IF (Knp)-10.13 KA
[6 empty] | 2017-01-21 15:31 | 2017-01-21 18:59 |  |  |  | 0.14444 | 0 | 0 | 0 |  |  |  | OSFT | To avoid induction during restoration of Jumper in VNS-KNP-I line.
[6 empty] | 2017-01-25 12:32 | 2017-01-25 18:28 |  |  |  | 0.24722 | 0 | 0 | 0 |  |  |  | OSFT | S/D for avoid induction in rectification of snapped Jumper of Ckt-I
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.50208 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 464326.7319 | 98.3804
B |  | 400 KV TRANS LINES |  |  | --
1 | NR140001 | 400KV AGRA-AGRA(UP)-I | 29.982 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2017-01-04 02:46 | 2017-01-04 07:56 | -- | -- | -- | 0 | 0 | 0 | 0.21528 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2017-01-12 00:19 | 2017-01-12 07:56 |  |  |  | 0 | 0 | 0 | 0.31736 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-12 21:13 | 2017-01-13 06:10 |  |  |  | 0 | 0 | 0 | 0.37292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-14 00:07 | 2017-01-14 09:29 |  |  |  | 0 | 0 | 0 | 0.39028 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2017-01-16 23:26 | 2017-01-17 08:20 |  |  |  | 0 | 0 | 0 | 0.37083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-426kV
[6 empty] | 2017-01-26 00:32 | 2017-01-30 07:02 |  |  |  | 0 | 0 | 0 | 1900-01-03 06:30 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 22:30 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2017-01-01 00:26 | 2017-01-02 07:02 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:36 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-04 21:04 | 2017-01-05 06:32 |  |  |  | 0 | 0 | 0 | 0.39444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
[6 empty] | 2017-01-07 01:42 | 2017-01-07 15:25 |  |  |  | 0 | 0 | 0 | 0.57153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2017-01-08 00:27 | 2017-01-08 07:03 |  |  |  | 0 | 0 | 0 | 0.275 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV
[6 empty] | 2017-01-08 23:52 | 2017-01-09 08:32 |  |  |  | 0 | 0 | 0 | 0.36111 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2017-01-14 21:11 | 2017-01-15 09:12 |  |  |  | 0 | 0 | 0 | 0.50069 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2017-01-15 23:34 | 2017-01-16 08:58 |  |  |  | 0 | 0 | 0 | 0.39167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2017-01-20 00:27 | 2017-01-20 06:08 |  |  |  | 0 | 0 | 0 | 0.23681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-21 00:22 | 2017-01-21 06:13 |  |  |  | 0 | 0 | 0 | 0.24375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-23 20:56 | 2017-01-24 08:07 |  |  |  | 0 | 0 | 0 | 0.46597 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV
[6 empty] | 2017-01-24 21:17 | 2017-01-25 07:04 |  |  |  | 0 | 0 | 0 | 0.40764 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV
[6 empty] | 2017-01-26 01:06 | 2017-01-31 09:43 |  |  |  | 0 | 0 | 0 | 1900-01-04 08:37 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2017-01-31 21:27 | 2017-02-01 |  |  |  | 0 | 0 | 0 | 0.10625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 14:08 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- | 2017-01-01 01:19 | 2017-01-01 10:38 | -- | -- | -- | 0 | 0 | 0 | 0.38819 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2017-01-15 23:55 | 2017-01-16 07:44 |  |  |  | 0 | 0 | 0 | 0.32569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[6 empty] | 2017-01-17 00:18 | 2017-01-17 06:25 |  |  |  | 0 | 0 | 0 | 0.25486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mrt-800 kV
[6 empty] | 2017-01-23 23:28 | 2017-01-24 06:55 |  |  |  | 0 | 0 | 0 | 0.31042 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV
[6 empty] | 2017-01-25 00:07 | 2017-01-25 07:11 |  |  |  | 0 | 0 | 0 | 0.29444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2017-01-31 21:36 | 2017-02-01 |  |  |  | 0 | 0 | 0 | 0.1 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 16:10 | [6 empty] | 744 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2017-01-31 22:07 | 2017-02-01 | -- | -- | -- | 0 | 0 | 0 | 0.078472 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.078472 | [6 empty] | 744 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2017-01-01 | 2017-01-01 06:52 | -- | -- | -- | 0 | 0 | 0 | 0.28611 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-429 kV. Open since 2033hrs on 31.12.16
[6 empty] | 2017-01-01 19:50 | 2017-01-02 06:38 |  |  |  | 0 | 0 | 0 | 0.45 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[6 empty] | 2017-01-02 20:53 | 2017-01-03 06:59 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
[6 empty] | 2017-01-03 20:15 | 2017-01-04 10:17 |  |  |  | 0 | 0 | 0 | 0.58472 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
[6 empty] | 2017-01-04 19:58 | 2017-01-05 06:04 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
[6 empty] | 2017-01-05 20:17 | 2017-01-06 07:02 |  |  |  | 0 | 0 | 0 | 0.44792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
[6 empty] | 2017-01-06 19:28 | 2017-01-07 15:27 |  |  |  | 0 | 0 | 0 | 0.83264 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV
[6 empty] | 2017-01-07 20:17 | 2017-01-08 07:00 |  |  |  | 0 | 0 | 0 | 0.44653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-08 15:22 | 2017-01-09 04:47 |  |  |  | 0 | 0 | 0 | 0.55903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV
[6 empty] | 2017-01-09 21:05 | 2017-01-10 08:53 |  |  |  | 0 | 0 | 0 | 0.49167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV
[6 empty] | 2017-01-10 21:09 | 2017-01-11 07:17 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV
[6 empty] | 2017-01-11 21:08 | 2017-01-12 07:15 |  |  |  | 0 | 0 | 0 | 0.42153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV
[6 empty] | 2017-01-12 20:15 | 2017-01-13 06:29 |  |  |  | 0 | 0 | 0 | 0.42639 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV
[6 empty] | 2017-01-13 20:52 | 2017-01-14 05:56 |  |  |  | 0 | 0 | 0 | 0.37778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV
[6 empty] | 2017-01-14 20:06 | 2017-01-15 09:04 |  |  |  | 0 | 0 | 0 | 0.54028 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV
[6 empty] | 2017-01-15 19:13 | 2017-06-16 06:21 |  |  |  | 0 | 0 | 0 | 1900-05-30 11:08 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-429kV
[6 empty] | 2017-01-16 20:16 | 2017-01-17 08:02 |  |  |  | 0 | 0 | 0 | 0.49028 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-17 20:43 | 2017-01-18 06:26 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-18 20:55 | 2017-01-19 06:25 |  |  |  | 0 | 0 | 0 | 0.39583 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-19 20:34 | 2017-01-20 06:01 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-20 20:21 | 2017-01-21 06:17 |  |  |  | 0 | 0 | 0 | 0.41389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-21 19:58 | 2017-01-22 06:04 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-22 16:07 | 2017-01-23 07:26 |  |  |  | 0 | 0 | 0 | 0.63819 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-23 20:43 | 2017-01-24 06:39 |  |  |  | 0 | 0 | 0 | 0.41389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-24 19:51 | 2017-01-25 06:59 |  |  |  | 0 | 0 | 0 | 0.46389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[6 empty] | 2017-01-25 19:50 | 2017-01-26 07:10 |  |  |  | 0 | 0 | 0 | 0.47222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-26 10:57 | 2017-01-27 04:52 |  |  |  | 0 | 0 | 0 | 0.74653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-27 13:37 | 2017-01-28 06:57 |  |  |  | 0 | 0 | 0 | 0.72222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-28 21:01 | 2017-01-30 06:43 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:42 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-30 13:25 | 2017-01-31 06:03 |  |  |  | 0 | 0 | 0 | 0.69306 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[6 empty] | 2017-01-31 13:12 | 2017-02-01 |  |  |  | 0 | 0 | 0 | 0.45 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-06-15 02:47 | [6 empty] | 744 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | 2017-01-03 02:06 | 2017-01-03 02:06 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on Y-N fault, FLR:Agra-51.5km, Blb-128.6km
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | 2017-01-03 07:21 | 2017-01-03 20:23 |  |  |  | 0 | 0 | 0 | 0.54306 |  |  |  | OSPD | S/D by UPPCL for stringing of 400KV D/C Allahabad-Rewa Road line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.54306 | -- | -- | -- |  |  |  | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
10 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | 2017-01-03 07:20 | 2017-01-03 20:25 |  |  |  | 0 | 0 | 0 | 0.54514 |  |  |  | OSPD | S/D by UPPCL for stringing of 400KV D/C Allahabad-Rewa Road line.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.54514 | -- | -- | -- |  |  |  | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
11 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 155.932 | 80304.98 | 80304.98 | 100
12 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 224 | 115360 | 115360 | 100
13 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 98.792 | 50877.88 | 50877.88 | 100
14 | NR140016 | 400KV ALLD-SASARAM | 212 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 369 | 212 | 78228 | 78228 | 100
13 | NR140017 | 400KV BALIA-BIHARSHRF-I | 241.79 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 598 | 241.79 | 144590.42 | 144590.42 | 100
14 | NR140020 | 400KV BALIA-BIHARSHRF-II | 241.79 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 598 | 241.79 | 144590.42 | 144590.42 | 100
15 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
16 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
17 | NR140021 | 400KV BALIA-PATNA-I | 195.32 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 195.32 | 134966.12 | 134966.12 | 100
18 | NR140022 | 400KV BALIA-PATNA-II | 195.32 | NR3 | -- | 2017-01-25 10:10 | 2017-01-25 11:50 | -- | -- | -- | 0.069444 | 0 | 0 | 0 | -- | -- | -- | OSFT | Hand tripped due to sparking in isolator at Balia end
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.069444 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 195.32 | 134966.12 | 134663.7765 | 99.776
19 | NR140136 | 400KV BALIA-PATNA-III | 185 | NR3 | -- | 2017-01-12 09:32 | 2017-01-12 16:19 | -- | -- |  | 0.28264 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for decapped insulator replacement at loc. 550 & 554.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.28264 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 524 | 185 | 96940 | 96056.1608 | 99.0883
20 | NR140137 | 400KV BALIA-PATNA-IV | 185 | NR3 | -- | 2017-01-13 09:47 | 2017-01-13 16:18 | -- | -- | -- | 0.27153 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for insulator cleaning and maintenance .
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.27153 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 524 | 185 | 96940 | 96090.9064 | 99.1241
21 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | 2017-01-07 00:15 | 2017-01-07 10:32 |  |  |  | 0 | 0 | 0 | 0.42847 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sohawal-429 kV
[6 empty] | 2017-01-14 07:43 | 2017-01-14 08:57 |  |  |  | 0.051389 | 0 | 0 | 0 |  |  |  | OSFT | Hand tripped due to NGR Buchaltz relay alarm at Balia.
[5 empty] | -- | 2017-01-23 15:40 | 2017-01-23 20:24 |  |  |  | 0.19722 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work of line element.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.24861 | 0 | 0 | 0.42847 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 51602.8155 | 99.198
22 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | 2017-01-23 22:14 | 2017-01-24 09:07 |  |  |  | 0 | 0 | 0 | 0.45347 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Sohawal-424kV
[5 empty] | -- | 2017-01-24 09:07 | 2017-01-24 18:45 |  |  |  | 0.40139 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.40139 | 0 | 0 | 0.45347 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 51346.4445 | 98.7052
23 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.45347 | -- | -- | -- |  |  |  | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
24 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.45347 | -- | -- | --
25 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
26 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
27 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- | 2017-01-20 10:51 | 2017-01-20 11:01 | -- | -- | -- | 0.0069444 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for taking L/R out, to attend hot spot in bushing at Brly.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.0069444 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 331 | 278.76 | 92269.56 | 92248.8903 | 99.9776
28 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | 2017-01-09 10:25 | 2017-01-09 11:38 |  |  |  | 0 | 0.050694 | 0 | 0 |  |  |  | OMSU | Line tripped on Y-B fault due to kite thread. FLR-BLY-11.8km, IF-19.17 KA, MRD-74.44 km
[6 empty] | 2017-01-10 17:50 | 2017-01-10 18:31 |  |  |  | 0.028472 | 0 | 0 | 0 |  |  |  | LPPT | Line tripped on R-B fault. FLR:BLY-11.6km, IF-17.2 KA, MRD-79.62 km
[6 empty] | 2017-01-27 01:57 | 2017-01-27 02:02 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection operated at Mrdbd end. DT received at Bareily end.
[6 empty] | 2017-01-27 02:02 | 2017-01-28 08:02 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:00 |  |  |  | LVRD | Line kept open for Voltage regulation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.028472 | 0.050694 | 0.0034722 | 1899-12-31 06:00 | -- | -- | -- |  |  |  | 743.9167 | 515 | 92.68 | 47730.2 | 47686.3569 | 99.9081
29 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | 2017-01-30 06:16 | 2017-01-30 06:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on Y-N fault, BLY=52.8km.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
30 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR3 |  | 2017-01-26 23:48 | 2017-01-26 23:53 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection operated at Rosa end. DT received at Bareily end.
[6 empty] | 2017-01-26 23:53 | 2017-01-27 12:41 |  |  |  | 0 | 0 | 0 | 0.53333 |  |  |  | LVRD | Line kept open for Voltage regulation.
[6 empty] | 2017-01-27 12:41 | 2017-01-27 19:35 |  |  |  | 0 | 0 | 0 | 0.2875 |  |  |  | OSFD | S/D by UPPCL to attend hot spot at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.0034722 | 0.82083 | [6 empty] | 743.9167 | 515 | 115.926 | 59701.89 | 59701.89 | 100
31 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 115.926 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
31 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 | 100
32 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 |  | 2017-01-23 12:34 | 2017-01-23 13:19 |  |  |  | 0 | 0.03125 | 0 | 0 |  |  |  | OMSU | Line A/R from Brly end and tripped from Kashipur end due to auto recloser problem at Kashipur end on R-N fault. FLR-Kashipur-9.5 km, If- 6.673 kAmp
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.03125 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
33 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
34 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2017-01-15 23:29 | 2017-01-16 07:36 | -- | -- | -- | 0 | 0 | 0 | 0.33819 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Mnp-422kV
[6 empty] | 2017-01-16 23:25 | 2017-01-17 10:12 |  |  |  | 0 | 0 | 0 | 0.44931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-17 10:12 | 2017-01-17 13:22 |  |  |  | 0.13194 | 0 | 0 | 0 |  |  |  | OSFT | S/D for faulty CVT replacement at Blbgrh.
[6 empty] | 2017-01-18 00:07 | 2017-01-18 06:52 |  |  |  | 0 | 0 | 0 | 0.28125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-427 kV
[6 empty] | 2017-01-18 23:09 | 2017-01-19 06:17 |  |  |  | 0 | 0 | 0 | 0.29722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-19 21:14 | 2017-01-20 07:09 |  |  |  | 0 | 0 | 0 | 0.41319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-24 21:07 | 2017-01-25 06:55 |  |  |  | 0 | 0 | 0 | 0.40833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-25 19:51 | 2017-01-26 09:07 |  |  |  | 0 | 0 | 0 | 0.55278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-26 14:58 | 2017-01-27 08:55 |  |  |  | 0 | 0 | 0 | 0.74792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV
[6 empty] | 2017-01-27 21:58 | 2017-01-28 06:21 |  |  |  | 0 | 0 | 0 | 0.34931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV
[6 empty] | 2017-01-28 23:24 | 2017-01-29 06:17 |  |  |  | 0 | 0 | 0 | 0.28681 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV
[6 empty] | 2017-01-29 23:18 | 2017-01-30 06:50 |  |  |  | 0 | 0 | 0 | 0.31389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-427kV
[6 empty] | 2017-01-30 22:04 | 2017-01-31 05:25 |  |  |  | 0 | 0 | 0 | 0.30625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-427kV
[6 empty] | 2017-01-01 | 2017-01-01 07:43 |  |  |  | 0 | 0 | 0 | 0.32153 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-432 kV. Open since 2347hrs on 31.12.16
[6 empty] | 2017-01-01 21:18 | 2017-01-02 07:24 |  |  |  | 0 | 0 | 0 | 0.42083 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-429kV
[6 empty] | 2017-01-02 23:18 | 2017-01-03 07:38 |  |  |  | 0 | 0 | 0 | 0.34722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-03 21:14 | 2017-01-04 06:13 |  |  |  | 0 | 0 | 0 | 0.37431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-04 21:06 | 2017-01-05 06:41 |  |  |  | 0 | 0 | 0 | 0.39931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-05 21:17 | 2017-01-06 07:03 |  |  |  | 0 | 0 | 0 | 0.40694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-06 21:51 | 2017-01-07 10:08 |  |  |  | 0 | 0 | 0 | 0.51181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-07 23:55 | 2017-01-08 08:36 |  |  |  | 0 | 0 | 0 | 0.36181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-08 15:04 | 2017-01-09 07:13 |  |  |  | 0 | 0 | 0 | 0.67292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-431 kV
[6 empty] | 2017-01-09 22:09 | 2017-01-10 06:45 |  |  |  | 0 | 0 | 0 | 0.35833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-10 23:40 | 2017-01-11 07:06 |  |  |  | 0 | 0 | 0 | 0.30972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-12 00:18 | 2017-01-12 06:05 |  |  |  | 0 | 0 | 0 | 0.24097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-13 00:08 | 2017-01-13 05:38 |  |  |  | 0 | 0 | 0 | 0.22917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-14 03:02 | 2017-01-14 03:05 |  |  |  | 0 | 0 | 0.0020833 | 0 |  |  |  | GOVC | Trip on O/VOL protn from Ballabgarh, BLB=435kv.
[6 empty] | 2017-01-14 03:05 | 2017-01-14 06:40 |  |  |  | 0 | 0 | 0 | 0.14931 |  |  |  | LVRD | Kept open on Voltage regulation, BLB=429kv.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.13194 | 0 | 0.0020833 | 1900-01-08 20:22 | -- | -- | -- |  |  |  | 743.95 | 515 | 235.952 | 121515.28 | 120998.0431 | 99.5743
35 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- | 2017-01-21 00:11 | 2017-01-21 06:11 | -- | -- |  | 0 | 0 | 0 | 0.25 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-21 21:14 | 2017-01-22 06:17 |  |  |  | 0 | 0 | 0 | 0.37708 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-22 21:02 | 2017-01-23 07:15 |  |  |  | 0 | 0 | 0 | 0.42569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-23 20:52 | 2017-01-24 06:29 |  |  |  | 0 | 0 | 0 | 0.40069 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-13 22:28 | 2017-01-14 06:48 |  |  |  | 0 | 0 | 0 | 0.34722 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-14 21:08 | 2017-01-15 07:19 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 05:24 | -- | -- | -- |  |  |  | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
36 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2017-01-01 | 2017-01-01 07:43 | -- | -- | -- | 0 | 0 | 0 | 0.32153 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP-432 kV. Open since 2348hrs on 31.12.16
[6 empty] | 2017-01-01 21:19 | 2017-01-02 07:24 |  |  |  | 0 | 0 | 0 | 0.42014 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-429kV
[6 empty] | 2017-01-03 21:07 | 2017-01-04 06:14 |  |  |  | 0 | 0 | 0 | 0.37986 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-04 21:06 | 2017-01-05 07:03 |  |  |  | 0 | 0 | 0 | 0.41458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-05 21:17 | 2017-01-06 07:05 |  |  |  | 0 | 0 | 0 | 0.40833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-06 21:52 | 2017-01-07 10:05 |  |  |  | 0 | 0 | 0 | 0.50903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-07 23:55 | 2017-01-08 08:26 |  |  |  | 0 | 0 | 0 | 0.35486 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-427 kV
[6 empty] | 2017-01-08 21:05 | 2017-01-09 07:14 |  |  |  | 0 | 0 | 0 | 0.42292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP-422 kV
[6 empty] | 2017-01-09 22:09 | 2017-01-10 06:45 |  |  |  | 0 | 0 | 0 | 0.35833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-10 23:40 | 2017-01-11 07:06 |  |  |  | 0 | 0 | 0 | 0.30972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-12 00:20 | 2017-01-12 06:07 |  |  |  | 0 | 0 | 0 | 0.24097 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-13 00:09 | 2017-01-13 05:37 |  |  |  | 0 | 0 | 0 | 0.22778 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-15 23:35 | 2017-01-16 07:38 |  |  |  | 0 | 0 | 0 | 0.33542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-422 kV
[6 empty] | 2017-01-16 23:24 | 2017-01-17 08:20 |  |  |  | 0 | 0 | 0 | 0.37222 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-18 23:12 | 2017-01-19 06:18 |  |  |  | 0 | 0 | 0 | 0.29583 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-19 21:14 | 2017-01-20 06:20 |  |  |  | 0 | 0 | 0 | 0.37917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-21 00:11 | 2017-01-21 06:12 |  |  |  | 0 | 0 | 0 | 0.25069 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-21 21:15 | 2017-01-22 06:15 |  |  |  | 0 | 0 | 0 | 0.375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-22 21:03 | 2017-01-23 07:16 |  |  |  | 0 | 0 | 0 | 0.42569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-23 20:51 | 2017-01-24 06:30 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-25 19:55 | 2017-01-26 09:11 |  |  |  | 0 | 0 | 0 | 0.55278 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[5 empty] | -- | 2017-01-26 14:58 | 2017-01-27 08:55 | -- | -- | -- | 0 | 0 | 0 | 0.74792 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV
[6 empty] | 2017-01-28 00:24 | 2017-01-28 06:10 |  |  |  | 0 | 0 | 0 | 0.24028 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV
[6 empty] | 2017-01-28 23:25 | 2017-01-29 06:16 |  |  |  | 0 | 0 | 0 | 0.28542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV
[6 empty] | 2017-01-30 22:03 | 2017-01-31 05:27 |  |  |  | 0 | 0 | 0 | 0.30833 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ftpr-423kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 08:08 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
37 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- | 2017-01-02 23:18 | 2017-01-03 07:37 | -- | -- | -- | 0 | 0 | 0 | 0.34653 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV
[6 empty] | 2017-01-13 22:28 | 2017-01-14 06:43 |  |  |  | 0 | 0 | 0 | 0.34375 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-14 21:09 | 2017-01-15 07:20 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV
[6 empty] | 2017-01-18 00:06 | 2017-01-18 06:52 |  |  |  | 0 | 0 | 0 | 0.28194 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-427 kV
[6 empty] | 2017-01-24 16:39 | 2017-01-24 17:20 |  |  |  | 0.028472 | 0 | 0 | 0 |  |  |  | OMST | Line tripped as DT received at Fathepur end.
[6 empty] | 2017-01-24 21:10 | 2017-01-25 06:55 |  |  |  | 0 | 0 | 0 | 0.40625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV
[6 empty] | 2017-01-29 23:18 | 2017-01-30 06:49 |  |  |  | 0 | 0 | 0 | 0.31319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ftpr-423kV
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.028472 | 0 | 0 | 1900-01-01 02:47 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 121851.9002 | 99.9082
38 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
39 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
40 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 291 | 240 | 69840 | 69840 | 100
41 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 72.6 | 37389 | 37389 | 100
42 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.2 | 37698 | 37698 | 100
43 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2017-01-03 21:00 | 2017-01-04 09:27 | -- | -- |  | 0 | 0 | 0 | 0.51875 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-04 21:01 | 2017-01-05 06:29 |  |  |  | 0 | 0 | 0 | 0.39444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-05 21:04 | 2017-01-06 06:57 |  |  |  | 0 | 0 | 0 | 0.41181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-09 01:44 | 2017-01-09 06:58 |  |  |  | 0 | 0 | 0 | 0.21806 |  |  |  | LVRD | Line hand tripped for Voltage regulation. KNP-429 kV
[6 empty] | 2017-01-10 01:03 | 2017-01-10 06:35 |  |  |  | 0 | 0 | 0 | 0.23056 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-430 kV
[6 empty] | 2017-01-15 23:59 | 2017-01-16 17:01 |  |  |  | 0 | 0 | 0 | 0.70972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV
[6 empty] | 2017-01-19 21:14 | 2017-01-20 06:24 |  |  |  | 0 | 0 | 0 | 0.38194 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-21 00:08 | 2017-01-21 06:07 |  |  |  | 0 | 0 | 0 | 0.24931 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-27 02:32 | 2017-01-27 02:37 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection operated at Blb end. DT received at Knp end. Blb>432 kV
[6 empty] | 2017-01-27 02:37 | 2017-01-27 04:04 |  |  |  | 0 | 0 | 0 | 0.060417 |  |  |  | LVRD | Line kept open for Voltage regulation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.0034722 | 1900-01-02 04:12 | -- | -- | -- |  |  |  | 743.9167 | 342 | 385.69 | 131905.98 | 131905.98 | 100
44 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- | 2017-01-14 21:11 | 2017-01-15 07:28 | -- | -- |  | 0 | 0 | 0 | 0.42847 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV
[6 empty] | 2017-01-21 21:08 | 2017-01-22 05:54 |  |  |  | 0 | 0 | 0 | 0.36528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-23 20:50 | 2017-01-24 08:02 |  |  |  | 0 | 0 | 0 | 0.46667 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-25 01:06 | 2017-01-25 07:01 |  |  |  | 0 | 0 | 0 | 0.24653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-27 00:05 | 2017-01-27 05:14 |  |  |  | 0 | 0 | 0 | 0.21458 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 17:19 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
45 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- | 2017-01-01 | 2017-01-01 07:56 | -- | -- | -- | 0 | 0 | 0 | 0.33056 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB-427 kV. Open since 2324hrs on 31.12.16
[6 empty] | 2017-01-01 21:22 | 2017-01-02 08:08 |  |  |  | 0 | 0 | 0 | 0.44861 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-02 20:58 | 2017-01-03 08:00 |  |  |  | 0 | 0 | 0 | 0.45972 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-06 21:47 | 2017-01-07 18:31 |  |  |  | 0 | 0 | 0 | 0.86389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-07 20:59 | 2017-01-08 08:43 |  |  |  | 0 | 0 | 0 | 0.48889 |  |  |  | LVRD | Line hand tripped for Voltage regulation. KNP-428 kV
[6 empty] | 2017-01-08 15:12 | 2017-01-09 10:00 |  |  |  | 0 | 0 | 0 | 0.78333 |  |  |  | LVRD | Line hand tripped for Voltage regulation. KNP-429 kV
[6 empty] | 2017-01-10 20:52 | 2017-01-11 07:58 |  |  |  | 0 | 0 | 0 | 0.4625 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV
[6 empty] | 2017-01-12 00:30 | 2017-01-12 08:29 |  |  |  | 0 | 0 | 0 | 0.33264 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-13 00:15 | 2017-01-13 07:40 |  |  |  | 0 | 0 | 0 | 0.30903 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV
[6 empty] | 2017-01-13 22:28 | 2017-01-14 06:15 |  |  |  | 0 | 0 | 0 | 0.32431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV
[6 empty] | 2017-01-15 21:29 | 2017-01-16 07:22 |  |  |  | 0 | 0 | 0 | 0.41181 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV
[6 empty] | 2017-01-16 23:29 | 2017-01-17 09:15 |  |  |  | 0 | 0 | 0 | 0.40694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV
[6 empty] | 2017-01-18 01:12 | 2017-01-18 08:03 |  |  |  | 0 | 0 | 0 | 0.28542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-429 kV
[6 empty] | 2017-01-19 00:09 | 2017-01-19 06:02 |  |  |  | 0 | 0 | 0 | 0.24514 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-22 21:04 | 2017-01-23 09:37 |  |  |  | 0 | 0 | 0 | 0.52292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-23 23:30 | 2017-01-24 06:45 |  |  |  | 0 | 0 | 0 | 0.30208 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV
[6 empty] | 2017-01-24 21:06 | 2017-01-25 10:06 |  |  |  | 0 | 0 | 0 | 0.54167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV
[6 empty] | 2017-01-25 21:02 | 2017-01-26 10:16 |  |  |  | 0 | 0 | 0 | 0.55139 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-418 kV
[6 empty] | 2017-01-26 20:34 | 2017-01-27 07:37 |  |  |  | 0 | 0 | 0 | 0.46042 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV
[6 empty] | 2017-01-27 21:56 | 2017-01-28 06:53 |  |  |  | 0 | 0 | 0 | 0.37292 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV
[6 empty] | 2017-01-28 23:22 | 2017-01-29 06:07 |  |  |  | 0 | 0 | 0 | 0.28125 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV
[6 empty] | 2017-01-29 23:24 | 2017-01-30 07:01 |  |  |  | 0 | 0 | 0 | 0.31736 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-429 kV
[6 empty] | 2017-01-30 22:12 | 2017-01-31 05:34 |  |  |  | 0 | 0 | 0 | 0.30694 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-429 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 19:26 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
46 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 107.079 | 55145.685 | 55145.685 | 100
47 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 107.1 | 55156.5 | 55156.5 | 100
48 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 5.922 | 3049.83 | 3049.83 | 100
49 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | 2017-01-23 18:04 | 2017-01-24 15:04 |  |  |  | 0 | 0 | 0 | 0.875 |  |  |  | OSFD | Line hand tripped by Panki end due to sparking in R-phase breaker at UPPCL end. DT received at KNP end .
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.875 | -- | -- | -- |  |  |  | 744 | 515 | 5.86 | 3017.9 | 3017.9 | 100
50 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- | 2017-01-08 00:33 | 2017-01-08 08:43 | -- | -- |  | 0 | 0 | 0 | 0.34028 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. LKO=435kv.
[6 empty] | 2017-01-28 12:02 | 2017-01-28 15:09 |  |  |  | 0.12986 | 0 | 0 | 0 |  |  |  | OSPT | S/D for jumpher tightening at loc. No. 202 by Gkp.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.12986 | 0 | 0 | 0.34028 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 75957.109 | 99.5811
51 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- | 2017-01-08 00:33 | 2017-01-08 08:50 | -- | -- | -- | 0 | 0 | 0 | 0.34514 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. LKO=435kv.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.34514 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
52 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
53 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
54 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
55 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR3 | -- | 2017-01-27 03:47 | 2017-01-27 03:52 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection operated at Rosa end. DT received at Lko end. Rosa>432 kV
[6 empty] | 2017-01-27 03:52 | 2017-01-27 12:41 |  |  |  | 0 | 0 | 0 | 0.36736 |  |  |  | LVRD | Line kept open for Voltage regulation.
[6 empty] | 2017-01-27 12:41 | 2017-01-27 19:28 |  |  |  | 0 | 0 | 0 | 0.28264 |  |  |  | OSFD | S/D by UPPCL to attend hot spot at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.0034722 | 0.65 | -- | -- | -- |  |  |  | 743.9167 | 371 | 169.785 | 62990.235 | 62990.235 | 100
56 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 |  | 2017-01-16 14:42 | 2017-01-16 15:10 |  |  |  | 0.019444 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking L/R in service at LKO end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.019444 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 169.729 | 87410.435 | 87355.6077 | 99.9373
57 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- | 2017-01-07 00:12 | 2017-01-07 10:14 | -- | -- | -- | 0 | 0 | 0 | 0.41806 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Sohawal-429 kV
[6 empty] | 2017-01-23 09:10 | 2017-01-23 15:18 |  |  |  | 0.25556 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP of line element and testing of SAS & SCADA at sohawla.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.25556 | 0 | 0 | 0.41806 | -- | -- | -- |  |  |  | 744 | 515 | 98.281 | 50614.715 | 50197.4611 | 99.1756
58 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  | 2017-01-25 09:17 | 2017-01-25 17:31 | -- | -- | -- | 0.34306 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for AMP work
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.34306 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50054.597 | 98.8934
59 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
60 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | 2017-01-18 08:37 | 2017-01-18 20:58 |  |  |  | 0 | 0 | 0 | 0.51458 |  |  |  | OSFD | S/D by UPPCL for replacement of broken conductor at Unnao S/Y.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.51458 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
61 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
62 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 30.703 | 21215.773 | 21215.773 | 100
63 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 31.159 | 21530.869 | 21530.869 | 100
64 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- | 2017-01-12 09:15 | 2017-01-12 18:47 | -- | -- | -- | 0.39722 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for insulator cleaning and maintenance .
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.39722 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 119363.7507 | 98.7186
65 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | 2017-01-11 10:08 | 2017-01-11 19:02 |  |  |  | 0.37083 | 0 | 0 | 0 |  |  |  | OSPT | S/D for insulator cleaning and maintenance .
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.37083 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 119466.6785 | 98.8038
66 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 210 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 368 | 210 | 77280 | 77280 | 100
67 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 210 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 368 | 210 | 77280 | 77280 | 100
68 | NR140090 | 400KV SASARAM-SARNATH | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 76 | 39140 | 39140 | 100
| NR340003 | 400KV VARANASI-SASARAM(ER) | 47.52 | NR3 | -- | 2017-01-20 09:27 | 2017-01-20 15:40 | -- | -- | -- | 0.25903 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D by ER for for attending hot spot in isolator at their end.
[6 empty] | 2017-01-25 09:18 | 2017-01-25 19:07 |  |  |  | 0.40903 | 0 | 0 | 0 |  |  |  | OSFT | S/D by ER for isolator rectification work at Sasaram
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.66806 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 47.52 | 24472.8 | 23945.4068 | 97.845
69 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | 2017-01-03 09:39 | 2017-01-03 18:38 |  |  |  | 0.37431 | 0 | 0 | 0 |  |  |  | OSPT | S/D for Insulator cleaning and AMP work
[6 empty] | 2017-01-03 18:38 | 2017-01-03 21:22 |  |  |  | 0 | 0 | 0 | 0.11389 |  |  |  | OSPD | S/D continued by Singrauli NTPC for CT testing work.
[6 empty] | 2017-01-04 09:43 | 2017-01-04 18:24 |  |  |  | 0.36181 | 0 | 0 | 0 |  |  |  | OSPT | S/D for Insulator cleaning and AMP work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.73611 | 0 | 0 | 0.11389 | -- | -- | -- |  |  |  | 744 | 332 | 224 | 74368 | 72602.0932 | 97.6254
70 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | 2017-01-05 08:15 | 2017-01-05 18:46 |  |  |  | 0.43819 | 0 | 0 | 0 |  |  |  | OSPT | S/D for Insulator cleaning and AMP work
[6 empty] | 2017-01-05 08:15 | 2017-01-05 18:46 |  |  |  | 0.43819 | 0 | 0 | 0 |  |  |  | OSPT | S/D for Insulator cleaning and AMP work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.87639 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 306 | 202 | 61812 | 60064.5371 | 97.1729
71 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- | 2017-01-02 00:15 | 2017-01-02 02:10 | -- | -- | -- | 0 | 0 | 0.079861 | 0 | -- | -- | -- | LNCC | Tripped on R-N fault during dense fog, FLR:Sing-N/a. Anpara-1.3km.
[6 empty] | 2017-01-23 17:09 | 2017-01-23 19:50 |  |  |  | 0.11181 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken by NTPC for testing of PLCC.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.11181 | 0 | 0.079861 | 0 | -- | -- | -- |  |  |  | 742.0833 | 515 | 25.057 | 12904.355 | 12857.6935 | 99.6384
72 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 236 | 330.953 | 78104.908 | 78104.908 | 100
73 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- | 2017-01-07 10:34 | 2017-01-07 18:15 | -- | -- |  | 0.32014 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for insulator cleaning and other maintenance work in line. PTW returned by PG at 17:30 hrs.
[6 empty] | 2017-01-07 18:15 | 2017-01-07 21:32 |  |  |  | 0 | 0 | 0 | 0.13681 |  |  |  | OSFD | S/D continued by Sing NTPC for CT testing work.
[6 empty] | 2017-01-08 09:34 | 2017-01-08 19:23 | -- | -- |  | 0.40903 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for insulator cleaning and other maintenance work in line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.72917 | 0 | 0 | 0.13681 | -- | -- | -- |  |  |  | 744 | 337 | 408.6 | 137698.2 | 134459.331 | 97.6478
74 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 42.026 | 21643.39 | 21643.39 | 100
75 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- | 2017-01-02 00:33 | 2017-01-02 01:09 | -- | -- |  | 0 | 0 | 0.025 | 0 | -- | -- | -- | LNCC | Tripped on R-N fault during dense fog. FLR:Sing-15km, Rhnd-25km
[6 empty] | 2017-01-09 07:36 | 2017-01-09 09:17 |  |  |  | 0.070139 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped on R-N fault. FLR:Rh-24.8 km, Sing-12.5km
[6 empty] | 2017-01-09 19:40 | 2017-01-09 20:38 |  |  |  | 0 | 0.040278 | 0 | 0 |  |  |  | OMSU | A/R from Sing but tripped from Rihand-NTPC due to A/R problem on R-N fault. FLR:Sing-16.83km, Rhnd-24.7km
[6 empty] | 2017-01-10 11:08 | 2017-01-10 17:05 |  |  |  | 0.24792 | 0 | 0 | 0 |  |  |  | OSFT | S/D for damage Insulator replacement.
[6 empty] | 2017-01-10 17:05 | 2017-01-10 18:29 | -- | -- |  | 0 | 0 | 0 | 0.058333 | -- | -- | -- | OSFD | S/D continued by Rihand (NTPC) for relay testing work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.31806 | 0.040278 | 0.025 | 0.058333 | [6 empty] | 743.4 | 515 | 43.952 | 22635.28 | 22402.8578 | 98.9732
76 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 3.341 | 1720.615 | 1720.615 | 100
77 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | 2017-01-19 10:40 | 2017-01-19 22:54 |  |  |  | 0 | 0 | 0 | 0.50972 |  |  |  | SCSD | S/D for retrofitmet of PLCC & LMU at Vindh PG.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.50972 | -- | -- | -- |  |  |  | 744 | 515 | 3.317 | 1708.255 | 1708.255 | 100
78 | NR140164 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | 2017-01-01 08:40 | 2017-01-03 12:51 |  |  |  | 0 | 0 | 0 | 1900-01-01 04:11 |  |  |  | LPRD | Line hand tripped for Power regulation
[6 empty] | 2017-01-05 12:50 | 2017-01-05 13:24 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OMSU | Tripped due to CVT fuse fail at Sarnath/UPPCL end.
[6 empty] | 2017-01-11 14:03 | 2017-01-17 08:54 |  |  |  | 0 | 0 | 0 | 1900-01-04 18:51 |  |  |  | LPRD | Line hand tripped for Power regulation.
[6 empty] | 2017-01-23 01:15 | 2017-01-23 02:24 |  |  |  | 0.047917 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault FLR 2.5 Km from Vrnsi.
[6 empty] | 2017-01-27 06:47 | 2017-01-27 07:11 |  |  |  | 0.016667 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault, FLR, Vrns-2.5km
[6 empty] | 2017-01-28 11:35 | 2017-01-28 17:39 |  |  |  | 0.25278 | 0 | 0 | 0 |  |  |  | OSPT | S/D for tightening of OPGW wire by VNS T/L.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.31736 | 0 | 0 | 1900-01-06 23:02 | -- | -- | -- |  |  |  | 744 | 515 | 69.677 | 35883.655 | 35516.2977 | 98.9763
79 | NR140165 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | 2017-01-01 09:17 | 2017-01-11 18:42 |  |  |  | 0 | 0 | 0 | 1900-01-09 09:25 |  |  |  | LPRD | Line hand tripped for Power regulation
[6 empty] | 2017-01-16 08:35 | 2017-01-16 08:50 |  |  |  | 0 | 0.010417 | 0 | 0 |  |  |  | OMSU | CB A/trip at Sarnath-UP end only due to local problem. Line remain charged from VNS end. No flag Facia reported.
[6 empty] | 2017-01-16 16:58 | 2017-01-22 11:17 |  |  |  | 0 | 0 | 0 | 1900-01-04 18:19 |  |  |  | OSPD | S/D by UPPCL for attending CB air leakage at Sarnath end.
[6 empty] | 2017-01-27 06:47 | 2017-01-27 11:54 |  |  |  | 0 | 0.21319 | 0 | 0 |  |  |  | OMSU | CB auto tripped only from Sarnath(UPPCL) end. Remain charged from Vrnsi end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.22361 | 0 | 1900-01-15 03:44 | -- | -- | -- |  |  |  | 744 | 515 | 69.677 | 35883.655 | 35883.655 | 100
80 | N-W40004 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
81 | N-W40004 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
10 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
11 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- | 2017-01-13 12:07 | 2017-01-13 15:27 | -- | -- |  | 0 | 0 | 0 | 0.13889 | -- | -- | -- | OSPD | S/D by Dhganga-NHPC to attend CB problem.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.13889 | -- | -- | -- |  |  |  | 744 | 109 | 234.59 | 25570.31 | 25570.31 | 100
17 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- | 2017-01-07 01:03 | 2017-01-07 07:21 | -- | -- | -- | 0 | 0 | 0.2625 | 0 | -- | -- | -- | GOVC | Trip on O/VOL protn at Dhauliganga-NHPC, D/T recd at Pithoragh. D,ganga=238kv.
[6 empty] | 2017-01-26 22:32 | 2017-01-26 22:37 |  |  |  | 0 | 0 | 0.0034722 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection operated at Dganga end. DT received at Pthrgrh end.
[6 empty] | 2017-01-26 22:37 | 2017-01-27 08:04 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | LVRD | Line kept open for Voltage regulation.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.26597 | 0.39375 | -- | -- | -- |  |  |  | 737.6167 | 156 | 59.01 | 9205.56 | 9205.56 | 100
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- | 2017-01-28 11:38 | 2017-01-28 16:33 | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | OSPD | S/D by UPPCL to attend burnt isolator at their end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- | 2017-01-16 08:56 | 2017-01-16 15:07 | -- | -- |  | 0 | 0 | 0 | 0.25764 | -- | -- | -- | OSFD | Line hand tripped by UPPCL due to melting of R-ph isolator contact at their end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.25764 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | 2017-01-07 12:26 | 2017-01-07 17:02 |  |  |  | 0 | 0 | 0 | 0.19167 |  |  |  | OSPD | S/D by UPPCL for maintenance work at KNP(S) end.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.19167 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
21 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | 2017-01-01 14:00 | 2017-01-01 15:42 |  |  |  | 0 | 0.070833 | 0 | 0 |  |  |  | OMSU | Tripped on R-Y fault in UPPCL portion, FLR:Fthpr-73 km, Naubasta-3.4km.
[6 empty] | 2017-01-07 11:01 | 2017-01-07 13:49 |  |  |  | 0 | 0 | 0 | 0.11667 |  |  |  | OSPD | S/D by UPPCL for maintenance work at Naubasta end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.070833 | 0 | 0.11667 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
28 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- | 2017-01-12 17:26 | 2017-01-12 20:32 |  |  | -- | 0 | 0 | 0 | 0.12917 | -- | -- | -- | OSFD | S/D taken by UPPCL for maintenance at Mainpuri end.
[6 empty] | 2017-01-18 13:00 | 2017-01-18 18:45 |  |  |  | 0 | 0 | 0 | 0.23958 |  |  |  | LCSD | S/D for stringing of new 400kV Lucknow-Kanpur D/C line.
[6 empty] | 2017-01-19 13:20 | 2017-01-19 19:31 |  |  |  | 0 | 0 | 0 | 0.25764 |  |  |  | LCSD | S/D for stringing of new 400kV Lucknow-Kanpur D/C line.
[5 empty] | -- | 2017-01-20 13:24 | 2017-01-20 19:26 | -- | -- | -- | 0 | 0 | 0 | 0.25139 | -- | -- | -- | LCSD | S/D for stringing of new 400kV Lucknow-Kanpur D/C line.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.87778 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
29 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
30 | NR122018 | 220KV KNP-PANKI-I | 10.4 | NR3 | -- | 2017-01-27 03:34 | 2017-01-27 05:19 | -- | -- | -- | 0.072917 | 0 | 0 | 0 | -- | -- | -- | LART | A/R from Knp end & tripped at Panki end, FLR, Panki- 5.29 km.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.072917 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1359.1954 | 99.7648
31 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
32 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
33 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
34 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
35 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
42 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | 2017-01-09 15:35 | 2017-01-09 17:01 |  |  |  | 0 | 0.059722 | 0 | 0 |  |  |  | OMSU | Line tripped on R-Y fault in Z-2. Fault in UP system. FLR-PTH-178.7Km (Line length-177.7km)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.059722 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 156 | 177.88 | 27749.28 | 27749.28 | 100
43 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
44 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR3 | -- | 2017-01-03 03:50 | 2017-01-03 05:11 |  |  |  | 0 | 0.05625 | 0 | 0 |  |  |  | OMSU | CB auto tripped at Lko(UP) end due to disturbance in UPPCL system. Line remain charged from Raibareilly.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.05625 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
54 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 105.72 | 13955.04 | 13955.04 | 100
55 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | 2017-01-27 03:45 | 2017-01-27 07:13 |  |  |  | 0 | 0 | 0.14444 | 0 |  |  |  | GOVC | Tripped on Over Voltage protection operated at Tanakpur end. DT received at Bareily end.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.14444 | 0 | -- | -- | -- |  |  |  | 740.5333 | 132 | 106 | 13992 | 13992 | 100
56 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 42.55 | 5616.6 | 5616.6 | 100
57 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
58 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
59 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 42.5 | 5610 | 5610 | 100
[5 empty] | -- | [17 empty] | 1831.389
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 | 58 | 2900 | 2900 | 100
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-06 23:08 | 0.53264 | 1899-12-31 14:09 | 1900-10-02 02:14 | [8 empty] | 19666.447 | 10751535.6 | 10722292.2465 | 99.728 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.843 | % (AC) | 99.557 | %'(HVDC)
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
7 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS) | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
8 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS) | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
9 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
10 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- | 2017-01-13 09:32 | 2017-01-13 15:55 | -- | -- |  | 0 | 0 | 0 | 0.26597 | -- | -- | -- | SCSD | S/D for replace m,ent of R-ph with spare unit.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.26597 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
13 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- | 2017-01-12 10:47 | 2017-01-12 11:51 | -- | -- |  | 0 | 0 | 0 | 0.044444 | -- | -- | -- | LVRD | S/D for tap changing for V/regulation by NRLDC instruction.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.044444 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
14 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- | 2017-01-12 11:58 | 2017-01-12 12:31 | -- | -- |  | 0 | 0 | 0 | 0.022917 | -- | -- | -- | LVRD | S/D for tap changing for V/regulation by NRLDC instruction.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.022917 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 |  | 2017-01-08 16:48 | 2017-01-08 19:11 |  |  |  | 0.099306 | 0 | 0 | 0 | -- | -- | -- | OMST | ICT tripped on PRD operation.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.099306 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1495.1949 | 99.6797
16 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 |  | 2017-01-17 16:52 | 2017-01-17 17:04 |  |  |  | 0.0083333 | 0 | 0 | 0 | -- | -- | -- | OSFT | S/D for topping of SF-6 Gas in 33 kV tertiary Breaker.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.0083333 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1499.5968 | 99.9731
F |  | 400/220 KV ICT'S |  | NR3 | --
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | 2017-01-11 13:20 | 2017-01-11 14:37 |  |  |  | 0 | 0 | 0 | 0.053472 |  |  |  | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. |  | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | 2017-01-11 14:39 | 2017-01-11 14:52 |  |  |  | 0 | 0 | 0 | 0.0090278 |  |  |  | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. |  | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 |  | 2017-01-11 14:55 | 2017-01-11 15:10 |  |  |  | 0 | 0 | 0 | 0.010417 |  |  |  | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. |  | 744 | 315 |  | 315 | 315 | 100
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | 2017-01-04 21:06 | 2017-01-04 21:42 |  |  |  | 0.025 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to 400KV Bus Bar-II protection operated during opening of 400KV BLB and FTPR-I line for V/regulation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.025 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 314.746 | 99.9194
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.025 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 314.746 | 99.9194
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR3 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | 2017-01-27 02:32 | 2017-01-27 09:12 |  |  |  | 0 | 0 | 0.27778 | 0 |  |  |  | GOFC | ICT trippings on Over Fluxing.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.27778 | 0 | -- | -- | -- |  |  |  | 737.3333 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | 2017-01-27 03:20 | 2017-01-27 09:12 |  |  |  | 0 | 0 | 0.24444 | 0 |  |  |  | GOFC | ICT trippings on Over Fluxing. |  | 738.1333 | 100 |  | 100 | 100 | 100
[11 empty] | 0 | 0 | 0.24444 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
--
41 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 0.29028 | 0 | 1899-12-31 01:04 | 0.73958 | [7 empty] | 30925 |  | 30925 | 30919.2836 | 99.9815 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2017-01-02 00:43 | 2017-01-02 00:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | DC line transient fault. FLR:Rihand-0.77km, Dad-814.23km
[6 empty] | 2017-01-02 00:44 | 2017-01-02 01:54 |  |  |  | 0.048611 | 0 | 0 | 0 |  |  |  | OMST | Tripped on DC line differential protection during dense fog.
[6 empty] | 2017-01-30 06:12 | 2017-01-30 06:12 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | T/Fault, Rh=152.96km, DDR=662.04km.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.048611 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 610291.4987 | 99.8432
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2017-12-06 07:12 | 2017-12-06 07:12 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | DC line transient Fault, Rh=527.14km, DDR=287.86km.
[6 empty] | 2017-01-27 06:16 | 2017-01-27 06:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FLR, Rhnd-445.7 km, Dad-445.7km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 611250 | 100
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | 2017-01-27 03:45 | 2017-01-27 03:45 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FLR BWD-341.420 km, Balia- 448.37 km, Faulty loc-1229
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2017-01-18 20:36 | 2017-01-18 20:36 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. Balia-223.14km, Bwd-566.4km, loc-612.
[6 empty] | 2017-01-29 21:45 | 2017-01-29 21:45 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | T/Fault, FLR: BWD=26.45km, Balia=763.33km
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
4 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2017-01-05 12:41 | 2017-01-09 08:10 |  |  |  | 0 | 0 | 0 | 1900-01-02 19:29 |  |  |  | LVRD | Line hand tripped for Voltage regulation in NER-BNC end.
[6 empty] | 2017-01-11 09:01 | 2017-01-31 12:04 |  |  |  | 0 | 0 | 0 | 1900-01-19 03:03 |  |  |  | LVRD | Line kept open for Voltage regulation due to high voltage at BNC
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-22 22:32 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2592000 | 100
1 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | 2017-01-01 | 2017-01-05 11:39 |  |  |  | 0 | 0 | 0 | 1900-01-03 11:39 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Open since 1315hrs on 22.12.16
[6 empty] | 2017-01-05 15:32 | 2017-01-05 16:04 |  |  |  | 0.022222 | 0 | 0 | 0 |  |  |  | OMST | Trip due to auxiliary supply problem in Valve cooling system at BNC end.
[6 empty] | 2017-01-09 07:33 | 2017-01-09 14:34 |  |  |  | 0.29236 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to auxilary Supply Failure at BNC end.
[6 empty] | 2017-01-09 14:34 | 2017-01-11 09:10 |  |  |  | 0 | 0 | 0 | 1899-12-31 18:36 |  |  |  | LVRD | Kept open for Voltage regulation due to high voltage at BNC
[6 empty] | 2017-01-30 12:41 | 2017-01-30 13:35 |  |  |  | 0.0375 | 0 | 0 | 0 |  |  |  | OMST | Trip on DC line fault at Agra end.
[6 empty] | 2017-01-30 13:45 | 2017-01-30 14:35 |  |  |  | 0.034722 | 0 | 0 | 0 |  |  |  | OSFT | Force S/D due to sparking observed on electrode line at Ag.
[6 empty] | 2017-01-31 10:44 | 2017-02-01 |  |  |  | 0 | 0 | 0 | 0.55278 |  |  |  | LVRD | Hand tripped for V/regulation due to NER grid voltage high.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.38681 | 0 | 0 | 1900-01-05 19:31 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2559658.0645 | 98.7522
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0.43542 | 0 | 0 | 1900-01-29 18:03 | 0 | 0 | 0 | [5 empty] | 6665.572 | 8380965 | 8347664.5632 | 99.6027 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2017-01-20 17:10 | 2017-01-21 01:48 |  |  |  | 0.35972 | 0 | 0 | 0 |  |  |  | OMST | Block tripped on DC over current protection.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.35972 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 247.099 | 98.8396
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 0.35972 | 0 | 0 | 0 | [9 empty] | 500 | 497.099 | 99.4198 | %
HVDC BTB SASARAM
| NEDCB01 | +/-500MW HVDC B/B SASARAM | 500 |  |  | 2017-01-10 06:39 | 2017-01-10 07:42 |  |  |  | 0.04375 | 0 | 0 | 0 |  |  |  | OMST | TRIPPED DUE TO FAILURE OF VALVE COOLING SYSTEM.
[6 empty] | 2017-01-10 08:02 | 2017-01-10 12:52 |  |  |  | 0.20139 | 0 | 0 | 0 |  |  |  | OMST | BLOCKED DUE TO AUXILIARY POWER UNBALANCE SUPPLY
[6 empty] | 2017-01-10 13:23 | 2017-01-12 11:44 |  |  |  | 1899-12-31 22:21 | 0 | 0 | 0 |  |  |  | OMST | BLOCKED DUE TO AUXILIARY POWER UNBALANCE SUPPLY
[6 empty] | 2017-01-12 13:36 | 2017-01-12 15:06 |  |  |  | 0.0625 | 0 | 0 | 0 |  |  |  | OMST | BLOCKED DUE TO AUXILIARY POWER UNBALANCE SUPPLY
[6 empty] | 2017-01-14 05:03 | 2017-01-14 09:00 |  |  |  | 0.16458 | 0 | 0 | 0 |  |  |  | OMST | BLOCKED DUE TO SYS FAIL ALARM.
|  | TOTAL FOR HVDC SASARAM | [8 empty] | 1900-01-01 09:41 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 461.2343 | 92.2469
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 530 | 530 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY | 50 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 50 | NR3 | -- | 2017-01-21 12:15 | 2017-01-21 13:33 |  |  |  | 0.054167 | 0 | 0 | 0 |  |  |  | OSFT | Forcely open to attend sparking in R ph isolator.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.054167 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 239.5806 | 99.8253
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
20 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | 2017-01-01 10:18 | 2017-01-01 19:55 |  |  |  | 0 | 0 | 0 | 0.40069 |  |  |  | SVRD | H/ tripped for voltage regulation<755kv. (Standing Instrn)
[6 empty] | 2017-01-04 10:10 | 2017-01-04 21:20 |  |  |  | 0 | 0 | 0 | 0.46528 |  |  |  | SVRD | H/ tripped for voltage regulation<755kv. (Standing Instrn)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.86597 | -- | -- | -- |  |  |  | 744 | 330 |  | 330 | 330 | 100
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 125 |  | 125 | 125 | 100
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
28 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 240 |  | 240 | 240 | 100
29 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
30 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
31 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
32 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
33 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
34 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
35 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
36 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
37 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
38 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
39 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
40 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
41 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
42 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
43 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
44 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
45 | NR1SRT24 | GORAKH 80MVAR S/R BARH-I LINE | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
46 | NR1SRT25 | GORAKH 80MVAR S/R BARH-II LINE | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
47 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
48 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
49 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
50 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
51 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
52 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
53 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
54 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
55 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
56 | NR1BRT51 | 330MVAR B/Reactor-II VARANASI | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0.10833 | 0 | 0 | 1899-12-31 17:34 | [9 empty] | 8068.4 | 8067.9806 | 99.9948 | %
|  | TOTAL | [8 empty] | 1900-01-08 03:47 | 0.53264 | 1900-01-01 15:13 | 1900-11-04 07:36
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L11:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M11:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N11:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O11:[Deemed Available, row above])
Note on C11: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C67: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C70: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C75: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C94: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C98: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C252: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C255: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C493: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C500: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C676: DOC-15/06/14
Note on C677: DOC-26/09/14

## Sheet1
POWER GRID CORPORATION OF INDIA LTD.
NORTHERN REGION - 1
CPCC, N. DELHI
DOC No: NR-I/CPCC/II
MONTH – JAN-2017 LINE/ ICT OUTAGE DETAILS
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Classification/ Category Code | REASON OF OUTAGE | NRLDC CODE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Code
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12
NEDCB01 | ** | +/-500MW HVDC B/B SASARAM | 2017-01-10 06:39 | 2017-01-10 07:42 | 0.04375 | 0 | 0 | 0 | OMST | TRIPPED DUE TO FAILURE OF VALVE COOLING SYSTEM.
NEDCB01 | ** | +/-500MW HVDC B/B SASARAM | 2017-01-10 08:02 | 2017-01-10 12:52 | 0.20139 | 0 | 0 | 0 | OMST | BLOCKED DUE TO AUXILIARY POWER UNBALANCE SUPPLY
NEDCB01 | ** | +/-500MW HVDC B/B SASARAM | 2017-01-10 13:23 | 2017-01-12 11:44 | 1899-12-31 22:21 | 0 | 0 | 0 | OMST | BLOCKED DUE TO AUXILIARY POWER UNBALANCE SUPPLY
NEDCB01 | ** | +/-500MW HVDC B/B SASARAM | 2017-01-12 13:36 | 2017-01-12 15:06 | 0.0625 | 0 | 0 | 0 | OMST | BLOCKED DUE TO AUXILIARY POWER UNBALANCE SUPPLY
NEDCB01 | ** | +/-500MW HVDC B/B SASARAM | 2017-01-14 05:03 | 2017-01-14 09:00 | 0.16458 | 0 | 0 | 0 | OMST | BLOCKED DUE TO SYS FAIL ALARM.
|  | 500MW HVDC B/B SASARAM Total |  |  | 1900-01-01 09:41 | 0 | 0 | 0
NR1DCB01 | 101409 | VINDH HVDC B/B BLOCK-I | 2017-01-20 17:10 | 2017-01-21 01:48 | 0.35972 | 0 | 0 | 0 | OMST | Block tripped on DC over current protection.
|  | VINDH HVDC B/B BLOCK-I Total |  |  | 0.35972 | 0 | 0 | 0
NRNEDCP01 | 101094 | 800KV HVDC AGRA-BNC POLE-I | 2017-01-05 12:41 | 2017-01-09 08:10 | 0 | 0 | 0 | 1900-01-02 19:29 | LVRD | Line hand tripped for Voltage regulation in NER-BNC end. | N-435
NRNEDCP01 | 101220 | 800KV HVDC AGRA-BNC POLE-I | 2017-01-11 09:01 | 2017-01-31 12:04 | 0 | 0 | 0 | 1900-01-19 03:03 | LVRD | Line kept open for Voltage regulation due to high voltage at BNC | N-1132
|  | 800KV HVDC AGRA-BNC POLE-I Total |  |  | 0 | 0 | 0 | 1900-01-22 22:32
NRNEDCP02 | 112518 | 800KV HVDC AGRA-BNC POLE-II | 2017-01-01 | 2017-01-05 11:39 | 0 | 0 | 0 | 1900-01-03 11:39 | LVRD | Line hand tripped for Voltage regulation. Open since 1315hrs on 22.12.16 | N-3753
NRNEDCP02 | 101096 | 800KV HVDC AGRA-BNC POLE-II | 2017-01-05 15:32 | 2017-01-05 16:04 | 0.022222 | 0 | 0 | 0 | OMST | Trip due to auxiliary supply problem in Valve cooling system at BNC end.
NRNEDCP02 | 101185 | 800KV HVDC AGRA-BNC POLE-II | 2017-01-09 07:33 | 2017-01-09 14:34 | 0.29236 | 0 | 0 | 0 | OMST | Tripped due to auxilary Supply Failure at BNC end.
NRNEDCP02 | 101189 | 800KV HVDC AGRA-BNC POLE-II | 2017-01-09 14:34 | 2017-01-11 09:10 | 0 | 0 | 0 | 1899-12-31 18:36 | LVRD | Kept open for Voltage regulation due to high voltage at BNC | N-977
NRNEDCP02 | 101655 | 800KV HVDC AGRA-BNC POLE-II | 2017-01-30 12:41 | 2017-01-30 13:35 | 0.0375 | 0 | 0 | 0 | OMST | Trip on DC line fault at Agra end.
NRNEDCP02 | 101658 | 800KV HVDC AGRA-BNC POLE-II | 2017-01-30 13:45 | 2017-01-30 14:35 | 0.034722 | 0 | 0 | 0 | OSFT | Force S/D due to sparking observed on electrode line at Ag.
NRNEDCP02 | 101671 | 800KV HVDC AGRA-BNC POLE-II | 2017-01-31 10:44 | 2017-02-01 | 0 | 0 | 0 | 0.55278 | LVRD | Hand tripped for V/regulation due to NER grid voltage high. | N-3179
|  | 800KV HVDC AGRA-BNC POLE-II Total |  |  | 0.38681 | 0 | 0 | 1900-01-05 19:31
NR1DCP01 | 101030 | 500KV HVDC R-D POLE-I | 2017-01-02 00:43 | 2017-01-02 00:43 | 0 | 0 | 0 | 0 | LART | DC line transient fault. FLR:Rihand-0.77km, Dad-814.23km
NR1DCP01 | 101031 | 500KV HVDC R-D POLE-I | 2017-01-02 00:44 | 2017-01-02 01:54 | 0.048611 | 0 | 0 | 0 | OMST | Tripped on DC line differential protection during dense fog.
NR1DCP01 | 101652 | 500KV HVDC R-D POLE-I | 2017-01-30 06:12 | 2017-01-30 06:12 | 0 | 0 | 0 | 0 | LART | T/Fault, Rh=152.96km, DDR=662.04km.
|  | 500KV HVDC R-D POLE-I Total |  |  | 0.048611 | 0 | 0 | 0
NR1DCP02 | 101107 | 500KV HVDC R-D POLE-II | 2017-12-06 07:12 | 2017-12-06 07:12 | 0 | 0 | 0 | 0 | LART | DC line transient Fault, Rh=527.14km, DDR=287.86km.
NR1DCP02 | 101597 | 500KV HVDC R-D POLE-II | 2017-01-27 06:16 | 2017-01-27 06:16 | 0 | 0 | 0 | 0 | LART | Transient fault. FLR, Rhnd-445.7 km, Dad-445.7km
|  | 500KV HVDC R-D POLE-II Total |  |  | 0 | 0 | 0 | 0
NR1DCP03 | 101589 | 500KV HVDC BALIA-BHWD POLE-I | 2017-01-27 03:45 | 2017-01-27 03:45 | 0 | 0 | 0 | 0 | LART | Transient fault. FLR BWD-341.420 km, Balia- 448.37 km, Faulty loc-1229
|  | 500KV HVDC BALIA-BHWD POLE-I Total |  |  | 0 | 0 | 0 | 0
NR1DCP04 | 101373 | 500KV HVDC BALIA-BHWD POLE-II | 2017-01-18 20:36 | 2017-01-18 20:36 | 0 | 0 | 0 | 0 | LART | Transient fault. Balia-223.14km, Bwd-566.4km, loc-612.
NR1DCP04 | 101644 | 500KV HVDC BALIA-BHWD POLE-II | 2017-01-29 21:45 | 2017-01-29 21:45 | 0 | 0 | 0 | 0 | LART | T/Fault, FLR: BWD=26.45km, Balia=763.33km
|  | 500KV HVDC BALIA-BHWD POLE-II Total |  |  | 0 | 0 | 0 | 0
NR176502 | 101048 | 765KV AGRA-FATEHPUR-I | 2017-01-02 23:44 | 2017-01-03 08:30 | 0 | 0 | 0 | 0.36528 | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV | N-187
NR176502 | 101202 | 765KV AGRA-FATEHPUR-I | 2017-01-10 01:12 | 2017-01-10 06:49 | 0 | 0 | 0 | 0.23403 | LVRD | Line hand tripped for Voltage regulation. Agra-789 kV | N-986
NR176502 | 101239 | 765KV AGRA-FATEHPUR-I | 2017-01-12 00:25 | 2017-01-12 06:12 | 0 | 0 | 0 | 0.24097 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-1214
NR176502 | 101259 | 765KV AGRA-FATEHPUR-I | 2017-01-12 21:09 | 2017-01-13 06:29 | 0 | 0 | 0 | 0.38889 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-1314
NR176502 | 101284 | 765KV AGRA-FATEHPUR-I | 2017-01-14 00:16 | 2017-01-14 07:37 | 0 | 0 | 0 | 0.30625 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-1415
NR176502 | 101344 | 765KV AGRA-FATEHPUR-I | 2017-01-17 01:32 | 2017-01-17 08:16 | 0 | 0 | 0 | 0.28056 | LVRD | Line hand tripped for Voltage regulation. Ftpr-802kV | N-1701
NR176502 | 101482 | 765KV AGRA-FATEHPUR-I | 2017-01-24 01:04 | 2017-01-24 06:59 | 0 | 0 | 0 | 0.24653 | LVRD | Line hand tripped for Voltage regulation. Agra-781 kV | N-2361
NR176502 | 101538 | 765KV AGRA-FATEHPUR-I | 2017-01-26 01:38 | 2017-01-27 05:14 | 0 | 0 | 0 | 1899-12-31 03:36 | LVRD | Line hand tripped for Voltage regulation. Agra-793kV | N-2601
|  | 765KV AGRA-FATEHPUR-I Total |  |  | 0 | 0 | 0 | 1900-01-02 05:06
NR176507 | 101007 | 765KV AGRA-FATEHPUR-II | 2017-01-01 01:21 | 2017-01-01 07:29 | 0 | 0 | 0 | 0.25556 | LVRD | Line hand tripped for Voltage regulation. Agra-798 kV | N-15
NR176507 | 101025 | 765KV AGRA-FATEHPUR-II | 2017-01-01 23:40 | 2017-01-02 07:30 | 0 | 0 | 0 | 0.32639 | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV | N-93
NR176507 | 101073 | 765KV AGRA-FATEHPUR-II | 2017-01-03 21:37 | 2017-01-04 08:12 | 0 | 0 | 0 | 0.44097 | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV | N-280
NR176507 | 101091 | 765KV AGRA-FATEHPUR-II | 2017-01-05 00:05 | 2017-01-05 06:42 | 0 | 0 | 0 | 0.27569 | LVRD | Line hand tripped for Voltage regulation. Agra-785 kV | N-390
NR176507 | 101135 | 765KV AGRA-FATEHPUR-II | 2017-01-07 04:41 | 2017-01-07 09:18 | 0 | 0 | 0 | 0.19236 | LVRD | Line hand tripped for Voltage regulation. Agra-795 kV | N-592
NR176507 | 101153 | 765KV AGRA-FATEHPUR-II | 2017-01-07 23:14 | 2017-01-08 06:08 | 0 | 0 | 0 | 0.2875 | LVRD | Line hand tripped for Voltage regulation. Agra-782kV | N-753
NR176507 | 101166 | 765KV AGRA-FATEHPUR-II | 2017-01-08 15:08 | 2017-01-09 07:16 | 0 | 0 | 0 | 0.67222 | LVRD | Line hand tripped for Voltage regulation. Agra-790kV | N-821
NR176507 | 101216 | 765KV AGRA-FATEHPUR-II | 2017-01-11 00:11 | 2017-01-11 07:25 | 0 | 0 | 0 | 0.30139 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-1100
NR176507 | 101304 | 765KV AGRA-FATEHPUR-II | 2017-01-15 00:02 | 2017-01-15 07:16 | 0 | 0 | 0 | 0.30139 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-1504
NR176507 | 101322 | 765KV AGRA-FATEHPUR-II | 2017-01-16 00:06 | 2017-01-16 08:15 | 0 | 0 | 0 | 0.33958 | LVRD | Line hand tripped for Voltage regulation. Agra-798 kV | N-1567
NR176507 | 101358 | 765KV AGRA-FATEHPUR-II | 2017-01-17 22:05 | 2017-01-18 06:14 | 0 | 0 | 0 | 0.33958 | LVRD | Line hand tripped for Voltage regulation. Agra-786kV | N-1796
NR176507 | 101380 | 765KV AGRA-FATEHPUR-II | 2017-01-18 23:45 | 2017-01-19 06:49 | 0 | 0 | 0 | 0.29444 | LVRD | Line hand tripped for Voltage regulation. Agra-429 kV | N-1908
NR176507 | 101393 | 765KV AGRA-FATEHPUR-II | 2017-01-19 20:50 | 2017-01-20 06:26 | 0 | 0 | 0 | 0.4 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-1990
NR176507 | 101418 | 765KV AGRA-FATEHPUR-II | 2017-01-20 20:59 | 2017-01-21 05:59 | 0 | 0 | 0 | 0.375 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-2092
NR176507 | 101440 | 765KV AGRA-FATEHPUR-II | 2017-01-21 23:54 | 2017-01-22 07:16 | 0 | 0 | 0 | 0.30694 | LVRD | Line hand tripped for Voltage regulation. Agra-790 kV | N-2186
NR176507 | 101456 | 765KV AGRA-FATEHPUR-II | 2017-01-22 23:27 | 2017-01-23 06:56 | 0 | 0 | 0 | 0.31181 | LVRD | Line hand tripped for Voltage regulation. Agra-781 kV | N-2252
NR176507 | 101507 | 765KV AGRA-FATEHPUR-II | 2017-01-25 01:11 | 2017-01-25 08:23 | 0 | 0 | 0 | 0.3 | LVRD | Line hand tripped for Voltage regulation. Agra-781 kV | N-2361
NR176507 | 101527 | 765KV AGRA-FATEHPUR-II | 2017-01-25 22:10 | 2017-01-26 06:36 | 0 | 0 | 0 | 0.35139 | LVRD | Line hand tripped for Voltage regulation. Agra-789 kV | N-2577
NR176507 | 101556 | 765KV AGRA-FATEHPUR-II | 2017-01-26 21:57 | 2017-01-27 07:41 | 0 | 0 | 0 | 0.40556 | LVRD | Line hand tripped for Voltage regulation. Agra-787kV | N-2708
NR176507 | 101614 | 765KV AGRA-FATEHPUR-II | 2017-01-27 22:25 | 2017-01-28 09:33 | 0 | 0 | 0 | 0.46389 | LVRD | Line hand tripped for Voltage regulation. Agra-787kV | N-2876
NR176507 | 101631 | 765KV AGRA-FATEHPUR-II | 2017-01-28 23:15 | 2017-01-29 07:03 | 0 | 0 | 0 | 0.325 | LVRD | Line hand tripped for Voltage regulation. Agra-787kV | N-2959
NR176507 | 101641 | 765KV AGRA-FATEHPUR-II | 2017-01-29 21:07 | 2017-01-30 06:51 | 0 | 0 | 0 | 0.40556 | LVRD | Line hand tripped for Voltage regulation. Agra-787kV | N-3029
NR176507 | 101667 | 765KV AGRA-FATEHPUR-II | 2017-01-30 22:43 | 2017-01-31 07:26 | 0 | 0 | 0 | 0.36319 | LVRD | Line hand tripped for Voltage regulation. Agra-784 kV | N-3136
NR176507 | 101677 | 765KV AGRA-FATEHPUR-II | 2017-01-31 21:19 | 2017-02-01 | 0 | 0 | 0 | 0.11181 | LVRD | Line hand tripped for Voltage regulation. Agra-784 kV | N-3214
|  | 765KV AGRA-FATEHPUR-II Total |  |  | 0 | 0 | 0 | 1900-01-07 03:32
NR376503 | 101026 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-01 23:48 | 2017-01-02 08:25 | 0 | 0 | 0 | 0.35903 | LVRD | Line hand tripped for Voltage regulation. Jhat-805 kV | N-94
NR376503 | 101050 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-03 01:07 | 2017-01-03 10:11 | 0 | 0 | 0 | 0.37778 | LVRD | Line hand tripped for Voltage regulation. Jhatkr-806 kV | N-190
NR376503 | 101075 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-04 03:00 | 2017-01-04 07:39 | 0 | 0 | 0 | 0.19375 | LVRD | Line hand tripped for Voltage regulation. Jhatkr-806 kV | N-291
NR376503 | 101122 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-06 23:32 | 2017-01-07 06:58 | 0 | 0 | 0 | 0.30972 | LVRD | Line hand tripped for Voltage regulation. Jhatkr-806 kV | N-564
NR376503 | 101160 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-08 01:30 | 2017-01-08 07:29 | 0 | 0 | 0 | 0.24931 | LVRD | Line hand tripped for Voltage regulation. Jhatkr-804 kV | N-767
NR376503 | 101201 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-10 01:09 | 2017-01-10 08:17 | 0 | 0 | 0 | 0.29722 | LVRD | Line hand tripped for Voltage regulation. JHTR-807kV | N-985
NR376503 | 101217 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-11 00:13 | 2017-01-11 07:45 | 0 | 0 | 0 | 0.31389 | LVRD | Line hand tripped for Voltage regulation. JHTR-802kV | N-1101
NR376503 | 101305 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-15 01:49 | 2017-01-15 05:55 | 0 | 0 | 0 | 0.17083 | LVRD | Line hand tripped for Voltage regulation. JHTR-807kV | N-1506
NR376503 | 101363 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-18 02:26 | 2017-01-18 06:47 | 0 | 0 | 0 | 0.18125 | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV | N-1813
NR376503 | 101383 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-19 00:48 | 2017-01-19 06:41 | 0 | 0 | 0 | 0.24514 | LVRD | Line hand tripped for Voltage regulation. Jhtk-801 kV | N-1913
NR376503 | 101442 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-22 01:19 | 2017-01-22 07:07 | 0 | 0 | 0 | 0.24167 | LVRD | Line hand tripped for Voltage regulation. Jhtk-801 kV | N-2191
NR376503 | 101455 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-22 23:25 | 2017-01-23 08:06 | 0 | 0 | 0 | 0.36181 | LVRD | Line hand tripped for Voltage regulation. Jhtk-800 kV | N-2251
NR376503 | 101529 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-25 23:22 | 2017-01-26 09:49 | 0 | 0 | 0 | 0.43542 | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV | N-2583
NR376503 | 101548 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-26 13:05 | 2017-01-27 07:26 | 0 | 0 | 0 | 0.76458 | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV | N-2656
NR376503 | 101619 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-28 00:43 | 2017-01-28 07:36 | 0 | 0 | 0 | 0.28681 | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV | N-2880
NR376503 | 101635 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-29 00:15 | 2017-01-29 06:44 | 0 | 0 | 0 | 0.27014 | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV | N-2963
NR376503 | 101648 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-29 23:33 | 2017-01-30 10:09 | 0 | 0 | 0 | 0.44167 | LVRD | Line hand tripped for Voltage regulation. Jhtk-807 kV | N-3040
NR376503 | 101668 | 765KV KANPUR(GIS)-JHATIKRA-I | 2017-01-30 22:45 | 2017-01-31 07:38 | 0 | 0 | 0 | 0.37014 | LVRD | Line hand tripped for Voltage regulation Jhat-784 kV | N-3137
|  | 765KV KANPUR(GIS)-JHATIKRA-I Total |  |  | 0 | 0 | 0 | 1900-01-04 20:53
NR176501 | 101458 | 765KV LUCKNOW-BALIA | 2017-01-23 03:03 | 2017-01-23 09:51 | 0 | 0 | 0 | 0.28333 | LVRD | Line hand tripped for Voltage regulation. Lko-805 kV | N-2255
NR176501 | 101579 | 765KV LUCKNOW-BALIA | 2017-01-27 02:00 | 2017-01-27 11:40 | 0 | 0 | 0 | 0.40278 | LVRD | Line hand tripped for Voltage regulation. Lko-804 kV | N-2737
|  | 765KV LUCKNOW-BALIA Total |  |  | 0 | 0 | 0 | 0.68611
NR176508 | 101408 | 765KV LUCKNOW-BAREILLY | 2017-01-20 16:07 | 2017-01-20 16:07 | 0 | 0 | 0 | 0 | LART | Line A/R on Y-N fault, FLR-Brly-53.63Km, If-4.4KA.
|  | 765KV LUCKNOW-BAREILLY Total |  |  | 0 | 0 | 0 | 0
NR176512 | 101348 | 765KV VARANASI-BALIA | 2017-01-17 09:49 | 2017-01-17 19:29 | 0.40278 | 0 | 0 | 0 | OSPT | S/D for AMP work at Varanasi. | N-1744
|  | 765KV VARANASI-BALIA Total |  |  | 0.40278 | 0 | 0 | 0
NR176513 | 101141 | 765KV VARANASI-FATEHPUR | 2017-01-07 14:44 | 2017-01-07 20:35 | 0.24375 | 0 | 0 | 0 | LPPT | Line tripped on R-Y fault. FLR:VNS-50.2 km, If- 9.3kAmp
|  | 765KV VARANASI-FATEHPUR Total |  |  | 0.24375 | 0 | 0 | 0
NR376501 | 101426 | 765KV VARANASI-KANPUR(GIS)-I | 2017-01-21 06:36 | 2017-01-21 18:41 | 0 | 0 | 0.50347 | 0 | LNCC | Line tripped on B-N fault, FLR-Knp-56.4Km, Vns-255.8Km If-6.2KA, Charging attempt fail & SOTF optd.during dense fog.
NR376501 | 101509 | 765KV VARANASI-KANPUR(GIS)-I | 2017-01-25 05:06 | 2017-01-25 18:25 | 0 | 0 | 0.55486 | 0 | LNCC | Tripped due to severe fog on B-N fault. FLR- KNP- 54.0 km, If-6.17 kAmp, VNS- 258.4 km. Jumper snapped found at loc-46/0
|  | 765KV VARANASI-KANPUR(GIS)-I Total |  |  | 0 | 0 | 1899-12-31 01:24 | 0
NR376502 | 101192 | 765KV VARANASI-KANPUR(GIS)-II | 2017-01-09 19:44 | 2017-01-09 22:23 | 0.11042 | 0 | 0 | 0 | LEFT | Tripped on R-N fault, FLR:Knp-0.2km, Vrns-397km, IF (Knp)-10.13 KA
NR376502 | 101429 | 765KV VARANASI-KANPUR(GIS)-II | 2017-01-21 15:31 | 2017-01-21 18:59 | 0.14444 | 0 | 0 | 0 | OSFT | To avoid induction during restoration of Jumper in VNS-KNP-I line. | N-2153
NR376502 | 101513 | 765KV VARANASI-KANPUR(GIS)-II | 2017-01-25 12:32 | 2017-01-25 18:28 | 0.24722 | 0 | 0 | 0 | OSFT | S/D for avoid induction in rectification of snapped Jumper of Ckt-I | N-2515
|  | 765KV VARANASI-KANPUR(GIS)-II Total |  |  | 0.50208 | 0 | 0 | 0
NR140003 | 101074 | 400KV AGRA-AURAIYA-I | 2017-01-04 02:46 | 2017-01-04 07:56 | 0 | 0 | 0 | 0.21528 | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | N-289
NR140003 | 101237 | 400KV AGRA-AURAIYA-I | 2017-01-12 00:19 | 2017-01-12 07:56 | 0 | 0 | 0 | 0.31736 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-1212
NR140003 | 101262 | 400KV AGRA-AURAIYA-I | 2017-01-12 21:13 | 2017-01-13 06:10 | 0 | 0 | 0 | 0.37292 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-1316
NR140003 | 101283 | 400KV AGRA-AURAIYA-I | 2017-01-14 00:07 | 2017-01-14 09:29 | 0 | 0 | 0 | 0.39028 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-1413
NR140003 | 101339 | 400KV AGRA-AURAIYA-I | 2017-01-16 23:26 | 2017-01-17 08:20 | 0 | 0 | 0 | 0.37083 | LVRD | Line hand tripped for Voltage regulation. Agra-426kV | N-1690
NR140003 | 101532 | 400KV AGRA-AURAIYA-I | 2017-01-26 00:32 | 2017-01-30 07:02 | 0 | 0 | 0 | 1900-01-03 06:30 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-2593
|  | 400KV AGRA-AURAIYA-I Total |  |  | 0 | 0 | 0 | 1900-01-04 22:30
NR140004 | 101001 | 400KV AGRA-AURAIYA-II | 2017-01-01 00:26 | 2017-01-02 07:02 | 0 | 0 | 0 | 1899-12-31 06:36 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-02
NR140004 | 101082 | 400KV AGRA-AURAIYA-II | 2017-01-04 21:04 | 2017-01-05 06:32 | 0 | 0 | 0 | 0.39444 | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | N-379
NR140004 | 101129 | 400KV AGRA-AURAIYA-II | 2017-01-07 01:42 | 2017-01-07 15:25 | 0 | 0 | 0 | 0.57153 | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV | N-580
NR140004 | 101156 | 400KV AGRA-AURAIYA-II | 2017-01-08 00:27 | 2017-01-08 07:03 | 0 | 0 | 0 | 0.275 | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV | N-762
NR140004 | 101179 | 400KV AGRA-AURAIYA-II | 2017-01-08 23:52 | 2017-01-09 08:32 | 0 | 0 | 0 | 0.36111 | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | N-858
NR140004 | 101301 | 400KV AGRA-AURAIYA-II | 2017-01-14 21:11 | 2017-01-15 09:12 | 0 | 0 | 0 | 0.50069 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-1494
NR140004 | 101317 | 400KV AGRA-AURAIYA-II | 2017-01-15 23:34 | 2017-01-16 08:58 | 0 | 0 | 0 | 0.39167 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-1561
NR140004 | 101401 | 400KV AGRA-AURAIYA-II | 2017-01-20 00:27 | 2017-01-20 06:08 | 0 | 0 | 0 | 0.23681 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2005
NR140004 | 101423 | 400KV AGRA-AURAIYA-II | 2017-01-21 00:22 | 2017-01-21 06:13 | 0 | 0 | 0 | 0.24375 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2102
NR140004 | 101476 | 400KV AGRA-AURAIYA-II | 2017-01-23 20:56 | 2017-01-24 08:07 | 0 | 0 | 0 | 0.46597 | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | N-2344
NR140004 | 101501 | 400KV AGRA-AURAIYA-II | 2017-01-24 21:17 | 2017-01-25 07:04 | 0 | 0 | 0 | 0.40764 | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | N-2453
NR140004 | 101534 | 400KV AGRA-AURAIYA-II | 2017-01-26 01:06 | 2017-01-31 09:43 | 0 | 0 | 0 | 1900-01-04 08:37 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-2597
NR140004 | 101678 | 400KV AGRA-AURAIYA-II | 2017-01-31 21:27 | 2017-02-01 | 0 | 0 | 0 | 0.10625 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-3216
|  | 400KV AGRA-AURAIYA-II Total |  |  | 0 | 0 | 0 | 1900-01-09 14:08
NR140005 | 101006 | 400KV AGRA-BASSI-I | 2017-01-01 01:19 | 2017-01-01 10:38 | 0 | 0 | 0 | 0.38819 | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | N-14
NR140005 | 101320 | 400KV AGRA-BASSI-I | 2017-01-15 23:55 | 2017-01-16 07:44 | 0 | 0 | 0 | 0.32569 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-1565
NR140005 | 101342 | 400KV AGRA-BASSI-I | 2017-01-17 00:18 | 2017-01-17 06:25 | 0 | 0 | 0 | 0.25486 | LVRD | Line hand tripped for Voltage regulation. Mrt-800 kV | N-1693
NR140005 | 101480 | 400KV AGRA-BASSI-I | 2017-01-23 23:28 | 2017-01-24 06:55 | 0 | 0 | 0 | 0.31042 | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV | N-2356
NR140005 | 101505 | 400KV AGRA-BASSI-I | 2017-01-25 00:07 | 2017-01-25 07:11 | 0 | 0 | 0 | 0.29444 | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | N-2465
NR140005 | 101679 | 400KV AGRA-BASSI-I | 2017-01-31 21:36 | 2017-02-01 | 0 | 0 | 0 | 0.1 | LVRD | Line hand tripped for Voltage regulation. Agra-433 kV | N-3218
|  | 400KV AGRA-BASSI-I Total |  |  | 0 | 0 | 0 | 1899-12-31 16:10
NR140008 | 101681 | 400KV AGRA-BHIWADI-I | 2017-01-31 22:07 | 2017-02-01 | 0 | 0 | 0 | 0.078472 | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | N-3222
|  | 400KV AGRA-BHIWADI-I Total |  |  | 0 | 0 | 0 | 0.078472
NR140009 | 112714 | 400KV AGRA-BHIWADI-II | 2017-01-01 | 2017-01-01 06:52 | 0 | 0 | 0 | 0.28611 | LVRD | Line hand tripped for Voltage regulation. Agra-429 kV. Open since 2033hrs on 31.12.16 | N-4776
NR140009 | 101015 | 400KV AGRA-BHIWADI-II | 2017-01-01 19:50 | 2017-01-02 06:38 | 0 | 0 | 0 | 0.45 | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | N-75
NR140009 | 101043 | 400KV AGRA-BHIWADI-II | 2017-01-02 20:53 | 2017-01-03 06:59 | 0 | 0 | 0 | 0.42083 | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV | N-179
NR140009 | 101061 | 400KV AGRA-BHIWADI-II | 2017-01-03 20:15 | 2017-01-04 10:17 | 0 | 0 | 0 | 0.58472 | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV | N-270
NR140009 | 101080 | 400KV AGRA-BHIWADI-II | 2017-01-04 19:58 | 2017-01-05 06:04 | 0 | 0 | 0 | 0.42083 | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV | N-373
NR140009 | 101099 | 400KV AGRA-BHIWADI-II | 2017-01-05 20:17 | 2017-01-06 07:02 | 0 | 0 | 0 | 0.44792 | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV | N-234
NR140009 | 101111 | 400KV AGRA-BHIWADI-II | 2017-01-06 19:28 | 2017-01-07 15:27 | 0 | 0 | 0 | 0.83264 | LVRD | Line hand tripped for Voltage regulation. Bwd-434 kV | N-543
NR140009 | 101145 | 400KV AGRA-BHIWADI-II | 2017-01-07 20:17 | 2017-01-08 07:00 | 0 | 0 | 0 | 0.44653 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-736
NR140009 | 101170 | 400KV AGRA-BHIWADI-II | 2017-01-08 15:22 | 2017-01-09 04:47 | 0 | 0 | 0 | 0.55903 | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV | N-826
NR140009 | 101195 | 400KV AGRA-BHIWADI-II | 2017-01-09 21:05 | 2017-01-10 08:53 | 0 | 0 | 0 | 0.49167 | LVRD | Line hand tripped for Voltage regulation. Bwd-431 kV | N-970
NR140009 | 101211 | 400KV AGRA-BHIWADI-II | 2017-01-10 21:09 | 2017-01-11 07:17 | 0 | 0 | 0 | 0.42222 | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV | N-1089
NR140009 | 101230 | 400KV AGRA-BHIWADI-II | 2017-01-11 21:08 | 2017-01-12 07:15 | 0 | 0 | 0 | 0.42153 | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV | N-1203
NR140009 | 101256 | 400KV AGRA-BHIWADI-II | 2017-01-12 20:15 | 2017-01-13 06:29 | 0 | 0 | 0 | 0.42639 | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV | N-1312
NR140009 | 101278 | 400KV AGRA-BHIWADI-II | 2017-01-13 20:52 | 2017-01-14 05:56 | 0 | 0 | 0 | 0.37778 | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV | N-1401
NR140009 | 101295 | 400KV AGRA-BHIWADI-II | 2017-01-14 20:06 | 2017-01-15 09:04 | 0 | 0 | 0 | 0.54028 | LVRD | Line hand tripped for Voltage regulation. Bwd-430 kV | N-1485
NR140009 | 101307 | 400KV AGRA-BHIWADI-II | 2017-01-15 19:13 | 2017-06-16 06:21 | 0 | 0 | 0 | 1900-05-30 11:08 | LVRD | Line hand tripped for Voltage regulation. Agra-429kV | N-1544
NR140009 | 101333 | 400KV AGRA-BHIWADI-II | 2017-01-16 20:16 | 2017-01-17 08:02 | 0 | 0 | 0 | 0.49028 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-1677
NR140009 | 101354 | 400KV AGRA-BHIWADI-II | 2017-01-17 20:43 | 2017-01-18 06:26 | 0 | 0 | 0 | 0.40486 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-1789
NR140009 | 101375 | 400KV AGRA-BHIWADI-II | 2017-01-18 20:55 | 2017-01-19 06:25 | 0 | 0 | 0 | 0.39583 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-1899
NR140009 | 101391 | 400KV AGRA-BHIWADI-II | 2017-01-19 20:34 | 2017-01-20 06:01 | 0 | 0 | 0 | 0.39375 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-1988
NR140009 | 101415 | 400KV AGRA-BHIWADI-II | 2017-01-20 20:21 | 2017-01-21 06:17 | 0 | 0 | 0 | 0.41389 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2087
NR140009 | 101431 | 400KV AGRA-BHIWADI-II | 2017-01-21 19:58 | 2017-01-22 06:04 | 0 | 0 | 0 | 0.42083 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2174
NR140009 | 101446 | 400KV AGRA-BHIWADI-II | 2017-01-22 16:07 | 2017-01-23 07:26 | 0 | 0 | 0 | 0.63819 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2233
NR140009 | 101470 | 400KV AGRA-BHIWADI-II | 2017-01-23 20:43 | 2017-01-24 06:39 | 0 | 0 | 0 | 0.41389 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2340
NR140009 | 101493 | 400KV AGRA-BHIWADI-II | 2017-01-24 19:51 | 2017-01-25 06:59 | 0 | 0 | 0 | 0.46389 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2449
NR140009 | 101519 | 400KV AGRA-BHIWADI-II | 2017-01-25 19:50 | 2017-01-26 07:10 | 0 | 0 | 0 | 0.47222 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-2567
NR140009 | 101547 | 400KV AGRA-BHIWADI-II | 2017-01-26 10:57 | 2017-01-27 04:52 | 0 | 0 | 0 | 0.74653 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-2650
NR140009 | 101606 | 400KV AGRA-BHIWADI-II | 2017-01-27 13:37 | 2017-01-28 06:57 | 0 | 0 | 0 | 0.72222 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-2840
NR140009 | 101625 | 400KV AGRA-BHIWADI-II | 2017-01-28 21:01 | 2017-01-30 06:43 | 0 | 0 | 0 | 1899-12-31 09:42 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-2952
NR140009 | 101657 | 400KV AGRA-BHIWADI-II | 2017-01-30 13:25 | 2017-01-31 06:03 | 0 | 0 | 0 | 0.69306 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-3095
NR140009 | 101672 | 400KV AGRA-BHIWADI-II | 2017-01-31 13:12 | 2017-02-01 | 0 | 0 | 0 | 0.45 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-3186
|  | 400KV AGRA-BHIWADI-II Total |  |  | 0 | 0 | 0 | 1900-06-15 02:47
NR140010 | 101052 | 400KV AGRA-BLBGRH | 2017-01-03 02:06 | 2017-01-03 02:06 | 0 | 0 | 0 | 0 | LART | A/R on Y-N fault, FLR:Agra-51.5km, Blb-128.6km
|  | 400KV AGRA-BLBGRH Total |  |  | 0 | 0 | 0 | 0
NR140122 | 101057 | 400KV ALLD-FATEHPUR-I | 2017-01-03 07:21 | 2017-01-03 20:23 | 0 | 0 | 0 | 0.54306 | OSPD | S/D by UPPCL for stringing of 400KV D/C Allahabad-Rewa Road line. | N-209
|  | 400KV ALLD-FATEHPUR-I Total |  |  | 0 | 0 | 0 | 0.54306
NR140123 | 101056 | 400KV ALLD-FATEHPUR-II | 2017-01-03 07:20 | 2017-01-03 20:25 | 0 | 0 | 0 | 0.54514 | OSPD | S/D by UPPCL for stringing of 400KV D/C Allahabad-Rewa Road line. | N-209
|  | 400KV ALLD-FATEHPUR-II Total |  |  | 0 | 0 | 0 | 0.54514
NR140022 | 101512 | 400KV BALIA-PATNA-II | 2017-01-25 10:10 | 2017-01-25 11:50 | 0.069444 | 0 | 0 | 0 | OSFT | Hand tripped due to sparking in isolator at Balia end
|  | 400KV BALIA-PATNA-II Total |  |  | 0.069444 | 0 | 0 | 0
NR140136 | 101242 | 400KV BALIA-PATNA-III | 2017-01-12 09:32 | 2017-01-12 16:19 | 0.28264 | 0 | 0 | 0 | OSPT | S/D for decapped insulator replacement at loc. 550 & 554. | N-1243
|  | 400KV BALIA-PATNA-III Total |  |  | 0.28264 | 0 | 0 | 0
NR140137 | 101270 | 400KV BALIA-PATNA-IV | 2017-01-13 09:47 | 2017-01-13 16:18 | 0.27153 | 0 | 0 | 0 | OSPT | S/D for insulator cleaning and maintenance . | N-1360
|  | 400KV BALIA-PATNA-IV Total |  |  | 0.27153 | 0 | 0 | 0
NR140140 | 101124 | 400KV BALIA-SOHAWAL-I | 2017-01-07 00:15 | 2017-01-07 10:32 | 0 | 0 | 0 | 0.42847 | LVRD | Line hand tripped for Voltage regulation. Sohawal-429 kV | N-567
NR140140 | 101288 | 400KV BALIA-SOHAWAL-I | 2017-01-14 07:43 | 2017-01-14 08:57 | 0.051389 | 0 | 0 | 0 | OSFT | Hand tripped due to NGR Buchaltz relay alarm at Balia.
NR140140 | 101463 | 400KV BALIA-SOHAWAL-I | 2017-01-23 15:40 | 2017-01-23 20:24 | 0.19722 | 0 | 0 | 0 | OSPT | S/D taken for AMP work of line element. | N-2310
|  | 400KV BALIA-SOHAWAL-I Total |  |  | 0.24861 | 0 | 0 | 0.42847
NR140120 | 101479 | 400KV BALIA-SOHAWAL-II | 2017-01-23 22:14 | 2017-01-24 09:07 | 0 | 0 | 0 | 0.45347 | LVRD | Line hand tripped for Voltage regulation. Sohawal-424kV | N-2346
NR140120 | 101487 | 400KV BALIA-SOHAWAL-II | 2017-01-24 09:07 | 2017-01-24 18:45 | 0.40139 | 0 | 0 | 0 | OSPT | S/D taken for AMP work. | N-2388
|  | 400KV BALIA-SOHAWAL-II Total |  |  | 0.40139 | 0 | 0 | 0.45347
NR140025 | 101405 | 400KV BAREILLY-LKO(UP) | 2017-01-20 10:51 | 2017-01-20 11:01 | 0.0069444 | 0 | 0 | 0 | OSFT | S/D for taking L/R out, to attend hot spot in bushing at Brly. | N-2046
|  | 400KV BAREILLY-LKO(UP) Total |  |  | 0.0069444 | 0 | 0 | 0
NR140026 | 101188 | 400KV BAREILLY-MBAD-I | 2017-01-09 10:25 | 2017-01-09 11:38 | 0 | 0.050694 | 0 | 0 | OMSU | Line tripped on Y-B fault due to kite thread. FLR-BLY-11.8km, IF-19.17 KA, MRD-74.44 km
NR140026 | 101207 | 400KV BAREILLY-MBAD-I | 2017-01-10 17:50 | 2017-01-10 18:31 | 0.028472 | 0 | 0 | 0 | LPPT | Line tripped on R-B fault. FLR:BLY-11.6km, IF-17.2 KA, MRD-79.62 km
NR140026 | 101577 | 400KV BAREILLY-MBAD-I | 2017-01-27 01:57 | 2017-01-27 02:02 | 0 | 0 | 0.0034722 | 0 | GOVC | Tripped on Over Voltage protection operated at Mrdbd end. DT received at Bareily end.
NR140026 | 101580 | 400KV BAREILLY-MBAD-I | 2017-01-27 02:02 | 2017-01-28 08:02 | 0 | 0 | 0 | 1899-12-31 06:00 | LVRD | Line kept open for Voltage regulation. | N-2342
|  | 400KV BAREILLY-MBAD-I Total |  |  | 0.028472 | 0.050694 | 0.0034722 | 1899-12-31 06:00
NR140027 | 101653 | 400KV BAREILLY-MBAD-II | 2017-01-30 06:16 | 2017-01-30 06:16 | 0 | 0 | 0 | 0 | LART | A/R on Y-N fault, BLY=52.8km.
|  | 400KV BAREILLY-MBAD-II Total |  |  | 0 | 0 | 0 | 0
NR140115 | 101568 | 400KV BAREILLY-ROSA-I | 2017-01-26 23:48 | 2017-01-26 23:53 | 0 | 0 | 0.0034722 | 0 | GOVC | Tripped on Over Voltage protection operated at Rosa end. DT received at Bareily end.
NR140115 | 101569 | 400KV BAREILLY-ROSA-I | 2017-01-26 23:53 | 2017-01-27 12:41 | 0 | 0 | 0 | 0.53333 | LVRD | Line kept open for Voltage regulation. | N-2726
NR140115 | 101605 | 400KV BAREILLY-ROSA-I | 2017-01-27 12:41 | 2017-01-27 19:35 | 0 | 0 | 0 | 0.2875 | OSFD | S/D by UPPCL to attend hot spot at their end. | N-2834
|  | 400KV BAREILLY-ROSA-I Total |  |  | 0 | 0 | 0.0034722 | 0.82083
NR140158 | 101462 | 400KV BARLY(765)-KASHIPUR-I | 2017-01-23 12:34 | 2017-01-23 13:19 | 0 | 0.03125 | 0 | 0 | OMSU | Line A/R from Brly end and tripped from Kashipur end due to auto recloser problem at Kashipur end on R-N fault. FLR-Kashipur-9.5 km, If- 6.673 kAmp
|  | 400KV BARLY(765)-KASHIPUR-I Total |  |  | 0 | 0.03125 | 0 | 0
NR140037 | 101316 | 400KV BLBGRH-MAINPURI-I | 2017-01-15 23:29 | 2017-01-16 07:36 | 0 | 0 | 0 | 0.33819 | LVRD | Line hand tripped for Voltage regulation. Mnp-422kV | N-1562
NR140037 | 101338 | 400KV BLBGRH-MAINPURI-I | 2017-01-16 23:25 | 2017-01-17 10:12 | 0 | 0 | 0 | 0.44931 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1690
NR140037 | 101351 | 400KV BLBGRH-MAINPURI-I | 2017-01-17 10:12 | 2017-01-17 13:22 | 0.13194 | 0 | 0 | 0 | OSFT | S/D for faulty CVT replacement at Blbgrh. | N-1749
NR140037 | 101360 | 400KV BLBGRH-MAINPURI-I | 2017-01-18 00:07 | 2017-01-18 06:52 | 0 | 0 | 0 | 0.28125 | LVRD | Line hand tripped for Voltage regulation. Mnp-427 kV | N-1807
NR140037 | 101378 | 400KV BLBGRH-MAINPURI-I | 2017-01-18 23:09 | 2017-01-19 06:17 | 0 | 0 | 0 | 0.29722 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-1907
NR140037 | 101395 | 400KV BLBGRH-MAINPURI-I | 2017-01-19 21:14 | 2017-01-20 07:09 | 0 | 0 | 0 | 0.41319 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-1993
NR140037 | 101498 | 400KV BLBGRH-MAINPURI-I | 2017-01-24 21:07 | 2017-01-25 06:55 | 0 | 0 | 0 | 0.40833 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-2453
NR140037 | 101520 | 400KV BLBGRH-MAINPURI-I | 2017-01-25 19:51 | 2017-01-26 09:07 | 0 | 0 | 0 | 0.55278 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-2567
NR140037 | 101553 | 400KV BLBGRH-MAINPURI-I | 2017-01-26 14:58 | 2017-01-27 08:55 | 0 | 0 | 0 | 0.74792 | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV | N-2671
NR140037 | 101611 | 400KV BLBGRH-MAINPURI-I | 2017-01-27 21:58 | 2017-01-28 06:21 | 0 | 0 | 0 | 0.34931 | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV | N-2871
NR140037 | 101633 | 400KV BLBGRH-MAINPURI-I | 2017-01-28 23:24 | 2017-01-29 06:17 | 0 | 0 | 0 | 0.28681 | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV | N-2961
NR140037 | 101646 | 400KV BLBGRH-MAINPURI-I | 2017-01-29 23:18 | 2017-01-30 06:50 | 0 | 0 | 0 | 0.31389 | LVRD | Line hand tripped for Voltage regulation. Mnp-427kV | N-3038
NR140037 | 101662 | 400KV BLBGRH-MAINPURI-I | 2017-01-30 22:04 | 2017-01-31 05:25 | 0 | 0 | 0 | 0.30625 | LVRD | Line hand tripped for Voltage regulation. Mnp-427kV | N-3130
NR140037 | 112718 | 400KV BLBGRH-MAINPURI-I | 2017-01-01 | 2017-01-01 07:43 | 0 | 0 | 0 | 0.32153 | LVRD | Line hand tripped for Voltage regulation. MNP-432 kV. Open since 2347hrs on 31.12.16 | N-4785
NR140037 | 101020 | 400KV BLBGRH-MAINPURI-I | 2017-01-01 21:18 | 2017-01-02 07:24 | 0 | 0 | 0 | 0.42083 | LVRD | Line hand tripped for Voltage regulation. Mnp-429kV | N-83
NR140037 | 101045 | 400KV BLBGRH-MAINPURI-I | 2017-01-02 23:18 | 2017-01-03 07:38 | 0 | 0 | 0 | 0.34722 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-184
NR140037 | 101070 | 400KV BLBGRH-MAINPURI-I | 2017-01-03 21:14 | 2017-01-04 06:13 | 0 | 0 | 0 | 0.37431 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-273
NR140037 | 101084 | 400KV BLBGRH-MAINPURI-I | 2017-01-04 21:06 | 2017-01-05 06:41 | 0 | 0 | 0 | 0.39931 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-379
NR140037 | 101101 | 400KV BLBGRH-MAINPURI-I | 2017-01-05 21:17 | 2017-01-06 07:03 | 0 | 0 | 0 | 0.40694 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-466
NR140037 | 101119 | 400KV BLBGRH-MAINPURI-I | 2017-01-06 21:51 | 2017-01-07 10:08 | 0 | 0 | 0 | 0.51181 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-559
NR140037 | 101155 | 400KV BLBGRH-MAINPURI-I | 2017-01-07 23:55 | 2017-01-08 08:36 | 0 | 0 | 0 | 0.36181 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-757
NR140037 | 101164 | 400KV BLBGRH-MAINPURI-I | 2017-01-08 15:04 | 2017-01-09 07:13 | 0 | 0 | 0 | 0.67292 | LVRD | Line hand tripped for Voltage regulation. BLB-431 kV | N-823
NR140037 | 101199 | 400KV BLBGRH-MAINPURI-I | 2017-01-09 22:09 | 2017-01-10 06:45 | 0 | 0 | 0 | 0.35833 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-972
NR140037 | 101213 | 400KV BLBGRH-MAINPURI-I | 2017-01-10 23:40 | 2017-01-11 07:06 | 0 | 0 | 0 | 0.30972 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1094
NR140037 | 101235 | 400KV BLBGRH-MAINPURI-I | 2017-01-12 00:18 | 2017-01-12 06:05 | 0 | 0 | 0 | 0.24097 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1212
NR140037 | 101263 | 400KV BLBGRH-MAINPURI-I | 2017-01-13 00:08 | 2017-01-13 05:38 | 0 | 0 | 0 | 0.22917 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1327
NR140037 | 101286 | 400KV BLBGRH-MAINPURI-I | 2017-01-14 03:02 | 2017-01-14 03:05 | 0 | 0 | 0.0020833 | 0 | GOVC | Trip on O/VOL protn from Ballabgarh, BLB=435kv.
NR140037 | 101287 | 400KV BLBGRH-MAINPURI-I | 2017-01-14 03:05 | 2017-01-14 06:40 | 0 | 0 | 0 | 0.14931 | LVRD | Kept open on Voltage regulation, BLB=429kv. | N-1423
|  | 400KV BLBGRH-MAINPURI-I Total |  |  | 0.13194 | 0 | 0.0020833 | 1900-01-08 20:22
NR140038 | 101420 | 400KV BLBGRH-MAINPURI-II | 2017-01-21 00:11 | 2017-01-21 06:11 | 0 | 0 | 0 | 0.25 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-2099
NR140038 | 101438 | 400KV BLBGRH-MAINPURI-II | 2017-01-21 21:14 | 2017-01-22 06:17 | 0 | 0 | 0 | 0.37708 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-2181
NR140038 | 101448 | 400KV BLBGRH-MAINPURI-II | 2017-01-22 21:02 | 2017-01-23 07:15 | 0 | 0 | 0 | 0.42569 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-2244
NR140038 | 101473 | 400KV BLBGRH-MAINPURI-II | 2017-01-23 20:52 | 2017-01-24 06:29 | 0 | 0 | 0 | 0.40069 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-2342
NR140038 | 101281 | 400KV BLBGRH-MAINPURI-II | 2017-01-13 22:28 | 2017-01-14 06:48 | 0 | 0 | 0 | 0.34722 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1411
NR140038 | 101299 | 400KV BLBGRH-MAINPURI-II | 2017-01-14 21:08 | 2017-01-15 07:19 | 0 | 0 | 0 | 0.42431 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1494
|  | 400KV BLBGRH-MAINPURI-II Total |  |  | 0 | 0 | 0 | 1900-01-01 05:24
NR140124 | 112719 | 400KV FATEHPUR-MAINPURI-I | 2017-01-01 | 2017-01-01 07:43 | 0 | 0 | 0 | 0.32153 | LVRD | Line hand tripped for Voltage regulation. MNP-432 kV. Open since 2348hrs on 31.12.16 | N-4785
NR140124 | 101021 | 400KV FATEHPUR-MAINPURI-I | 2017-01-01 21:19 | 2017-01-02 07:24 | 0 | 0 | 0 | 0.42014 | LVRD | Line hand tripped for Voltage regulation. Mnp-429kV | N-83
NR140124 | 101068 | 400KV FATEHPUR-MAINPURI-I | 2017-01-03 21:07 | 2017-01-04 06:14 | 0 | 0 | 0 | 0.37986 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-273
NR140124 | 101083 | 400KV FATEHPUR-MAINPURI-I | 2017-01-04 21:06 | 2017-01-05 07:03 | 0 | 0 | 0 | 0.41458 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-379
NR140124 | 101102 | 400KV FATEHPUR-MAINPURI-I | 2017-01-05 21:17 | 2017-01-06 07:05 | 0 | 0 | 0 | 0.40833 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-466
NR140124 | 101120 | 400KV FATEHPUR-MAINPURI-I | 2017-01-06 21:52 | 2017-01-07 10:05 | 0 | 0 | 0 | 0.50903 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-559
NR140124 | 101154 | 400KV FATEHPUR-MAINPURI-I | 2017-01-07 23:55 | 2017-01-08 08:26 | 0 | 0 | 0 | 0.35486 | LVRD | Line hand tripped for Voltage regulation. Mnp-427 kV | N-757
NR140124 | 101176 | 400KV FATEHPUR-MAINPURI-I | 2017-01-08 21:05 | 2017-01-09 07:14 | 0 | 0 | 0 | 0.42292 | LVRD | Line hand tripped for Voltage regulation. MNP-422 kV | N-846
NR140124 | 101198 | 400KV FATEHPUR-MAINPURI-I | 2017-01-09 22:09 | 2017-01-10 06:45 | 0 | 0 | 0 | 0.35833 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-972
NR140124 | 101214 | 400KV FATEHPUR-MAINPURI-I | 2017-01-10 23:40 | 2017-01-11 07:06 | 0 | 0 | 0 | 0.30972 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1097
NR140124 | 101236 | 400KV FATEHPUR-MAINPURI-I | 2017-01-12 00:20 | 2017-01-12 06:07 | 0 | 0 | 0 | 0.24097 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1212
NR140124 | 101264 | 400KV FATEHPUR-MAINPURI-I | 2017-01-13 00:09 | 2017-01-13 05:37 | 0 | 0 | 0 | 0.22778 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1327
NR140124 | 101318 | 400KV FATEHPUR-MAINPURI-I | 2017-01-15 23:35 | 2017-01-16 07:38 | 0 | 0 | 0 | 0.33542 | LVRD | Line hand tripped for Voltage regulation. Mnp-422 kV | N-1561
NR140124 | 101337 | 400KV FATEHPUR-MAINPURI-I | 2017-01-16 23:24 | 2017-01-17 08:20 | 0 | 0 | 0 | 0.37222 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1690
NR140124 | 101379 | 400KV FATEHPUR-MAINPURI-I | 2017-01-18 23:12 | 2017-01-19 06:18 | 0 | 0 | 0 | 0.29583 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-1907
NR140124 | 101396 | 400KV FATEHPUR-MAINPURI-I | 2017-01-19 21:14 | 2017-01-20 06:20 | 0 | 0 | 0 | 0.37917 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-1993
NR140124 | 101421 | 400KV FATEHPUR-MAINPURI-I | 2017-01-21 00:11 | 2017-01-21 06:12 | 0 | 0 | 0 | 0.25069 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-2099
NR140124 | 101439 | 400KV FATEHPUR-MAINPURI-I | 2017-01-21 21:15 | 2017-01-22 06:15 | 0 | 0 | 0 | 0.375 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-2181
NR140124 | 101449 | 400KV FATEHPUR-MAINPURI-I | 2017-01-22 21:03 | 2017-01-23 07:16 | 0 | 0 | 0 | 0.42569 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-2244
NR140124 | 101472 | 400KV FATEHPUR-MAINPURI-I | 2017-01-23 20:51 | 2017-01-24 06:30 | 0 | 0 | 0 | 0.40208 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-2342
NR140124 | 101521 | 400KV FATEHPUR-MAINPURI-I | 2017-01-25 19:55 | 2017-01-26 09:11 | 0 | 0 | 0 | 0.55278 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-2567
NR140124 | 101554 | 400KV FATEHPUR-MAINPURI-I | 2017-01-26 14:58 | 2017-01-27 08:55 | 0 | 0 | 0 | 0.74792 | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV | N-2671
NR140124 | 101616 | 400KV FATEHPUR-MAINPURI-I | 2017-01-28 00:24 | 2017-01-28 06:10 | 0 | 0 | 0 | 0.24028 | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV | N-2878
NR140124 | 101634 | 400KV FATEHPUR-MAINPURI-I | 2017-01-28 23:25 | 2017-01-29 06:16 | 0 | 0 | 0 | 0.28542 | LVRD | Line hand tripped for Voltage regulation. Mnp-430 kV | N-2961
NR140124 | 101661 | 400KV FATEHPUR-MAINPURI-I | 2017-01-30 22:03 | 2017-01-31 05:27 | 0 | 0 | 0 | 0.30833 | LVRD | Line hand tripped for Voltage regulation. Ftpr-423kV | N-3130
|  | 400KV FATEHPUR-MAINPURI-I Total |  |  | 0 | 0 | 0 | 1900-01-08 08:08
NR140125 | 101046 | 400KV FATEHPUR-MAINPURI-II | 2017-01-02 23:18 | 2017-01-03 07:37 | 0 | 0 | 0 | 0.34653 | LVRD | Line hand tripped for Voltage regulation. MNP-427 kV | N-184
NR140125 | 101282 | 400KV FATEHPUR-MAINPURI-II | 2017-01-13 22:28 | 2017-01-14 06:43 | 0 | 0 | 0 | 0.34375 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1411
NR140125 | 101300 | 400KV FATEHPUR-MAINPURI-II | 2017-01-14 21:09 | 2017-01-15 07:20 | 0 | 0 | 0 | 0.42431 | LVRD | Line hand tripped for Voltage regulation. Mnp-428 kV | N-1494
NR140125 | 101359 | 400KV FATEHPUR-MAINPURI-II | 2017-01-18 00:06 | 2017-01-18 06:52 | 0 | 0 | 0 | 0.28194 | LVRD | Line hand tripped for Voltage regulation. Mnp-427 kV | N-1807
NR140125 | 101490 | 400KV FATEHPUR-MAINPURI-II | 2017-01-24 16:39 | 2017-01-24 17:20 | 0.028472 | 0 | 0 | 0 | OMST | Line tripped as DT received at Fathepur end.
NR140125 | 101499 | 400KV FATEHPUR-MAINPURI-II | 2017-01-24 21:10 | 2017-01-25 06:55 | 0 | 0 | 0 | 0.40625 | LVRD | Line hand tripped for Voltage regulation. Mnp-426 kV | N-2453
NR140125 | 101645 | 400KV FATEHPUR-MAINPURI-II | 2017-01-29 23:18 | 2017-01-30 06:49 | 0 | 0 | 0 | 0.31319 | LVRD | Line hand tripped for Voltage regulation. Ftpr-423kV | N-3038
|  | 400KV FATEHPUR-MAINPURI-II Total |  |  | 0.028472 | 0 | 0 | 1900-01-01 02:47
NR140055 | 101065 | 400KV KNP-BLBGARH-I | 2017-01-03 21:00 | 2017-01-04 09:27 | 0 | 0 | 0 | 0.51875 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-273
NR140055 | 101081 | 400KV KNP-BLBGARH-I | 2017-01-04 21:01 | 2017-01-05 06:29 | 0 | 0 | 0 | 0.39444 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-379
NR140055 | 101100 | 400KV KNP-BLBGARH-I | 2017-01-05 21:04 | 2017-01-06 06:57 | 0 | 0 | 0 | 0.41181 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-466
NR140055 | 101182 | 400KV KNP-BLBGARH-I | 2017-01-09 01:44 | 2017-01-09 06:58 | 0 | 0 | 0 | 0.21806 | LVRD | Line hand tripped for Voltage regulation. KNP-429 kV | N-867
NR140055 | 101200 | 400KV KNP-BLBGARH-I | 2017-01-10 01:03 | 2017-01-10 06:35 | 0 | 0 | 0 | 0.23056 | LVRD | Line hand tripped for Voltage regulation. BLB-430 kV | N-984
NR140055 | 101321 | 400KV KNP-BLBGARH-I | 2017-01-15 23:59 | 2017-01-16 17:01 | 0 | 0 | 0 | 0.70972 | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV | N-1566
NR140055 | 101397 | 400KV KNP-BLBGARH-I | 2017-01-19 21:14 | 2017-01-20 06:24 | 0 | 0 | 0 | 0.38194 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-1993
NR140055 | 101419 | 400KV KNP-BLBGARH-I | 2017-01-21 00:08 | 2017-01-21 06:07 | 0 | 0 | 0 | 0.24931 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-2099
NR140055 | 101582 | 400KV KNP-BLBGARH-I | 2017-01-27 02:32 | 2017-01-27 02:37 | 0 | 0 | 0.0034722 | 0 | GOVC | Tripped on Over Voltage protection operated at Blb end. DT received at Knp end. Blb>432 kV
NR140055 | 101584 | 400KV KNP-BLBGARH-I | 2017-01-27 02:37 | 2017-01-27 04:04 | 0 | 0 | 0 | 0.060417 | LVRD | Line kept open for Voltage regulation. | N-2741
|  | 400KV KNP-BLBGARH-I Total |  |  | 0 | 0 | 0.0034722 | 1900-01-02 04:12
NR140056 | 101302 | 400KV KNP-BLBGARH-II | 2017-01-14 21:11 | 2017-01-15 07:28 | 0 | 0 | 0 | 0.42847 | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV | N-1494
NR140056 | 101437 | 400KV KNP-BLBGARH-II | 2017-01-21 21:08 | 2017-01-22 05:54 | 0 | 0 | 0 | 0.36528 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-2181
NR140056 | 101471 | 400KV KNP-BLBGARH-II | 2017-01-23 20:50 | 2017-01-24 08:02 | 0 | 0 | 0 | 0.46667 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-2342
NR140056 | 101506 | 400KV KNP-BLBGARH-II | 2017-01-25 01:06 | 2017-01-25 07:01 | 0 | 0 | 0 | 0.24653 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-2469
NR140056 | 101570 | 400KV KNP-BLBGARH-II | 2017-01-27 00:05 | 2017-01-27 05:14 | 0 | 0 | 0 | 0.21458 | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV | N-2727
|  | 400KV KNP-BLBGARH-II Total |  |  | 0 | 0 | 0 | 1899-12-31 17:19
NR140057 | 112716 | 400KV KNP-BLBGARH-III | 2017-01-01 | 2017-01-01 07:56 | 0 | 0 | 0 | 0.33056 | LVRD | Line hand tripped for Voltage regulation. BLB-427 kV. Open since 2324hrs on 31.12.16 | N-4784
NR140057 | 101022 | 400KV KNP-BLBGARH-III | 2017-01-01 21:22 | 2017-01-02 08:08 | 0 | 0 | 0 | 0.44861 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-83
NR140057 | 101044 | 400KV KNP-BLBGARH-III | 2017-01-02 20:58 | 2017-01-03 08:00 | 0 | 0 | 0 | 0.45972 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-181
NR140057 | 101117 | 400KV KNP-BLBGARH-III | 2017-01-06 21:47 | 2017-01-07 18:31 | 0 | 0 | 0 | 0.86389 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-559
NR140057 | 101148 | 400KV KNP-BLBGARH-III | 2017-01-07 20:59 | 2017-01-08 08:43 | 0 | 0 | 0 | 0.48889 | LVRD | Line hand tripped for Voltage regulation. KNP-428 kV | N-743
NR140057 | 101167 | 400KV KNP-BLBGARH-III | 2017-01-08 15:12 | 2017-01-09 10:00 | 0 | 0 | 0 | 0.78333 | LVRD | Line hand tripped for Voltage regulation. KNP-429 kV | N-823
NR140057 | 101209 | 400KV KNP-BLBGARH-III | 2017-01-10 20:52 | 2017-01-11 07:58 | 0 | 0 | 0 | 0.4625 | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV | N-1089
NR140057 | 101234 | 400KV KNP-BLBGARH-III | 2017-01-12 00:30 | 2017-01-12 08:29 | 0 | 0 | 0 | 0.33264 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-1212
NR140057 | 101265 | 400KV KNP-BLBGARH-III | 2017-01-13 00:15 | 2017-01-13 07:40 | 0 | 0 | 0 | 0.30903 | LVRD | Line hand tripped for Voltage regulation. BLB-428 kV | N-1327
NR140057 | 101280 | 400KV KNP-BLBGARH-III | 2017-01-13 22:28 | 2017-01-14 06:15 | 0 | 0 | 0 | 0.32431 | LVRD | Line hand tripped for Voltage regulation. Agra-426 kV | N-1411
NR140057 | 101314 | 400KV KNP-BLBGARH-III | 2017-01-15 21:29 | 2017-01-16 07:22 | 0 | 0 | 0 | 0.41181 | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV | N-1552
NR140057 | 101340 | 400KV KNP-BLBGARH-III | 2017-01-16 23:29 | 2017-01-17 09:15 | 0 | 0 | 0 | 0.40694 | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV | N-1690
NR140057 | 101361 | 400KV KNP-BLBGARH-III | 2017-01-18 01:12 | 2017-01-18 08:03 | 0 | 0 | 0 | 0.28542 | LVRD | Line hand tripped for Voltage regulation. Blb-429 kV | N-1808
NR140057 | 101382 | 400KV KNP-BLBGARH-III | 2017-01-19 00:09 | 2017-01-19 06:02 | 0 | 0 | 0 | 0.24514 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-1911
NR140057 | 101451 | 400KV KNP-BLBGARH-III | 2017-01-22 21:04 | 2017-01-23 09:37 | 0 | 0 | 0 | 0.52292 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-2244
NR140057 | 101481 | 400KV KNP-BLBGARH-III | 2017-01-23 23:30 | 2017-01-24 06:45 | 0 | 0 | 0 | 0.30208 | LVRD | Line hand tripped for Voltage regulation. Blb-426 kV | N-2356
NR140057 | 101497 | 400KV KNP-BLBGARH-III | 2017-01-24 21:06 | 2017-01-25 10:06 | 0 | 0 | 0 | 0.54167 | LVRD | Line hand tripped for Voltage regulation. Blb-427 kV | N-2453
NR140057 | 101525 | 400KV KNP-BLBGARH-III | 2017-01-25 21:02 | 2017-01-26 10:16 | 0 | 0 | 0 | 0.55139 | LVRD | Line hand tripped for Voltage regulation. Blb-418 kV | N-2571
NR140057 | 101555 | 400KV KNP-BLBGARH-III | 2017-01-26 20:34 | 2017-01-27 07:37 | 0 | 0 | 0 | 0.46042 | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV | N-2697
NR140057 | 101612 | 400KV KNP-BLBGARH-III | 2017-01-27 21:56 | 2017-01-28 06:53 | 0 | 0 | 0 | 0.37292 | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV | N-2871
NR140057 | 101632 | 400KV KNP-BLBGARH-III | 2017-01-28 23:22 | 2017-01-29 06:07 | 0 | 0 | 0 | 0.28125 | LVRD | Line hand tripped for Voltage regulation. Blb-425 kV | N-2961
NR140057 | 101647 | 400KV KNP-BLBGARH-III | 2017-01-29 23:24 | 2017-01-30 07:01 | 0 | 0 | 0 | 0.31736 | LVRD | Line hand tripped for Voltage regulation. Blb-429 kV | N-3038
NR140057 | 101665 | 400KV KNP-BLBGARH-III | 2017-01-30 22:12 | 2017-01-31 05:34 | 0 | 0 | 0 | 0.30694 | LVRD | Line hand tripped for Voltage regulation. Blb-429 kV | N-3130
|  | 400KV KNP-BLBGARH-III Total |  |  | 0 | 0 | 0 | 1900-01-08 19:26
NR140059 | 101464 | 400KV KNP-PANKI-II | 2017-01-23 18:04 | 2017-01-24 15:04 | 0 | 0 | 0 | 0.875 | OSFD | Line hand tripped by Panki end due to sparking in R-phase breaker at UPPCL end. DT received at KNP end .
|  | 400KV KNP-PANKI-II Total |  |  | 0 | 0 | 0 | 0.875
NR140070 | 101158 | 400KV LUCKNOW-GORAKH-III | 2017-01-08 00:33 | 2017-01-08 08:43 | 0 | 0 | 0 | 0.34028 | LVRD | Line hand tripped for Voltage regulation. LKO=435kv. | N-759
NR140070 | 101623 | 400KV LUCKNOW-GORAKH-III | 2017-01-28 12:02 | 2017-01-28 15:09 | 0.12986 | 0 | 0 | 0 | OSPT | S/D for jumpher tightening at loc. No. 202 by Gkp. | N-2922
|  | 400KV LUCKNOW-GORAKH-III Total |  |  | 0.12986 | 0 | 0 | 0.34028
NR140071 | 101159 | 400KV LUCKNOW-GORAKH-IV | 2017-01-08 00:33 | 2017-01-08 08:50 | 0 | 0 | 0 | 0.34514 | LVRD | Line hand tripped for Voltage regulation. LKO=435kv. | N-759
|  | 400KV LUCKNOW-GORAKH-IV Total |  |  | 0 | 0 | 0 | 0.34514
NR140114 | 101594 | 400KV LUCKNOW-ROSA-I | 2017-01-27 03:47 | 2017-01-27 03:52 | 0 | 0 | 0.0034722 | 0 | GOVC | Tripped on Over Voltage protection operated at Rosa end. DT received at Lko end. Rosa>432 kV
NR140114 | 101595 | 400KV LUCKNOW-ROSA-I | 2017-01-27 03:52 | 2017-01-27 12:41 | 0 | 0 | 0 | 0.36736 | LVRD | Line kept open for Voltage regulation. | N-2746
NR140114 | 101604 | 400KV LUCKNOW-ROSA-I | 2017-01-27 12:41 | 2017-01-27 19:28 | 0 | 0 | 0 | 0.28264 | OSFD | S/D by UPPCL to attend hot spot at their end. | N-2834
|  | 400KV LUCKNOW-ROSA-I Total |  |  | 0 | 0 | 0.0034722 | 0.65
NR140153 | 101328 | 400KV LUCKNOW-SHAHJHNPR-II | 2017-01-16 14:42 | 2017-01-16 15:10 | 0.019444 | 0 | 0 | 0 | OSPT | S/D for taking L/R in service at LKO end. | N-1646
|  | 400KV LUCKNOW-SHAHJHNPR-I Total |  |  | 0.019444 | 0 | 0 | 0
NR140141 | 101123 | 400KV LUCKNOW-SOHAWAL-I | 2017-01-07 00:12 | 2017-01-07 10:14 | 0 | 0 | 0 | 0.41806 | LVRD | Line hand tripped for Voltage regulation. Sohawal-429 kV | N-567
NR140141 | 101460 | 400KV LUCKNOW-SOHAWAL-I | 2017-01-23 09:10 | 2017-01-23 15:18 | 0.25556 | 0 | 0 | 0 | OSPT | S/D taken for AMP of line element and testing of SAS & SCADA at sohawla. | N-2279
|  | 400KV LUCKNOW-SOHAWAL-I Total |  |  | 0.25556 | 0 | 0 | 0.41806
NR140121 | 101510 | 400KV LUCKNOW-SOHAWAL-II | 2017-01-25 09:17 | 2017-01-25 17:31 | 0.34306 | 0 | 0 | 0 | OSPT | S/D for AMP work | N-2493
|  | 400KV LUCKNOW-SOHAWAL-II Total |  |  | 0.34306 | 0 | 0 | 0
NR140074 | 101367 | 400KV LUCKNOW-UNNAO-I | 2017-01-18 08:37 | 2017-01-18 20:58 | 0 | 0 | 0 | 0.51458 | OSFD | S/D by UPPCL for replacement of broken conductor at Unnao S/Y. | N-1835
|  | 400KV LUCKNOW-UNNAO-I Total |  |  | 0 | 0 | 0 | 0.51458
NR140084 | 101241 | 400KV RIHAND-ALLD-I | 2017-01-12 09:15 | 2017-01-12 18:47 | 0.39722 | 0 | 0 | 0 | OSPT | S/D for insulator cleaning and maintenance . | N-1248
|  | 400KV RIHAND-ALLD-I Total |  |  | 0.39722 | 0 | 0 | 0
NR140085 | 101221 | 400KV RIHAND-ALLD-II | 2017-01-11 10:08 | 2017-01-11 19:02 | 0.37083 | 0 | 0 | 0 | OSPT | S/D for insulator cleaning and maintenance . | N-1136
|  | 400KV RIHAND-ALLD-II Total |  |  | 0.37083 | 0 | 0 | 0
NR140091 | 101058 | 400KV SING-ALLD-I | 2017-01-03 09:39 | 2017-01-03 18:38 | 0.37431 | 0 | 0 | 0 | OSPT | S/D for Insulator cleaning and AMP work | N-229
NR140091 | 101060 | 400KV SING-ALLD-I | 2017-01-03 18:38 | 2017-01-03 21:22 | 0 | 0 | 0 | 0.11389 | OSPD | S/D continued by Singrauli NTPC for CT testing work. | N-229
NR140091 | 101076 | 400KV SING-ALLD-I | 2017-01-04 09:43 | 2017-01-04 18:24 | 0.36181 | 0 | 0 | 0 | OSPT | S/D for Insulator cleaning and AMP work | N-326
|  | 400KV SING-ALLD-I Total |  |  | 0.73611 | 0 | 0 | 0.11389
NR140092 | 101093 | 400KV SING-ALLD-II | 2017-01-05 08:15 | 2017-01-05 18:46 | 0.43819 | 0 | 0 | 0 | OSPT | S/D for Insulator cleaning and AMP work | N-410
NR140092 | 101108 | 400KV SING-ALLD-II | 2017-01-05 08:15 | 2017-01-05 18:46 | 0.43819 | 0 | 0 | 0 | OSPT | S/D for Insulator cleaning and AMP work | N-495
|  | 400KV SING-ALLD-II Total |  |  | 0.87639 | 0 | 0 | 0
NR140093 | 101028 | 400KV SING-ANPARA | 2017-01-02 00:15 | 2017-01-02 02:10 | 0 | 0 | 0.079861 | 0 | LNCC | Tripped on R-N fault during dense fog, FLR:Sing-N/a. Anpara-1.3km.
NR140093 | 101465 | 400KV SING-ANPARA | 2017-01-23 17:09 | 2017-01-23 19:50 | 0.11181 | 0 | 0 | 0 | OSPT | S/D taken by NTPC for testing of PLCC. | N- 2321
|  | 400KV SING-ANPARA Total |  |  | 0.11181 | 0 | 0.079861 | 0
NR140095 | 101138 | 400KV SING-LKO(UP) | 2017-01-07 10:34 | 2017-01-07 18:15 | 0.32014 | 0 | 0 | 0 | OSPT | S/D for insulator cleaning and other maintenance work in line. PTW returned by PG at 17:30 hrs. | N-655
NR140095 | 101142 | 400KV SING-LKO(UP) | 2017-01-07 18:15 | 2017-01-07 21:32 | 0 | 0 | 0 | 0.13681 | OSFD | S/D continued by Sing NTPC for CT testing work. | N-655
NR140095 | 101163 | 400KV SING-LKO(UP) | 2017-01-08 09:34 | 2017-01-08 19:23 | 0.40903 | 0 | 0 | 0 | OSPT | S/D for insulator cleaning and other maintenance work in line. | N-794
|  | 400KV SING-LKO(UP) Total |  |  | 0.72917 | 0 | 0 | 0.13681
NR140097 | 101029 | 400KV SING-RIHAND-II | 2017-01-02 00:33 | 2017-01-02 01:09 | 0 | 0 | 0.025 | 0 | LNCC | Tripped on R-N fault during dense fog. FLR:Sing-15km, Rhnd-25km
NR140097 | 101186 | 400KV SING-RIHAND-II | 2017-01-09 07:36 | 2017-01-09 09:17 | 0.070139 | 0 | 0 | 0 | LEFT | Line tripped on R-N fault. FLR:Rh-24.8 km, Sing-12.5km
NR140097 | 101191 | 400KV SING-RIHAND-II | 2017-01-09 19:40 | 2017-01-09 20:38 | 0 | 0.040278 | 0 | 0 | OMSU | A/R from Sing but tripped from Rihand-NTPC due to A/R problem on R-N fault. FLR:Sing-16.83km, Rhnd-24.7km
NR140097 | 101205 | 400KV SING-RIHAND-II | 2017-01-10 11:08 | 2017-01-10 17:05 | 0.24792 | 0 | 0 | 0 | OSFT | S/D for damage Insulator replacement. | N-1015
NR140097 | 101206 | 400KV SING-RIHAND-II | 2017-01-10 17:05 | 2017-01-10 18:29 | 0 | 0 | 0 | 0.058333 | OSFD | S/D continued by Rihand (NTPC) for relay testing work. | N-1015
|  | 400KV SING-RIHAND-II Total |  |  | 0.31806 | 0.040278 | 0.025 | 0.058333
N-W40002 | 101384 | 400KV SING-VINDH-II | 2017-01-19 10:40 | 2017-01-19 22:54 | 0 | 0 | 0 | 0.50972 | SCSD | S/D for retrofitmet of PLCC & LMU at Vindh PG. | N-1942
|  | 400KV SING-VINDH-II Total |  |  | 0 | 0 | 0 | 0.50972
NR340004 | 101009 | 400KV VARANASI-SARNATH-I | 2017-01-01 08:40 | 2017-01-03 12:51 | 0 | 0 | 0 | 1900-01-01 04:11 | LPRD | Line hand tripped for Power regulation | N-41
NR340004 | 101095 | 400KV VARANASI-SARNATH-I | 2017-01-05 12:50 | 2017-01-05 13:24 | 0 | 0 | 0 | 0 | OMSU | Tripped due to CVT fuse fail at Sarnath/UPPCL end.
NR340004 | 101223 | 400KV VARANASI-SARNATH-I | 2017-01-11 14:03 | 2017-01-17 08:54 | 0 | 0 | 0 | 1900-01-04 18:51 | LPRD | Line hand tripped for Power regulation. | N-1161
NR340004 | 101457 | 400KV VARANASI-SARNATH-I | 2017-01-23 01:15 | 2017-01-23 02:24 | 0.047917 | 0 | 0 | 0 | LEFT | Tripped on B-N fault FLR 2.5 Km from Vrnsi.
NR340004 | 101598 | 400KV VARANASI-SARNATH-I | 2017-01-27 06:47 | 2017-01-27 07:11 | 0.016667 | 0 | 0 | 0 | LEFT | Tripped on B-N fault, FLR, Vrns-2.5km
NR340004 | 101621 | 400KV VARANASI-SARNATH-I | 2017-01-28 11:35 | 2017-01-28 17:39 | 0.25278 | 0 | 0 | 0 | OSPT | S/D for tightening of OPGW wire by VNS T/L. | N-2913
|  | 400KV VARANASI-SARNATH-I Total |  |  | 0.31736 | 0 | 0 | 1900-01-06 23:02
NR340005 | 101011 | 400KV VARANASI-SARNATH-II | 2017-01-01 09:17 | 2017-01-11 18:42 | 0 | 0 | 0 | 1900-01-09 09:25 | LPRD | Line hand tripped for Power regulation | N-44
NR340005 | 101326 | 400KV VARANASI-SARNATH-II | 2017-01-16 08:35 | 2017-01-16 08:50 | 0 | 0.010417 | 0 | 0 | OMSU | CB A/trip at Sarnath-UP end only due to local problem. Line remain charged from VNS end. No flag Facia reported.
NR340005 | 101329 | 400KV VARANASI-SARNATH-II | 2017-01-16 16:58 | 2017-01-22 11:17 | 0 | 0 | 0 | 1900-01-04 18:19 | OSPD | S/D by UPPCL for attending CB air leakage at Sarnath end. | N-1657
NR340005 | 101599 | 400KV VARANASI-SARNATH-II | 2017-01-27 06:47 | 2017-01-27 11:54 | 0 | 0.21319 | 0 | 0 | OMSU | CB auto tripped only from Sarnath(UPPCL) end. Remain charged from Vrnsi end
|  | 400KV VARANASI-SARNATH-II Total |  |  | 0 | 0.22361 | 0 | 1900-01-15 03:44
NR340003 | 101403 | 400KV VARANASI-SASARAM(ER) | 2017-01-20 09:27 | 2017-01-20 15:40 | 0.25903 | 0 | 0 | 0 | OSFT | S/D by ER for for attending hot spot in isolator at their end. | N-2034
NR340003 | 101511 | 400KV VARANASI-SASARAM(ER) | 2017-01-25 09:18 | 2017-01-25 19:07 | 0.40903 | 0 | 0 | 0 | OSFT | S/D by ER for isolator rectification work at Sasaram | N-2491
|  | 400KV VARANASI-SASARAM(ER) Total |  |  | 0.66806 | 0 | 0 | 0
NR122012 | 101271 | 220KV DGANGA-BLY(UP)-II | 2017-01-13 12:07 | 2017-01-13 15:27 | 0 | 0 | 0 | 0.13889 | OSPD | S/D by Dhganga-NHPC to attend CB problem. | N-1364
|  | 220KV DGANGA-BLY(UP)-II Total |  |  | 0 | 0 | 0 | 0.13889
NR122013 | 101128 | 220KV DGANGA-PITHORAGRH | 2017-01-07 01:03 | 2017-01-07 07:21 | 0 | 0 | 0.2625 | 0 | GOVC | Trip on O/VOL protn at Dhauliganga-NHPC, D/T recd at Pithoragh. D,ganga=238kv.
NR122013 | 101561 | 220KV DGANGA-PITHORAGRH | 2017-01-26 22:32 | 2017-01-26 22:37 | 0 | 0 | 0.0034722 | 0 | GOVC | Tripped on Over Voltage protection operated at Dganga end. DT received at Pthrgrh end.
NR122013 | 101562 | 220KV DGANGA-PITHORAGRH | 2017-01-26 22:37 | 2017-01-27 08:04 | 0 | 0 | 0 | 0.39375 | LVRD | Line kept open for Voltage regulation. | N-2721
|  | 220KV DGANGA-PITHORAGRH Total |  |  | 0 | 0 | 0.26597 | 0.39375
NR122038 | 101622 | 220KV FATEHPUR-FTHPR(UP)-I | 2017-01-28 11:38 | 2017-01-28 16:33 | 0 | 0 | 0 | 0.20486 | OSPD | S/D by UPPCL to attend burnt isolator at their end. | N-2919
|  | 220KV FATEHPUR-FTHPR(UP)-I Total |  |  | 0 | 0 | 0 | 0.20486
NR122039 | 101327 | 220KV FATEHPUR-FTHPR(UP)-II | 2017-01-16 08:56 | 2017-01-16 15:07 | 0 | 0 | 0 | 0.25764 | OSFD | Line hand tripped by UPPCL due to melting of R-ph isolator contact at their end.
|  | 220KV FATEHPUR-FTHPR(UP)-II Total |  |  | 0 | 0 | 0 | 0.25764
NR122040 | 101140 | 220KV FATEHPUR-KNP SOUTH | 2017-01-07 12:26 | 2017-01-07 17:02 | 0 | 0 | 0 | 0.19167 | OSPD | S/D by UPPCL for maintenance work at KNP(S) end. | N-665
|  | 220KV FATEHPUR-KNP SOUTH Total |  |  | 0 | 0 | 0 | 0.19167
NR122041 | 101013 | 220KV FATEHPUR-NAUBASTA | 2017-01-01 14:00 | 2017-01-01 15:42 | 0 | 0.070833 | 0 | 0 | OMSU | Tripped on R-Y fault in UPPCL portion, FLR:Fthpr-73 km, Naubasta-3.4km.
NR122041 | 101139 | 220KV FATEHPUR-NAUBASTA | 2017-01-07 11:01 | 2017-01-07 13:49 | 0 | 0 | 0 | 0.11667 | OSPD | S/D by UPPCL for maintenance work at Naubasta end. | N-651
|  | 220KV FATEHPUR-NAUBASTA Total |  |  | 0 | 0.070833 | 0 | 0.11667
NR122016 | 101251 | 220KV KNP-MAINPURI | 2017-01-12 17:26 | 2017-01-12 20:32 | 0 | 0 | 0 | 0.12917 | OSFD | S/D taken by UPPCL for maintenance at Mainpuri end. | N-1291
NR122016 | 101371 | 220KV KNP-MAINPURI | 2017-01-18 13:00 | 2017-01-18 18:45 | 0 | 0 | 0 | 0.23958 | LCSD | S/D for stringing of new 400kV Lucknow-Kanpur D/C line. | N-1854
NR122016 | 101385 | 220KV KNP-MAINPURI | 2017-01-19 13:20 | 2017-01-19 19:31 | 0 | 0 | 0 | 0.25764 | LCSD | S/D for stringing of new 400kV Lucknow-Kanpur D/C line. | N-1959
NR122016 | 101407 | 220KV KNP-MAINPURI | 2017-01-20 13:24 | 2017-01-20 19:26 | 0 | 0 | 0 | 0.25139 | LCSD | S/D for stringing of new 400kV Lucknow-Kanpur D/C line. | N-2058
|  | 220KV KNP-MAINPURI Total |  |  | 0 | 0 | 0 | 0.87778
NR122018 | 101586 | 220KV KNP-PANKI-I | 2017-01-27 03:34 | 2017-01-27 05:19 | 0.072917 | 0 | 0 | 0 | LART | A/R from Knp end & tripped at Panki end, FLR, Panki- 5.29 km.
|  | 220KV KNP-PANKI-I Total |  |  | 0.072917 | 0 | 0 | 0
NR122024 | 101190 | 220KV PITHORAGRH-BRLY(UP) | 2017-01-09 15:35 | 2017-01-09 17:01 | 0 | 0.059722 | 0 | 0 | OMSU | Line tripped on R-Y fault in Z-2. Fault in UP system. FLR-PTH-178.7Km (Line length-177.7km)
|  | 220KV PITHORAGRH-BRLY(UP) Total |  |  | 0 | 0.059722 | 0 | 0
NR122026 | 101054 | 220KV RAIBRLY-LKO(UP) | 2017-01-03 03:50 | 2017-01-03 05:11 | 0 | 0.05625 | 0 | 0 | OMSU | CB auto tripped at Lko(UP) end due to disturbance in UPPCL system. Line remain charged from Raibareilly.
|  | 220KV RAIBRLY-LKO(UP) Total |  |  | 0 | 0.05625 | 0 | 0
NR122033 | 101600 | 220KV TNKPR-BLY(UP) | 2017-01-27 03:45 | 2017-01-27 07:13 | 0 | 0 | 0.14444 | 0 | GOVC | Tripped on Over Voltage protection operated at Tanakpur end. DT received at Bareily end.
|  | 220KV TNKPR-BLY(UP) Total |  |  | 0 | 0 | 0.14444 | 0
NR1ICT43 | 101583 | 100MVA ICT-I PITHORAGRH | 2017-01-27 02:32 | 2017-01-27 09:12 | 0 | 0 | 0.27778 | 0 | GOFC | ICT trippings on Over Fluxing.
|  | 100MVA ICT-I PITHORAGRH Total |  |  | 0 | 0 | 0.27778 | 0
NR1ICT44 | 101585 | 100MVA ICT-II PITHORAGRH | 2017-01-27 03:20 | 2017-01-27 09:12 | 0 | 0 | 0.24444 | 0 | GOFC | ICT trippings on Over Fluxing.
|  | 100MVA ICT-II PITHORAGRH Total |  |  | 0 | 0 | 0.24444 | 0
NR1ICT01 | 101222 | 315MVA ICT-I ALLAHABAD | 2017-01-11 13:20 | 2017-01-11 14:37 | 0 | 0 | 0 | 0.053472 | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. | N-1171
|  | 315MVA ICT-I ALLAHABAD Total |  |  | 0 | 0 | 0 | 0.053472
NR1ICT02 | 101224 | 315MVA ICT-II ALLAHABAD | 2017-01-11 14:39 | 2017-01-11 14:52 | 0 | 0 | 0 | 0.0090278 | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. | N-1171
|  | 315MVA ICT-II ALLAHABAD Total |  |  | 0 | 0 | 0 | 0.0090278
NR1ICT67 | 101225 | 315MVA ICT-III ALLAHABAD | 2017-01-11 14:55 | 2017-01-11 15:10 | 0 | 0 | 0 | 0.010417 | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. | N-1171
|  | 315MVA ICT-III ALLAHABAD Total |  |  | 0 | 0 | 0 | 0.010417
NR1ICT26 | 101085 | 315MVA ICT-I MAINPURI | 2017-01-04 21:06 | 2017-01-04 21:42 | 0 | 0 | 0 | 0 | OMST | Tripped due to 400KV Bus Bar-II protection operated during opening of 400KV BLB and FTPR-I line for V/regulation.
|  | 315MVA ICT-I MAINPURI Total |  |  | 0 | 0 | 0 | 0
NR1ICT715 | 101243 | 765/400KV ICT-I BAREILLY | 2017-01-12 10:47 | 2017-01-12 11:51 | 0 | 0 | 0 | 0.044444 | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. | N-1262
|  | 765/400KV ICT-I BAREILLY Total |  |  | 0 | 0 | 0 | 0.044444
NR1ICT716 | 101246 | 765/400KV ICT-II BAREILLY | 2017-01-12 11:58 | 2017-01-12 12:31 | 0 | 0 | 0 | 0.022917 | LVRD | S/D for tap changing for V/regulation by NRLDC instruction. | N-1266
|  | 765/400KV ICT-II BAREILLY Total |  |  | 0 | 0 | 0 | 0.022917
NR1ICT717 | 101173 | 765/400KV ICT-I VARANASI | 2017-01-08 16:48 | 2017-01-08 19:11 | 0.099306 | 0 | 0 | 0 | OMST | ICT tripped on PRD operation.
|  | 765/400KV ICT-I VARANASI Total |  |  | 0.099306 | 0 | 0 | 0
NR1ICT718 | 101352 | 765/400KV ICT-II VARANASI | 2017-01-17 16:52 | 2017-01-17 17:04 | 0.0083333 | 0 | 0 | 0 | OSFT | S/D for topping of SF-6 Gas in 33 kV tertiary Breaker. | N-1773
|  | 765/400KV ICT-II VARANASI Total |  |  | 0.0083333 | 0 | 0 | 0
NR1ICT704 | 101269 | 765/400KV ICT-II LUCKNOW | 2017-01-13 09:32 | 2017-01-13 15:55 | 0 | 0 | 0 | 0.26597 | SCSD | S/D for replace m,ent of R-ph with spare unit. | N-1359
|  | 765/400KV ICT-II LUCKNOW Total |  |  | 0 | 0 | 0 | 0.26597
NR3ICT701 | 101428 | 240MVAR B/Reactor-I BAREILLY-765 | 2017-01-21 12:15 | 2017-01-21 13:33 | 0.054167 | 0 | 0 | 0 | OSFT | Forcely open to attend sparking in R ph isolator. | N-2146
|  | 240MVAR B/Reactor-I BAREILLY-765 Total |  |  | 0.054167 | 0 | 0 | 0
NR1BRT23 | ** | 330MVAR B/Reactor-III FTHPR-765 | 2017-01-01 10:18 | 2017-01-01 19:55 | 0 | 0 | 0 | 0.40069 | SVRD | H/ tripped for voltage regulation<755kv. (Standing Instrn)
NR1BRT23 | ** | 330MVAR B/Reactor-III FTHPR-765 | 2017-01-04 10:10 | 2017-01-04 21:20 | 0 | 0 | 0 | 0.46528 | SVRD | H/ tripped for voltage regulation<755kv. (Standing Instrn)
|  | SUB TOTAL |  |  | 0 | 0 | 0 | 0.86597
[5 empty] | 1900-01-10 07:47 | 0.53264 | 1900-01-01 02:41 | 1900-11-02 20:51
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Classification/ Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUBTOTAL(9,F13:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Classification/ Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUBTOTAL(9,G13:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Classification/ Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUBTOTAL(9,H13:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Classification/ Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUBTOTAL(9,I13:[Deemed Available, row above])