## SOP DATA NR3 Oct-16
POWERGRID CORPORATION OF INDIA LIMITED.
SUMMARY OF ELEMENT WISE OUTAGES & AVAILABILITY
NAME OF REGION : NR-III
Availability calculation for the Period : From 01.10.2016 to 31.10.2016
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES | [17 empty] | NRPC | [6 empty] | 0
1 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR3 | -- | 2016-10-02 09:25 | 2016-10-02 19:18 |  |  |  | 0 | 0 | 0 | 0.41181 |  |  |  | LCSD | S/D by WR for OPGW stringing in Diamond formation at crossing of Agra-Gwalior D/C line. | [7 empty] | 744
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.41181 | [6 empty] | 744 | 1327 | 148.034 | 196441.118 | 196441.118 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2016-10-02 17:31 | 2016-10-03 14:55 |  |  |  | 0 | 0 | 0 | 0.89167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra=780kv.
[6 empty] | 2016-10-05 03:18 | 2016-10-05 10:36 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra=780kv.
[6 empty] | 2016-10-05 23:20 | 2016-10-06 12:51 |  |  |  | 0 | 0 | 0 | 0.56319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra=774kv.
[6 empty] | 2016-10-07 01:09 | 2016-10-07 10:08 |  |  |  | 0 | 0 | 0 | 0.37431 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra=777kv.
[6 empty] | 2016-10-09 16:40 | 2016-10-10 10:32 |  |  |  | 0 | 0 | 0 | 0.74444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 788 kv.
[6 empty] | 2016-10-11 09:11 | 2016-10-12 09:33 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:22 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 788 kv.
[6 empty] | 2016-10-12 17:40 | 2016-10-13 09:58 |  |  |  | 0 | 0 | 0 | 0.67917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 788 kv.
[6 empty] | 2016-10-13 22:52 | 2016-10-14 09:24 |  |  |  | 0 | 0 | 0 | 0.43889 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 778 kv.
[6 empty] | 2016-10-14 21:55 | 2016-10-17 09:25 |  |  |  | 0 | 0 | 0 | 1900-01-01 11:30 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 786 kv.
[6 empty] | 2016-10-17 21:32 | 2016-10-18 09:38 |  |  |  | 0 | 0 | 0 | 0.50417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 786 kv.
[6 empty] | 2016-10-22 01:33 | 2016-10-23 11:52 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:19 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra- 780 kv.
[6 empty] | 2016-10-25 23:07 | 2016-10-26 09:41 |  |  |  | 0 | 0 | 0 | 0.44028 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra>780kv
[6 empty] | 2016-10-28 02:11 | 2016-10-28 10:07 |  |  |  | 0 | 0 | 0 | 0.33056 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789 kv
[6 empty] | 2016-10-29 16:06 | 2016-11-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:54 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-789 kv
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-11 12:35 | [6 empty] | 744 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2016-10-23 21:07 | 2016-10-24 10:04 |  |  |  | 0 | 0 | 0 | 0.50417 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra- 785 kv.
[6 empty] | 2016-10-24 21:50 | 2016-10-25 09:40 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:19 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra- 785 kv.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 22:25 | [6 empty] | 744 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176504 | 765KV AGRA-JHATIKALA | 253.076 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1747 | 253.076 | 442123.772 | 442123.772 | 100
5 | NR176503 | 765KV FATEHPUR-GAYA | 484.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1070 | 484.6 | 518522 | 518522 | 100
6 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1067 | 355.008 | 378793.536 | 378793.536 | 100
7 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
8 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 256393.647 | 100
9 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | 2016-10-05 10:33 | 2016-10-05 20:07 |  |  |  | 0 | 0 | 0 | 0.39861 |  |  |  | LCSD | S/D for Jumpering/ commissioning of new Bus reactor unit at Varanasi.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.39861 | [6 empty] | 744 | 1419 | 165.98 | 235525.62 | 235525.62 | 100
10 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | 2016-10-05 09:31 | 2016-10-05 19:53 |  |  |  | 0 | 0 | 0 | 0.43194 |  |  |  | LCSD | S/D for Jumpering/ commissioning of new Bus reactor unit at Varanasi.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.43194 | [6 empty] | 744 | 1393 | 223 | 310639 | 310639 | 100
11 | NR176514 | 765KV VARANASI-GAYA-I | 264 | NR3 | -- | 2016-10-07 16:20 | 2016-10-07 18:57 |  |  |  | 0.10903 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend R-Ph L/R oil leakage at Varanasi end. Line charged without L/R at VNS.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10903 | 0 | 0 | 0 | [6 empty] | 744 | 1108 | 264 | 292512 | 291483.228 | 99.6483
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1440 | 465.8 | 670752 | 670752 | 100
13 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
14 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
B |  | 400 KV TRANS LINES |  |  | --
1 | NR140001 | 400KV AGRA-AGRA(UP)-I | 29.982 | NR3 | -- | 2016-10-15 08:34 | 2016-10-19 12:34 | -- | -- |  | 0 | 0 | 0 | 1900-01-03 04:00 | -- | -- | -- | LCSD | S/D for LILO of this line at Fatehabad 765kv UP sub-station under Lalitpur-Agra transmission project. LILO lines synchronised successfully.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-03 04:00 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2016-10-01 | 2016-10-04 09:39 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 09:39 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV. Open since 0728hrs on 28.09.16
[6 empty] | 2016-10-09 16:26 | 2016-10-18 08:36 |  |  |  | 0 | 0 | 0 | 1900-01-07 16:10 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv.
[6 empty] | 2016-10-23 08:34 | 2016-10-23 19:21 |  |  |  | 0 | 0 | 0 | 0.44931 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-24 08:44 | 2016-10-24 19:12 |  |  |  | 0 | 0 | 0 | 0.43611 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-25 08:24 | 2016-10-25 18:51 |  |  |  | 0 | 0 | 0 | 0.43542 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-26 08:07 | 2016-10-26 19:38 |  |  |  | 0 | 0 | 0 | 0.47986 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-27 08:03 | 2016-10-27 18:33 |  |  |  | 0 | 0 | 0 | 0.4375 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-13 07:32 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2016-10-05 15:30 | 2016-10-05 16:17 |  |  |  | 0.032639 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault in reclaim time. FLR:Agra-91.2km
[6 empty] | 2016-10-18 08:46 | 2016-10-18 19:33 |  |  |  | 0 | 0 | 0 | 0.44931 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-19 07:32 | 2016-10-19 19:23 |  |  |  | 0 | 0 | 0 | 0.49375 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-20 08:19 | 2016-10-20 19:34 |  |  |  | 0 | 0 | 0 | 0.46875 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-21 07:55 | 2016-10-21 19:26 |  |  |  | 0 | 0 | 0 | 0.47986 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-22 08:11 | 2016-10-22 19:06 |  |  |  | 0 | 0 | 0 | 0.45486 |  |  |  | LCSD | S/D for polymer insulator installation for grid strengthening.
[6 empty] | 2016-10-29 10:05 | 2016-10-29 11:40 |  |  |  | 0.065972 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending sparking in relay panel at Agra end.
[6 empty] | 2016-10-30 21:58 | 2016-11-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:02 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.098611 | 0 | 0 | 1900-01-02 10:21 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61167.206 | 99.6819
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- | 2016-10-16 04:25 | 2016-10-17 09:06 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 04:41 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra= 432 kv.
[6 empty] | 2016-10-31 21:44 | 2016-11-01 |  |  |  | 0 | 0 | 0 | 0.094444 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:57 | [6 empty] | 744 | 245 | 211.433 | 51801.085 | 51801.085 | 100
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2016-10-14 02:56 | 2016-10-14 06:58 | -- | -- | -- | 0 | 0 | 0 | 0.16806 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra=437kv.
[6 empty] | 2016-10-28 22:17 | 2016-10-29 06:38 |  |  |  | 0 | 0 | 0 | 0.34792 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.51597 | [6 empty] | 744 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2016-10-01 | 2016-10-03 11:02 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 11:02 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV. Open since 1803hrs on 26.09.16
[6 empty] | 2016-10-03 17:41 | 2016-10-06 14:58 |  |  |  | 0 | 0 | 0 | 1900-01-01 21:17 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 433 kv.
[6 empty] | 2016-10-08 04:05 | 2016-10-11 18:59 |  |  |  | 0 | 0 | 0 | 1900-01-02 14:54 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv.
[6 empty] | 2016-10-12 00:11 | 2016-10-12 10:24 |  |  |  | 0 | 0 | 0 | 0.42569 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv.
[6 empty] | 2016-10-13 03:10 | 2016-10-15 12:42 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:32 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv.
[6 empty] | 2016-10-15 21:53 | 2016-10-16 11:59 |  |  |  | 0 | 0 | 0 | 0.5875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 432 kv.
[6 empty] | 2016-10-16 15:22 | 2016-10-20 09:50 |  |  |  | 0 | 0 | 0 | 1900-01-02 18:28 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv.
[6 empty] | 2016-10-22 21:43 | 2016-10-24 09:24 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:41 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV
[6 empty] | 2016-10-24 21:19 | 2016-10-28 07:24 |  |  |  | 0 | 0 | 0 | 1900-01-02 10:05 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV
[6 empty] | 2016-10-29 21:32 | 2016-11-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 02:28 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-22 03:46 | [6 empty] | 744 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | 2016-10-17 13:52 | 2016-10-17 13:52 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on R-N fault. ALLD=64.5km, Fpur=67km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
10 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
11 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 155.932 | 80304.98 | 80304.98 | 100
12 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 224 | 115360 | 115360 | 100
13 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 98.792 | 50877.88 | 50877.88 | 100
14 | NR140016 | 400KV ALLD-SASARAM | 212 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 369 | 212 | 78228 | 78228 | 100
13 | NR140017 | 400KV BALIA-BIHARSHRF-I | 241.79 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 598 | 241.79 | 144590.42 | 144590.42 | 100
14 | NR140020 | 400KV BALIA-BIHARSHRF-II | 241.79 | NR3 | -- | 2016-10-09 06:40 | 2016-10-09 06:40 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | LART | A/R on Y-N fault. FLR:Balia- 135.2 km , IF(Balia)-3.73 KA
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 598 | 241.79 | 144590.42 | 144590.42 | 100
15 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- | 2016-10-04 11:20 | 2016-10-04 15:39 | -- | -- |  | 0 | 0.17986 | 0 | 0 | -- | -- | -- | SEFU | Tripped due to bus fault at Mau UPPCL, caused by CB blast of their 400 kV Anpara Line.
[6 empty] | 2016-10-04 15:39 | 2016-10-05 14:06 |  |  |  | 0 | 0 | 0 | 0.93542 |  |  |  | OSFD | Line charged from Balia end but remain open due to forced S/D by UPPCL to attend Bus & DC earth fault at Mau.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.17986 | 0 | 0.93542 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
16 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- | 2016-10-04 11:20 | 2016-10-04 15:39 | -- | -- | -- | 0 | 0.17986 | 0 | 0 | -- | -- | -- | SEFU | Tripped due to bus fault at Mau UPPCL, caused by CB blast of their 400 kV Anpara Line.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.17986 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 13 | 6695 | 6695 | 100
17 | NR140021 | 400KV BALIA-PATNA-I | 195.32 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 195.32 | 134966.12 | 134966.12 | 100
18 | NR140022 | 400KV BALIA-PATNA-II | 195.32 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 195.32 | 134966.12 | 134966.12 | 100
19 | NR140136 | 400KV BALIA-PATNA-III | 185 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 524 | 185 | 96940 | 96940 | 100
20 | NR140137 | 400KV BALIA-PATNA-IV | 185 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 524 | 185 | 96940 | 96940 | 100
21 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | 2016-10-14 10:52 | 2016-10-14 13:55 |  |  |  | 0.12708 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending CVT problem at Sohawal end.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.12708 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 51806.747 | 99.5901
22 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 227 | 229.163 | 52020.001 | 52020.001 | 100
23 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
24 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
25 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
26 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 9.2 | 4738 | 4738 | 100
27 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 331 | 278.76 | 92269.56 | 92269.56 | 100
28 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
29 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | 2016-10-24 15:57 | 2016-10-24 15:57 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/R on B-N fault, FLR-Brly-58.8Km.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
30 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
31 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 115.926 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
31 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 | 100
32 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 |  | 2016-10-01 13:30 | 2016-10-01 18:10 |  |  |  | 0.19444 | 0 | 0 | 0 |  |  |  | LEFT | Trip on R-N fault in reclaim time. Brly=47.5km.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.19444 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 101.841 | 69964.767 | 69525.9199 | 99.3728
33 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 |  | 2016-10-06 13:38 | 2016-10-06 13:38 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on B-N fault. FLR:Bly-71.99 km, IF-1.73 kA.
[6 empty] | 2016-10-09 13:54 | 2016-10-09 13:54 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/Reclosed on Y-N fault. FLR-34.9 km(BRLY)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
34 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2016-10-16 04:17 | 2016-10-16 12:02 | -- | -- | -- | 0 | 0 | 0 | 0.32292 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv.
[6 empty] | 2016-10-16 21:58 | 2016-10-17 10:18 |  |  |  | 0 | 0 | 0 | 0.51389 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv.
[6 empty] | 2016-10-23 21:29 | 2016-10-24 09:24 |  |  |  | 0 | 0 | 0 | 0.49653 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV
[6 empty] | 2016-10-25 23:09 | 2016-10-26 07:33 |  |  |  | 0 | 0 | 0 | 0.35 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv.
[6 empty] | 2016-10-28 01:24 | 2016-10-28 07:32 |  |  |  | 0 | 0 | 0 | 0.25556 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv.
[6 empty] | 2016-10-29 01:11 | 2016-10-29 08:45 |  |  |  | 0 | 0 | 0 | 0.31528 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 06:06 | -- | -- | -- |  |  |  | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
35 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- | 2016-10-30 00:52 | 2016-11-01 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 23:08 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. Blb-430 kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 23:08 | -- | -- | -- |  |  |  | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
36 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2016-10-16 04:20 | 2016-10-16 12:06 | -- | -- | -- | 0 | 0 | 0 | 0.32361 | -- | -- | -- | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv.
[6 empty] | 2016-10-16 21:58 | 2016-10-17 10:17 |  |  |  | 0 | 0 | 0 | 0.51319 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv.
[6 empty] | 2016-10-23 17:11 | 2016-10-24 10:04 |  |  |  | 0 | 0 | 0 | 0.70347 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Ftpr-425 kV
[6 empty] | 2016-10-25 23:11 | 2016-10-26 07:11 |  |  |  | 0 | 0 | 0 | 0.33333 |  |  |  | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 20:58 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
37 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
38 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- | 2016-10-06 10:10 | 2016-10-06 19:09 | -- | -- | -- | 0.37431 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for AMP and priwinter maintenance work.
[6 empty] | 2016-10-07 09:26 | 2016-10-07 18:47 |  |  |  | 0.38958 | 0 | 0 | 0 |  |  |  | OSPT | S/D for AMP and priwinter maintenance work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.76389 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23076.1025 | 97.5358
39 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | 2016-10-20 09:32 | 2016-10-20 20:03 |  |  |  | 0.43819 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work by GKP s/s.
[6 empty] | 2016-10-21 09:50 | 2016-10-21 18:58 |  |  |  | 0.38056 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work by GKP(Pg) S/S.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.81875 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 45.94 | 23659.1 | 23034.2326 | 97.3589
40 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | 2016-10-19 11:34 | 2016-10-19 13:00 |  |  |  | 0.059722 | 0 | 0 | 0 |  |  |  | OSPT | S/D for taking line reactor in Service at KNP end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.059722 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 291 | 240 | 69840 | 69705.4516 | 99.8073
41 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | 2016-10-05 09:20 | 2016-10-06 17:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:07 |  |  |  | OSPD | S/D by NTPC for AMP at Auraiya end.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:07 | -- | -- | -- |  |  |  | 744 | 515 | 72.6 | 37389 | 37389 | 100
42 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.2 | 37698 | 37698 | 100
43 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2016-10-04 12:24 | 2016-10-04 12:24 | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- | LART | Line A/R on R-N fault. FLR:BLB-145.6 km , IF - 2.3 KA
[6 empty] | 2016-10-16 04:22 | 2016-10-16 14:40 |  |  |  | 0 | 0 | 0 | 0.42917 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv.
[6 empty] | 2016-10-16 21:59 | 2016-10-17 12:02 |  |  |  | 0 | 0 | 0 | 0.58542 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv.
[6 empty] | 2016-10-18 04:35 | 2016-10-18 04:35 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on B-N fault. KNP=144.6km,
[6 empty] | 2016-10-23 21:31 | 2016-10-24 11:10 |  |  |  | 0 | 0 | 0 | 0.56875 |  |  |  | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV
[6 empty] | 2016-10-24 11:10 | 2016-10-24 13:51 |  |  |  | 0.11181 | 0 | 0 | 0 |  |  |  | OSFT | S/D for attending broken conductor strand by MNP T/L.
[6 empty] | 2016-10-28 02:04 | 2016-10-28 06:40 |  |  |  | 0 | 0 | 0 | 0.19167 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb>422kv.
[6 empty] | 2016-10-30 00:16 | 2016-10-30 00:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on R-N fault, FLR:Knp-250km
[6 empty] | 2016-10-30 15:44 | 2016-11-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:16 |  |  |  | LVRD | Line hand tripped for Voltage regulation. Blb-431 kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.11181 | 0 | 0 | 1900-01-02 02:52 | -- | -- | -- |  |  |  | 744 | 342 | 385.69 | 131905.98 | 131430.2438 | 99.6393
44 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
45 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- | 2016-10-14 13:57 | 2016-10-14 13:57 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | LART | A/R on Y-N fault, FLR, Blb-22.3km, Knp-302.49km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
46 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- | 2016-10-14 09:48 | 2016-10-17 19:01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 09:13 | -- | -- | -- | LCSD | S/D for line isolator retrofitment at Knp, under Add cap.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 09:13 | -- | -- | -- |  |  |  | 744 | 515 | 107.079 | 55145.685 | 55145.685 | 100
47 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 107.1 | 55156.5 | 55156.5 | 100
48 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 5.922 | 3049.83 | 3049.83 | 100
49 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 5.86 | 3017.9 | 3017.9 | 100
50 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- | 2016-10-26 09:36 | 2016-10-26 19:15 | -- | -- |  | 0.40208 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for line and other AMP work.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.40208 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 75287.2962 | 98.703
51 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- | 2016-10-27 09:40 | 2016-10-27 19:20 | -- | -- | -- | 0.40278 | 0 | 0 | 0 | -- | -- | -- | OSPT | S/D for line and other AMP work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.40278 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 289 | 263.933 | 76276.637 | 75285.5875 | 98.7007
52 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
53 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
54 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
55 | NR140114 | 400KV LUCKNOW-ROSA-I | 169.785 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 371 | 169.785 | 62990.235 | 62990.235 | 100
56 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 169.729 | 87410.435 | 87410.435 | 100
57 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
58 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
59 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- | 2016-10-07 12:43 | 2016-10-07 15:50 | -- | -- | -- | 0 | 0.12986 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on Y-N fault in UPPCL portion. FLR-Lko-83.6Km, If-3.97KA.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.12986 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
60 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
61 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
62 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 30.703 | 21215.773 | 21215.773 | 100
63 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 691 | 31.159 | 21530.869 | 21530.869 | 100
64 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- | 2016-10-08 02:44 | 2016-10-08 03:03 | -- | -- | -- | 0.013194 | 0 | 0 | 0 | -- | -- | -- | LEFT | Line tripped from Alld and remain chrged from Rihand end, on Y-N fault, FLR-Rhd-175.7Km, Allah-192Km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.013194 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 120861.6211 | 99.9574
65 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | 2016-10-08 02:44 | 2016-10-08 02:44 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Line A/R on Y-N fault, FLR-Rhd-264Km, Allah-192Km, If-1.156KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 433 | 279.245 | 120913.085 | 120913.085 | 100
66 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 210 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 368 | 210 | 77280 | 77280 | 100
67 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 210 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 368 | 210 | 77280 | 77280 | 100
68 | NR140090 | 400KV SASARAM-SARNATH | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 76 | 39140 | 39140 | 100
| NR340003 | 400KV VARANASI-SASARAM(ER) | 47.52 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 47.52 | 24472.8 | 24472.8 | 100
69 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 332 | 224 | 74368 | 74368 | 100
70 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 306 | 202 | 61812 | 61812 | 100
71 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 25.057 | 12904.355 | 12904.355 | 100
72 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | 2016-10-04 12:29 | 2016-10-04 13:04 |  |  |  | 0.024306 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped on B-N fault. FLR:Ftpr-225.2 km , IF-3.6 KA
[6 empty] | 2016-10-04 16:42 | 2016-10-04 20:38 |  |  |  | 0.16389 | 0 | 0 | 0 |  |  |  | OSFT | S/D to attend line isolator jumper problem at Fatehpur.
[6 empty] | 2016-10-05 13:03 | 2016-10-05 19:07 |  |  |  | 0.25278 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on R-N fault in reclaim time. FLR:Fthpr-237.3km
[6 empty] | 2016-10-08 10:46 | 2016-10-08 19:06 |  |  |  | 0.34722 | 0 | 0 | 0 |  |  |  | OSPT | S/D for replacement of damaged insulator string by Mirzapur.
[6 empty] | 2016-10-09 17:06 | 2016-10-09 17:34 |  |  |  | 0.019444 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped on B-N fault. FLR-FTPR-67.1km.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.80764 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 236 | 330.953 | 78104.908 | 76070.0512 | 97.3947
73 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- | 2016-10-09 23:25 | 2016-10-10 00:01 | -- | -- |  | 0 | 0.019444 | 0 | 0 | -- | -- | -- | SEFU | Line tripped due to R-Phase WT burn at singrauli end.
[6 empty] | 2016-10-10 00:01 | 2016-10-10 20:31 |  |  |  | 0 | 0 | 0 | 0.85417 |  |  |  | OSFD | Forced S/D taken by NTPC for replacement of faulty Wave trap at Singaurali.
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.019444 | 0 | 0.85417 | -- | -- | -- |  |  |  | 744 | 337 | 408.6 | 137698.2 | 137698.2 | 100
74 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 42.026 | 21643.39 | 21643.39 | 100
75 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 43.952 | 22635.28 | 22635.28 | 100
76 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | 2016-10-12 12:35 | 2016-10-12 16:49 |  |  |  | 0.17639 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped on B-N fault. No FLR at both end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.17639 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 3.341 | 1720.615 | 1710.8248 | 99.431
77 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 515 | 3.317 | 1708.255 | 1708.255 | 100
78 | NR140164 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | 2016-10-25 09:27 | 2016-10-25 20:11 |  |  |  | 0 | 0 | 0 | 0.44722 |  |  |  | LPRD | Line hand tripped for Power regulation.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.44722 | -- | -- | -- |  |  |  | 744 | 515 | 69.677 | 35883.655 | 35883.655 | 100
79 | NR140165 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | 2016-10-25 10:14 | 2016-10-25 20:22 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | LPRD | Line hand tripped for Power regulation.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.42222 | -- | -- | -- |  |  |  | 744 | 515 | 69.677 | 35883.655 | 35883.655 | 100
80 | N-W40004 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
81 | N-W40004 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR3 | -- | 2016-10-09 08:41 | 2016-10-09 12:13 | -- | -- |  | 0 | 0 | 0 | 0.14722 | -- | -- | -- | OSFD | S/D taken by UPPCL for attending hot spot at Jhusi end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.14722 | -- | -- | -- |  |  |  | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- | 2016-10-16 08:48 | 2016-10-16 20:31 | -- | -- |  | 0 | 0 | 0 | 0.48819 | -- | -- | -- | OSPD | S/D for stringing of 220kv D/C Allahabad-GSS Naini line by Railway.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.48819 | -- | -- | -- |  |  |  | 744 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | 2016-10-06 13:41 | 2016-10-06 21:01 |  |  |  | 0 | 0 | 0 | 0.30556 |  |  |  | OSFD | S/D by UPPCL to attend hotspot in Bus A isolator clamp at Rewa Road .
[5 empty] | -- | 2016-10-16 08:48 | 2016-10-16 20:31 |  |  |  | 0 | 0 | 0 | 0.48819 |  |  |  | OSPD | S/D for stringing of 220kv D/C Allahabad-GSS Naini line by Railway.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.79375 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
10 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
11 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
16 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 109 | 234.59 | 25570.31 | 25570.31 | 100
17 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 156 | 59.01 | 9205.56 | 9205.56 | 100
18 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
19 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
20 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | 2016-10-06 00:23 | 2016-10-06 00:42 |  |  |  | 0 | 0.013194 | 0 | 0 |  |  |  | OMSU | A/R from Fthpr but tripped from Knp(UPPCL) end on B-N fault in their portion. FLR:Fthpr-3.5km
[6 empty] | 2016-10-11 11:58 | 2016-10-11 12:56 |  |  |  | 0 | 0.040278 | 0 | 0 |  |  |  | OMSU | Line tripped on R-N fault in UPPCL portion. Ftpr-17.5Km
[6 empty] | 2016-10-14 12:34 | 2016-10-14 12:57 |  |  |  | 0 | 0.015972 | 0 | 0 |  |  |  | OMSU | A/R at Fthpr(Pg) but tripped from Knp (UP) end on R-N fault in their portion. FLR:Fthpr-26.7 km.
[6 empty] | 2016-10-15 15:31 | 2016-10-15 20:08 |  |  |  | 0 | 0.19236 | 0 | 0 |  |  |  | OMSU | Line tripped on R-N fault in UPPCL portion. FLR-Fthpr-25.5km. If-5.94KA,
[5 empty] | -- | 2016-10-24 11:45 | 2016-10-24 20:40 |  |  |  | 0 | 0.37153 | 0 | 0 |  |  |  | OMSU | Line tripped on R-Y Fault in UPPCL portion. FLR-Ftpr-77.5Km, If-6.02KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.63333 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
21 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | 2016-10-07 12:30 | 2016-10-07 14:49 |  |  |  | 0 | 0.19236 | 0 | 0 |  |  |  | OMSU | Line tripped on B-N fault in UPPCL portion. FLR-Ftpr-39.7Km, If-9.6KA.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.19236 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
28 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- | 2016-10-11 11:54 | 2016-10-11 17:46 |  |  | -- | 0 | 0.24444 | 0 | 0 | -- | -- | -- | OMSU | Line tripped on B-N fault in UPPCL portion. FLR-MNP-24Km, If-4.56KA, KNP-134.2Km
[6 empty] | 2016-10-12 11:11 | 2016-10-12 19:17 |  |  |  | 0 | 0.3375 | 0 | 0 |  |  |  | OMSU | Line tripped on B-N fault in UPPCL portion. Z-II, FLR-MNP-11.9Km, KNP-160.6Km
[6 empty] | 2016-10-14 06:09 | 2016-10-14 22:15 |  |  |  | 0 | 0 | 0 | 0.67083 |  |  |  | OSFD | S/D by UPPCL for attending sparking at loc-435-436 under their jurisdiction.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.58194 | 0 | 0.67083 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
29 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | 2016-10-16 12:56 | 2016-10-16 16:16 |  |  |  | 0 | 0 | 0 | 0.13889 |  |  |  | OSPD | S/D by UPPCL for maintenance at Naubasta end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.13889 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
30 | NR122018 | 220KV KNP-PANKI-I | 10.4 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
31 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
32 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | 2016-10-05 21:35 | 2016-10-05 21:35 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on R-N fault, FLR, Knp-67.41 km
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
33 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- | 2016-10-19 13:53 | 2016-10-19 14:18 | -- | -- | -- | 0 | 0.017361 | 0 | 0 | -- | -- | -- | OMSU | Line tripped only from Unchahar end on R-N fault and A/R from LKO end.FLR-UCHR-135.6 km , If-1.623 KAmp
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.017361 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
34 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
35 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
42 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 156 | 177.88 | 27749.28 | 27749.28 | 100
43 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
44 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
54 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 105.72 | 13955.04 | 13955.04 | 100
55 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 106 | 13992 | 13992 | 100
56 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 42.55 | 5616.6 | 5616.6 | 100
57 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
58 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
59 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 132 | 42.5 | 5610 | 5610 | 100
[5 empty] | -- | [17 empty] | 1831.389
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 | 58 | 2900 | 2900 | 100
| Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-03 02:03 | 1899-12-31 22:25 | 0 | 1900-03-21 09:45 | [8 empty] | 19666.447 | 10751535.6 | 10743764.8821 | 99.9277 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.955 | % (AC) | 93.1226 | %'(HVDC)
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
7 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS) | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
8 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS) | 1500 | NR3 | -- | 2016-10-03 18:47 | 2016-10-03 22:37 |  |  |  | 0.15972 | 0 | 0 | 0 | -- | -- | -- | OSFT | Forced S/D due to high Acetelene gas content in its B-phase unit.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.15972 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1492.2715 | 99.4848
9 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
10 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT713 | 765/400kv ICT-I MEERUT | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT714 | 765/400kv ICT-II MEERUT | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
13 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
14 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 1500 |  | 1500 | 1500 | 100
F |  | 400/220 KV ICT'S |  | NR3 | --
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | 2016-10-22 10:58 | 2016-10-23 04:47 |  |  |  | 0 | 0 | 0 | 0.74236 |  |  |  | LCSD | S/D for 220kV BUS extension work at Agra.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.74236 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 500 |  | 500 | 500 | 100
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 315 |  | 315 | 315 | 100
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR3 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
[11 empty] | 0 | 0 | 0 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | 2016-10-01 13:25 | 2016-10-01 18:20 |  |  |  | 0 | 0 | 0 | 0.20486 |  |  |  | OSFD | S/D by UPPCL to attend jackbus hotspot in their132kv S/Y.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.20486 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 100 | NR3 | -- | 2016-10-01 13:25 | 2016-10-01 18:20 |  |  |  | 0 | 0 | 0 | 0.20486 |  |  |  | OSFD | S/D by UPPCL to attend jackbus hotspot in their132kv S/Y.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.20486 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 100 | NR3 | -- | 2016-10-01 13:25 | 2016-10-01 18:20 |  |  |  | 0 | 0 | 0 | 0.20486 |  |  |  | OSFD | S/D by UPPCL to attend jackbus hotspot in their132kv S/Y.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.20486 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 100 |  | 100 | 100 | 100
--
41 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 0.31944 | 0 | 0 | 1900-01-01 17:08 | [7 empty] | 30925 |  | 30925 | 30917.2715 | 99.975 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2016-10-06 08:28 | 2016-10-06 22:04 |  |  |  | 0 | 0 | 0 | 0.56667 |  |  |  | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur.
[6 empty] | 2016-10-07 08:00 | 2016-10-07 22:24 |  |  |  | 0 | 0 | 0 | 0.6 |  |  |  | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur.
[6 empty] | 2016-10-25 11:03 | 2016-10-25 11:40 |  |  |  | 0.025694 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on DC line fault. FLR:Rh-91.5km, Dadri-725.5Km
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.025694 | 0 | 0 | 1899-12-31 04:00 | [6 empty] | 744 | 750 | 815 | 611250 | 610743.3636 | 99.9171
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2016-10-06 08:34 | 2016-10-06 22:17 |  |  |  | 0 | 0 | 0 | 0.57153 |  |  |  | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur.
[6 empty] | 2016-10-07 08:07 | 2016-10-07 20:10 |  |  |  | 0 | 0 | 0 | 0.50208 |  |  |  | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur.
[6 empty] | 2016-10-09 05:58 | 2016-10-09 05:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on transient fault. FLR:Rhnd-590.3km, Dad-224.7km
[6 empty] | 2016-10-14 01:26 | 2016-10-14 01:26 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | DC line transient fault. FLR:Rhnd-289.14km, Dad-525.86km
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 01:46 | [6 empty] | 744 | 750 | 815 | 611250 | 611250 | 100
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | 2016-10-22 00:43 | 2016-10-22 00:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | T/Fault, FLR:Bal-251.44km, Bhw-538.35km, faulty loc-688
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2016-10-01 02:23 | 2016-10-01 02:23 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | T/Fault. FLR:Bwd-558.2km, Balia-231.6km, Faulty loc-634
[6 empty] | 2016-10-18 03:07 | 2016-10-18 03:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | DC line T/Fault, BWD=532.56km, Balia=257.23km.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
4 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2016-10-13 01:52 | 2016-10-13 02:48 |  |  |  | 0.038889 | 0 | 0 | 0 |  |  |  | OMST | Trip due to Valve cooling problem at BNC end.
[6 empty] | 2016-10-18 09:51 | 2016-10-27 22:00 |  |  |  | 0 | 0 | 0 | 1900-01-08 12:09 |  |  |  | SCSD | S/D for Pole-3 equipment erection & integration in adjacent DC valve hall and Stringing work of Agra(UP)-Agra(S) line.
[6 empty] | 2016-10-27 22:00 | 2016-10-28 11:12 |  |  |  | 0 | 0 | 0 | 0.55 |  |  |  | LVRD | Kept open for Voltage/Power regulation at NER end after PTW returned and pole ready for charging.
[6 empty] | 2016-10-28 15:57 | 2016-10-28 16:43 |  |  |  | 0 | 0 | 0 | 0.031944 |  |  |  | LPRD | P/Flow blocked for switching over to metalic return mode.
[6 empty] | 2016-10-29 05:34 | 2016-10-29 09:37 |  |  |  | 0.16875 | 0 | 0 | 0 |  |  |  | OSFT | Pole-1 blocked due to heavy sparking observed in Y-Phase of AC PLC capacitor at Agra.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.20764 | 0 | 0 | 1900-01-09 02:07 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2574638.7097 | 99.3302
1 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | 2016-10-13 01:52 | 2016-10-13 02:48 |  |  |  | 0.038889 | 0 | 0 | 0 |  |  |  | OMST | Trip due to Valve cooling problem at BNC end.
[6 empty] | 2016-10-13 15:49 | 2016-10-13 22:18 |  |  |  | 0.27014 | 0 | 0 | 0 |  |  |  | OSFT | Hand tripped due to valve cooling auxiliary supply problem at Agra end.
[6 empty] | 2016-10-14 07:26 | 2016-10-14 09:45 |  |  |  | 0.096528 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to filer bank problem at BNC end.
[6 empty] | 2016-10-15 11:08 | 2016-10-15 12:30 |  |  |  | 0.056944 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to software problem found in valve cooling at Agra end.
[6 empty] | 2016-10-24 09:57 | 2016-10-24 14:05 |  |  |  | 0.17222 | 0 | 0 | 0 |  |  |  | OSFT | Forced S/D due to problem in the OLTC mechanism of Y-ph star converter transformer at BNC.
[6 empty] | 2016-10-26 21:36 | 2016-10-26 22:42 |  |  |  | 0 | 0 | 0.045833 | 0 |  |  |  | GOVC | Trip on O/VOL protn opted at BNC end.
[6 empty] | 2016-10-28 12:06 | 2016-10-29 18:16 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:10 |  |  |  | LPRD | Pole hand tripped for power regulation.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.63472 | 0 | 0.045833 | 1899-12-31 06:10 | [6 empty] | 742.9 | 1500 | 1728 | 2592000 | 2538850.4509 | 97.9495
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0.86806 | 0 | 0.045833 | 1900-01-12 14:03 | 0 | 0 | 0 | [5 empty] | 6665.572 | 8380965 | 8309947.5242 | 99.1526 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2016-10-01 | 2016-10-01 11:23 |  |  |  | 0.47431 | 0 | 0 | 0 |  |  |  | OMST | Trip on DC over current protn in Valve hall. Open since 0024hrs on 29.09.16
[6 empty] | 2016-10-07 10:27 | 2016-10-07 11:05 |  |  |  | 0.026389 | 0 | 0 | 0 |  |  |  | OSFT | S/D for isolating faulty AC harmonic filter breaker BIZ21.
[6 empty] | 2016-10-12 11:05 | 2016-10-12 14:03 |  |  |  | 0.12361 | 0 | 0 | 0 |  |  |  | OMST | Trip on fine water conductivity alarm.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.62431 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 244.9653 | 97.9861
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | 2016-10-14 21:56 | 2016-10-29 18:28 |  |  |  | 1900-01-13 20:32 | 0 | 0 | 0 |  |  |  | OMST | Tripped on AC-conductor ground fault protection. Out for damaged bushing replacement & AMP work.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-13 20:32 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 130.1971 | 52.0789
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-14 11:31 | 0 | 0 | 0 | [9 empty] | 500 | 375.1624 | 75.0325 | %
HVDC BTB SASARAM
| NEDCB01 | +/-500MW HVDC B/B SASARAM | 500 | [7 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | TOTAL FOR HVDC SASARAM | [8 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 530 | 530 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY | 50 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | --
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 50 |  | 50 | 50 | 100
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 50 | NR3 | -- | 2016-10-04 10:52 | 2016-10-11 17:26 |  |  |  | 0 | 0 | 0 | 1900-01-06 06:34 |  |  |  | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-06 06:34 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
20 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 330 |  | 330 | 330 | 100
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 125 |  | 125 | 125 | 100
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [15 empty] | 744 | 125 |  | 125 | 125 | 100
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
28 | NR1BRT41 | 240MVAR B/Reactor-I MEERUT-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 744 | 240 |  | 240 | 240 | 100
29 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | 2016-10-21 09:02 | 2016-10-30 03:02 |  |  |  | 0 | 0 | 0 | 1900-01-07 18:00 |  |  |  | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 18:00 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
30 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 80 |  | 80 | 80 | 100
31 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
32 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
33 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
34 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | --
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 125 |  | 125 | 125 | 100
35 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
36 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
37 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
38 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
39 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
40 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
41 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
42 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
43 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
44 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
45 | NR1SRT24 | GORAKH 80MVAR S/R BARH-I LINE | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
46 | NR1SRT25 | GORAKH 80MVAR S/R BARH-II LINE | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
47 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
48 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
49 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
50 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
51 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
52 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
53 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
54 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
55 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  |  | 744 | 240 |  | 240 | 240 | 100
56 | NR1BRT51 | 330MVAR B/Reactor-II VARANASI | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
|  | TOTAL FOR BUS REACTORS | [8 empty] | 0 | 0 | 0 | 1900-01-31 01:08 | [9 empty] | 8068.4 | 8068.4 | 100 | %
|  | TOTAL | [8 empty] | 1900-01-19 18:04 | 1899-12-31 22:25 | 0.045833 | 1900-05-08 18:04
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L11:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M11:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N11:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O11:[Deemed Available, row above])
Note on C11: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C52: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C55: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C58: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C77: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C81: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C211: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C214: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C386: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C389: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C568: DOC-15/06/14
Note on C569: DOC-26/09/14

## Sheet1
POWER GRID CORPORATION OF INDIA LTD.
NORTHERN REGION - 1
CPCC, N. DELHI
DOC No: NR-I/CPCC/II
MONTH – Oct-2016 LINE/ ICT OUTAGE DETAILS
NRLDC CODE | CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Classification/ Category Code | REASON OF OUTAGE | NRLDC CODE
|  |  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[6 empty] | @ (T) | # (U) | & ( C ) | * (D)
[6 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Code
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12
| NR1DCB01 | 109211 | VINDH HVDC B/B BLOCK-I | 2016-10-01 | 2016-10-01 11:23 | 0.47431 | 0 | 0 | 0 | OMST | Trip on DC over current protn in Valve hall. Open since 0024hrs on 29.09.16
| NR1DCB01 | 110078 | VINDH HVDC B/B BLOCK-I | 2016-10-07 10:27 | 2016-10-07 11:05 | 0.026389 | 0 | 0 | 0 | OSFT | S/D for isolating faulty AC harmonic filter breaker BIZ21. | N-452
| NR1DCB01 | 110121 | VINDH HVDC B/B BLOCK-I | 2016-10-12 11:05 | 2016-10-12 14:03 | 0.12361 | 0 | 0 | 0 | OMST | Trip on fine water conductivity alarm.
|  |  | VINDH HVDC B/B BLOCK-I Total |  |  | 0.62431 | 0 | 0 | 0
| NR1DCB02 | 110165 | VINDH HVDC B/B BLOCK-II | 2016-10-14 21:56 | 2016-10-29 18:28 | 1900-01-13 20:32 | 0 | 0 | 0 | OMST | Tripped on AC-conductor ground fault protection. Out for damaged bushing replacement & AMP work.
|  |  | VINDH HVDC B/B BLOCK-II Total |  |  | 1900-01-13 20:32 | 0 | 0 | 0
| NRNEDCP01 | 110128 | 800KV HVDC AGRA-BNC POLE-I | 2016-10-13 01:52 | 2016-10-13 02:48 | 0.038889 | 0 | 0 | 0 | OMST | Trip due to Valve cooling problem at BNC end.
| NRNEDCP01 | 110206 | 800KV HVDC AGRA-BNC POLE-I | 2016-10-18 09:51 | 2016-10-27 22:00 | 0 | 0 | 0 | 1900-01-08 12:09 | SCSD | S/D for Pole-3 equipment erection & integration in adjacent DC valve hall and Stringing work of Agra(UP)-Agra(S) line. | NL-522
N-435 | NRNEDCP01 | 110305 | 800KV HVDC AGRA-BNC POLE-I | 2016-10-27 22:00 | 2016-10-28 11:12 | 0 | 0 | 0 | 0.55 | LVRD | Kept open for Voltage/Power regulation at NER end after PTW returned and pole ready for charging.
N-1132 | NRNEDCP01 | 110314 | 800KV HVDC AGRA-BNC POLE-I | 2016-10-28 15:57 | 2016-10-28 16:43 | 0 | 0 | 0 | 0.031944 | LPRD | P/Flow blocked for switching over to metalic return mode. | NL-902
| NRNEDCP01 | 110324 | 800KV HVDC AGRA-BNC POLE-I | 2016-10-29 05:34 | 2016-10-29 09:37 | 0.16875 | 0 | 0 | 0 | OSFT | Pole-1 blocked due to heavy sparking observed in Y-Phase of AC PLC capacitor at Agra.
N-3753 |  |  | 800KV HVDC AGRA-BNC POLE-I Total |  |  | 0.20764 | 0 | 0 | 1900-01-09 02:07
| NRNEDCP02 | 110129 | 800KV HVDC AGRA-BNC POLE-II | 2016-10-13 01:52 | 2016-10-13 02:48 | 0.038889 | 0 | 0 | 0 | OMST | Trip due to Valve cooling problem at BNC end.
| NRNEDCP02 | 110138 | 800KV HVDC AGRA-BNC POLE-II | 2016-10-13 15:49 | 2016-10-13 22:18 | 0.27014 | 0 | 0 | 0 | OSFT | Hand tripped due to valve cooling auxiliary supply problem at Agra end.
N-977 | NRNEDCP02 | 110149 | 800KV HVDC AGRA-BNC POLE-II | 2016-10-14 07:26 | 2016-10-14 09:45 | 0.096528 | 0 | 0 | 0 | OMST | Tripped due to filer bank problem at BNC end.
| NRNEDCP02 | 110170 | 800KV HVDC AGRA-BNC POLE-II | 2016-10-15 11:08 | 2016-10-15 12:30 | 0.056944 | 0 | 0 | 0 | OMST | Tripped due to software problem found in valve cooling at Agra end.
| NRNEDCP02 | 110265 | 800KV HVDC AGRA-BNC POLE-II | 2016-10-24 09:57 | 2016-10-24 14:05 | 0.17222 | 0 | 0 | 0 | OSFT | Forced S/D due to problem in the OLTC mechanism of Y-ph star converter transformer at BNC.
N-3179 | NRNEDCP02 | 110294 | 800KV HVDC AGRA-BNC POLE-II | 2016-10-26 21:36 | 2016-10-26 22:42 | 0 | 0 | 0.045833 | 0 | GOVC | Trip on O/VOL protn opted at BNC end.
| NRNEDCP02 | 110313 | 800KV HVDC AGRA-BNC POLE-II | 2016-10-28 12:06 | 2016-10-29 18:16 | 0 | 0 | 0 | 1899-12-31 06:10 | LPRD | Pole hand tripped for power regulation. | NL-900
|  |  | 800KV HVDC AGRA-BNC POLE-II Total |  |  | 0.63472 | 0 | 0.045833 | 1899-12-31 06:10
| NR1DCP01 | 110058 | 500KV HVDC R-D POLE-I | 2016-10-06 08:28 | 2016-10-06 22:04 | 0 | 0 | 0 | 0.56667 | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur. | N- 351
| NR1DCP01 | 110072 | 500KV HVDC R-D POLE-I | 2016-10-07 08:00 | 2016-10-07 22:24 | 0 | 0 | 0 | 0.6 | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur. | N-435
| NR1DCP01 | 110282 | 500KV HVDC R-D POLE-I | 2016-10-25 11:03 | 2016-10-25 11:40 | 0.025694 | 0 | 0 | 0 | LEFT | Tripped on DC line fault. FLR:Rh-91.5km, Dadri-725.5Km
|  |  | 500KV HVDC R-D POLE-I Total |  |  | 0.025694 | 0 | 0 | 1899-12-31 04:00
| NR1DCP02 | 110059 | 500KV HVDC R-D POLE-II | 2016-10-06 08:34 | 2016-10-06 22:17 | 0 | 0 | 0 | 0.57153 | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur. | N- 352
| NR1DCP02 | 110074 | 500KV HVDC R-D POLE-II | 2016-10-07 08:07 | 2016-10-07 20:10 | 0 | 0 | 0 | 0.50208 | LCSD | S/D by UPPCL for stringing of their line & diversion work by POWERGRID-Kanpur. | N-436
| NR1DCP02 | 110090 | 500KV HVDC R-D POLE-II | 2016-10-09 05:58 | 2016-10-09 05:58 | 0 | 0 | 0 | 0 | LART | A/R on transient fault. FLR:Rhnd-590.3km, Dad-224.7km
| NR1DCP02 | 110146 | 500KV HVDC R-D POLE-II | 2016-10-14 01:26 | 2016-10-14 01:26 | 0 | 0 | 0 | 0 | LART | DC line transient fault. FLR:Rhnd-289.14km, Dad-525.86km
|  |  | 500KV HVDC R-D POLE-II Total |  |  | 0 | 0 | 0 | 1899-12-31 01:46
| NR1DCP03 | 110234 | 500KV HVDC BALIA-BHWD POLE-I | 2016-10-22 00:43 | 2016-10-22 00:43 | 0 | 0 | 0 | 0 | LART | T/Fault, FLR:Bal-251.44km, Bhw-538.35km, faulty loc-688
|  |  | 500KV HVDC BALIA-BHWD POLE-I Total |  |  | 0 | 0 | 0 | 0
N-187 | NR1DCP04 | 110001 | 500KV HVDC BALIA-BHWD POLE-II | 2016-10-01 02:23 | 2016-10-01 02:23 | 0 | 0 | 0 | 0 | LART | T/Fault. FLR:Bwd-558.2km, Balia-231.6km, Faulty loc-634
N-986 | NR1DCP04 | 110201 | 500KV HVDC BALIA-BHWD POLE-II | 2016-10-18 03:07 | 2016-10-18 03:07 | 0 | 0 | 0 | 0 | LART | DC line T/Fault, BWD=532.56km, Balia=257.23km.
N-1214 |  |  | 500KV HVDC BALIA-BHWD POLE-II Total |  |  | 0 | 0 | 0 | 0
N-1314 | NR176502 | 110022 | 765KV AGRA-FATEHPUR-I | 2016-10-02 17:31 | 2016-10-03 14:55 | 0 | 0 | 0 | 0.89167 | LVRD | Line hand tripped for Voltage regulation. Agra=780kv. | N-98
N-1415 | NR176502 | 110039 | 765KV AGRA-FATEHPUR-I | 2016-10-05 03:18 | 2016-10-05 10:36 | 0 | 0 | 0 | 0.30417 | LVRD | Line hand tripped for Voltage regulation. Agra=780kv. | N-260
N-1701 | NR176502 | 110056 | 765KV AGRA-FATEHPUR-I | 2016-10-05 23:20 | 2016-10-06 12:51 | 0 | 0 | 0 | 0.56319 | LVRD | Line hand tripped for Voltage regulation. Agra=774kv. | N-336
N-2361 | NR176502 | 110067 | 765KV AGRA-FATEHPUR-I | 2016-10-07 01:09 | 2016-10-07 10:08 | 0 | 0 | 0 | 0.37431 | LVRD | Line hand tripped for Voltage regulation. Agra=777kv. | N-419
N-2601 | NR176502 | 110096 | 765KV AGRA-FATEHPUR-I | 2016-10-09 16:40 | 2016-10-10 10:32 | 0 | 0 | 0 | 0.74444 | LVRD | Line hand tripped for Voltage regulation. Agra= 788 kv. | N-585
| NR176502 | 110107 | 765KV AGRA-FATEHPUR-I | 2016-10-11 09:11 | 2016-10-12 09:33 | 0 | 0 | 0 | 1899-12-31 00:22 | LVRD | Line hand tripped for Voltage regulation. Agra= 788 kv. | N-675
N-15 | NR176502 | 110125 | 765KV AGRA-FATEHPUR-I | 2016-10-12 17:40 | 2016-10-13 09:58 | 0 | 0 | 0 | 0.67917 | LVRD | Line hand tripped for Voltage regulation. Agra= 788 kv. | N-759
N-93 | NR176502 | 110142 | 765KV AGRA-FATEHPUR-I | 2016-10-13 22:52 | 2016-10-14 09:24 | 0 | 0 | 0 | 0.43889 | LVRD | Line hand tripped for Voltage regulation. Agra= 778 kv. | N-862
N-280 | NR176502 | 110164 | 765KV AGRA-FATEHPUR-I | 2016-10-14 21:55 | 2016-10-17 09:25 | 0 | 0 | 0 | 1900-01-01 11:30 | LVRD | Line hand tripped for Voltage regulation. Agra= 786 kv. | N-974
N-390 | NR176502 | 110200 | 765KV AGRA-FATEHPUR-I | 2016-10-17 21:32 | 2016-10-18 09:38 | 0 | 0 | 0 | 0.50417 | LVRD | Line hand tripped for Voltage regulation. Agra= 786 kv. | N-1209
N-592 | NR176502 | 110235 | 765KV AGRA-FATEHPUR-I | 2016-10-22 01:33 | 2016-10-23 11:52 | 0 | 0 | 0 | 1899-12-31 10:19 | LVRD | Line hand tripped for Voltage regulation. Agra- 780 kv. | N-1592
N-753 | NR176502 | 110283 | 765KV AGRA-FATEHPUR-I | 2016-10-25 23:07 | 2016-10-26 09:41 | 0 | 0 | 0 | 0.44028 | LVRD | Line hand tripped for Voltage regulation. Agra>780kv | N-1947
N-821 | NR176502 | 110310 | 765KV AGRA-FATEHPUR-I | 2016-10-28 02:11 | 2016-10-28 10:07 | 0 | 0 | 0 | 0.33056 | LVRD | Line hand tripped for Voltage regulation. Agra-789 kv | N-2147
N-1100 | NR176502 | 110329 | 765KV AGRA-FATEHPUR-I | 2016-10-29 16:06 | 2016-11-01 | 0 | 0 | 0 | 1900-01-01 07:54 | LVRD | Line hand tripped for Voltage regulation. Agra-789 kv | N-2280
N-1504 |  |  | 765KV AGRA-FATEHPUR-I Total |  |  | 0 | 0 | 0 | 1900-01-11 12:35
N-1567 | NR176507 | 110256 | 765KV AGRA-FATEHPUR-II | 2016-10-23 21:07 | 2016-10-24 10:04 | 0 | 0 | 0 | 0.53958 | LVRD | Line hand tripped for Voltage regulation. Agra- 785 kv. | N-1739
N-1796 | NR176507 | 110273 | 765KV AGRA-FATEHPUR-II | 2016-10-24 21:50 | 2016-10-25 09:40 | 0 | 0 | 0 | 0.49306 | LVRD | Line hand tripped for Voltage regulation. Agra- 785 kv. | N-1855
N-1908 |  |  | 765KV AGRA-FATEHPUR-II Total |  |  | 0 | 0 | 0 | 1899-12-31 00:47
N-1990 | NR176510 | 110017 | 765KV AGRA-GR.NOIDA | 2016-10-02 09:25 | 2016-10-02 19:18 | 0 | 0 | 0 | 0.41181 | LCSD | S/D by WR for OPGW stringing in Diamond formation at crossing of Agra-Gwalior D/C line. | N-68
N-2092 |  |  | 765KV AGRA-GR.NOIDA Total |  |  | 0 | 0 | 0 | 0.41181
N-2186 | NR176512 | 110044 | 765KV VARANASI-BALIA | 2016-10-05 10:33 | 2016-10-05 20:07 | 0 | 0 | 0 | 0.39861 | LCSD | S/D for Jumpering/ commissioning of new Bus reactor unit at Varanasi. | N-273
N-2252 |  |  | 765KV VARANASI-BALIA Total |  |  | 0 | 0 | 0 | 0.39861
N-2361 | NR176513 | 110043 | 765KV VARANASI-FATEHPUR | 2016-10-05 09:31 | 2016-10-05 19:53 | 0 | 0 | 0 | 0.43194 | LCSD | S/D for Jumpering/ commissioning of new Bus reactor unit at Varanasi. | N-272
N-2577 |  |  | 765KV VARANASI-FATEHPUR Total |  |  | 0 | 0 | 0 | 0.43194
N-2708 | NR176514 | 110081 | 765KV VARANASI-GAYA-I | 2016-10-07 16:20 | 2016-10-07 18:57 | 0.10903 | 0 | 0 | 0 | OSFT | S/D to attend R-Ph L/R oil leakage at Varanasi end. Line charged without L/R at VNS. | N-471
N-2876 |  |  | 765KV VARANASI-GAYA-I Total |  |  | 0.10903 | 0 | 0 | 0
N-2959 | NR140001 | 110166 | 400KV AGRA-AGRA(UP)-I | 2016-10-15 08:34 | 2016-10-19 12:34 | 0 | 0 | 0 | 1900-01-03 04:00 | LCSD | S/D for LILO of this line at Fatehabad 765kv UP sub-station under Lalitpur-Agra transmission project. LILO lines synchronised successfully. | N-999
N-3029 |  |  | 400KV AGRA-AGRA(UP)-I Total |  |  | 0 | 0 | 0 | 1900-01-03 04:00
N-3136 | NR140003 | 109201 | 400KV AGRA-AURAIYA-I | 2016-10-01 | 2016-10-04 09:39 | 0 | 0 | 0 | 1900-01-02 09:39 | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV. Open since 0728hrs on 28.09.16 | N-1516
N-3214 | NR140003 | 110095 | 400KV AGRA-AURAIYA-I | 2016-10-09 16:26 | 2016-10-18 08:36 | 0 | 0 | 0 | 1900-01-07 16:10 | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv. | N-584
| NR140003 | 110246 | 400KV AGRA-AURAIYA-I | 2016-10-23 08:34 | 2016-10-23 19:21 | 0 | 0 | 0 | 0.44931 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1690
N-94 | NR140003 | 110261 | 400KV AGRA-AURAIYA-I | 2016-10-24 08:44 | 2016-10-24 19:12 | 0 | 0 | 0 | 0.43611 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1770
N-190 | NR140003 | 110279 | 400KV AGRA-AURAIYA-I | 2016-10-25 08:24 | 2016-10-25 18:51 | 0 | 0 | 0 | 0.43542 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1875
N-291 | NR140003 | 110287 | 400KV AGRA-AURAIYA-I | 2016-10-26 08:07 | 2016-10-26 19:38 | 0 | 0 | 0 | 0.47986 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1969
N-564 | NR140003 | 110296 | 400KV AGRA-AURAIYA-I | 2016-10-27 08:03 | 2016-10-27 18:33 | 0 | 0 | 0 | 0.4375 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-2060
N-767 |  |  | 400KV AGRA-AURAIYA-I Total |  |  | 0 | 0 | 0 | 1900-01-13 07:32
N-985 | NR140004 | 110050 | 400KV AGRA-AURAIYA-II | 2016-10-05 15:30 | 2016-10-05 16:17 | 0.032639 | 0 | 0 | 0 | LEFT | Tripped on B-N fault in reclaim time. FLR:Agra-91.2km
N-1101 | NR140004 | 110205 | 400KV AGRA-AURAIYA-II | 2016-10-18 08:46 | 2016-10-18 19:33 | 0 | 0 | 0 | 0.44931 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1227
N-1506 | NR140004 | 110212 | 400KV AGRA-AURAIYA-II | 2016-10-19 07:32 | 2016-10-19 19:23 | 0 | 0 | 0 | 0.49375 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1298
N-1813 | NR140004 | 110223 | 400KV AGRA-AURAIYA-II | 2016-10-20 08:19 | 2016-10-20 19:34 | 0 | 0 | 0 | 0.46875 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1407
N-1913 | NR140004 | 110229 | 400KV AGRA-AURAIYA-II | 2016-10-21 07:55 | 2016-10-21 19:26 | 0 | 0 | 0 | 0.47986 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1511
N-2191 | NR140004 | 110236 | 400KV AGRA-AURAIYA-II | 2016-10-22 08:11 | 2016-10-22 19:06 | 0 | 0 | 0 | 0.45486 | LCSD | S/D for polymer insulator installation for grid strengthening. | N-1604
N-2251 | NR140004 | 110326 | 400KV AGRA-AURAIYA-II | 2016-10-29 10:05 | 2016-10-29 11:40 | 0.065972 | 0 | 0 | 0 | OSFT | S/D for attending sparking in relay panel at Agra end. | N-2260
N-2583 | NR140004 | 110348 | 400KV AGRA-AURAIYA-II | 2016-10-30 21:58 | 2016-11-01 | 0 | 0 | 0 | 1899-12-31 02:02 | LVRD | Line hand tripped for Voltage regulation. Agra-431 kV | N-2360
N-2656 |  |  | 400KV AGRA-AURAIYA-II Total |  |  | 0.098611 | 0 | 0 | 1900-01-02 10:21
N-2880 | NR140005 | 110180 | 400KV AGRA-BASSI-I | 2016-10-16 04:25 | 2016-10-17 09:06 | 0 | 0 | 0 | 1899-12-31 04:41 | LVRD | Line hand tripped for Voltage regulation. Agra= 432 kv. | N-1056
N-2963 | NR140005 | 110357 | 400KV AGRA-BASSI-I | 2016-10-31 21:44 | 2016-11-01 | 0 | 0 | 0 | 0.094444 | LVRD | Line hand tripped for Voltage regulation. Agra-430 kV | N-2409
N-3040 |  |  | 400KV AGRA-BASSI-I Total |  |  | 0 | 0 | 0 | 1899-12-31 06:57
N-3137 | NR140008 | 110147 | 400KV AGRA-BHIWADI-I | 2016-10-14 02:56 | 2016-10-14 06:58 | 0 | 0 | 0 | 0.16806 | LVRD | Line hand tripped for Voltage regulation. Agra=437kv. | N-873
| NR140008 | 110320 | 400KV AGRA-BHIWADI-I | 2016-10-28 22:17 | 2016-10-29 06:38 | 0 | 0 | 0 | 0.34792 | LVRD | Line hand tripped for Voltage regulation. Agra-432 kV | N-2219
N-2255 |  |  | 400KV AGRA-BHIWADI-I Total |  |  | 0 | 0 | 0 | 0.51597
N-2737 | NR140009 | 109188 | 400KV AGRA-BHIWADI-II | 2016-10-01 | 2016-10-03 11:02 | 0 | 0 | 0 | 1900-01-01 11:02 | LVRD | Line hand tripped for Voltage regulation. Agra-435 kV. Open since 1803hrs on 26.09.16 | N-1431
| NR140009 | 110025 | 400KV AGRA-BHIWADI-II | 2016-10-03 17:41 | 2016-10-06 14:58 | 0 | 0 | 0 | 1900-01-01 21:17 | LVRD | Line hand tripped for Voltage regulation. Agra= 433 kv. | N-168
| NR140009 | 110085 | 400KV AGRA-BHIWADI-II | 2016-10-08 04:05 | 2016-10-11 18:59 | 0 | 0 | 0 | 1900-01-02 14:54 | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv. | N-501
| NR140009 | 110115 | 400KV AGRA-BHIWADI-II | 2016-10-12 00:11 | 2016-10-12 10:24 | 0 | 0 | 0 | 0.42569 | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv. | N-713
N-1744 | NR140009 | 110130 | 400KV AGRA-BHIWADI-II | 2016-10-13 03:10 | 2016-10-15 12:42 | 0 | 0 | 0 | 1900-01-01 09:32 | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv. | N-776
| NR140009 | 110175 | 400KV AGRA-BHIWADI-II | 2016-10-15 21:53 | 2016-10-16 11:59 | 0 | 0 | 0 | 0.5875 | LVRD | Line hand tripped for Voltage regulation. Agra= 432 kv. | N-1045
| NR140009 | 110185 | 400KV AGRA-BHIWADI-II | 2016-10-16 15:22 | 2016-10-20 09:50 | 0 | 0 | 0 | 1900-01-02 18:28 | LVRD | Line hand tripped for Voltage regulation. Agra= 435 kv. | N-1100
| NR140009 | 110244 | 400KV AGRA-BHIWADI-II | 2016-10-22 21:43 | 2016-10-24 09:24 | 0 | 0 | 0 | 1899-12-31 11:41 | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | N-1664
| NR140009 | 110269 | 400KV AGRA-BHIWADI-II | 2016-10-24 21:19 | 2016-10-28 07:24 | 0 | 0 | 0 | 1900-01-02 10:05 | LVRD | Line hand tripped for Voltage regulation. Agra-427 kV | N-1851
| NR140009 | 110335 | 400KV AGRA-BHIWADI-II | 2016-10-29 21:32 | 2016-11-01 | 0 | 0 | 0 | 1900-01-01 02:28 | LVRD | Line hand tripped for Voltage regulation. Agra-428 kV | N-2298
|  |  | 400KV AGRA-BHIWADI-II Total |  |  | 0 | 0 | 0 | 1900-01-22 03:46
| NR140122 | 110193 | 400KV ALLD-FATEHPUR-I | 2016-10-17 13:52 | 2016-10-17 13:52 | 0 | 0 | 0 | 0 | LART | A/R on R-N fault. ALLD=64.5km, Fpur=67km.
N-2153 |  |  | 400KV ALLD-FATEHPUR-I Total |  |  | 0 | 0 | 0 | 0
N-2515 | NR140018 | 110091 | 400KV BALIA-BIHARSHRF-II | 2016-10-09 06:40 | 2016-10-09 06:40 | 0 | 0 | 0 | 0 | LART | A/R on Y-N fault. FLR:Balia- 135.2 km , IF(Balia)-3.73 KA
|  |  | 400KV BALIA-BIHARSHRF-II Total |  |  | 0 | 0 | 0 | 0
N-289 | NR140019 | 110030 | 400KV BALIA-MAU-I | 2016-10-04 11:20 | 2016-10-04 15:39 | 0 | 0.17986 | 0 | 0 | SEFU | Tripped due to bus fault at Mau UPPCL, caused by CB blast of their 400 kV Anpara Line.
N-1212 | NR140019 | 110038 | 400KV BALIA-MAU-I | 2016-10-04 15:39 | 2016-10-05 14:06 | 0 | 0 | 0 | 0.93542 | OSFD | Line charged from Balia end but remain open due to forced S/D by UPPCL to attend Bus & DC earth fault at Mau.
N-1316 |  |  | 400KV BALIA-MAU-I Total |  |  | 0 | 0.17986 | 0 | 0.93542
N-1413 | NR140020 | 110031 | 400KV BALIA-MAU-II | 2016-10-04 11:20 | 2016-10-04 15:39 | 0 | 0.17986 | 0 | 0 | SEFU | Tripped due to bus fault at Mau UPPCL, caused by CB blast of their 400 kV Anpara Line.
N-1690 |  |  | 400KV BALIA-MAU-II Total |  |  | 0 | 0.17986 | 0 | 0
N-2593 | NR140140 | 110155 | 400KV BALIA-SOHAWAL-I | 2016-10-14 10:52 | 2016-10-14 13:55 | 0.12708 | 0 | 0 | 0 | OSFT | S/D for attending CVT problem at Sohawal end. | N-913
|  |  | 400KV BALIA-SOHAWAL-I Total |  |  | 0.12708 | 0 | 0 | 0
N-02 | NR140027 | 110267 | 400KV BAREILLY-MBAD-II | 2016-10-24 15:57 | 2016-10-24 15:57 | 0 | 0 | 0 | 0 | LART | Line A/R on B-N fault, FLR-Brly-58.8Km.
N-379 |  |  | 400KV BAREILLY-MBAD-II Total |  |  | 0 | 0 | 0 | 0
N-580 | NR140158 | 110008 | 400KV BARLY(765)-KASHIPUR-I | 2016-10-01 13:30 | 2016-10-01 18:10 | 0.19444 | 0 | 0 | 0 | LEFT | Trip on R-N fault in reclaim time. Brly=47.5km.
N-762 |  |  | 400KV BARLY(765)-KASHIPUR-I Total |  |  | 0.19444 | 0 | 0 | 0
N-858 | NR140159 | 110062 | 400KV BARLY(765)-KASHIPUR-II | 2016-10-06 13:38 | 2016-10-06 13:38 | 0 | 0 | 0 | 0 | LART | A/R on B-N fault. FLR:Bly-71.99 km, IF-1.73 kA.
N-1494 | NR140159 | 110094 | 400KV BARLY(765)-KASHIPUR-II | 2016-10-09 13:54 | 2016-10-09 13:54 | 0 | 0 | 0 | 0 | LART | Line A/Reclosed on Y-N fault. FLR-34.9 km(BRLY)
N-1561 |  |  | 400KV BARLY(765)-KASHIPUR-II Total |  |  | 0 | 0 | 0 | 0
N-2005 | NR140037 | 110177 | 400KV BLBGRH-MAINPURI-I | 2016-10-16 04:17 | 2016-10-16 12:02 | 0 | 0 | 0 | 0.32292 | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv. | N-1056
N-2102 | NR140037 | 110186 | 400KV BLBGRH-MAINPURI-I | 2016-10-16 21:58 | 2016-10-17 10:18 | 0 | 0 | 0 | 0.51389 | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv. | N-1119
N-2344 | NR140037 | 110258 | 400KV BLBGRH-MAINPURI-I | 2016-10-23 21:29 | 2016-10-24 09:24 | 0 | 0 | 0 | 0.49653 | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV | N-1743
N-2453 | NR140037 | 110284 | 400KV BLBGRH-MAINPURI-I | 2016-10-25 23:09 | 2016-10-26 07:33 | 0 | 0 | 0 | 0.35 | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv. | N-1948
N-2597 | NR140037 | 110308 | 400KV BLBGRH-MAINPURI-I | 2016-10-28 01:24 | 2016-10-28 07:32 | 0 | 0 | 0 | 0.25556 | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv. | N-2145
N-3216 | NR140037 | 110321 | 400KV BLBGRH-MAINPURI-I | 2016-10-29 01:11 | 2016-10-29 08:45 | 0 | 0 | 0 | 0.31528 | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv. | N-2232
|  |  | 400KV BLBGRH-MAINPURI-I Total |  |  | 0 | 0 | 0 | 1900-01-01 06:06
N-14 | NR140038 | 110339 | 400KV BLBGRH-MAINPURI-II | 2016-10-30 00:52 | 2016-11-01 | 0 | 0 | 0 | 1899-12-31 23:08 | LVRD | Line hand tripped for Voltage regulation. Blb-430 kV | N-2308
N-1565 |  |  | 400KV BLBGRH-MAINPURI-II Total |  |  | 0 | 0 | 0 | 1899-12-31 23:08
N-1693 | NR140124 | 110178 | 400KV FATEHPUR-MAINPURI-I | 2016-10-16 04:20 | 2016-10-16 12:06 | 0 | 0 | 0 | 0.32361 | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv. | N-1056
N-2356 | NR140124 | 110187 | 400KV FATEHPUR-MAINPURI-I | 2016-10-16 21:58 | 2016-10-17 10:17 | 0 | 0 | 0 | 0.51319 | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv. | N-1119
N-2465 | NR140124 | 110254 | 400KV FATEHPUR-MAINPURI-I | 2016-10-23 17:11 | 2016-10-24 10:04 | 0 | 0 | 0 | 0.70347 | LVRD | Line hand tripped for Voltage regulation. Ftpr-425 kV | N-1727
N-3218 | NR140124 | 110285 | 400KV FATEHPUR-MAINPURI-I | 2016-10-25 23:11 | 2016-10-26 07:11 | 0 | 0 | 0 | 0.33333 | LVRD | Line hand tripped for Voltage regulation. MNP= 423 kv. | N-1948
|  |  | 400KV FATEHPUR-MAINPURI-I Total |  |  | 0 | 0 | 0 | 1899-12-31 20:58
N-3222 | NR140046 | 110060 | 400KV GORAKH-GORAKH-I | 2016-10-06 10:10 | 2016-10-06 19:09 | 0.37431 | 0 | 0 | 0 | OSPT | S/D for AMP and priwinter maintenance work. | N-355
| NR140046 | 110075 | 400KV GORAKH-GORAKH-I | 2016-10-07 09:26 | 2016-10-07 18:47 | 0.38958 | 0 | 0 | 0 | OSPT | S/D for AMP and priwinter maintenance work. | N-440
N-4776 |  |  | 400KV GORAKH-GORAKH-I Total |  |  | 0.76389 | 0 | 0 | 0
N-75 | NR140047 | 110225 | 400KV GORAKH-GORAKH-II | 2016-10-20 09:32 | 2016-10-20 20:03 | 0.43819 | 0 | 0 | 0 | OSPT | S/D taken for AMP work by GKP s/s. | N-1413
N-179 | NR140047 | 110231 | 400KV GORAKH-GORAKH-II | 2016-10-21 09:50 | 2016-10-21 18:58 | 0.38056 | 0 | 0 | 0 | OSPT | S/D taken for AMP work by GKP(Pg) S/S. | N-1527
N-270 |  |  | 400KV GORAKH-GORAKH-II Total |  |  | 0.81875 | 0 | 0 | 0
N-373 | NR140052 | 110213 | 400KV KNP-AGRA | 2016-10-19 11:34 | 2016-10-19 13:00 | 0.059722 | 0 | 0 | 0 | OSPT | S/D for taking line reactor in Service at KNP end. | N-1313
N-234 |  |  | 400KV KNP-AGRA Total |  |  | 0.059722 | 0 | 0 | 0
N-543 | NR140053 | 110042 | 400KV KNP-AURAIYA-I | 2016-10-05 09:20 | 2016-10-06 17:27 | 0 | 0 | 0 | 1899-12-31 08:07 | OSPD | S/D by NTPC for AMP at Auraiya end. | N-271
N-736 |  |  | 400KV KNP-AURAIYA-I Total |  |  | 0 | 0 | 0 | 1899-12-31 08:07
N-826 | NR140055 | 110032 | 400KV KNP-BLBGARH-I | 2016-10-04 12:24 | 2016-10-04 12:24 | 0 | 0 | 0 | 0 | LART | Line A/R on R-N fault. FLR:BLB-145.6 km , IF - 2.3 KA
N-970 | NR140055 | 110179 | 400KV KNP-BLBGARH-I | 2016-10-16 04:22 | 2016-10-16 14:40 | 0 | 0 | 0 | 0.42917 | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv. | N-1056
N-1089 | NR140055 | 110188 | 400KV KNP-BLBGARH-I | 2016-10-16 21:59 | 2016-10-17 12:02 | 0 | 0 | 0 | 0.58542 | LVRD | Line hand tripped for Voltage regulation. BLB= 423 kv. | N-1119
N-1203 | NR140055 | 110203 | 400KV KNP-BLBGARH-I | 2016-10-18 04:35 | 2016-10-18 04:35 | 0 | 0 | 0 | 0 | LART | A/R on B-N fault. KNP=144.6km,
N-1312 | NR140055 | 110259 | 400KV KNP-BLBGARH-I | 2016-10-23 21:31 | 2016-10-24 11:10 | 0 | 0 | 0 | 0.56875 | LVRD | Line hand tripped for Voltage regulation. BLB-425 kV | N-1743
N-1401 | NR140055 | 110263 | 400KV KNP-BLBGARH-I | 2016-10-24 11:10 | 2016-10-24 13:51 | 0.11181 | 0 | 0 | 0 | OSFT | S/D for attending broken conductor strand by MNP T/L. | N-1791
N-1485 | NR140055 | 110309 | 400KV KNP-BLBGARH-I | 2016-10-28 02:04 | 2016-10-28 06:40 | 0 | 0 | 0 | 0.19167 | LVRD | Line hand tripped for Voltage regulation. Blb>422kv. | N-2146
N-1544 | NR140055 | 110338 | 400KV KNP-BLBGARH-I | 2016-10-30 00:16 | 2016-10-30 00:16 | 0 | 0 | 0 | 0 | LART | A/R on R-N fault, FLR:Knp-250km
N-1677 | NR140055 | 110340 | 400KV KNP-BLBGARH-I | 2016-10-30 15:44 | 2016-11-01 | 0 | 0 | 0 | 1899-12-31 08:16 | LVRD | Line hand tripped for Voltage regulation. Blb-431 kV | N-2336
N-1789 |  |  | 400KV KNP-BLBGARH-I Total |  |  | 0.11181 | 0 | 0 | 1900-01-02 02:52
N-1899 | NR140057 | 110157 | 400KV KNP-BLBGARH-III | 2016-10-14 13:57 | 2016-10-14 13:57 | 0 | 0 | 0 | 0 | LART | A/R on Y-N fault, FLR, Blb-22.3km, Knp-302.49km
N-1988 |  |  | 400KV KNP-BLBGARH-III Total |  |  | 0 | 0 | 0 | 0
N-2087 | NR140110 | 110153 | 400KV KNP-FATEHPUR-I | 2016-10-14 09:48 | 2016-10-17 19:01 | 0 | 0 | 0 | 1900-01-02 09:13 | LCSD | S/D for line isolator retrofitment at Knp, under Add cap. | N-904
N-2174 |  |  | 400KV KNP-FATEHPUR-I Total |  |  | 0 | 0 | 0 | 1900-01-02 09:13
N-2233 | NR140070 | 110290 | 400KV LUCKNOW-GORAKH-III | 2016-10-26 09:36 | 2016-10-26 19:15 | 0.40208 | 0 | 0 | 0 | OSPT | S/D for line and other AMP work. | N-1985
N-2340 |  |  | 400KV LUCKNOW-GORAKH-III Total |  |  | 0.40208 | 0 | 0 | 0
N-2449 | NR140071 | 110297 | 400KV LUCKNOW-GORAKH-IV | 2016-10-27 09:40 | 2016-10-27 19:20 | 0.40278 | 0 | 0 | 0 | OSPT | S/D for line and other AMP work. | N-2077
N-2567 |  |  | 400KV LUCKNOW-GORAKH-IV Total |  |  | 0.40278 | 0 | 0 | 0
N-2650 | NR140073 | 110080 | 400KV LUCKNOW-SULTANPR | 2016-10-07 12:43 | 2016-10-07 15:50 | 0 | 0.12986 | 0 | 0 | OMSU | Line tripped on Y-N fault in UPPCL portion. FLR-Lko-83.6Km, If-3.97KA.
N-2840 |  |  | 400KV LUCKNOW-SULTANPR Total |  |  | 0 | 0.12986 | 0 | 0
N-2952 | NR140084 | 110082 | 400KV RIHAND-ALLD-I | 2016-10-08 02:44 | 2016-10-08 03:03 | 0.013194 | 0 | 0 | 0 | LEFT | Line tripped from Alld and remain chrged from Rihand end, on Y-N fault, FLR-Rhd-175.7Km, Allah-192Km.
N-3095 |  |  | 400KV RIHAND-ALLD-I Total |  |  | 0.013194 | 0 | 0 | 0
N-3186 | NR140085 | 110083 | 400KV RIHAND-ALLD-II | 2016-10-08 02:44 | 2016-10-08 02:44 | 0 | 0 | 0 | 0 | LART | Line A/R on Y-N fault, FLR-Rhd-264Km, Allah-192Km, If-1.156KA.
|  |  | 400KV RIHAND-ALLD-II Total |  |  | 0 | 0 | 0 | 0
| NR140111 | 110033 | 400KV SING-FATEHPUR | 2016-10-04 12:29 | 2016-10-04 13:04 | 0.024306 | 0 | 0 | 0 | LEFT | Line tripped on B-N fault. FLR:Ftpr-225.2 km , IF-3.6 KA
| NR140111 | 110035 | 400KV SING-FATEHPUR | 2016-10-04 16:42 | 2016-10-04 20:38 | 0.16389 | 0 | 0 | 0 | OSFT | S/D to attend line isolator jumper problem at Fatehpur. | N-225
N-209 | NR140111 | 110049 | 400KV SING-FATEHPUR | 2016-10-05 13:03 | 2016-10-05 19:07 | 0.25278 | 0 | 0 | 0 | LEFT | Tripped on R-N fault in reclaim time. FLR:Fthpr-237.3km
| NR140111 | 110087 | 400KV SING-FATEHPUR | 2016-10-08 10:46 | 2016-10-08 19:06 | 0.34722 | 0 | 0 | 0 | OSPT | S/D for replacement of damaged insulator string by Mirzapur. | N-518
N-209 | NR140111 | 110097 | 400KV SING-FATEHPUR | 2016-10-09 17:06 | 2016-10-09 17:34 | 0.019444 | 0 | 0 | 0 | LEFT | Line tripped on B-N fault. FLR-FTPR-67.1km.
|  |  | 400KV SING-FATEHPUR Total |  |  | 0.80764 | 0 | 0 | 0
| NR140095 | 110100 | 400KV SING-LKO(UP) | 2016-10-09 23:25 | 2016-10-10 00:01 | 0 | 0.025 | 0 | 0 | SEFU | Line tripped due to R-Phase WT burn at singrauli end.
| NR140095 | 110101 | 400KV SING-LKO(UP) | 2016-10-10 00:01 | 2016-10-10 20:31 | 0 | 0 | 0 | 0.85417 | OSFD | Forced S/D taken by NTPC for replacement of faulty Wave trap at Singaurali. | N-611
N-1243 |  |  | 400KV SING-LKO(UP) Total |  |  | 0 | 0.025 | 0 | 0.85417
| N-W40001 | 110122 | 400KV SING-VINDH-I | 2016-10-12 12:35 | 2016-10-12 16:49 | 0.17639 | 0 | 0 | 0 | LEFT | Line tripped on B-N fault. No FLR at both end.
N-1360 |  |  | 400KV SING-VINDH-I Total |  |  | 0.17639 | 0 | 0 | 0
| NR340003 | 110280 | 400KV VARANASI-SARNATH-I | 2016-10-25 09:27 | 2016-10-25 20:11 | 0 | 0 | 0 | 0.44722 | LPRD | Line hand tripped for Power regulation. | N-1881
N-567 |  |  | 400KV VARANASI-SARNATH-I Total |  |  | 0 | 0 | 0 | 0.44722
| NR340004 | 110281 | 400KV VARANASI-SARNATH-II | 2016-10-25 10:14 | 2016-10-25 20:22 | 0 | 0 | 0 | 0.42222 | LPRD | Line hand tripped for Power regulation. | N-1894
N-2310 |  |  | 400KV VARANASI-SARNATH-II Total |  |  | 0 | 0 | 0 | 0.42222
| BILUP2209 | 110093 | 220KV ALLD-JHUSI(UP) | 2016-10-09 08:41 | 2016-10-09 12:13 | 0 | 0 | 0 | 0.14722 | OSFD | S/D taken by UPPCL for attending hot spot at Jhusi end. | N-565
N-2346 |  |  | 220KV ALLD-JHUSI(UP) Total |  |  | 0 | 0 | 0 | 0.14722
N-2388 | BILUP2202 | 110181 | 220KV ALLD-REWA RD-I | 2016-10-16 08:48 | 2016-10-16 20:31 | 0 | 0 | 0 | 0.48819 | OSPD | S/D for stringing of 220kv D/C Allahabad-GSS Naini line by Railway. | N-1037
|  |  | 220KV ALLD-REWA RD-I Total |  |  | 0 | 0 | 0 | 0.48819
N-2046 | BILUP2203 | 110063 | 220KV ALLD-REWA RD-II | 2016-10-06 13:41 | 2016-10-06 21:01 | 0 | 0 | 0 | 0.30556 | OSFD | S/D by UPPCL to attend hotspot in Bus A isolator clamp at Rewa Road . | N- 373
| BILUP2203 | 110182 | 220KV ALLD-REWA RD-II | 2016-10-16 08:48 | 2016-10-16 20:31 | 0 | 0 | 0 | 0.48819 | OSPD | S/D for stringing of 220kv D/C Allahabad-GSS Naini line by Railway. | N-1037
|  |  | 220KV ALLD-REWA RD-II Total |  |  | 0 | 0 | 0 | 0.79375
| NR122040 | 110057 | 220KV FATEHPUR-KNP SOUTH | 2016-10-06 00:23 | 2016-10-06 00:42 | 0 | 0.013194 | 0 | 0 | OMSU | A/R from Fthpr but tripped from Knp(UPPCL) end on B-N fault in their portion. FLR:Fthpr-3.5km
| NR122040 | 110109 | 220KV FATEHPUR-KNP SOUTH | 2016-10-11 11:58 | 2016-10-11 12:56 | 0 | 0.040278 | 0 | 0 | OMSU | Line tripped on R-N fault in UPPCL portion. Ftpr-17.5Km
N-2342 | NR122040 | 110156 | 220KV FATEHPUR-KNP SOUTH | 2016-10-14 12:34 | 2016-10-14 12:57 | 0 | 0.015972 | 0 | 0 | OMSU | A/R at Fthpr(Pg) but tripped from Knp (UP) end on R-N fault in their portion. FLR:Fthpr-26.7 km.
| NR122040 | 110172 | 220KV FATEHPUR-KNP SOUTH | 2016-10-15 15:31 | 2016-10-15 20:08 | 0 | 0.19236 | 0 | 0 | OMSU | Line tripped on R-N fault in UPPCL portion. FLR-Fthpr-25.5km. If-5.94KA,
| NR122040 | 110264 | 220KV FATEHPUR-KNP SOUTH | 2016-10-24 11:45 | 2016-10-24 20:40 | 0 | 0.37153 | 0 | 0 | OMSU | Line tripped on R-Y Fault in UPPCL portion. FLR-Ftpr-77.5Km, If-6.02KA.
|  |  | 220KV FATEHPUR-KNP SOUTH Total |  |  | 0 | 0.63333 | 0 | 0
| NR122041 | 110079 | 220KV FATEHPUR-NAUBASTA | 2016-10-07 12:30 | 2016-10-07 14:49 | 0 | 0.096528 | 0 | 0 | OMSU | Line tripped on B-N fault in UPPCL portion. FLR-Ftpr-39.7Km, If-9.6KA.
N-2726 |  |  | 220KV FATEHPUR-NAUBASTA Total |  |  | 0 | 0.096528 | 0 | 0
N-2834 | NR122016 | 110108 | 220KV KNP-MAINPURI | 2016-10-11 11:54 | 2016-10-11 17:46 | 0 | 0.24444 | 0 | 0 | OMSU | Line tripped on B-N fault in UPPCL portion. FLR-MNP-24Km, If-4.56KA, KNP-134.2Km
| NR122016 | 110120 | 220KV KNP-MAINPURI | 2016-10-12 11:11 | 2016-10-12 19:17 | 0 | 0.3375 | 0 | 0 | OMSU | Line tripped on B-N fault in UPPCL portion. Z-II, FLR-MNP-11.9Km, KNP-160.6Km
| NR122016 | 110148 | 220KV KNP-MAINPURI | 2016-10-14 06:09 | 2016-10-14 22:15 | 0 | 0 | 0 | 0.67083 | OSFD | S/D by UPPCL for attending sparking at loc-435-436 under their jurisdiction. | N-879
|  |  | 220KV KNP-MAINPURI Total |  |  | 0 | 0.58194 | 0 | 0.67083
N-1562 | NR122017 | 110184 | 220KV KNP-NAUBASTA | 2016-10-16 12:56 | 2016-10-16 16:16 | 0 | 0 | 0 | 0.13889 | OSPD | S/D by UPPCL for maintenance at Naubasta end. | N-1090
N-1690 |  |  | 220KV KNP-NAUBASTA Total |  |  | 0 | 0 | 0 | 0.13889
N-1749 | NR122020 | 110055 | 220KV KNP-UNCHR-I | 2016-10-05 21:35 | 2016-10-05 21:35 | 0 | 0 | 0 | 0 | LART | A/R on R-N fault, FLR, Knp-67.41 km
N-1807 |  |  | 220KV KNP-UNCHR-I Total |  |  | 0 | 0 | 0 | 0
N-1907 | NR122021 | 110215 | 220KV KNP-UNCHR-II | 2016-10-19 13:53 | 2016-10-19 14:18 | 0 | 0.017361 | 0 | 0 | OMSU | Line tripped only from Unchahar end on R-N fault and A/R from LKO end.FLR-UCHR-135.6 km , If-1.623 KAmp
N-1993 |  |  | 220KV KNP-UNCHR-II Total |  |  | 0 | 0.017361 | 0 | 0
N-2453 | NR1ICT47 | 110005 | 100MVA ICT-I RAIBAREILLY | 2016-10-01 13:25 | 2016-10-01 18:20 | 0 | 0 | 0 | 0.20486 | OSFD | S/D by UPPCL to attend jackbus hotspot in their132kv S/Y. | N-21
N-2567 |  |  | 100MVA ICT-I RAIBAREILLY Total |  |  | 0 | 0 | 0 | 0.20486
N-2671 | NR1ICT38 | 110006 | 100MVA ICT-II RAIBAREILLY | 2016-10-01 13:25 | 2016-10-01 18:20 | 0 | 0 | 0 | 0.20486 | OSFD | S/D by UPPCL to attend jackbus hotspot in their132kv S/Y. | N-21
N-2871 |  |  | 100MVA ICT-II RAIBAREILLY Total |  |  | 0 | 0 | 0 | 0.20486
N-2961 | NR1ICT39 | 110007 | 100MVA ICT-III RAIBAREILLY | 2016-10-01 13:25 | 2016-10-01 18:20 | 0 | 0 | 0 | 0.20486 | OSFD | S/D by UPPCL to attend jackbus hotspot in their132kv S/Y. | N-21
N-3038 |  |  | 100MVA ICT-III RAIBAREILLY Total |  |  | 0 | 0 | 0 | 0.20486
N-3130 | NR1ICT70 | 110240 | 315MVA ICT-I AGRA | 2016-10-22 10:58 | 2016-10-23 04:47 | 0 | 0 | 0 | 0.74236 | LCSD | S/D for 220kV BUS extension work at Agra. | N-1616
N-4785 |  |  | 315MVA ICT-I AGRA Total |  |  | 0 | 0 | 0 | 0.74236
N-83 | NR3ICT702 | 110026 | 765/400kv ICT-II KANPUR(GIS) | 2016-10-03 18:47 | 2016-10-03 22:37 | 0.15972 | 0 | 0 | 0 | OSFT | Forced S/D due to high Acetelene gas content in its B-phase unit. | N-171
N-184 |  |  | 765/400kv ICT-II KANPUR(GIS) Total |  |  | 0.15972 | 0 | 0 | 0
N-273 | NR1BRT49 |  | 125MVAR B/Reactor-I SHAHJHNPR | 2016-10-21 09:02 | 2016-10-30 03:02 | 0 | 0 | 0 | 1900-01-07 18:00 | SVRD | H/ tripped for voltage regulation<392kv. (Standing Instrn)
N-379 |  |  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-07 18:00
N-466 | NR1BRT50 |  | 240MVAR B/Reactor-I BAREILLY-765 | 2016-10-04 10:52 | 2016-10-11 17:26 | 0 | 0 | 0 | 1900-01-06 06:34 | SVRD | H/ tripped for voltage regulation<394kv. (Standing Instrn)
N-559 |  |  | SUB TOTAL |  |  | 0 | 0 | 0 | 1900-01-06 06:34
N-757
N-823 | [5 empty] | 1900-01-19 14:14 | 1899-12-31 20:15 | 0.045833 | 1900-04-20 11:18
N-972
N-1094
N-1212
N-1327
N-1423
N-2099
N-2181
N-2244
N-2342
N-1411
N-1494
N-4785
N-83
N-273
N-379
N-466
N-559
N-757
N-846
N-972
N-1097
N-1212
N-1327
N-1561
N-1690
N-1907
N-1993
N-2099
N-2181
N-2244
N-2342
N-2567
N-2671
N-2878
N-2961
N-3130
N-184
N-1411
N-1494
N-1807
N-2453
N-3038
N-273
N-379
N-466
N-867
N-984
N-1566
N-1993
N-2099
N-2741
N-1494
N-2181
N-2342
N-2469
N-2727
N-4784
N-83
N-181
N-559
N-743
N-823
N-1089
N-1212
N-1327
N-1411
N-1552
N-1690
N-1808
N-1911
N-2244
N-2356
N-2453
N-2571
N-2697
N-2871
N-2961
N-3038
N-3130
N-759
N-2922
N-759
N-2746
N-2834
N-1646
N-567
N-2279
N-2493
N-1835
N-1248
N-1136
N-229
N-229
N-326
N-410
N-495
N- 2321
N-655
N-655
N-794
N-1015
N-1015
N-1942
N-41
N-1161
N-2913
N-44
N-1657
N-2034
N-2491
N-1364
N-2721
N-2919
N-665
N-651
N-1291
N-1854
N-1959
N-2058
N-1171
N-1171
N-1171
N-1262
N-1266
N-1773
N-1359
N-2146
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(RIGHT([Classification/ Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
DURATION OF OUTAGE ATTRIBUTABLE TO = SUBTOTAL(9,G13:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(RIGHT([Classification/ Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUBTOTAL(9,H13:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Classification/ Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUBTOTAL(9,I13:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Classification/ Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUBTOTAL(9,J13:[Deemed Available, row above])
Note on D71: LILO of 765KV FATEHPUR-GAYA at VARANASI