## SOP DATA NR3
POWERGRID CORPORATION OF INDIA LIMITED.
Standard of Performance data for the month of APRIL-2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD, NORTHERN REGION - III | [25 empty] | ANNEXURE-I
ANNEXTURE- A
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES
1 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 720
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1327 | 148.034 | 196441.118 | 196441.118 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2018-04-01 | 2018-04-03 06:50 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:50 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
[6 empty] | 2018-04-04 13:34 | 2018-04-04 19:23 |  |  |  | 0 | 0 | 0 | 0.24236 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
[6 empty] | 2018-04-05 07:39 | 2018-04-05 10:31 |  |  |  | 0 | 0 | 0 | 0.11944 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
[6 empty] | 2018-04-06 08:19 | 2018-04-06 16:44 |  |  |  | 0 | 0 | 0 | 0.35069 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[6 empty] | 2018-04-08 11:24 | 2018-04-09 14:06 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:42 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
[6 empty] | 2018-04-10 07:13 | 2018-04-10 14:21 |  |  |  | 0 | 0 | 0 | 0.29722 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
[6 empty] | 2018-04-12 00:41 | 2018-04-12 09:57 |  |  |  | 0 | 0 | 0 | 0.38611 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=781kV
[6 empty] | 2018-04-13 07:54 | 2018-04-13 20:22 |  |  |  | 0 | 0 | 0 | 0.51944 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=783kV
[6 empty] | 2018-04-23 12:26 | 2018-04-23 19:42 |  |  |  | 0 | 0 | 0 | 0.30278 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
[6 empty] | 2018-04-24 13:07 | 2018-04-25 10:36 |  |  |  | 0 | 0 | 0 | 0.89514 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 12:15 | [6 empty] | 720 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2018-04-03 08:10 | 2018-04-04 11:09 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:59 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
[6 empty] | 2018-04-06 17:51 | 2018-04-07 16:51 |  |  |  | 0 | 0 | 0 | 0.95833 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=797kV
[6 empty] | 2018-04-09 07:07 | 2018-04-11 21:09 |  |  |  | 0 | 0 | 0 | 1900-01-01 14:02 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
[6 empty] | 2018-04-14 06:58 | 2018-04-15 19:54 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:56 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2018-04-16 08:37 | 2018-04-22 18:01 |  |  |  | 0 | 0 | 0 | 1900-01-05 09:24 |  |  |  | LCSD | S/D availed for completion of balance stringing and final shifting of line to new section for completion of diversion for DFCC.
[6 empty] | 2018-04-24 06:58 | 2018-04-24 10:47 |  |  |  | 0 | 0 | 0 | 0.15903 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
[6 empty] | 2018-04-25 12:47 | 2018-04-30 10:25 |  |  |  | 0 | 0 | 0 | 1900-01-03 21:38 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=781kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-16 15:48 | [6 empty] | 720 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
5 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 256393.647 | 100
6 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1419 | 165.98 | 235525.62 | 235525.62 | 100
7 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 223 | 310639 | 310639 | 100
8 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1440 | 465.8 | 670752 | 670752 | 100
9 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | 2018-04-11 07:43 | 2018-04-11 15:47 |  |  |  | 0 | 0 | 0 | 0.33611 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=812kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.33611 | [6 empty] | 720 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
10 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
11 | NR376504 | 765KV ALIGARH-JHATIKARA | 158 | NR3 | -- | 2018-04-06 16:54 | 2018-04-06 21:26 |  |  |  | 0 | 0 | 0.18889 | 0 |  |  |  | LNCC | Tripped due to B-N fault during heavy thunderstorm. FD: Aligarh-96.7km, Jhatikara-54km. FC: Aligarh-6.4KA, Jhatikara-11.2KA. Fault in NR-1 jurisdiction.
[6 empty] | 2018-04-20 00:39 | 2018-04-20 05:07 |  |  |  | 0.18611 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.18611 | 0 | 0.18889 | 0 | [6 empty] | 715.4667 | 1393 | 158 | 220094 | 218719.9506 | 99.3757
12 | NR376505 | 765KV KANPUR(GIS)-ALIGARH | 327 | NR3 | -- | 2018-04-20 00:39 | 2018-04-20 04:49 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
[6 empty] | 2018-04-22 13:17 | 2018-04-22 14:15 |  |  |  | 0.040278 | 0 | 0 | 0 |  |  |  | OMST | Tripped only from Kanpur end due to DT received
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.040278 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 327 | 455511 | 454899.4343 | 99.8657
13 | NR376506 | 765KV AGRA-ALIGARH | 122.5 | NR3 | -- | 2018-04-07 15:52 | 2018-04-07 17:34 |  |  |  | 0.070833 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to remove rope between location No 18 and 19 which fell down on conductor due to heavy storm.
[6 empty] | 2018-04-11 19:15 | 2018-04-13 19:38 |  |  |  | 0 | 0 | 1900-01-01 00:23 | 0 |  |  |  | LNCC | Tripped due to heavy storm on Y-N fault , F.D.=12.7KM from Agra, F.C.= 10KAmp at Agra.
[6 empty] | 2018-04-20 00:39 | 2018-04-24 20:15 |  |  |  | 1900-01-03 19:36 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-03 21:18 | 0 | 1900-01-01 00:23 | 0 | [6 empty] | 671.6167 | 1393 | 122.5 | 170642.5 | 140839.2413 | 82.5347
14 | NR376507 | 765KV ALIGARH-GR.NOIDA | 51 | NR3 | -- | 2018-04-20 00:39 | 2018-04-20 05:36 |  |  |  | 0.20625 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.20625 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 51 | 71043 | 70554.5794 | 99.3125
15 | NR376508 | 765KV ORAI-ALIGARH-II | 331.958 | NR3 | -- | 2018-04-06 16:54 | 2018-04-06 17:07 |  |  |  | 0 | 0 | 0.0090278 | 0 |  |  |  | LNCC | Tripped due to B-N fault during heavy thunderstorm. FD: Orai-247.79km, FC: Orai-1.3KA
[6 empty] | 2018-04-16 19:31 | 2018-04-16 22:08 |  |  |  | 0.10903 | 0 | 0 | 0 |  |  |  | SICT | Tripped due to DT received at Aligarh end caused by operation of PRD of its Y-Phase line reactor at Orai end.Line charged without line reactor at Orai.
[6 empty] | 2018-04-20 00:39 | 2018-04-24 20:45 |  |  |  | 1900-01-03 20:06 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
[6 empty] | 2018-04-18 21:11 | 2018-04-18 21:32 |  |  |  | 0.014583 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for taking its L/R at Orai end into service
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-03 23:04 | 0 | 0.0090278 | 0 | [6 empty] | 719.7833 | 1393 | 331.958 | 462417.494 | 385924.323 | 83.458
16 | NR376509 | 765KV ORAI-ALIGARH-I | 331.958 | NR3 | -- | 2018-04-15 18:00 | 2018-04-15 19:52 |  |  |  | 0.077778 | 0 | 0 | 0 |  |  |  | SICT | Tripped due to DT received at Aligarh end caused by operation of PRD of its B-Phase line reactor at Orai end.Line charged without line reactor at Orai.
[6 empty] | 2018-04-17 21:44 | 2018-04-17 22:05 |  |  |  | 0.014583 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for taking its L/R at Orai end into service
[6 empty] | 2018-04-20 00:39 | 2018-04-20 06:01 |  |  |  | 0.22361 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.31597 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 331.958 | 462417.494 | 457547.1246 | 98.9468
B |  | 400 KV TRANS LINES |  |  | --
1 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 29.982 | NR3 | -- | 2018-04-11 19:19 | 2018-04-11 20:39 | -- | -- |  | 0 | 0 | 0.055556 | 0 |  |  |  | LNCC | Tripped due to B-N fault, F.D.= 30KM from Agra, F.C.= 16KAMP, The fault was in UPPTCL juridiction.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.055556 | 0 | [6 empty] | 718.6667 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- | 2018-04-11 19:18 | 2018-04-28 04:29 | -- | -- |  | 0 | 0 | 1900-01-15 09:11 | 0 |  |  |  | LNCC | Tripped due to Heavy storm on B-N fault, F.D.= 14KM from Agra, F.C.= 13KAMP.Fault in Agra jurisdiction. Tower No 36B, 36C, 36D ,37 are damaged.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 1900-01-15 09:11 | 0 | [6 empty] | 326.8167 | 515 | 29.982 | 15440.73 | 15440.73 | 100
| NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 57.159 | NR3 | -- | 2018-04-06 19:42 | 2018-04-07 13:31 | -- | -- |  | 0 | 0.74236 | 0 | 0 |  |  |  | OMSU | Tripped due to R-phase Pantograph isolator broken at Agra (UP). Fault in UPPCL jurisdiction.
[6 empty] | 2018-04-07 13:31 | 2018-04-08 22:53 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:22 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending R-phase broken Pantograph isolator at Agra (UP).
[5 empty] | -- | 2018-04-11 19:18 | 2018-04-28 04:31 | -- | -- |  | 0 | 0 | 1900-01-15 09:13 | 0 |  |  |  | LNCC | Tripped due to heavy storm on B-N fault, F.D.= 13KM from Agra(UP), F.C.= 5.07KAMP at fatehabad, The fault was in Agra juridiction. Tower No 36B ,36C, 36D, 37 are damaged.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.74236 | 1900-01-15 09:13 | 1899-12-31 09:22 | [6 empty] | 326.7833 | 515 | 57.159 | 29436.885 | 29436.885 | 100
3 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2018-04-12 11:44 | 2018-04-12 13:31 | -- | -- | -- | 0.074306 | 0 | 0 | 0 |  |  |  | OSFT | Emergency Hand tripped due to hot spot in R-phase isolator of L/R at Agra.
[6 empty] | 2018-04-18 13:35 | 2018-04-19 23:35 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:00 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2018-04-21 13:35 | 2018-04-23 09:57 |  |  |  | 0 | 0 | 0 | 1899-12-31 20:22 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
[6 empty] | 2018-04-26 06:13 | 2018-05-01 |  |  |  | 0 | 0 | 0 | 1900-01-03 17:47 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=435kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.074306 | 0 | 0 | 1900-01-07 00:09 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 61210.4144 | 99.7523
4 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2018-04-06 22:08 | 2018-04-10 10:44 |  |  |  | 0 | 0 | 0 | 1900-01-02 12:36 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-04-10 10:44 | 2018-04-16 20:11 |  |  |  | 0 | 0 | 0 | 1900-01-05 09:27 |  |  |  | LCSD | S/D availed for Retrofittment & SCADA integration work at HVDC Agra
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 22:03 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- | 2018-04-25 13:34 | 2018-04-25 18:33 | -- | -- | -- | 0.20764 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault, F.D.= 172.7KM from Agra end and 20.56kM from BASSI end, F.C.= 2.19KAMP at Agra and 11.03kAmp at Bassi end. The fault was in NR-1 juridiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.20764 | 0 | 0 | 0 | [6 empty] | 720 | 245 | 211.433 | 51801.085 | 51442.5543 | 99.3079
6 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2018-04-13 07:51 | 2018-04-13 11:05 | -- | -- | -- | 0 | 0 | 0 | 0.13472 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[6 empty] | 2018-04-24 13:05 | 2018-04-28 17:02 |  |  |  | 0 | 0 | 0 | 1900-01-03 03:57 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2018-04-30 03:13 | 2018-04-30 10:47 |  |  |  | 0 | 0 | 0 | 0.31528 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 14:45 | [6 empty] | 720 | 402 | 208.98 | 84009.96 | 84009.96 | 100
7 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2018-04-01 | 2018-04-07 15:51 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 15:51 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[6 empty] | 2018-04-08 09:07 | 2018-04-12 08:50 |  |  |  | 0 | 0 | 0 | 1900-01-02 23:43 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2018-04-14 06:50 | 2018-04-20 18:10 |  |  |  | 0 | 0 | 0 | 1900-01-05 11:20 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[6 empty] | 2018-04-21 13:32 | 2018-04-21 17:04 |  |  |  | 0 | 0 | 0 | 0.14722 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[6 empty] | 2018-04-22 10:06 | 2018-04-22 23:42 |  |  |  | 0 | 0 | 0 | 0.56667 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-16 20:02 | [6 empty] | 720 | 515 | 209.51 | 107897.65 | 107897.65 | 100
8 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 382 | 181.137 | 69194.334 | 69194.334 | 100
9 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | 2018-04-09 14:44 | 2018-04-10 13:26 |  |  |  | 0 | 0 | 0 | 0.94583 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. ALLD=430kV
[6 empty] | 2018-04-12 04:42 | 2018-04-12 23:18 |  |  |  | 0 | 0 | 0 | 0.775 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=432kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 17:18 | [6 empty] | 720 | 332 | 139.73 | 46390.36 | 46390.36 | 100
10 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 332 | 139.73 | 46390.36 | 46390.36 | 100
11 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- | 2018-04-14 14:16 | 2018-04-14 14:39 | -- | -- | -- | 0.015972 | 0 | 0 | 0 |  |  |  | OMST | Taken under emergency S/D for isolating lockout breaker no 404(main bay of FTP-3) at Allahabad
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.015972 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 155.932 | 80304.98 | 80262.225 | 99.9468
12 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 224 | 115360 | 115360 | 100
13 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.792 | 50877.88 | 50877.88 | 100
14 | NR140016 | 400KV ALLD-SASARAM | 212 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 17:18 | [6 empty] | 720 | 369 | 212 | 78228 | 78228 | 100
15 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 13 | 6695 | 6695 | 100
16 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 13 | 6695 | 6695 | 100
17 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 227 | 229.163 | 52020.001 | 52020.001 | 100
18 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 227 | 229.163 | 52020.001 | 52020.001 | 100
19 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 1.559 | 1071.033 | 1071.033 | 100
20 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 1.559 | 1071.033 | 1071.033 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
21 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | 2018-04-05 22:39 | 2018-04-05 23:12 |  |  |  | 0 | 0.033333 | 0 | 0 |  |  |  | SBBU | Tripped due to bus fault at Bareilly(UP) end.
[6 empty] | 2018-04-08 10:51 | 2018-04-08 12:33 |  |  |  | 0 | 0.070833 | 0 | 0 |  |  |  | SBBU | Bus bar protection operated at Bareilly(UP) end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.10417 | 0 | 0 | [6 empty] | 720 | 515 | 9.2 | 4738 | 4738 | 100
22 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | 2018-04-05 22:39 | 2018-04-05 23:33 |  |  |  | 0 | 0.0375 | 0 | 0 |  |  |  | SBBU | Tripped due to bus fault at Bareilly(UP) end.
[5 empty] | -- | 2018-04-08 10:51 | 2018-04-08 12:59 |  |  |  | 0 | 0.088889 | 0 | 0 |  |  |  | SBBU | Bus bar protection operated at Bareilly(UP) end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.12639 | 0 | 0 | [6 empty] | 720 | 515 | 9.2 | 4738 | 4738 | 100
23 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- | 2018-04-17 12:58 | 2018-04-17 13:46 | -- | -- | -- | 0 | 0.033333 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault,F.D.=279km from Bareily,F.C.=1.83KA(UPPCL Jurisdiction)
[6 empty] | 2018-04-17 13:49 | 2018-04-17 23:13 |  |  |  | 0 | 0.39167 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault,F.D.=279km from Bareily,F.C.=1.839KA(UPPCL Jurisdiction)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.425 | 0 | 0 | [6 empty] | 720 | 331 | 278.76 | 92269.56 | 92269.56 | 100
24 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | 2018-04-16 11:39 | 2018-04-16 13:40 |  |  |  | 0.084028 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for attending hot spot in line isolator at Moradabad(UP) end.
[6 empty] | 2018-04-21 10:24 | 2018-04-21 13:01 |  |  |  | 0 | 0 | 0 | 0.10903 |  |  |  | OSFD | Emergency S/D availed by UPPCL to attend sparking in Y Ph wave trap at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.084028 | 0 | 0 | 0.10903 | [6 empty] | 720 | 515 | 92.68 | 47730.2 | 47596.5112 | 99.7199
25 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 92.68 | 47730.2 | 47730.2 | 100
26 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR3
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 115.926 | 59701.89 | 59701.89 | 100
27 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 115.926 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 115.926 | 59701.89 | 59701.89 | 100
28 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 116.03 | 59755.45 | 59755.45 | 100
29 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 101.841 | 69964.767 | 69964.767 | 100
30 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 |  | 2018-04-17 13:43 | 2018-04-17 18:13 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault,F.D.=12.33km from Bareily,F.C.=14.03KA(Bareily Jurisdiction)
[6 empty] | 2018-04-18 12:09 | 2018-04-18 15:58 |  |  |  | 0.15903 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault,F.D.=27.75km from Bareily,F.C.=9.025KA(Bareily Jurisdiction)
[6 empty] | 2018-04-25 13:09 | 2018-04-25 13:28 |  |  |  | 0.013194 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault, F.D.= 19.51KM from BRLY end, F.C.= 11.03KAMP at BRLY end, The fault was in BRLY TL juridiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.17222 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 101.841 | 69964.767 | 69563.1174 | 99.4259
31 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2018-04-01 07:23 | 2018-04-02 09:50 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
[6 empty] | 2018-04-06 17:54 | 2018-04-08 09:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 15:50 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2018-04-09 07:18 | 2018-04-10 20:58 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:40 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2018-04-11 06:39 | 2018-04-11 15:22 |  |  |  | 0.36319 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault. Maninpuri=171.4kM(Tripped) and 169.9kM(A/R), 2.55kA(A/R) and 2.32kA(tripped). Fault in NR-1 jurisdiction.
[6 empty] | 2018-04-12 03:37 | 2018-04-17 11:21 |  |  |  | 0 | 0 | 0 | 1900-01-04 07:44 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2018-04-18 13:16 | 2018-04-19 08:44 |  |  |  | 0 | 0 | 0 | 0.81111 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2018-04-20 12:55 | 2018-04-20 18:28 |  |  |  | 0 | 0 | 0 | 0.23125 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2018-04-22 13:12 | 2018-04-22 21:44 |  |  |  | 0 | 0 | 0 | 0.35556 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri-430kV
[6 empty] | 2018-04-24 07:10 | 2018-04-24 10:54 |  |  |  | 0 | 0 | 0 | 0.15556 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNPR=430kV
[6 empty] | 2018-04-28 07:03 | 2018-04-28 16:43 |  |  |  | 0 | 0 | 0 | 0.40278 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2018-04-29 17:51 | 2018-05-01 00:58 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:07 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.36319 | 0 | 0 | 1900-01-10 19:18 | [6 empty] | 720 | 515 | 235.952 | 121515.28 | 120044.1575 | 98.7894
32 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 235.952 | 121515.28 | 121515.28 | 100
33 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2018-04-06 17:54 | 2018-04-08 19:13 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 01:19 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2018-04-09 07:19 | 2018-04-10 20:46 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:27 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2018-04-20 12:55 | 2018-04-20 18:27 |  |  |  | 0 | 0 | 0 | 0.23056 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 20:18 | [6 empty] | 720 | 469 | 260.051 | 121963.919 | 121963.919 | 100
34 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- | 2018-04-01 07:20 | 2018-04-02 09:54 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 02:34 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
[6 empty] | 2018-04-11 07:12 | 2018-04-11 19:56 |  |  |  | 0 | 0 | 0 | 0.53056 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[6 empty] | 2018-04-11 21:35 | 2018-04-17 11:12 |  |  |  | 0 | 0 | 0 | 1900-01-04 13:37 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=431kV
[6 empty] | 2018-04-18 13:24 | 2018-04-19 08:43 |  |  |  | 0 | 0 | 0 | 0.80486 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2018-04-22 13:12 | 2018-04-22 21:14 |  |  |  | 0 | 0 | 0 | 0.33472 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri-430kV
[6 empty] | 2018-04-24 07:09 | 2018-04-24 10:53 |  |  |  | 0 | 0 | 0 | 0.15556 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNPR=430kV
[6 empty] | 2018-04-28 07:02 | 2018-04-28 16:21 |  |  |  | 0 | 0 | 0 | 0.38819 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2018-04-29 17:51 | 2018-05-01 00:45 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:54 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 04:13 | [6 empty] | 720 | 469 | 260.051 | 121963.919 | 121963.919 | 100
35 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 45.94 | 23659.1 | 23659.1 | 100
36 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 45.94 | 23659.1 | 23659.1 | 100
37 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | 2018-04-13 11:10 | 2018-04-13 11:33 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OMST | Taken under S/D to take L/R into service
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 291 | 240 | 69840 | 69840 | 100
38 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | 2018-04-14 12:40 | 2018-04-14 20:32 |  |  |  | 0.32778 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault. FD: KNP-43.61km, FC: KNP-9.69KA. Fault in Auraiya TL group jurisdiction
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.32778 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 72.6 | 37389 | 36980.4906 | 98.9074
39 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 73.2 | 37698 | 37698 | 100
40 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2018-04-13 02:30 | 2018-04-13 02:30 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on B-N fault. F.D.=147KM from Kanpur & 247.4KM from Ballabhgarh. F.C.= 2.8KAmp at Kanpur & 1.9KAmp at Ballabhgarh, The fault was in Mainpuri juridiction.
[6 empty] | 2018-04-15 07:16 | 2018-04-24 20:29 |  |  |  | 0 | 0 | 0 | 1900-01-08 13:13 |  |  |  | LCSD | S/D availed by NR-1 for diversion of line due to newly constructed eastern periphery road of NHAI.
[6 empty] | 2018-04-25 11:40 | 2018-04-25 11:40 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on B-N fault, F.D.= 226KM from KNP and 139kM from BLB end, F.C.= 1.6KAMP at KNP and 2.4kAmp at BLB end, The fault was in Mainpuri juridiction.
[6 empty] | 2018-04-25 12:41 | 2018-04-25 16:57 |  |  |  | 0.17778 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on B-N fault, F.D.= 33.5KM from KNP and 324kM from BLB end, F.C.= 9.26KAMP at KNP and 1.3kAmp at BLB end, The fault was in Kanpur TL juridiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.17778 | 0 | 0 | 1900-01-08 13:13 | [6 empty] | 720 | 342 | 385.69 | 131905.98 | 131124.3149 | 99.4074
47 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 361 | 370.772 | 133848.692 | 133848.692 | 100
41 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- | 2018-04-28 07:24 | 2018-04-30 07:56 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 00:32 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=418kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 00:32 | [6 empty] | 720 | 361 | 370.772 | 133848.692 | 133848.692 | 100
42 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 107.079 | 55145.685 | 55145.685 | 100
43 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 107.1 | 55156.5 | 55156.5 | 100
44 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 5.922 | 3049.83 | 3049.83 | 100
45 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 5.86 | 3017.9 | 3017.9 | 100
46 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 289 | 263.933 | 76276.637 | 76276.637 | 100
47 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 289 | 263.933 | 76276.637 | 76276.637 | 100
48 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 | 100
49 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 | 100
50 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | 2018-04-03 12:16 | 2018-04-03 12:44 |  |  |  | 0 | 0.019444 | 0 | 0 |  |  |  | OMSU | Tripped due to Y-N fault. F.D.= 63.6KM from Lucknow(PG), F.C.= 3.193KAmp at Lucknow(PG). The fault was in UPPCL juridiction
[6 empty] | 2018-04-06 15:01 | 2018-04-06 17:40 |  |  |  | 0 | 0 | 0 | 0.11042 |  |  |  | OSFD | Emergency S/D availed by UPPCL for atteding hot spot on jumper at loc no 371B
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.019444 | 0 | 0.11042 | [6 empty] | 720 | 515 | 41.743 | 21497.645 | 21497.645 | 100
51 | NR140114 | 400KV LUCKNOW-SHAHJHNPR-I | 169.785 | NR3 | -- | 2018-04-29 22:40 | 2018-04-29 23:31 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LNCC | Tripped on Y-B fault due to heavy thunderstorm. FD: Shahajahapur-169.7km. FC: Shahajahapur-Y-2.2KA, B-2.3KA. Fault in Lucknow jurisdiction
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 371 | 169.785 | 62990.235 | 62990.235 | 100
52 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 169.729 | 87410.435 | 87410.435 | 100
53 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.281 | 50614.715 | 50614.715 | 100
54 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  | 2018-04-06 09:59 | 2018-04-06 16:48 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for replacement of B Ph CVT due to drift in CVT secondary voltage more than 4 volts as compared to other phases
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.281 | 50614.715 | 50614.715 | 100
55 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- | 2018-04-02 16:37 | 2018-04-02 17:36 | -- | -- | -- | 0 | 0.040972 | 0 | 0 |  |  |  | OMSU | Tripped only from UPPCL sultanpur end due to problem at their end
[6 empty] | 2018-04-05 09:05 | 2018-04-05 10:54 |  |  |  | 0.075694 | 0 | 0 | 0 |  |  |  | LPPT | Tripped due to Y-B fault. FD: LKO- 18.2km, FC: LKO- Y-17.39KA, B-17.40KA.
[6 empty] | 2018-04-05 11:22 | 2018-04-05 16:36 |  |  |  | 0 | 0 | 0 | 0.21806 |  |  |  | OSFD | Emergency S/D availed by UPPCL for testing work at their end.
[6 empty] | 2018-04-23 11:53 | 2018-04-23 17:36 |  |  |  | 0 | 0 | 0 | 0.23819 |  |  |  | OSFD | Emergency S/D availed by UPPCL to attend heavy leakage of oil from R phase CT and hot point on Bus side CT clamp of Rphase CT at Sultanpur end(UPPCl end).
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.075694 | 0.040972 | 0 | 0.45625 | [6 empty] | 720 | 515 | 41.743 | 21497.645 | 21443.4033 | 99.7477
56 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 73.826 | 38020.39 | 38020.39 | 100
57 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- | 2018-04-01 14:43 | 2018-04-01 15:16 | -- | -- | -- | 0.022917 | 0 | 0 | 0 |  |  |  | LPPT | Tripped due to R-Y ph fault,F.D.=26.64km from Lucknow,F.C.-Ir=12.71KA,Iy=12.72KA,F.D.=37.9km from Unnao(Lucknow jurisdiction)
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.022917 | 0 | 0 | 0 | [6 empty] | 734.52 | 515 | 73.826 | 38020.39 | 37991.9208 | 99.9251
58 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 691 | 30.703 | 21215.773 | 21215.773 | 100
59 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 691 | 31.159 | 21530.869 | 21530.869 | 100
60 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
61 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
62 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 433 | 279.245 | 120913.085 | 120913.085 | 100
63 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 433 | 279.245 | 120913.085 | 120913.085 | 100
64 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | 2018-04-19 14:52 | 2018-04-19 15:27 |  |  |  | 0 | 0.024306 | 0 | 0 |  |  |  | OMSU | Tripped only from Singrauli (NTPC) end on Y-N fault, F.D.= 22.4KM from Allahabad, F.C.= 12.1KAmp at Allahabad
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.024306 | 0 | 0 | [6 empty] | 720 | 332 | 224 | 74368 | 74368 | 100
65 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 306 | 202 | 61812 | 61812 | 100
66 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 25.057 | 12904.355 | 12904.355 | 100
67 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 236 | 330.953 | 78104.908 | 78104.908 | 100
68 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- | 2018-04-11 05:47 | 2018-04-11 07:01 | -- | -- |  | 0.051389 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on R-N fault. FD:142.6kM from Lucknow(UP) FC:2.39kA at Lucknow(UP). Fault in Allahabad jurisdiction.
[6 empty] | 2018-04-27 08:57 | 2018-05-01 |  |  |  | 0 | 0 | 0 | 1900-01-02 15:03 |  |  |  | LCSD | Diverson of Line for MUNPL ( Meza Urza Nigam Ltd.) at Allahabad of existing Singarauli-Lucknow line on account of Railway siding construction work.
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.051389 | 0 | 0 | 1900-01-02 15:03 | [6 empty] | 720 | 337 | 408.6 | 137698.2 | 137462.3281 | 99.8287
69 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- | 2018-04-21 08:25 | 2018-04-21 09:23 | -- | -- |  | 0 | 0.040278 | 0 | 0 |  |  |  | OMSU | Tripped due to CT blast of 400KV Rihand-Rihand-1 at Rihand(NTPC)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.040278 | 0 | 0 | [6 empty] | 720 | 515 | 42.026 | 21643.39 | 21643.39 | 100
70 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- | 2018-04-21 08:25 | 2018-04-21 12:44 | -- | -- |  | 0 | 0.17986 | 0 | 0 |  |  |  | OMSU | Tripped due to CT blast of 400KV Rihand-Rihand-1 at Rihand(NTPC)
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.17986 | 0 | 0 | [6 empty] | 720 | 515 | 43.952 | 22635.28 | 22635.28 | 100
71 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 3.341 | 1720.615 | 1720.615 | 100
72 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 3.317 | 1708.255 | 1708.255 | 100
73 | NR140164 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 69.677 | 35883.655 | 35883.655 | 100
74 | NR140165 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | 2018-04-04 08:01 | 2018-04-05 22:59 |  |  |  | 0 | 0 | 0 | 1899-12-31 14:58 |  |  |  | OSPD | S/D taken by UPPTCL for AMP & replacement of old and outlived CTs , LA and CVTs at Sarnath end.
[6 empty] | 2018-04-24 08:34 | 2018-04-24 11:02 |  |  |  | 0 | 0 | 0 | 0.10278 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending oil leakage in R-phase line CT at their end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 17:26 | [6 empty] | 720 | 515 | 69.677 | 35883.655 | 35883.655 | 100
75 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 21.233 | 14587.071 | 14587.071 | 100
76 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | 2018-04-18 10:00 | 2018-04-18 17:46 |  |  |  | 0.32361 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.32361 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 21.233 | 14587.071 | 14429.7197 | 98.9213
77 | NR340008 | 400KV LKO(765)-KANPUR(GIS)-I | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 159.7 | 109713.9 | 109713.9 | 100
78 | NR340009 | 400KV LKO(765)-KANPUR(GIS)-II | 159.7 | NR3 | -- | 2018-04-18 10:00 | 2018-04-18 17:46 |  |  |  | 0.32361 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.32361 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 159.7 | 109713.9 | 108530.4121 | 98.9213
79 | NR340010 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR3 | -- | 2018-04-08 00:25 | 2018-04-08 01:44 |  |  |  | 0 | 0.054861 | 0 | 0 |  |  |  | OMSU | Tripped due to heavy thunder storm and rain and black out of Meza S/s due to tripping of all asociated feeder at Meza S/S.
[6 empty] | 2018-04-09 15:18 | 2018-04-09 17:39 |  |  |  | 0 | 0 | 0 | 0.097917 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. ALLD=430kV
[6 empty] | 2018-04-12 05:13 | 2018-04-16 15:07 |  |  |  | 0 | 0 | 0 | 1900-01-03 09:54 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=432kV
[6 empty] | 2018-04-18 13:01 | 2018-05-01 |  |  |  | 0 | 0 | 0 | 0.054861 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=426kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.054861 | 0 | 1900-01-03 13:34 | [6 empty] | 720 | 687 | 28.19 | 19366.53 | 19366.53 | 100
80 | NR340011 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR3 | -- | 2018-04-08 00:25 | 2018-04-08 03:49 |  |  |  | 0 | 0.14167 | 0 | 0 |  |  |  | OMSU | Tripped due to heavy thunder storm and rain and black out of Meza S/s due to tripping of all asociated feeder at Meza S/S.
[6 empty] | 2018-04-16 13:49 | 2018-04-18 10:33 |  |  |  | 0 | 1899-12-31 20:44 | 0 | 0 |  |  |  | OMSU | Tripped due to DT received at Allahabad end caused by problem at Meja(NTPC) end.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 1900-01-01 00:08 | 0 | 0 | [6 empty] | 720 | 515 | 28.19 | 14517.85 | 14517.85 | 100
81 |  | 400KV Kanpur(GIS)-Allahabad-1 | 239.5 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 239.5 | 123342.5 | 123342.5 | 100
82 |  | 400KV Kanpur(GIS)-Allahabad-2 | 239.5 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 239.5 | 123342.5 | 123342.5 | 100
83 |  | 400KV ORAI-ORAI(UP)-I | 41.832 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 41.832 | 21543.48 | 21543.48 | 100
84 |  | 400KV ORAI-ORAI(UP)-II | 41.832 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 41.832 | 21543.48 | 21543.48 | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- | 2018-04-03 11:52 | 2018-04-03 15:36 | -- | -- |  | 0 | 0 | 0 | 0.15556 |  |  |  | OSFD | S/D taken by UPPCL to attend hot spot at their end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.15556 | [6 empty] | 720 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 3 | 396 | 396 | 100
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | 2018-04-25 10:01 | 2018-04-25 18:02 |  |  |  | 0.33403 | 0 | 0 | 0 |  |  |  | OMST | S/D/ availed by Powergrid for testing work
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.33403 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 182.176 | 24047.232 | 23779.4839 | 98.8866
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 182.176 | 24047.232 | 24047.232 | 100
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- | 2018-04-06 22:46 | 2018-04-06 23:27 | -- | -- |  | 0 | 0 | 0.028472 | 0 |  |  |  | GOVC | Tripped due to over voltage at Dhauliganga
[6 empty] | 2018-04-11 05:27 | 2018-04-11 17:35 |  |  |  | 0 | 0 | 0.50556 | 0 |  |  |  | GOVC | Tripped on Over voltage protection.
[6 empty] | 2018-04-12 17:33 | 2018-04-12 17:57 |  |  |  | 0 | 0 | 0.016667 | 0 |  |  |  | GOVC | Tripped on Over voltage protection.
[6 empty] | 2018-04-26 10:26 | 2018-04-26 17:44 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | OSPD | S/D availed by NHPC for testing of protection Relay at their end.
[6 empty] | 2018-04-27 10:25 | 2018-04-27 17:27 |  |  |  | 0 | 0 | 0 | 0.29306 |  |  |  | OSPD | S/D availed by Dhauliganga (NHPC) for maintenance & relay work
[6 empty] | 2018-04-29 11:35 | 2018-04-29 17:34 |  |  |  | 0 | 0 | 0 | 0.24931 |  |  |  | OSPD | S/D availed by NHPC for testing work at their end
[6 empty] | 2018-04-30 11:58 | 2018-04-30 17:35 |  |  |  | 0 | 0 | 0 | 0.23403 |  |  |  | OSPD | S/D availed by NHPC for testing work at their end
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.55069 | 1899-12-31 01:56 | [6 empty] | 706.7833 | 109 | 234.59 | 25570.31 | 25570.31 | 100
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- | 2018-04-06 22:49 | 2018-04-07 10:53 | -- | -- | -- | 0 | 0 | 0.50278 | 0 |  |  |  | GOVC | Tripped due to over voltage at Dhauliganga
[6 empty] | 2018-04-08 14:04 | 2018-04-08 18:23 |  |  |  | 0 | 0 | 0.17986 | 0 |  |  |  | GOVC | Tripped due to over voltage at Dhauliganga and DT received at Pithoragarh end.
[6 empty] | 2018-04-09 14:31 | 2018-04-09 18:19 |  |  |  | 0 | 0 | 0.15833 | 0 |  |  |  | GOVC | Tripped due to over voltage at Dhauliganga and DT received at Pithoragarh end.
[6 empty] | 2018-04-11 05:27 | 2018-04-11 18:12 |  |  |  | 0 | 0 | 0.53125 | 0 |  |  |  | GOVC | Tripped on Over voltage protection.
[6 empty] | 2018-04-12 17:33 | 2018-04-12 17:54 |  |  |  | 0 | 0 | 0.014583 | 0 |  |  |  | GOVC | Tripped on Over voltage protection.
[6 empty] | 2018-04-15 13:26 | 2018-04-15 16:57 |  |  |  | 0 | 0 | 0 | 0.14653 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Pithoragarh=236kV.
[6 empty] | 2018-04-22 12:55 | 2018-04-22 17:11 |  |  |  | 0 | 0 | 0 | 0.17778 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. D'Ganga=239kV
[6 empty] | 2018-04-24 10:03 | 2018-04-24 16:59 |  |  |  | 0 | 0 | 0 | 0.28889 |  |  |  | OSPD | S/D availed by NHPC for testing of protection Relay at their end.
[6 empty] | 2018-04-25 10:09 | 2018-04-25 17:18 |  |  |  | 0 | 0 | 0 | 0.29792 |  |  |  | OSPD | S/D availed by NHPC for testing of protection Relay at their end.
[6 empty] | 2018-04-29 11:20 | 2018-04-29 17:37 |  |  |  | 0 | 0 | 0 | 0.26181 |  |  |  | OSPD | S/D availed by NHPC for testing work at their end
[5 empty] | -- | 2018-04-30 11:50 | 2018-04-30 17:35 | -- | -- | -- | 0 | 0 | 0 | 0.23958 |  |  |  | OSPD | S/D availed by NHPC for testing work at their end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 1899-12-31 09:17 | 1899-12-31 09:54 | [6 empty] | 686.7167 | 156 | 59.01 | 9205.56 | 9205.56 | 100
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- | 2018-04-04 16:08 | 2018-04-04 17:14 | -- | -- |  | 0 | 0.045833 | 0 | 0 |  |  |  | OMSU | Tripped due to Bus fault at Fatehpur (UP) end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.045833 | 0 | 0 | [6 empty] | 720 | 131 | 5.284 | 692.204 | 692.204 | 100
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- | 2018-04-04 16:08 | 2018-04-04 17:15 | -- | -- |  | 0 | 0.046528 | 0 | 0 |  |  |  | OMSU | Tripped due to Bus fault at Fatehpur (UP) end.
[6 empty] | 2018-04-05 08:20 | 2018-04-05 13:09 |  |  |  | 0 | 0 | 0 | 0.20069 |  |  |  | OSFD | Emergency S/D availed by UPPCL to attend hot spot /sparking at their end.
[6 empty] | 2018-04-08 09:25 | 2018-04-08 14:15 |  |  |  | 0 | 0.20139 | 0 | 0 |  |  |  | OMSU | Tripped on R-Y fault.FD:0.5kM from Fatehpur FC:Iy=15.76kA, Ir=15.4kA. Tripped due to UPPCL working on New 220kV Fatehpur(PG)-Sarh 1&2 line tower and earth wire fallen on 220KV FATEHPUR-FTHPR(UP)-II.
[6 empty] | 2018-04-12 08:45 | 2018-04-12 18:57 |  |  |  | 0 | 0 | 0 | 0.425 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending hot spot in Y-phase CT at Fatehpur(UP) end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.24792 | 0 | 0.62569 | [6 empty] | 720 | 131 | 5.284 | 692.204 | 692.204 | 100
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | 2018-04-10 12:47 | 2018-04-10 18:48 |  |  |  | 0 | 0.25069 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault. FD: 54.2kM from Fatehpur. FC:2.97kA at Fatehpur. Fault in UPPCL jurisdiction.
[6 empty] | 2018-04-16 12:56 | 2018-04-16 14:55 |  |  |  | 0 | 0.082639 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault. FD: 9.5kM from Fatehpur. FC: 6.05kA at Fatehpur. Fault in UPPCL jurisdiction.
[6 empty] | 2018-04-28 09:49 | 2018-05-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 14:11 |  |  |  | OSPD | S/D availed by UPPCL for General maintenance --diversion of line (Tower erection & stringing) for DFCC at Sarsaul
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.33333 | 0 | 1900-01-01 14:11 | [6 empty] | 720 | 131 | 6.17 | 808.27 | 808.27 | 100
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | 2018-04-15 12:09 | 2018-04-15 12:40 |  |  |  | 0 | 0.021528 | 0 | 0 |  |  |  | OMSU | Tripped due to B-N fault. FD: 39.5kM from Fatehpur and 41 kM from Naubasta(UP) end. FC: 3.6kA at Fatehpur. Fault in UPPCL jurisdiction.
[6 empty] | 2018-04-19 12:43 | 2018-04-19 15:00 |  |  |  | 0 | 0.095139 | 0 | 0 |  |  |  | OMSU | Tripped on B-N fault. F.D.=7.6KM from Fatehpur, F.C.= 2.5KAmp. The fault was in UPPTCL juridiction.
[6 empty] | 2018-04-26 13:01 | 2018-04-26 16:17 |  |  |  | 0 | 0.13611 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault. FD:73kM from Fatehpur. Fault in UPPCL jurisidiction.
[6 empty] | 2018-04-28 09:44 | 2018-05-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 14:16 |  |  |  | OSPD | S/D availed by UPPCL for General maintenance --diversion of line (Tower erection & stringing) for DFCC at Sarsaul
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.25278 | 0 | 1900-01-01 14:16 | [6 empty] | 720 | 131 | 6.17 | 808.27 | 808.27 | 100
13 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- | 2018-04-25 12:41 | 2018-04-25 17:45 |  |  | -- | 0 | 0.21111 | 0 | 0 |  |  |  | OMSU | Tripped on B-N fault, F.D.= 71KM from KNP and 116.4kM from MNP end, F.C.= 2.3KAMP at KNP and 11.49kAmp at MNP end, The fault was in UPPCL juridiction.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.21111 | 0 | 0 | [6 empty] | 720 | 131 | 10.4 | 1362.4 | 1362.4 | 100
14 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 14.86 | 1946.66 | 1946.66 | 100
15 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)-1 | 8.717 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 8.717 | 1141.927 | 1141.927 | 100
16 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 14.86 | 1946.66 | 1946.66 | 100
17 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 143.553 | 18805.443 | 18805.443 | 100
18 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 143.553 | 18805.443 | 18805.443 | 100
19 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 144.63 | 18946.53 | 18946.53 | 100
20 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 144.63 | 18946.53 | 18946.53 | 100
21 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | 2018-04-11 06:31 | 2018-04-11 06:57 |  |  |  | 0 | 0 | 0 | 0.018056 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Pithoragarh=240kV
[6 empty] | 2018-04-11 17:24 | 2018-04-11 18:50 |  |  |  | 0 | 0 | 0 | 0.059722 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
[6 empty] | 2018-04-13 01:30 | 2018-04-13 08:45 |  |  |  | 0 | 0 | 0 | 0.30208 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Pithoragarh=233KV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.37986 | [6 empty] | 720 | 156 | 177.88 | 27749.28 | 27749.28 | 100
22 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR3 | -- | 2018-04-01 | 2018-05-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-29 |  |  |  | OSPD | S/D availed by UPPCL for LILO work at New 220kV C.G.City S/S.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-29 | [6 empty] | 720 | 132 | 1.19 | 157.08 | 157.08 | 100
23 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 1.19 | 157.08 | 157.08 | 100
24 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- | 2018-04-06 17:02 | 2018-04-06 19:50 | -- | -- | -- | 0.11667 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for atteding hot spot in line isolator at CB Ganj
[6 empty] | 2018-04-09 11:08 | 2018-04-09 14:16 |  |  |  | 0.13056 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault. FD: Sitarganj-56.45km, FC: Sitarganj-1.564KA. Fault in Bareilly TL jurisdiction.
[6 empty] | 2018-04-17 12:50 | 2018-04-17 13:30 |  |  |  | 0 | 0.027778 | 0 | 0 |  |  |  | OMSU | Tripped only from Bareily(UP) end due to problem at their end
[6 empty] | 2018-04-18 11:12 | 2018-04-18 14:54 |  |  |  | 0 | 0.15417 | 0 | 0 |  |  |  | OMSU | Tripped due to broken of Y ph jumper at Bareily(UP) end
[6 empty] | 2018-04-21 10:44 | 2018-04-21 17:49 |  |  |  | 0 | 0 | 0 | 0.29514 |  |  |  | OSFD | Emergency S/D availed by UPPCL to attend highly damaged R & Y Ph jumper at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.24722 | 0.18194 | 0 | 0.29514 | [6 empty] | 720 | 132 | 105.72 | 13955.04 | 13840.0401 | 99.1759
25 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | 2018-04-06 03:11 | 2018-04-06 12:06 |  |  |  | 0 | 0.37153 | 0 | 0 |  |  |  | OMSU | Tripped due to CB problem at Tanakpur end.
[6 empty] | 2018-04-18 15:53 | 2018-04-18 17:58 |  |  |  | 0 | 0 | 0 | 0.086806 |  |  |  | OSFD | E/S/D taken by UPPCL for attending heavy sparking in line isolator at Bareily(UP) end
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.37153 | 0 | 0.086806 | [6 empty] | 720 | 132 | 106 | 13992 | 13992 | 100
26 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | 2018-04-09 12:35 | 2018-04-09 12:46 |  |  |  | 0 | 0 | 0 | 0.0076389 |  |  |  | OSFD | Breaker opened at Sitarganj end as requested by Tanakpur as Tanakpur S/S was dead.
[6 empty] | 2018-04-18 11:12 | 2018-04-18 13:12 |  |  |  | 0 | 0.083333 | 0 | 0 |  |  |  | OMSU | Tripped only from NHPC/Tanakpur end due to problem at their end
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.083333 | 0 | 0.0076389 | [6 empty] | 720 | 132 | 42.55 | 5616.6 | 5616.6 | 100
27 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 0.92 | 121.44 | 121.44 | 100
28 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 0.92 | 121.44 | 121.44 | 100
29 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 42.5 | 5610 | 5610 | 100
30 | NR320001 | 220KV KNP-RANIA | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 18.372 | 2425.104 | 2425.104 | 100
[5 empty] | -- | [17 empty] | 2420.56
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 | 58 | 2900 | 2900 | 100
131 | Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-12 09:34 | 1900-01-04 11:47 | 1900-02-04 23:22 | 1900-06-04 01:45 | [8 empty] | 19577.92 | 10646592.644 | 10527159.7326 | 98.8782 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 75.0111 | % (HVDC) | 90.5506
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | 2018-04-02 12:06 | 2018-04-03 03:42 |  |  |  | 0.65 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work and neutral jumper modification work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.65 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1467.5 | 97.8333
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | 2018-04-04 10:18 | 2018-04-04 22:00 |  |  |  | 0.4875 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.4875 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1475.625 | 98.375
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
17 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
18 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
19 | NR3ICT701 | 765/400KV ICT-I Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
20 | NR3ICT702 | 765/400KV ICT-II Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
21 | NR3ICT05 | 1000MVA ICT-1 ORAI(GIS) | 1000 | NR3 |  | 2018-04-10 11:24 | 2018-04-10 13:53 |  |  |  | 0.10347 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to attend leakage on top of tank pipe line of R-phase unit of ICT-1 and mog alarm has appeared.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.10347 | 0 | 0 | 0 | [6 empty] | 720 | 1000 |  | 1000 | 996.5509 | 99.6551
21 | NR3ICT06 | 1000MVA ICT-2 ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1000 |  | 1000 | 1000 | 100
F |  | 400/220 KV ICT'S |  | NR3 | --
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | 2018-04-04 09:14 | 2018-04-04 18:35 |  |  |  | 0.38958 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work. |  | 720 | 315 |  | 315 | 310.9094 | 98.7014
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | 2018-04-06 09:13 | 2018-04-06 18:10 |  |  |  | 0.37292 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work. |  | 720 | 315 |  | 315 | 311.0844 | 98.7569
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 |  | 2018-04-05 09:12 | 2018-04-05 19:48 |  |  |  | 0.44167 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for AMP work. |  | 720 | 315 |  | 315 | 310.3625 | 98.5278
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | 2018-04-30 02:33 | 2018-05-01 |  |  |  | 0.89375 | 0 | 0 | 0 |  |  |  | SICT | Tripped due to buchholz relay operation
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.89375 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 305.6156 | 97.0208
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR3 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | 2018-04-06 23:06 | 2018-04-06 23:53 |  |  |  | 0 | 0 | 0.032639 | 0 |  |  |  | GOFC | Tripped due to over flux
[6 empty] | 2018-04-07 02:50 | 2018-04-07 06:31 |  |  |  | 0 | 0 | 0.15347 | 0 |  |  |  | GOFC | Tripped due to over flux
[6 empty] | 2018-04-08 14:05 | 2018-04-08 18:28 |  |  |  | 0 | 0 | 0.18264 | 0 |  |  |  | GOFC | Tripped due to over flux relay operated.
[6 empty] | 2018-04-09 10:54 | 2018-04-09 18:05 |  |  |  | 0 | 0 | 0.29931 | 0 |  |  |  | GOFC | Tripped due to over flux relay operated.
[6 empty] | 2018-04-11 05:44 | 2018-04-11 08:24 |  |  |  | 0 | 0 | 0.11111 | 0 |  |  |  | GOFC | Tripped on Over Fluxing protection.
[6 empty] | 2018-04-11 12:06 | 2018-04-11 18:32 |  |  |  | 0 | 0 | 0.26806 | 0 |  |  |  | GOFC | Tripped on Over Fluxing protection.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1899-12-31 01:08 | 0 | [6 empty] | 694.8667 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | 2018-04-06 23:06 | 2018-04-06 23:53 |  |  |  | 0 | 0 | 0.032639 | 0 |  |  |  | GOFC | Tripped due to over flux |  | 719.2167 | 100 |  | 100 | 100 | 100
[6 empty] | 2018-04-07 02:46 | 2018-04-07 06:46 |  |  |  | 0 | 0 | 0.16667 | 0 |  |  |  | GOFC | Tripped due to over flux
[6 empty] | 2018-04-08 14:04 | 2018-04-08 18:27 |  |  |  | 0 | 0 | 0.18264 | 0 |  |  |  | GOFC | Tripped due to over flux relay operated.
[6 empty] | 2018-04-09 10:51 | 2018-04-09 18:06 |  |  |  | 0 | 0 | 0.30208 | 0 |  |  |  | GOFC | Tripped due to over flux relay operated.
[6 empty] | 2018-04-11 05:44 | 2018-04-11 09:00 |  |  |  | 0 | 0 | 0.13611 | 0 |  |  |  | GOFC | Tripped on Over Fluxing protection.
[6 empty] | 2018-04-11 12:08 | 2018-04-11 18:32 |  |  |  | 0 | 0 | 0.26667 | 0 |  |  |  | GOFC | Tripped on Over Fluxing protection.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1899-12-31 02:05 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1900-01-01 04:10 | 0 | [6 empty] | 667.8333 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 200 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 200 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
--
45 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 1900-01-01 17:41 | 0 | 1900-01-02 05:18 | 0 | [7 empty] | 31425 |  | 31425 | 31342.6478 | 99.7379 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2018-04-02 15:20 | 2018-04-02 15:20 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC transient earth fault,F.D.=387.6km from Rihand, F.D.=427.4km from Dadri (Kanpur Jurisdiction)
[6 empty] | 2018-04-07 17:02 | 2018-04-07 17:02 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient DC earth fault. FD: 786.08kM from Rihand and 28.92kM from dadri. Fault in NR-1 jurisdiction.
[6 empty] | 2018-04-08 03:56 | 2018-04-08 03:56 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient DC earth fault. FD: 785.95kM from Rihand and 29.05kM from dadri. Fault in NR-1 jurisdiction.
[6 empty] | 2018-04-24 03:03 | 2018-04-24 03:03 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: 735.4kM from Rihand and 79.6kM from Dadri. Fault in NR-1 jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2018-04-01 12:45 | 2018-04-01 12:45 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC transient earth fault,F.D.=761.58km from Rihand, F.D.=53.42km from Dadri (NR-1 Jurisdiction)
[6 empty] | 2018-04-01 19:07 | 2018-04-01 19:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC transient earth fault,F.D.=564.77km from Rihand, F.D.=250.23km from Dadri (Mainpuri Jurisdiction)
[6 empty] | 2018-04-08 23:31 | 2018-04-08 23:31 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient DC earth fault. FD: 755.25kM from Rihand and 59.75kM from dadri. Fault in NR-1 jurisdiction.
[6 empty] | 2018-04-16 11:42 | 2018-04-16 11:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient DC earth fault. FD: 641.96kM from Rihand and 173.04kM from dadri. Fault in Mainpuri jurisdiction.
[6 empty] | 2018-04-24 23:08 | 2018-04-24 23:08 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: 320.65kM from Rihand and 494.35kM from Dadri. Fault in Allahabad jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 611250 | 100
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | 2018-04-22 04:47 | 2018-04-22 06:02 |  |  |  | 0.052083 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to spare transformer isolator status intermidiate alarm at Ballia
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.052083 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 985518.5547 | 99.8264
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2018-04-25 11:27 | 2018-04-25 11:27 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: 394.895kM from Bhiwadi. Fault in Kanpur TL jurisdiction.
[6 empty] | 2018-04-30 03:12 | 2018-04-30 03:45 |  |  |  | 0.022917 | 0 | 0 | 0 |  |  |  | OSFT | Emergency hand tripped due to heavy sparking in smoothening reactor
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.022917 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 986478.3641 | 99.9236
5 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2018-04-01 16:31 | 2018-04-08 08:54 |  |  |  | 0 | 0 | 0 | 1900-01-05 16:23 |  |  |  | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
[6 empty] | 2018-04-10 08:27 | 2018-04-21 13:06 |  |  |  | 0 | 0 | 0 | 1900-01-10 04:39 |  |  |  | LCSD | S/D availed by ER-1 for Shifting of line to pile foundation at loc no 1787.
[6 empty] | 2018-04-23 09:03 | 2018-04-24 09:51 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:48 |  |  |  | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-17 21:50 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000 | 100
6 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | 2018-04-01 | 2018-04-01 17:34 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
[6 empty] | 2018-04-08 06:55 | 2018-04-10 08:27 |  |  |  | 0 | 0 | 0 | 1900-01-01 01:32 |  |  |  | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
[6 empty] | 2018-04-10 08:27 | 2018-04-20 23:24 |  |  |  | 0 | 0 | 0 | 1900-01-09 14:57 |  |  |  | LCSD | S/D availed by ER-1 for Shifting of line to pile foundation at loc no 1787.
[6 empty] | 2018-04-20 23:24 | 2018-04-23 22:22 |  |  |  | 0 | 0 | 0 | 1900-01-01 22:58 |  |  |  | LVRD | kept Blocked on voltage regulation. Readiness sent via email on dtd 20.04.18
[6 empty] | 2018-04-24 10:47 | 2018-04-24 12:56 |  |  |  | 0.089583 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on DC line fault. FD: 456.9kM from Agra. Tower No 3208/A-7(57/1). Fault in lucknow jurisdiction.
[6 empty] | 2018-04-24 13:48 | 2018-04-24 19:56 |  |  |  | 0.25556 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on DC line fault. FD: 456.9kM from Agra. Tower No 3208/A-7(57/1). Fault in lucknow jurisdiction.
[6 empty] | 2018-04-25 21:34 | 2018-04-25 22:31 |  |  |  | 0.039583 | 0 | 0 | 0 |  |  |  | OSFT | Blocked to attend spark on in Bus Isolator of Bus-I sectionalizer at BNC end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.38472 | 0 | 0 | 1900-01-14 15:27 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2558760 | 98.7176
7 | NR1DCP03 | 800KV HVDC AGRA-APD POLE-III | 789.786 | NR3 | -- | 2018-04-01 | 2018-04-25 19:13 |  |  |  | 0 | 0 | 0 | 1900-01-23 19:13 |  |  |  | LPRD | Blocked on Power regulation as per NLDC instruction(due to Coal based farakkha S/S is dead)
[6 empty] | 2018-04-30 04:32 | 2018-05-01 |  |  |  | 0 | 0 | 0 | 0.81111 |  |  |  | LVRD | Blocked for voltage regulation as per NLDC instruction
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-24 14:41 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000 | 100
8 | NR1DCP04 | 800KV HVDC AGRA-APD POLE-IV | 789.786 | NR3 | -- | 2018-04-01 | 2018-04-25 20:15 |  |  |  | 0 | 0 | 0 | 1900-01-23 20:15 |  |  |  | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-23 20:15 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000 | 100
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0.45972 | 0 | 0 | 1900-02-28 03:58 | [8 empty] | 10121.572 | 13564965 | 13529256.9187 | 99.7368 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2018-04-03 20:11 | 2018-04-04 02:38 |  |  |  | 0.26875 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to DC over current protection operated.
[6 empty] | 2018-04-09 03:02 | 2018-04-09 05:48 |  |  |  | 0.11528 | 0 | 0 | 0 |  |  |  | OMST | Tripped dueto DC Over current protection operated.
[6 empty] | 2018-04-17 15:35 | 2018-04-17 17:19 |  |  |  | 0.072222 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to operation of DC over current protection
[6 empty] | 2018-04-21 08:25 | 2018-04-21 10:42 |  |  |  | 0.095139 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to DC over current protection operated.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.55139 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 245.4051 | 98.162
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | 2018-04-01 | 2018-05-01 |  |  |  | 1900-01-29 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-29 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 0 | 0
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-29 13:14 | 0 | 0 | 0 | [9 empty] | 500 | 245.4051 | 49.081 | %
3 | NR1DCB02 | Sasaram HVDC B/B BLOCK-I | 250 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250 | 100
|  | HVDC BTB TOTAL |  |  | -- | [5 empty] | 1900-01-29 13:14 | 0 | 0 | 0 | [7 empty] | RC
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 530 | 530 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- | 2018-04-18 20:10 | 2018-04-19 13:25 | -- | -- |  | 0 | 0 | 0 | 0.71875 |  |  |  | SVRD
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.71875 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- | 2018-04-19 20:35 | 2018-04-20 06:43 | -- | -- |  | 0 | 0 | 0 | 0.42222 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV
[6 empty] | 2018-04-20 19:18 | 2018-04-21 08:29 |  |  |  | 0 | 0 | 0 | 0.54931 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=398kV
[6 empty] | 2018-04-21 18:42 | 2018-04-22 13:05 |  |  |  | 0 | 0 | 0 | 0.76597 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
[6 empty] | 2018-04-22 19:18 | 2018-04-23 06:10 |  |  |  | 0 | 0 | 0 | 0.45278 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
[6 empty] | 2018-04-29 00:33 | 2018-04-29 07:13 |  |  |  | 0 | 0 | 0 | 0.27778 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 11:14 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 2X50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- | 2018-04-19 20:40 | 2018-04-20 06:44 | -- | -- |  | 0 | 0 | 0 | 0.41944 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV
[6 empty] | 2018-04-20 19:21 | 2018-04-21 08:27 |  |  |  | 0 | 0 | 0 | 0.54583 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=398kV
[6 empty] | 2018-04-21 18:42 | 2018-04-22 13:06 |  |  |  | 0 | 0 | 0 | 0.76667 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
[6 empty] | 2018-04-22 19:18 | 2018-04-23 06:11 |  |  |  | 0 | 0 | 0 | 0.45347 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
[6 empty] | 2018-04-29 00:43 | 2018-04-29 07:14 |  |  |  | 0 | 0 | 0 | 0.27153 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 10:58 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
15 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
16 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | 2018-04-20 20:26 | 2018-04-22 13:15 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:49 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=734kV |  | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 16:49 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
17 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
18 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | 2018-04-20 20:26 | 2018-04-22 13:15 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:49 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=734kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 16:49 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
19 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
20 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
21 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
22 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
23 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
24 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
25 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
26 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
27 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
28 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
29 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
30 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
31 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
32 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
33 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
34 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
35 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
36 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
37 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
38 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
39 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
40 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
41 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
42 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
43 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
44 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
45 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
46 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
47 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
48 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
49 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | 2018-04-22 19:30 | 2018-04-25 00:42 |  |  |  | 0 | 0 | 0 | 1900-01-01 05:12 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=753kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 05:12 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
50 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
51 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
52 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100 | %
53 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100 | %
54 |  | 125MVAR B/Reactor-III KANPUR(GIS) | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100 | %
55 |  | 330MVAR B/Reactor-I ALIGARH | 330 | NR3 | -- | 2018-04-20 00:39 | 2018-04-20 05:18 |  |  |  | 0.19375 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.19375 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100 | %
56 |  | 330MVAR B/Reactor-II ALIGARH | 330 | NR3 | -- | 2018-04-20 00:39 | 2018-04-20 06:13 |  |  |  | 0.23194 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.23194 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100 | %
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L11:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M11:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N11:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O11:[Deemed Available, row above])
Note on C11: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C89: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C93: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C107: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C116: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C125: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C132: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C136: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C140: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C291: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C294: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C552: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C555: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C743: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C826: DOC-15/06/14
Note on C827: DOC-26/09/14

## Sheet1
1 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 11 | 12
NR1DCB01 | VINDH HVDC B/B BLOCK-I | 2018-04-03 20:11 | 2018-04-04 02:38 | 0.26875 | 0 | 0 | 0 | **** | OMST | Tripped due to DC over current protection operated.
NR1DCB01 | VINDH HVDC B/B BLOCK-I | 2018-04-09 03:02 | 2018-04-09 05:48 | 0.11528 | 0 | 0 | 0 | **** | OMST | Tripped dueto DC Over current protection operated.
NR1DCB01 | VINDH HVDC B/B BLOCK-I | 2018-04-17 15:35 | 2018-04-17 17:19 | 0.072222 | 0 | 0 | 0 | **** | OMST | Tripped due to operation of DC over current protection
NR1DCB01 | VINDH HVDC B/B BLOCK-I | 2018-04-21 08:25 | 2018-04-21 10:42 | 0.095139 | 0 | 0 | 0 |  | OMST | Tripped due to DC over current protection operated.
NR1DCB02 | VINDH HVDC B/B BLOCK-II | 2018-04-01 | 2018-05-01 | 1900-01-29 | 0 | 0 | 0 | **** | OMST | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL.
NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III | 2018-04-01 | 2018-04-25 19:13 | 0 | 0 | 0 | 1900-01-23 19:13 | NL-1252 | LPRD | Blocked on Power regulation as per NLDC instruction(due to Coal based farakkha S/S is dead)
NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III | 2018-04-30 04:32 | 2018-05-01 | 0 | 0 | 0 | 0.81111 | NL-1360 | LVRD | Blocked for voltage regulation as per NLDC instruction
NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV | 2018-04-01 | 2018-04-25 20:15 | 0 | 0 | 0 | 1900-01-23 20:15 | NL-136 | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I | 2018-04-01 16:31 | 2018-04-08 08:54 | 0 | 0 | 0 | 1900-01-05 16:23 | NL-10 | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I | 2018-04-10 08:27 | 2018-04-21 13:06 | 0 | 0 | 0 | 1900-01-10 04:39 | N-982 | LCSD | S/D availed by ER-1 for Shifting of line to pile foundation at loc no 1787.
NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I | 2018-04-23 09:03 | 2018-04-24 09:51 | 0 | 0 | 0 | 1899-12-31 00:48 | NL-1016 | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2018-04-01 | 2018-04-01 17:34 | 0 | 0 | 0 | 0.73194 | NL-248 | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2018-04-08 06:55 | 2018-04-10 08:27 | 0 | 0 | 0 | 1900-01-01 01:32 | N-719 | LPRD | Blocked on Power regulation as per NRLDC instruction(reverse power flow)
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2018-04-10 08:27 | 2018-04-20 23:24 | 0 | 0 | 0 | 1900-01-09 14:57 | N-983 | LCSD | S/D availed by ER-1 for Shifting of line to pile foundation at loc no 1787.
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2018-04-20 23:24 | 2018-04-23 22:22 | 0 | 0 | 0 | 1900-01-01 22:58 | **** | LVRD | kept Blocked on voltage regulation. Readiness sent via email on dtd 20.04.18
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2018-04-24 10:47 | 2018-04-24 12:56 | 0.089583 | 0 | 0 | 0 | **** | LEFT | Tripped on DC line fault. FD: 456.9kM from Agra. Tower No 3208/A-7(57/1). Fault in lucknow jurisdiction.
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2018-04-24 13:48 | 2018-04-24 19:56 | 0.25556 | 0 | 0 | 0 | **** | LEFT | Tripped on DC line fault. FD: 456.9kM from Agra. Tower No 3208/A-7(57/1). Fault in lucknow jurisdiction.
NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 2018-04-25 21:34 | 2018-04-25 22:31 | 0.039583 | 0 | 0 | 0 | NL-1185 | OSFT | Blocked to attend spark on in Bus Isolator of Bus-I sectionalizer at BNC end.
NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I | 2018-04-22 04:47 | 2018-04-22 06:02 | 0.052083 | 0 | 0 | 0 | **** | OMST | Tripped due to spare transformer isolator status intermidiate alarm at Ballia
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2018-04-25 11:27 | 2018-04-25 11:27 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: 394.895kM from Bhiwadi. Fault in Kanpur TL jurisdiction.
NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II | 2018-04-30 03:12 | 2018-04-30 03:45 | 0.022917 | 0 | 0 | 0 | **** | OSFT | Emergency hand tripped due to heavy sparking in smoothening reactor
NR1DCP01 | 500KV HVDC R-D POLE-I | 2018-04-02 15:20 | 2018-04-02 15:20 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient earth fault,F.D.=387.6km from Rihand, F.D.=427.4km from Dadri (Kanpur Jurisdiction)
NR1DCP01 | 500KV HVDC R-D POLE-I | 2018-04-07 17:02 | 2018-04-07 17:02 | 0 | 0 | 0 | 0 | **** | LART | Transient DC earth fault. FD: 786.08kM from Rihand and 28.92kM from dadri. Fault in NR-1 jurisdiction.
NR1DCP01 | 500KV HVDC R-D POLE-I | 2018-04-08 03:56 | 2018-04-08 03:56 | 0 | 0 | 0 | 0 | **** | LART | Transient DC earth fault. FD: 785.95kM from Rihand and 29.05kM from dadri. Fault in NR-1 jurisdiction.
NR1DCP01 | 500KV HVDC R-D POLE-I | 2018-04-24 03:03 | 2018-04-24 03:03 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: 735.4kM from Rihand and 79.6kM from Dadri. Fault in NR-1 jurisdiction.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2018-04-01 12:45 | 2018-04-01 12:45 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient earth fault,F.D.=761.58km from Rihand, F.D.=53.42km from Dadri (NR-1 Jurisdiction)
NR1DCP02 | 500KV HVDC R-D POLE-II | 2018-04-01 19:07 | 2018-04-01 19:07 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC transient earth fault,F.D.=564.77km from Rihand, F.D.=250.23km from Dadri (Mainpuri Jurisdiction)
NR1DCP02 | 500KV HVDC R-D POLE-II | 2018-04-08 23:31 | 2018-04-08 23:31 | 0 | 0 | 0 | 0 | **** | LART | Transient DC earth fault. FD: 755.25kM from Rihand and 59.75kM from dadri. Fault in NR-1 jurisdiction.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2018-04-16 11:42 | 2018-04-16 11:42 | 0 | 0 | 0 | 0 | **** | LART | Transient DC earth fault. FD: 641.96kM from Rihand and 173.04kM from dadri. Fault in Mainpuri jurisdiction.
NR1DCP02 | 500KV HVDC R-D POLE-II | 2018-04-24 23:08 | 2018-04-24 23:08 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: 320.65kM from Rihand and 494.35kM from Dadri. Fault in Allahabad jurisdiction.
NR376506 | 765KV AGRA-ALIGARH | 2018-04-07 15:52 | 2018-04-07 17:34 | 0.070833 | 0 | 0 | 0 | N-645 | OSFT | Emergency S/D availed to remove rope between location No 18 and 19 which fell down on conductor due to heavy storm.
NR376506 | 765KV AGRA-ALIGARH | 2018-04-11 19:15 | 2018-04-13 19:38 | 0 | 0 | 1900-01-01 00:23 | 0 | **** | LNCC | Tripped due to heavy storm on Y-N fault , F.D.=12.7KM from Agra, F.C.= 10KAmp at Agra.
NR376506 | 765KV AGRA-ALIGARH | 2018-04-20 00:39 | 2018-04-24 20:15 | 1900-01-03 19:36 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-01 | 2018-04-03 06:50 | 0 | 0 | 0 | 1900-01-01 06:50 | N-2557 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-04 13:34 | 2018-04-04 19:23 | 0 | 0 | 0 | 0.24236 | N-263 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-05 07:39 | 2018-04-05 10:31 | 0 | 0 | 0 | 0.11944 | N-322 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-06 08:19 | 2018-04-06 16:44 | 0 | 0 | 0 | 0.35069 | N-446 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-08 11:24 | 2018-04-09 14:06 | 0 | 0 | 0 | 1899-12-31 02:42 | N-746 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-10 07:13 | 2018-04-10 14:21 | 0 | 0 | 0 | 0.29722 | N-973 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-12 00:41 | 2018-04-12 09:57 | 0 | 0 | 0 | 0.38611 | N-1259 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=781kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-13 07:54 | 2018-04-13 20:22 | 0 | 0 | 0 | 0.51944 | N-1411 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=783kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-23 12:26 | 2018-04-23 19:42 | 0 | 0 | 0 | 0.30278 | N-2392 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
NR176502 | 765KV AGRA-FATEHPUR-I | 2018-04-24 13:07 | 2018-04-25 10:36 | 0 | 0 | 0 | 0.89514 | N-2487 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2018-04-03 08:10 | 2018-04-04 11:09 | 0 | 0 | 0 | 1899-12-31 02:59 | N-144 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=788kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2018-04-06 17:51 | 2018-04-07 16:51 | 0 | 0 | 0 | 0.95833 | N-509 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=797kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2018-04-09 07:07 | 2018-04-11 21:09 | 0 | 0 | 0 | 1900-01-01 14:02 | N-839 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=787kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2018-04-14 06:58 | 2018-04-15 19:54 | 0 | 0 | 0 | 1899-12-31 12:56 | N-1512 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2018-04-16 08:37 | 2018-04-22 18:01 | 0 | 0 | 0 | 1900-01-05 09:24 | N-1639 | LCSD | S/D availed for completion of balance stringing and final shifting of line to new section for completion of diversion for DFCC.
NR176507 | 765KV AGRA-FATEHPUR-II | 2018-04-24 06:58 | 2018-04-24 10:47 | 0 | 0 | 0 | 0.15903 | N-2439 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
NR176507 | 765KV AGRA-FATEHPUR-II | 2018-04-25 12:47 | 2018-04-30 10:25 | 0 | 0 | 0 | 1900-01-03 21:38 | N-2597 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=781kV
NR376507 | 765KV ALIGARH-GR.NOIDA | 2018-04-20 00:39 | 2018-04-20 05:36 | 0.20625 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
#N/A | 765KV ALIGARH-JHATIKRA-I | 2018-04-06 16:54 | 2018-04-06 21:26 | 0 | 0 | 0.18889 | 0 | **** | LNCC | Tripped due to B-N fault during heavy thunderstorm. FD: Aligarh-96.7km, Jhatikara-54km. FC: Aligarh-6.4KA, Jhatikara-11.2KA. Fault in NR-1 jurisdiction.
#N/A | 765KV ALIGARH-JHATIKRA-I | 2018-04-20 00:39 | 2018-04-20 05:07 | 0.18611 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
#N/A | 765KV KANPUR(GIS)-ALIGARH-I | 2018-04-20 00:39 | 2018-04-20 04:49 | 0.17361 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
#N/A | 765KV KANPUR(GIS)-ALIGARH-I | 2018-04-22 13:17 | 2018-04-22 14:15 | 0.040278 | 0 | 0 | 0 | **** | OMST | Tripped only from Kanpur end due to DT received
#N/A | 765KV ORAI-ALIGARH-I | 2018-04-15 18:00 | 2018-04-15 19:52 | 0.077778 | 0 | 0 | 0 | **** | SICT | Tripped due to DT received at Aligarh end caused by operation of PRD of its B-Phase line reactor at Orai end.Line charged without line reactor at Orai.
#N/A | 765KV ORAI-ALIGARH-I | 2018-04-17 21:44 | 2018-04-17 22:05 | 0.014583 | 0 | 0 | 0 | N-1829 | OSPT | S/D taken for taking its L/R at Orai end into service
#N/A | 765KV ORAI-ALIGARH-I | 2018-04-20 00:39 | 2018-04-20 06:01 | 0.22361 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
#N/A | 765KV ORAI-ALIGARH-II | 2018-04-06 16:54 | 2018-04-06 17:07 | 0 | 0 | 0.0090278 | 0 | **** | LNCC | Tripped due to B-N fault during heavy thunderstorm. FD: Orai-247.79km, FC: Orai-1.3KA
#N/A | 765KV ORAI-ALIGARH-II | 2018-04-16 19:31 | 2018-04-16 22:08 | 0.10903 | 0 | 0 | 0 | **** | SICT | Tripped due to DT received at Aligarh end caused by operation of PRD of its Y-Phase line reactor at Orai end.Line charged without line reactor at Orai.
#N/A | 765KV ORAI-ALIGARH-II | 2018-04-20 00:39 | 2018-04-24 20:45 | 1900-01-03 20:06 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
#N/A | 765KV ORAI-ALIGARH-II | 2018-04-18 21:11 | 2018-04-18 21:32 | 0.014583 | 0 | 0 | 0 | N-1947 | OSPT | S/D taken for taking its L/R at Orai end into service
NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 2018-04-11 07:43 | 2018-04-11 15:47 | 0 | 0 | 0 | 0.33611 | N-1107 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=812kV
NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2018-04-06 19:42 | 2018-04-07 13:31 | 0 | 0.74236 | 0 | 0 | **** | OMSU | Tripped due to R-phase Pantograph isolator broken at Agra (UP). Fault in UPPCL jurisdiction.
NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2018-04-07 13:31 | 2018-04-08 22:53 | 0 | 0 | 0 | 1899-12-31 09:22 | N-632 | OSFD | Emergency S/D availed by UPPCL for attending R-phase broken Pantograph isolator at Agra (UP).
NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2018-04-11 19:18 | 2018-04-28 04:31 | 0 | 0 | 1900-01-15 09:13 | 0 | **** | LNCC | Tripped due to heavy storm on B-N fault, F.D.= 13KM from Agra(UP), F.C.= 5.07KAMP at fatehabad, The fault was in Agra juridiction. Tower No 36B ,36C, 36D, 37 are damaged.
NR140002 | 400KV AGRA-AGRA(UP)-II | 2018-04-11 19:18 | 2018-04-28 04:29 | 0 | 0 | 1900-01-15 09:11 | 0 | **** | LNCC | Tripped due to Heavy storm on B-N fault, F.D.= 14KM from Agra, F.C.= 13KAMP.Fault in Agra jurisdiction. Tower No 36B, 36C, 36D ,37 are damaged.
NR140003 | 400KV AGRA-AURAIYA-I | 2018-04-12 11:44 | 2018-04-12 13:31 | 0.074306 | 0 | 0 | 0 | **** | OSFT | Emergency Hand tripped due to hot spot in R-phase isolator of L/R at Agra.
NR140003 | 400KV AGRA-AURAIYA-I | 2018-04-18 13:35 | 2018-04-19 23:35 | 0 | 0 | 0 | 1899-12-31 10:00 | N-1896 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140003 | 400KV AGRA-AURAIYA-I | 2018-04-21 13:35 | 2018-04-23 09:57 | 0 | 0 | 0 | 1899-12-31 20:22 | N-2220 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432kV
NR140003 | 400KV AGRA-AURAIYA-I | 2018-04-26 06:13 | 2018-05-01 | 0 | 0 | 0 | 1900-01-03 17:47 | N-2668 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=435kV
NR140004 | 400KV AGRA-AURAIYA-II | 2018-04-06 22:08 | 2018-04-10 10:44 | 0 | 0 | 0 | 1900-01-02 12:36 | N-552 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140004 | 400KV AGRA-AURAIYA-II | 2018-04-10 10:44 | 2018-04-16 20:11 | 0 | 0 | 0 | 1900-01-05 09:27 | N-1007 | LCSD | S/D availed for Retrofittment & SCADA integration work at HVDC Agra
NR140005 | 400KV AGRA-BASSI-I | 2018-04-25 13:34 | 2018-04-25 18:33 | 0.20764 | 0 | 0 | 0 | N-2638 | LEFT | Tripped on B-N fault, F.D.= 172.7KM from Agra end and 20.56kM from BASSI end, F.C.= 2.19KAMP at Agra and 11.03kAmp at Bassi end. The fault was in NR-1 juridiction.
NR140008 | 400KV AGRA-BHIWADI-I | 2018-04-13 07:51 | 2018-04-13 11:05 | 0 | 0 | 0 | 0.13472 | N-1412 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR140008 | 400KV AGRA-BHIWADI-I | 2018-04-24 13:05 | 2018-04-28 17:02 | 0 | 0 | 0 | 1900-01-03 03:57 | N-2488 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140008 | 400KV AGRA-BHIWADI-I | 2018-04-30 03:13 | 2018-04-30 10:47 | 0 | 0 | 0 | 0.31528 | N-2289 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR140009 | 400KV AGRA-BHIWADI-II | 2018-04-01 | 2018-04-07 15:51 | 0 | 0 | 0 | 1900-01-05 15:51 | N-2553 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140009 | 400KV AGRA-BHIWADI-II | 2018-04-08 09:07 | 2018-04-12 08:50 | 0 | 0 | 0 | 1900-01-02 23:43 | N-733 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140009 | 400KV AGRA-BHIWADI-II | 2018-04-14 06:50 | 2018-04-20 18:10 | 0 | 0 | 0 | 1900-01-05 11:20 | N-1511 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR140009 | 400KV AGRA-BHIWADI-II | 2018-04-21 13:32 | 2018-04-21 17:04 | 0 | 0 | 0 | 0.14722 | N-2219 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR140009 | 400KV AGRA-BHIWADI-II | 2018-04-22 10:06 | 2018-04-22 23:42 | 0 | 0 | 0 | 0.56667 | N-2287 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
NR340006 | 400KV AGRA-FATEHABD(UP)-I | 2018-04-11 19:19 | 2018-04-11 20:39 | 0 | 0 | 0.055556 | 0 | **** | LNCC | Tripped due to B-N fault, F.D.= 30KM from Agra, F.C.= 16KAMP, The fault was in UPPTCL juridiction.
NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 2018-04-08 00:25 | 2018-04-08 01:44 | 0 | 0.054861 | 0 | 0 | **** | OMSU | Tripped due to heavy thunder storm and rain and black out of Meza S/s due to tripping of all asociated feeder at Meza S/S.
NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 2018-04-09 15:18 | 2018-04-09 17:39 | 0 | 0 | 0 | 0.097917 | N-909 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. ALLD=430kV
NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 2018-04-12 05:13 | 2018-04-16 15:07 | 0 | 0 | 0 | 1900-01-03 09:54 | N-1270 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=432kV
NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 2018-04-18 13:01 | 2018-05-01 | 0 | 0 | 0 | 1900-01-11 10:59 | N-1887 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=426kV
NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 2018-04-08 00:25 | 2018-04-08 03:49 | 0 | 0.14167 | 0 | 0 | **** | OMSU | Tripped due to heavy thunder storm and rain and black out of Meza S/s due to tripping of all asociated feeder at Meza S/S.
NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 2018-04-16 13:49 | 2018-04-18 10:33 | 0 | 1899-12-31 20:44 | 0 | 0 | **** | OMSU | Tripped due to DT received at Allahabad end caused by problem at Meja(NTPC) end.
NR140122 | 400KV ALLD-FATEHPUR-I | 2018-04-09 14:44 | 2018-04-10 13:26 | 0 | 0 | 0 | 0.94583 | N-905 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. ALLD=430kV
NR140122 | 400KV ALLD-FATEHPUR-I | 2018-04-12 04:42 | 2018-04-12 23:18 | 0 | 0 | 0 | 0.775 | N-1270 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=432kV
NR140104 | 400KV ALLD-FATEHPUR-III | 2018-04-14 14:16 | 2018-04-14 14:39 | 0.015972 | 0 | 0 | 0 | N-1544 | OMST | Taken under emergency S/D for isolating lockout breaker no 404(main bay of FTP-3) at Allahabad
NR140023 | 400KV BAREILLY-BRLY(UP)-I | 2018-04-05 22:39 | 2018-04-05 23:12 | 0 | 0.022917 | 0 | 0 | **** | SBBU | Tripped due to bus fault at Bareilly(UP) end.
NR140023 | 400KV BAREILLY-BRLY(UP)-I | 2018-04-08 10:51 | 2018-04-08 12:33 | 0 | 0.070833 | 0 | 0 | **** | SBBU | Bus bar protection operated at Bareilly(UP) end.
NR140024 | 400KV BAREILLY-BRLY(UP)-II | 2018-04-05 22:39 | 2018-04-05 23:33 | 0 | 0.0375 | 0 | 0 | **** | SBBU | Tripped due to bus fault at Bareilly(UP) end.
NR140024 | 400KV BAREILLY-BRLY(UP)-II | 2018-04-08 10:51 | 2018-04-08 12:59 | 0 | 0.088889 | 0 | 0 | **** | SBBU | Bus bar protection operated at Bareilly(UP) end.
NR140025 | 400KV BAREILLY-LKO(UP) | 2018-04-17 12:58 | 2018-04-17 13:46 | 0 | 0.033333 | 0 | 0 | **** | OMSU | Tripped due to R-N fault,F.D.=279km from Bareily,F.C.=1.83KA(UPPCL Jurisdiction)
NR140025 | 400KV BAREILLY-LKO(UP) | 2018-04-17 13:49 | 2018-04-17 23:13 | 0 | 0.39167 | 0 | 0 | **** | OMSU | Tripped due to R-N fault,F.D.=279km from Bareily,F.C.=1.839KA(UPPCL Jurisdiction)
NR140026 | 400KV BAREILLY-MBAD-I | 2018-04-16 11:39 | 2018-04-16 13:40 | 0.084028 | 0 | 0 | 0 | N-1669 | OSPT | S/D availed for attending hot spot in line isolator at Moradabad(UP) end.
NR140026 | 400KV BAREILLY-MBAD-I | 2018-04-21 10:24 | 2018-04-21 13:01 | 0 | 0 | 0 | 0.10903 | N-2178 | OSFD | Emergency S/D availed by UPPCL to attend sparking in Y Ph wave trap at their end.
NR140159 | 400KV BARLY(765)-KASHIPUR-II | 2018-04-17 13:43 | 2018-04-17 18:13 | 0.1875 | 0 | 0 | 0 |  | LEFT | Tripped due to B-N fault,F.D.=12.33km from Bareily,F.C.=14.03KA(Bareily Jurisdiction)
NR140159 | 400KV BARLY(765)-KASHIPUR-II | 2018-04-18 12:09 | 2018-04-18 15:58 | 0.15903 | 0 | 0 | 0 |  | LEFT | Tripped due to B-N fault,F.D.=27.75km from Bareily,F.C.=9.025KA(Bareily Jurisdiction)
#N/A | 400KV BARLY-KASHIPUR-II | 2018-04-25 13:09 | 2018-04-25 13:28 | 0.013194 | 0 | 0 | 0 | N-2601 | LEFT | Tripped on B-N fault, F.D.= 19.51KM from BRLY end, F.C.= 11.03KAMP at BRLY end, The fault was in BRLY TL juridiction.
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-01 07:23 | 2018-04-02 09:50 | 0 | 0 | 0 | 1899-12-31 02:27 | N-12 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-06 17:54 | 2018-04-08 09:44 | 0 | 0 | 0 | 1899-12-31 15:50 | N-511 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-09 07:18 | 2018-04-10 20:58 | 0 | 0 | 0 | 1899-12-31 13:40 | N-837 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-11 06:39 | 2018-04-11 15:22 | 0.36319 | 0 | 0 | 0 | **** | LEFT | Tripped on B-N fault. Maninpuri=171.4kM(Tripped) and 169.9kM(A/R), 2.55kA(A/R) and 2.32kA(tripped). Fault in NR-1 jurisdiction.
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-12 03:37 | 2018-04-17 11:21 | 0 | 0 | 0 | 1900-01-04 07:44 | N-1267 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-18 13:16 | 2018-04-19 08:44 | 0 | 0 | 0 | 0.81111 | N-1896 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-20 12:55 | 2018-04-20 18:28 | 0 | 0 | 0 | 0.23125 | N-2085 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-22 13:12 | 2018-04-22 21:44 | 0 | 0 | 0 | 0.35556 | N-2299 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri-430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-24 07:10 | 2018-04-24 10:54 | 0 | 0 | 0 | 0.15556 | N-2441 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNPR=430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-28 07:03 | 2018-04-28 16:43 | 0 | 0 | 0 | 0.40278 | N-2842 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140037 | 400KV BLBGRH-MAINPURI-I | 2018-04-29 17:51 | 2018-05-01 00:58 | 0 | 0 | 0 | 1899-12-31 07:07 | N-2958 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2018-04-06 17:54 | 2018-04-08 19:13 | 0 | 0 | 0 | 1900-01-01 01:19 | N-511 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2018-04-09 07:19 | 2018-04-10 20:46 | 0 | 0 | 0 | 1899-12-31 13:27 | N-837 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140124 | 400KV FATEHPUR-MAINPURI-I | 2018-04-20 12:55 | 2018-04-20 18:27 | 0 | 0 | 0 | 0.23056 | N-2085 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-01 07:20 | 2018-04-02 09:54 | 0 | 0 | 0 | 1899-12-31 02:34 | N-12 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=430kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-11 07:12 | 2018-04-11 19:56 | 0 | 0 | 0 | 0.53056 | N-1105 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-11 21:35 | 2018-04-17 11:12 | 0 | 0 | 0 | 1900-01-04 13:37 | N-1243 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=431kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-18 13:24 | 2018-04-19 08:43 | 0 | 0 | 0 | 0.80486 | N-1896 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-22 13:12 | 2018-04-22 21:14 | 0 | 0 | 0 | 0.33472 | N-2299 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri-430kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-24 07:09 | 2018-04-24 10:53 | 0 | 0 | 0 | 0.15556 | N-2441 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNPR=430kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-28 07:02 | 2018-04-28 16:21 | 0 | 0 | 0 | 0.38819 | N-2842 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140125 | 400KV FATEHPUR-MAINPURI-II | 2018-04-29 17:51 | 2018-05-01 00:45 | 0 | 0 | 0 | 1899-12-31 06:54 | N-2958 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=422kV
NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 2018-04-18 10:00 | 2018-04-18 17:46 | 0.32361 | 0 | 0 | 0 | N-1864 | OSPT | S/D availed for AMP work
NR140052 | 400KV KNP-AGRA | 2018-04-13 11:10 | 2018-04-13 11:33 | 0.015972 | 0 | 0 | 0 | N-1429 | OMST | Taken under S/D to take L/R into service
NR140053 | 400KV KNP-AURAIYA-I | 2018-04-14 12:40 | 2018-04-14 20:32 | 0.32778 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault. FD: KNP-43.61km, FC: KNP-9.69KA. Fault in Auraiya TL group jurisdiction
NR140055 | 400KV KNP-BLBGARH-I | 2018-04-06 18:25 | 2018-04-06 22:13 | 0 | 0 | 0.15833 | 0 | **** | LNCC | Tripped due to R-N fault during heavy thunderstorm. FD: KNP-356.1km, FC: KNP-1.34KA. Fault in NR-1 jurisdiction.
NR140055 | 400KV KNP-BLBGARH-I | 2018-04-13 02:30 | 2018-04-13 02:30 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on B-N fault. F.D.=147KM from Kanpur & 247.4KM from Ballabhgarh. F.C.= 2.8KAmp at Kanpur & 1.9KAmp at Ballabhgarh, The fault was in Mainpuri juridiction.
NR140055 | 400KV KNP-BLBGARH-I | 2018-04-15 07:16 | 2018-04-24 20:29 | 0 | 0 | 0 | 1900-01-08 13:13 | N-1584 | LCSD | S/D availed by NR-1 for diversion of line due to newly constructed eastern periphery road of NHAI.
NR140055 | 400KV KNP-BLBGARH-I | 2018-04-25 11:40 | 2018-04-25 11:40 | 0 | 0 | 0 | 0 | **** | LART | A/R on B-N fault, F.D.= 226KM from KNP and 139kM from BLB end, F.C.= 1.6KAMP at KNP and 2.4kAmp at BLB end, The fault was in Mainpuri juridiction.
NR140055 | 400KV KNP-BLBGARH-I | 2018-04-25 12:41 | 2018-04-25 16:57 | 0.17778 | 0 | 0 | 0 | N-2617 | LEFT | Tripped on B-N fault, F.D.= 33.5KM from KNP and 324kM from BLB end, F.C.= 9.26KAMP at KNP and 1.3kAmp at BLB end, The fault was in Kanpur TL juridiction.
NR140057 | 400KV KNP-BLBGARH-III | 2018-04-28 07:24 | 2018-04-30 07:56 | 0 | 0 | 0 | 1900-01-01 00:32 | N-2842 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=418kV
NR140072 | 400KV LUCKNOW-LKO(UP) | 2018-04-03 12:16 | 2018-04-03 12:44 | 0 | 0.019444 | 0 | 0 | **** | OMSU | Tripped due to Y-N fault. F.D.= 63.6KM from Lucknow(PG), F.C.= 3.193KAmp at Lucknow(PG). The fault was in UPPCL juridiction
NR140072 | 400KV LUCKNOW-LKO(UP) | 2018-04-06 15:01 | 2018-04-06 17:40 | 0 | 0 | 0 | 0.11042 | N-486 | OSFD | Emergency S/D availed by UPPCL for atteding hot spot on jumper at loc no 371B
#N/A | 400KV LUCKNOW-SHAHJHNPR-I | 2018-04-29 22:40 | 2018-04-29 23:31 | 0 | 0 | 0.035417 | 0 | **** | LNCC | Tripped on Y-B fault due to heavy thunderstorm. FD: Shahajahapur-169.7km. FC: Shahajahapur-Y-2.2KA, B-2.3KA. Fault in Lucknow jurisdiction
NR140121 | 400KV LUCKNOW-SOHAWAL-II | 2018-04-06 09:59 | 2018-04-06 16:48 | 0.28403 | 0 | 0 | 0 | N-462 | OSPT | S/D taken for replacement of B Ph CVT due to drift in CVT secondary voltage more than 4 volts as compared to other phases
NR140073 | 400KV LUCKNOW-SULTANPR | 2018-04-02 16:37 | 2018-04-02 17:36 | 0 | 0.040972 | 0 | 0 | **** | OMSU | Tripped only from UPPCL sultanpur end due to problem at their end
NR140073 | 400KV LUCKNOW-SULTANPR | 2018-04-05 09:05 | 2018-04-05 10:54 | 0.075694 | 0 | 0 | 0 | **** | LPPT | Tripped due to Y-B fault. FD: LKO- 18.2km, FC: LKO- Y-17.39KA, B-17.40KA.
NR140073 | 400KV LUCKNOW-SULTANPR | 2018-04-05 11:22 | 2018-04-05 16:36 | 0 | 0 | 0 | 0.21806 | N-351 | OSFD | Emergency S/D availed by UPPCL for testing work at their end.
NR140073 | 400KV LUCKNOW-SULTANPR | 2018-04-23 11:53 | 2018-04-23 17:36 | 0 | 0 | 0 | 0.23819 | N-2384 | OSFD | Emergency S/D availed by UPPCL to attend heavy leakage of oil from R phase CT and hot point on Bus side CT clamp of Rphase CT at Sultanpur end(UPPCl end).
NR140075 | 400KV LUCKNOW-UNNAO-II | 2018-04-01 14:43 | 2018-04-01 15:16 | 0.022917 | 0 | 0 | 0 | **** | LPPT | Tripped due to R-Y ph fault,F.D.=26.64km from Lucknow,F.C.-Ir=12.71KA,Iy=12.72KA,F.D.=37.9km from Unnao(Lucknow jurisdiction)
NR140091 | 400KV SING-ALLD-I | 2018-04-19 14:52 | 2018-04-19 15:27 | 0 | 0.024306 | 0 | 0 | **** | OMSU | Tripped only from Singrauli (NTPC) end on Y-N fault, F.D.= 22.4KM from Allahabad, F.C.= 12.1KAmp at Allahabad
NR140095 | 400KV SING-LKO(UP)-I | 2018-04-11 05:47 | 2018-04-11 07:01 | 0.051389 | 0 | 0 | 0 | **** | LEFT | Tripped on R-N fault. FD:142.6kM from Lucknow(UP) FC:2.39kA at Lucknow(UP). Fault in Allahabad jurisdiction.
NR140095 | 400KV SING-LKO(UP)-I | 2018-04-27 08:57 | 2018-05-01 | 0 | 0 | 0 | 1900-01-02 15:03 | N-2772 | LCSD | Diverson of Line for MUNPL ( Meza Urza Nigam Ltd.) at Allahabad of existing Singarauli-Lucknow line on account of Railway siding construction work.
NR140096 | 400KV SING-RIHAND-I | 2018-04-21 08:25 | 2018-04-21 09:23 | 0 | 0.040278 | 0 | 0 | **** | OMSU | Tripped due to CT blast of 400KV Rihand-Rihand-1 at Rihand(NTPC)
NR140097 | 400KV SING-RIHAND-II | 2018-04-21 08:25 | 2018-04-21 12:44 | 0 | 0.17986 | 0 | 0 | **** | OMSU | Tripped due to CT blast of 400KV Rihand-Rihand-1 at Rihand(NTPC)
NR340005 | 400KV VARANASI-SARNATH-II | 2018-04-04 08:01 | 2018-04-05 22:59 | 0 | 0 | 0 | 1899-12-31 14:58 | N-223 | OSPD | S/D taken by UPPTCL for AMP & replacement of old and outlived CTs , LA and CVTs at Sarnath end.
NR340005 | 400KV VARANASI-SARNATH-II | 2018-04-24 08:34 | 2018-04-24 11:02 | 0 | 0 | 0 | 0.10278 | N-2453 | OSFD | Emergency S/D availed by UPPCL for attending oil leakage in R-phase line CT at their end.
BILUP2202 | 220KV ALLD-REWA RD-I | 2018-04-03 11:52 | 2018-04-03 15:36 | 0 | 0 | 0 | 0.15556 | N-170 | OSFD | S/D taken by UPPCL to attend hot spot at their end
#N/A | 220kV AURAIYA-SIKANDARA-I | 2018-04-25 10:01 | 2018-04-25 18:02 | 0.33403 | 0 | 0 | 0 | N-2590 | OMST | S/D/ availed by Powergrid for testing work
NR122012 | 220KV DGANGA-BLY(UP)-II | 2018-04-06 22:46 | 2018-04-06 23:27 | 0 | 0 | 0.028472 | 0 | **** | GOVC | Tripped due to over voltage at Dhauliganga
NR122012 | 220KV DGANGA-BLY(UP)-II | 2018-04-11 05:27 | 2018-04-11 17:35 | 0 | 0 | 0.50556 | 0 | **** | GOVC | Tripped on Over voltage protection.
NR122012 | 220KV DGANGA-BLY(UP)-II | 2018-04-12 17:33 | 2018-04-12 17:57 | 0 | 0 | 0.016667 | 0 | **** | GOVC | Tripped on Over voltage protection.
NR122012 | 220KV DGANGA-BLY(UP)-II | 2018-04-26 10:26 | 2018-04-26 17:44 | 0 | 0 | 0 | 0.30417 | N-2692 | OSPD | S/D availed by NHPC for testing of protection Relay at their end.
NR122012 | 220KV DGANGA-BLY(UP)-II | 2018-04-27 10:25 | 2018-04-27 17:27 | 0 | 0 | 0 | 0.29306 | N-2787 | OSPD | S/D availed by Dhauliganga (NHPC) for maintenance & relay work
NR122012 | 220KV DGANGA-BLY(UP)-II | 2018-04-29 11:35 | 2018-04-29 17:34 | 0 | 0 | 0 | 0.24931 | N-2941 | OSPD | S/D availed by NHPC for testing work at their end
NR122012 | 220KV DGANGA-BLY(UP)-II | 2018-04-30 11:58 | 2018-04-30 17:35 | 0 | 0 | 0 | 0.23403 | N-3027 | OSPD | S/D availed by NHPC for testing work at their end
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-06 22:49 | 2018-04-07 10:53 | 0 | 0 | 0.50278 | 0 | **** | GOVC | Tripped due to over voltage at Dhauliganga
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-08 14:04 | 2018-04-08 18:23 | 0 | 0 | 0.17986 | 0 | **** | GOVC | Tripped due to over voltage at Dhauliganga and DT received at Pithoragarh end.
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-09 14:31 | 2018-04-09 18:19 | 0 | 0 | 0.15833 | 0 | **** | GOVC | Tripped due to over voltage at Dhauliganga and DT received at Pithoragarh end.
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-11 05:27 | 2018-04-11 18:12 | 0 | 0 | 0.53125 | 0 | **** | GOVC | Tripped on Over voltage protection.
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-12 17:33 | 2018-04-12 17:54 | 0 | 0 | 0.014583 | 0 | **** | GOVC | Tripped on Over voltage protection.
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-15 13:26 | 2018-04-15 16:57 | 0 | 0 | 0 | 0.14653 | N-1602 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Pithoragarh=236kV.
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-22 12:55 | 2018-04-22 17:11 | 0 | 0 | 0 | 0.17778 | N-2295 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. D'Ganga=239kV
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-24 10:03 | 2018-04-24 16:59 | 0 | 0 | 0 | 0.28889 | N-2462 | OSPD | S/D availed by NHPC for testing of protection Relay at their end.
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-25 10:09 | 2018-04-25 17:18 | 0 | 0 | 0 | 0.29792 | N-2576 | OSPD | S/D availed by NHPC for testing of protection Relay at their end.
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-29 11:20 | 2018-04-29 17:37 | 0 | 0 | 0 | 0.26181 | N-2941 | OSPD | S/D availed by NHPC for testing work at their end
NR122013 | 220KV DGANGA-PITHORAGRH | 2018-04-30 11:50 | 2018-04-30 17:35 | 0 | 0 | 0 | 0.23958 | N-3027 | OSPD | S/D availed by NHPC for testing work at their end
NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 2018-04-04 16:08 | 2018-04-04 17:14 | 0 | 0.045833 | 0 | 0 | **** | OMSU | Tripped due to Bus fault at Fatehpur (UP) end.
NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 2018-04-04 16:08 | 2018-04-04 17:15 | 0 | 0.046528 | 0 | 0 | **** | OMSU | Tripped due to Bus fault at Fatehpur (UP) end.
NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 2018-04-05 08:20 | 2018-04-05 13:09 | 0 | 0 | 0 | 0.20069 | N-325 | OSFD | Emergency S/D availed by UPPCL to attend hot spot /sparking at their end.
NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 2018-04-08 09:25 | 2018-04-08 14:15 | 0 | 0.20139 | 0 | 0 | **** | OMSU | Tripped on R-Y fault.FD:0.5kM from Fatehpur FC:Iy=15.76kA, Ir=15.4kA. Tripped due to UPPCL working on New 220kV Fatehpur(PG)-Sarh 1&2 line tower and earth wire fallen on 220KV FATEHPUR-FTHPR(UP)-II.
NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 2018-04-12 08:45 | 2018-04-12 18:57 | 0 | 0 | 0 | 0.425 | N-1295 | OSFD | Emergency S/D availed by UPPCL for attending hot spot in Y-phase CT at Fatehpur(UP) end.
NR122040 | 220KV FATEHPUR-KNP SOUTH | 2018-04-10 12:47 | 2018-04-10 18:48 | 0 | 0.25069 | 0 | 0 | **** | OMSU | Tripped due to R-N fault. FD: 54.2kM from Fatehpur. FC:2.97kA at Fatehpur. Fault in UPPCL jurisdiction.
NR122040 | 220KV FATEHPUR-KNP SOUTH | 2018-04-16 12:56 | 2018-04-16 14:55 | 0 | 0.082639 | 0 | 0 | **** | OMSU | Tripped due to R-N fault. FD: 9.5kM from Fatehpur. FC: 6.05kA at Fatehpur. Fault in UPPCL jurisdiction.
NR122040 | 220KV FATEHPUR-KNP SOUTH | 2018-04-28 09:49 | 2018-05-01 | 0 | 0 | 0 | 1900-01-01 14:11 | N-2852 | OSPD | S/D availed by UPPCL for General maintenance --diversion of line (Tower erection & stringing) for DFCC at Sarsaul
NR122041 | 220KV FATEHPUR-NAUBASTA | 2018-04-15 12:09 | 2018-04-15 12:40 | 0 | 0.021528 | 0 | 0 | **** | OMSU | Tripped due to B-N fault. FD: 39.5kM from Fatehpur and 41 kM from Naubasta(UP) end. FC: 3.6kA at Fatehpur. Fault in UPPCL jurisdiction.
NR122041 | 220KV FATEHPUR-NAUBASTA | 2018-04-19 12:43 | 2018-04-19 15:00 | 0 | 0.095139 | 0 | 0 | **** | OMSU | Tripped on B-N fault. F.D.=7.6KM from Fatehpur, F.C.= 2.5KAmp. The fault was in UPPTCL juridiction.
NR122041 | 220KV FATEHPUR-NAUBASTA | 2018-04-26 13:01 | 2018-04-26 16:17 | 0 | 0.13611 | 0 | 0 | **** | OMSU | Tripped due to R-N fault. FD:73kM from Fatehpur. Fault in UPPCL jurisidiction.
NR122041 | 220KV FATEHPUR-NAUBASTA | 2018-04-28 09:44 | 2018-05-01 | 0 | 0 | 0 | 1900-01-01 14:16 | N-2853 | OSPD | S/D availed by UPPCL for General maintenance --diversion of line (Tower erection & stringing) for DFCC at Sarsaul
NR122016 | 220KV KNP-MAINPURI | 2018-04-25 12:41 | 2018-04-25 17:45 | 0 | 0.21111 | 0 | 0 | N-2637 | OMSU | Tripped on B-N fault, F.D.= 71KM from KNP and 116.4kM from MNP end, F.C.= 2.3KAMP at KNP and 11.49kAmp at MNP end, The fault was in UPPCL juridiction.
NR122024 | 220KV PITHORAGRH-BRLY(UP) | 2018-04-11 06:31 | 2018-04-11 06:57 | 0 | 0 | 0 | 0.018056 | N-1096 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Pithoragarh=240kV
NR122024 | 220KV PITHORAGRH-BRLY(UP) | 2018-04-11 17:24 | 2018-04-11 18:50 | 0 | 0 | 0 | 0.059722 | N-1180 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
NR122024 | 220KV PITHORAGRH-BRLY(UP) | 2018-04-13 01:30 | 2018-04-13 08:45 | 0 | 0 | 0 | 0.30208 | N-1403 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Pithoragarh=233KV
NR122025 | 220KV RAIBRLY-CHINHAT | 2018-04-01 | 2018-05-01 | 0 | 0 | 0 | 1900-01-29 | N-2778 | OSPD | S/D availed by UPPCL for LILO work at New 220kV C.G.City S/S.
NR122032 | 220KV SITARGANJ-BLY(UP) | 2018-04-06 17:02 | 2018-04-06 19:50 | 0.11667 | 0 | 0 | 0 | N-488 | OSFT | Emergency S/D availed for atteding hot spot in line isolator at CB Ganj
NR122032 | 220KV SITARGANJ-BLY(UP) | 2018-04-09 11:08 | 2018-04-09 14:16 | 0.13056 | 0 | 0 | 0 |  | LEFT | Tripped due to B-N fault. FD: Sitarganj-56.45km, FC: Sitarganj-1.564KA. Fault in Bareilly TL jurisdiction.
NR122032 | 220KV SITARGANJ-BLY(UP) | 2018-04-17 12:50 | 2018-04-17 13:30 | 0 | 0.027778 | 0 | 0 | **** | OMSU | Tripped only from Bareily(UP) end due to problem at their end
NR122032 | 220KV SITARGANJ-BLY(UP) | 2018-04-18 11:12 | 2018-04-18 14:54 | 0 | 0.15417 | 0 | 0 | **** | OMSU | Tripped due to broken of Y ph jumper at Bareily(UP) end
NR122032 | 220KV SITARGANJ-BLY(UP) | 2018-04-21 10:44 | 2018-04-21 17:49 | 0 | 0 | 0 | 0.29514 | N-2185 | OSFD | Emergency S/D availed by UPPCL to attend highly damaged R & Y Ph jumper at their end.
NR122033 | 220KV TNKPR-BLY(UP) | 2018-04-06 03:11 | 2018-04-06 12:06 | 0 | 0.37153 | 0 | 0 | **** | OMSU | Tripped due to CB problem at Tanakpur end.
NR122033 | 220KV TNKPR-BLY(UP) | 2018-04-18 15:53 | 2018-04-18 17:58 | 0 | 0 | 0 | 0.086806 | N-1906 | OSFD | E/S/D taken by UPPCL for attending heavy sparking in line isolator at Bareily(UP) end
NR122034 | 220KV TNKPR-SITARGANJ | 2018-04-09 12:35 | 2018-04-09 12:46 | 0 | 0 | 0 | 0.0076389 | N-889 | OSFD | Breaker opened at Sitarganj end as requested by Tanakpur as Tanakpur S/S was dead.
NR122034 | 220KV TNKPR-SITARGANJ | 2018-04-18 11:12 | 2018-04-18 13:12 | 0 | 0.083333 | 0 | 0 |  | OMSU | Tripped only from NHPC/Tanakpur end due to problem at their end
NR1ICT705 | 765/400KV ICT-I FATEHPUR | 2018-04-02 12:06 | 2018-04-03 03:42 | 0.65 | 0 | 0 | 0 | N-95 | OSPT | S/D availed for AMP work and neutral jumper modification work
#N/A | 765/400KV ICT-I ORAI | 2018-04-10 11:24 | 2018-04-10 13:53 | 0.10347 | 0 | 0 | 0 | N-1018 | OSFT | Emergency S/D availed to attend leakage on top of tank pipe line of R-phase unit of ICT-1 and mog alarm has appeared.
NR1ICT706 | 765/400KV ICT-II FATEHPUR | 2018-04-04 10:18 | 2018-04-04 22:00 | 0.4875 | 0 | 0 | 0 | N-243 | OSPT | S/D availed for AMP work.
NR1ICT01 | 315MVA ICT-I ALLAHABAD | 2018-04-04 09:14 | 2018-04-04 18:35 | 0.38958 | 0 | 0 | 0 | N-232 | OSPT | S/D availed for AMP work.
NR1ICT23 | 315MVA ICT-I LUCKNOW | 2018-04-30 02:33 | 2018-05-01 | 0.89375 | 0 | 0 | 0 | **** | SICT | Tripped due to buchholz relay operation
NR1ICT02 | 315MVA ICT-II ALLAHABAD | 2018-04-06 09:13 | 2018-04-06 18:10 | 0.37292 | 0 | 0 | 0 | N-454 | OSPT | S/D availed for AMP work.
NR1ICT67 | 315MVA ICT-III ALLAHABAD | 2018-04-05 09:12 | 2018-04-05 19:48 | 0.44167 | 0 | 0 | 0 | N-332 | OSPT | S/D availed for AMP work.
NR1ICT43 | 100MVA ICT-I PITHORAGRH | 2018-04-06 23:06 | 2018-04-06 23:53 | 0 | 0 | 0.032639 | 0 | **** | GOFC | Tripped due to over flux
NR1ICT43 | 100MVA ICT-I PITHORAGRH | 2018-04-07 02:50 | 2018-04-07 06:31 | 0 | 0 | 0.15347 | 0 | **** | GOFC | Tripped due to over flux
NR1ICT43 | 100MVA ICT-I PITHORAGRH | 2018-04-08 14:05 | 2018-04-08 18:28 | 0 | 0 | 0.18264 | 0 | **** | GOFC | Tripped due to over flux relay operated.
NR1ICT43 | 100MVA ICT-I PITHORAGRH | 2018-04-09 10:54 | 2018-04-09 18:05 | 0 | 0 | 0.29931 | 0 | **** | GOFC | Tripped due to over flux relay operated.
NR1ICT43 | 100MVA ICT-I PITHORAGRH | 2018-04-11 05:44 | 2018-04-11 08:24 | 0 | 0 | 0.11111 | 0 | **** | GOFC | Tripped on Over Fluxing protection.
NR1ICT43 | 100MVA ICT-I PITHORAGRH | 2018-04-11 12:06 | 2018-04-11 18:32 | 0 | 0 | 0.26806 | 0 | **** | GOFC | Tripped on Over Fluxing protection.
NR1ICT44 | 100MVA ICT-II PITHORAGRH | 2018-04-06 23:06 | 2018-04-06 23:53 | 0 | 0 | 0.032639 | 0 | **** | GOFC | Tripped due to over flux
NR1ICT44 | 100MVA ICT-II PITHORAGRH | 2018-04-07 02:46 | 2018-04-07 06:46 | 0 | 0 | 0.16667 | 0 | **** | GOFC | Tripped due to over flux
NR1ICT44 | 100MVA ICT-II PITHORAGRH | 2018-04-08 14:04 | 2018-04-08 18:27 | 0 | 0 | 0.18264 | 0 | **** | GOFC | Tripped due to over flux relay operated.
NR1ICT44 | 100MVA ICT-II PITHORAGRH | 2018-04-09 10:51 | 2018-04-09 18:06 | 0 | 0 | 0.30208 | 0 | **** | GOFC | Tripped due to over flux relay operated.
NR1ICT44 | 100MVA ICT-II PITHORAGRH | 2018-04-11 05:44 | 2018-04-11 09:00 | 0 | 0 | 0.13611 | 0 | **** | GOFC | Tripped on Over Fluxing protection.
NR1ICT44 | 100MVA ICT-II PITHORAGRH | 2018-04-11 12:08 | 2018-04-11 18:32 | 0 | 0 | 0.26667 | 0 | **** | GOFC | Tripped on Over Fluxing protection.
#N/A | 330MVAR B/Reactor-I ALIGARH | 2018-04-20 00:39 | 2018-04-20 05:18 | 0.19375 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
#N/A | 330MVAR B/Reactor-II ALIGARH | 2018-04-20 00:39 | 2018-04-20 06:13 | 0.23194 | 0 | 0 | 0 | **** | SEFT | Tripped due to Bus Bar- 1&2 differential protection operated due to GIS fault at Aligarh (GIS) S/S.
NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765 | 2018-04-20 20:26 | 2018-04-22 13:15 | 0 | 0 | 0 | 1899-12-31 16:49 | N-2146 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=734kV
NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 2018-04-18 20:10 | 2018-04-19 13:25 | 0 | 0 | 0 | 0.71875 | N-1943 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=758kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-04-22 19:30 | 2018-04-25 00:42 | 0 | 0 | 0 | 1900-01-01 05:12 | N-2334 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=753kV
NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-04-25 19:19 | 2018-04-30 03:08 | 0 | 0 | 0 | 1900-01-03 07:49 | N-2651 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=754kV
NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 2018-04-20 20:26 | 2018-04-22 13:15 | 0 | 0 | 0 | 1899-12-31 16:49 | N-2146 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=734kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2018-04-19 20:40 | 2018-04-20 06:44 | 0 | 0 | 0 | 0.41944 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2018-04-20 19:21 | 2018-04-21 08:27 | 0 | 0 | 0 | 0.54583 | N-2143 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=398kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2018-04-21 18:42 | 2018-04-22 13:06 | 0 | 0 | 0 | 0.76667 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2018-04-22 19:18 | 2018-04-23 06:11 | 0 | 0 | 0 | 0.45347 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
NR1BRT44 | 2x50MVAR B/Reactor BAREILLY | 2018-04-29 00:43 | 2018-04-29 07:14 | 0 | 0 | 0 | 0.27153 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2018-04-19 20:35 | 2018-04-20 06:43 | 0 | 0 | 0 | 0.42222 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2018-04-20 19:18 | 2018-04-21 08:29 | 0 | 0 | 0 | 0.54931 | N-2143 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=398kV
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2018-04-21 18:42 | 2018-04-22 13:05 | 0 | 0 | 0 | 0.76597 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2018-04-22 19:18 | 2018-04-23 06:10 | 0 | 0 | 0 | 0.45278 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
NR1BRT03 | 80MVAR B/Reactor BAREILLY | 2018-04-29 00:33 | 2018-04-29 07:13 | 0 | 0 | 0 | 0.27778 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=399kV

## Sheet3
400kv LINES |  |  |  | 220kv LINES |  | ICTs,HVDC & SVC. |  | OTHER LINES
400kv LINES NR-I |  | 400kv LINES NR-III |  | 220kv LINES & ICT & Reactor NR-I |  | 220kv LINES & ICT & Reactor NR-III
400KV AGRA-JAIPUR(S)-I | 1 | 400KV AGRA-FATEHABD(UP)-I | 1 | 220KV ANTA-BHIL-I | 1 | 220KV ALLD-JHUSI(UP) | RRVPNL | 220KV BASSI-KUKAS-I
400KV AGRA-JAIPUR(S)-II | 2 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2 | 220KV ANTA-BHIL-II | 2 | 220KV ALLD-REWA RD-I | RRVPNL | 220KV BASSI-KUNDA KI DHANI
400KV AGRA-SIKAR-I | 3 | 400KV AGRA-AGRA(UP)-II | 3 | 220KV ANTA-LALSOT | 3 | 220KV ALLD-REWA RD-II | RRVPNL | 220KV BHIWADI(PG)-BHIWADI
400KV AGRA-SIKAR-II | 4 | 400KV AGRA-AURAIYA-I | 4 | 220KV ANTA-RAPPC | 4 | 220KV AUR-SIKANDARA-I | RRVPNL | 220KV BHIWADI-KHUSHKHERA-I
400KV BASSI-BHIWADI-I | 5 | 400KV AGRA-AURAIYA-II | 5 | 220KV ANTA-S.MDHPR | 5 | 220KV AUR-SIKANDARA-II | RRVPNL | 220KV BHIWADI-KHUSHKHERA-II
400KV BASSI-HIRAPURA-I | 6 | 400KV AGRA-BASSI-I | 6 | 220KV BASSI-BAGRU | 6 | 220KV DGANGA-BLY(UP)-II | RRVPNL | 220KV BHIWADI-NIMRANA(RJ)
400KV BASSI-HIRAPURA-II | 7 | 400KV AGRA-BHIWADI-I | 7 | 220KV BASSI-DAUSA-I | 7 | 220KV DGANGA-PITHORAGRH | RRVPNL | 220KV BHINMAL-BHINMAL-I
400KV BASSI-JAIPUR(S)-I | 8 | 400KV AGRA-BHIWADI-II | 8 | 220KV BASSI-DAUSA-II | 8 | 220KV FATEHPUR-FTHPR(UP)-I | RRVPNL | 220KV BHINMAL-BHINMAL-II
400KV BASSI-JAIPUR(S)-II | 9 | 400KV AGRA-BLBGRH | 9 | 220KV BASSI-IG NAGAR | 9 | 220KV FATEHPUR-FTHPR(UP)-II | RRVPNL | 220KV BHINMAL-SANCHORE
400KV BASSI-KOTPUTLI | 10 | 400KV ALLD-FATEHPUR-I | 10 | 220KV FGPP-PALLA-I | 10 | 220KV FATEHPUR-KNP SOUTH | RRVPNL | 220KV BHINMAL-SIROHI
400KV BASSI-PHAGI-I | 11 | 400KV ALLD-FATEHPUR-II | 11 | 220KV FGPP-PALLA-II | 11 | 220KV FATEHPUR-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-CHAKSU-I |  | LEGENDS
400KV BASSI-PHAGI-II | 12 | 400KV ALLD-FATEHPUR-III | 12 | 220KV FGPP-SPUR-I | 12 | 220KV JHUSI(UP)-PHULPUR(UP) | RRVPNL | 220KV JAIPUR(S)-CHAKSU-II
400KV BHINMAL-ZERDA | 13 | 400KV ALLD-KNP-II | 13 | 220KV FGPP-SPUR-II | 13 | 220KV KNP-MAINPURI | RRVPNL | 220KV JAIPUR(S)-SEZ |  |  | Lines maintained by ER
400KV BHIWADI-GURGAON | 14 | 400KV ALLD-VARANASI | 14 | 220KV HIRAPURA-IG NAGAR | 14 | 220KV KNP-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-DOONI
400KV BHIWADI-HISAR-I | 15 | 400KV BALIA-MAU-I | 15 | 220KV HIRAPURA-SANGANER | 15 | 220 KV KANPUR(PG) - RANIYA( UP)-1 | RRVPNL | 220KV KANKROLI(PG)-BHILWARA
400KV BHIWADI-KOTPUTLI | 16 | 400KV BALIA-MAU-II | 16 | 220KV LALSOT-DAUSA | 16 | 220 KV RANIYA( UP) - PANKI (UP)-1 | RRVPNL | 220KV KANKROLI(PG)-KANK-I
400KV BHIWADI-NIMRANA-I | 17 | 400KV BALIA-SOHAWAL-I | 17 | 220KV MEERUT-MPURAM-I | 17 | 220KV KNP-PANKI-II | RRVPNL | 220KV KANKROLI(PG)-KANK-II
400KV BHIWADI-NIMRANA-II | 18 | 400KV BALIA-SOHAWAL-II | 18 | 220KV MEERUT-MPURAM-II | 18 | 220KV KNP-UNCHR-I | RRVPNL | 220KV KANKROLI-DEBARI |  |  | lines maintained by WR
400KV BLBGRH-GURGAON | 19 | 400KV BAREILLY-BRLY(765)-I | 19 | 220KV MEERUT-NARA | 19 | 220KV KNP-UNCHR-II | RRVPNL | 220KV KOTA-KTPS-1
400KV BLBGRH-MAHRANIBG | 20 | 400KV BAREILLY-BRLY(765)-II | 20 | 220KV MEERUT-SHTBDNGR | 20 | 220KV KNP-UNCHR-III | RRVPNL | 220KV KOTA-KTPS-2 |  |  | LILO portions only of POWERGRID
400KV BLBGRH-NAVADA(HVPN) | 21 | 400KV BAREILLY-BRLY(UP)-I | 21 | 220KV MEERUT-SIMBHOLI | 21 | 220KV KNP-UNCHR-IV | RRVPNL | 220KV KOTA-BHILWARA
400KV DAD-GR.NOIDA | 22 | 400KV BAREILLY-BRLY(UP)-II | 22 | 220KV RAPPB-CHITT-I | 22 | 220KV PITHORAGRH-BRLY(UP) | RRVPNL | 220KV KOTA-DHUNI |  |  | LILO portion maintained by constituents
400KV DAD-MAHRANIBG | 23 | 400KV BAREILLY-LKO(UP) | 23 | 220KV RAPPB-CHITT-II | 23 | 220KV RAIBRLY-CHINHAT | RRVPNL | 220KV KOTPUTLI-KOTPUTLI
400KV DAD-MANDOLA-I | 24 | 400KV BAREILLY-MBAD-I | 24 | 220KV RAPPB-RAPPC | 24 | 220KV RAIBRLY-LKO(UP) | RRVPNL | 220KV KOTPUTLI-MANOHARPUR
400KV DAD-MANDOLA-II | 25 | 400KV BAREILLY-MBAD-II | 25 | 220KV RAPPB-UDAIPUR | 25 | 220KV SITARGANJ-BLY(UP) | RRVPNL | 220KV NIMRANA-NIMRANA
400KV DAD-MURADNGR | 26 | 400KV BAREILLY-ROSA-I | 26 | 220KV S.MDHPR-DAUSA-I | 26 | 220KV TNKPR-BLY(UP) | RRVPNL | 220KV NIMRANA-KHUSHKHERA |  |  | Maintained by NR-1 & NR-II
400KV DAD-PANIPAT-I | 27 | 400KV BAREILLY-SHAHJHNPR-I | 27 | 220KV SIKAR-RATANGARH-I | 27 | 220KV TNKPR-SITARGANJ | HVPNL | 220KV BHIWADI-MAU
400KV DAD-PANIPAT-II | 28 | 400KV BAREILLY-SHAHJHNPR-II | 28 | 220KV SIKAR-RATANGARH-II | 28 | 220KV UNCHR-RAIBRLY-I | HVPNL | 220KV BHIWADI-REWARI-I
400KV GURGAON-MANESAR-I | 29 | 400KV BARLY(765)-KASHIPUR-I | 29 | 220KV SIKAR-SIKAR(RJ)-I | 29 | 220KV UNCHR-RAIBRLY-II | HVPNL | 220KV BHIWADI-REWARI-II
400KV GURGAON-MANESAR-II | 30 | 400KV BARLY(765)-KASHIPUR-II | 30 | 220KV SIKAR-SIKAR(RJ)-II | 30 | 220KV UNCHR-RAIBRLY-III | HVPNL | 220KV BHIWADI-BAWAL
400KV JHATIKALA-BAMNOLI-I | 31 | 400KV BLBGRH-MAINPURI-I | 31 | 220KV HISAR-HISAR I/A-I |  |  | HVPNL | 220KV GURGAON-GURGAON-I
400KV JHATIKALA-BAMNOLI-II | 32 | 400KV BLBGRH-MAINPURI-II | 32 | 220KV HISAR-HISAR I/A-II |  |  | HVPNL | 220KV GURGAON-GURGAON-II
400KV JHATIKALA-MUNDKA-I | 33 | 400KV FATEHPUR-MAINPURI-I |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-III
400KV JHATIKALA-MUNDKA-II | 34 | 400KV FATEHPUR-MAINPURI-II |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-IV
400KV KANKROLI-BHINMAL | 35 | 400KV GORAKH-GORAKH-I |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-I
400KV KANKROLI-JODHPUR | 36 | 400KV GORAKH-GORAKH-II |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-II
400KV KANKROLI-CHITTOR(RJ)-I | 37 | 400KV KNP-AGRA |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-I
400KV KANKROLI-RAPPC-II | 38 | 400KV KNP-AURAIYA-I |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-II
400KV KANKROLI-ZERDA-I | 39 | 400KV KNP-AURAIYA-II |  | 400KV & 220KV ICT NR-I |  |  | HVPNL | 220 KV MANESAR-BADSHAHPUR-I
400KV KOTA-BEAWAR | 40 | 400KV KNP-BLBGARH-I | 1 | 315MVA ICT-I BASSI |  | 400KV & 220KV ICT NR-III | HVPNL | 220 KV MANESAR-BADSHAHPUR-II
400KV KOTA-MERTA-I | 41 | 400KV KNP-BLBGARH-II | 2 | 315MVA ICT-II BASSI | 1 | 315MVA ICT-I AGRA | HVPNL | 220 KV MANESAR-MAU-I
400KV KOTA-RAPPC | 42 | 400KV KNP-BLBGARH-III | 3 | 500MVA ICT-III BASSI | 2 | 315MVA ICT-I ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-II
400KV KOTESHWR-KHEP-I | 43 | 400KV KNP-FATEHPUR-I | 4 | 315MVA ICT-III BAWANA | 3 | 315MVA ICT-II ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-III
400KV KOTESHWR-KHEP-II | 44 | 400KV KNP-FATEHPUR-II | 5 | 315MVA ICT-I BHINMAL | 4 | 315MVA ICT-III ALLAHABAD | HVPNL | 220 KV SONIPAT-MOHANA-I
400KV KOTESHWR-TEHRI-I | 45 | 400KV KNP-PANKI-I | 6 | 315MVA ICT-II BHINMAL | 5 | 315MVA ICT-I FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-I
400KV KOTESHWR-TEHRI-II | 46 | 400KV KNP-PANKI-II | 7 | 315MVA ICT-I BHIWADI | 6 | 315MVA ICT-II FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-II
400KV MBAD-MURADNGR | 47 | 400KV LUCKNOW-GORAKH-III | 8 | 315MVA ICT-II BHIWADI | 7 | 315MVA ICT-I GORAKHPR | HVPNL | 220KV HISAR-SRWL-I
400KV MEERUT-BAGPAT-I | 48 | 400KV LUCKNOW-GORAKH-IV | 9 | 315MVA ICT-III BHIWADI | 8 | 315MVA ICT-II GORAKHPR | HVPNL | 220KV HISAR-SRWL-II
400KV MEERUT-BAREILLY-I | 49 | 400KV LUCKNOW-LKO(765)-I | 10 | 500MVA ICT-I BLBGARH | 9 | 315MVA ICT-I KANPUR | HVPNL | 220KV HISAR-FATEHABAD-I
400KV MEERUT-BAREILLY-II | 50 | 400KV LUCKNOW-LKO(765)-II | 11 | 315MVA ICT-II BLBGARH | 10 | 315MVA ICT-II KANPUR | HVPNL | 220KV HISAR-FATEHABAD-II
400KV MEERUT-KOTESHWR-I | 51 | 400KV LUCKNOW-LKO(UP) | 12 | 315MVA ICT-III BLBGARH | 11 | 315MVA ICT-I LUCKNOW | NTPC | 132KV SING-VINDH-RIH
400KV MEERUT-KOTESHWR-II | 52 | 400KV LUCKNOW-ROSA-I | 13 | 315MVA ICT-IV BLBGARH | 12 | 500MVA ICT-II LUCKNOW | NTPC | 132KV SING-RENUSAGAR-PIPRI
400KV MEERUT-MND-I | 53 | 400KV LUCKNOW-SHAHJHNPR-I | 14 | 315MVA ICT-I GURGAON | 13 | 315MVA ICT-I MAINPURI | DTL | 400KV B'GARH-BAMNOLI-I
400KV MEERUT-MND-II | 54 | 400KV LUCKNOW-SHAHJHNPR-II | 15 | 315MVA ICT-II GURGAON | 14 | 315MVA ICT-II MAINPURI | DTL | 400KV B'GARH-BAMNOLI-II
400KV MEERUT-MND-III | 55 | 400KV LUCKNOW-SOHAWAL-I | 16 | 500MVA ICT-I JAIPUR(S) | 15 | 100MVA ICT-I PITHORAGRH | DTL | 400KV MND-BAWANA-I
400KV MEERUT-MND-IV | 56 | 400KV LUCKNOW-SOHAWAL-II | 17 | 500MVA ICT-II JAIPUR(S) | 16 | 100MVA ICT-II PITHORAGRH | DTL | 400KV MND-BAWANA-II
400KV MEERUT-MUZFRNGR | 57 | 400KV LUCKNOW-SULTANPR | 18 | 315MVA ICT-I KANKROLI | 17 | 100MVA ICT-I RAIBAREILLY | DTL | 220KV MND-S.WZRBD-I
400KV MERTA-BEAWAR | 58 | 400KV LUCKNOW-UNNAO-I | 19 | 315MVA ICT-II KANKROLI | 18 | 100MVA ICT-II RAIBAREILLY | DTL | 220KV MND-S.WZRBD-II
400KV NAVADA(HVPN)-GR.NOIDA | 59 | 400KV LUCKNOW-UNNAO-II | 20 | 315MVA ICT-III KANKROLI | 19 | 100MVA ICT-III RAIBAREILLY | DTL | 220KV MND-S.WZRBD-III
400KV NIMRANA-MANESAR-I | 60 | 400KV MEERUT-BAREILLY-I | 21 | 315MVA ICT-I KOTA | 20 | 500MVA ICT-I SHAHJHNPR | DTL | 220KV MND-S.WZRBD-IV
400KV NIMRANA-MANESAR-II | 61 | 400KV MEERUT-BAREILLY-II | 22 | 315MVA ICT-II KOTA | 21 | 500MVA ICT-II SHAHJHNPR | DTL | 220KV MND-NARELA-I
400KV NIMRANA-SIKAR-I | 62 | 400KV RIHAND-ALLD-I | 23 | 315MVA ICT-I KOTPUTLI | 22 | 100MVA ICT-I SITARGANJ | DTL | 220KV MND-NARELA-II
400KV NIMRANA-SIKAR-II | 63 | 400KV RIHAND-ALLD-II | 24 | 315MVA ICT-II KOTPUTLI | 23 | 100MVA ICT-II SITARGANJ | DTL | 220KV MND-GOPALPUR-I
400KV ROORKI-KASHIPUR-I | 64 | 400KV RIHAND3-VINDH(Pool)-I | 25 | 315MVA ICT-I MAHRANIBAG | 24 | 315MVA ICT-I SOHAWAL | DTL | 220KV MND-GOPALPUR-II
400KV ROORKI-KASHIPUR-II | 65 | 400KV RIHAND3-VINDH(Pool)-II | 26 | 315MVA ICT-II MAHRANIBAG | 25 | 315MVA ICT-II SOHAWAL | DTL | 220KV MBAG-SARITAVIHAR
400KV ROORKI-MUZFRNGR | 66 | 400KV SING-ALLD-I | 27 | 500MVA ICT-III MAHRANIBAG | 26 |  | DTL | 220KV MBAG-LODHIROAD-I
400KV ROORKI-RISHIKESH | 67 | 400KV SING-ALLD-II | 28 | 500MVA ICT-IV MAHRANIBAG | 27 |  | DTL | 220KV MBAG-LODHIROAD-II
400KV SIKAR-RATANGARH-I | 68 | 400KV SING(NTPC)-ANPARA(UP) | 29 | 500MVA ICT-I MANDOLA | 28 |  | DTL | 220KV MBAG-I P EXTN
400KV SIKAR-RATANGARH-II | 69 | 400KV SING-FATEHPUR | 30 | 500MVA ICT-II MANDOLA | 29 |  | UPPCL | 220KV AGRA-SHAMSABD-I
400KV MEERUT-BAGPAT-II | 70 | 400KV SING-LKO(UP)-I | 31 | 500MVA ICT-III MANDOLA | 30 |  | UPPCL | 220KV AGRA-FEROZABAD
400KV ROORKI-SAHARANPUR-I | 71 | 400KV SING-RIHAND-I | 32 | 500MVA ICT-IV MANDOLA |  |  | UPPCL | 220KV BAGHPAT(PG)-BAGHPAT(UP)
400KV ROORKI-SAHARANPUR-II | 72 | 400KV SING-RIHAND-II | 33 | 500MVA ICT-I MANESAR |  |  | UPPCL | 220KV BAGHPAT-MURADNGR
400KV RAPPC-CHITTOR(RJ)-I | 73 | 400KV SING-VINDH-I | 34 | 500MVA ICT-II MANESAR |  |  | UPPCL | 220KV BAGHPAT-SHAMLI
| 74 | 400KV SING-VINDH-II | 35 | 315MVA ICT-I MEERUT |  |  | UPPCL | 220KV GORAKH-BARHUA
| 75 | 400KV KANPUR-KANPUR(GIS)-I | 36 | 315MVA ICT-II MEERUT |  | 765KV ICT NR-III | UPPCL | 220KV GORAKH-BASTI
| 76 | 400KV KANPUR-KANPUR(GIS)-II | 37 | 315MVA ICT-III MEERUT | 1 | 765/400KV ICT-I BALIA | UPPCL | 220KV LKO(PG)-Bakhsi Ka Talab
| 77 | 400KV VARANASI-SASARAM(ER) | 38 | 500MVA ICT-IV MEERUT | 2 | 765/400KV ICT-II BALIA | UPPCL | 220KV LKO(PG)-CHINHAT
400KV BAHADURGRH-BAWANA | 78 | 400KV VARANASI-SARNATH-I | 39 | 315MVA ICT-III MUZFRNGR | 3 | 765/400KV ICT-I LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-I
400KV BAHADURGRH-SONIPAT-I | 79 | 400KV VARANASI-SARNATH-II | 40 | 315MVA ICT-II NIMRANA | 4 | 765/400KV ICT-II LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-II
400KV BAHADURGRH-SONIPAT-II | 80 | 400KV ALLAHABAD-MEJA(NTPC)-I | 41 | 315MVA ICT-I ROORKI | 5 | 765/400KV ICT-I FATEHPUR | UPPCL | 220KV M'PURI-ETAH
400KV BHIWANI-BAWANA | 81 | 400KV BALIA-BIHARSHRF-I | 42 | 315MVA ICT-II ROORKI | 6 | 765/400KV ICT-II FATEHPUR | UPPCL | 220KV M'PURI-SIRSAGANJ-I
400KV BHIWANI-BHIWANI(BBMB) | 82 | 400KV BALIA-BIHARSHRF-II | 43 | 315MVA ICT-I SIKAR | 7 | 765/400KV ICT-I AGRA | UPPCL | 220KV M'PURI-M'PURI(UP)-II
400KV BHIWANI-HISAR-I | 83 | 400KV ALLD-SASARAM | 44 | 315MVA ICT-II SIKAR | 8 | 765/400KV ICT-II AGRA | UPPCL | 220KV M'PURI-FEROZBD
400KV BHIWANI-HISAR-II | 84 | 400KV BALIA-PATNA-I | 45 | 500MVA ICT-I BAGPAT | 9 | 765/400KV ICT-I BAREILLY | UPPCL | 400KV M'PURI-ORAI-I
400KV BHIWANI-HISAR-III | 85 | 400KV BALIA-PATNA-II | 46 | 500MVA ICT-II BAGPAT | 10 | 765/400KV ICT-II BAREILLY | UPPCL | 400KV M'PURI-PARICHA-II
400KV BHIWANI-JIND-I | 86 | 400KV BALIA-PATNA-III | 47 | 315MVA ICT-I SAHARANPUR | 11 | 765/400KV ICT-I VARANASI | UPPCL | 220KV MEERUT-GAJRAULA
400KV BHIWANI-JIND-II | 87 | 400KV BALIA-PATNA-IV | 48 | 315MVA ICT-II SAHARANPUR | 12 | 765/400KV ICT-II VARANASI | UPPCL | 220KV MEERUT-NEHTAUR
400KV FATEHABAD-HISAR | 88 | 400KV LKO(765)-KANPUR(GIS)-I |  |  | 13 | 765/400KV ICT-I KANPUR(GIS) | UPPCL | 220KV ORAI-KANPUR
400KV BHIWADI-HISAR-II | 89 | 400KV LKO(765)-KANPUR(GIS)-II |  |  | 14 | 765/400KV ICT-II KANPUR(GIS) | UPPCL | 400KV PANKI-MURADNGR
400KV BHIWADI-HISAR-III | [6 empty] | UPPCL | 220KV SHAHJHNP-HARDOI
400KV HISAR-BHIWANI(BBMB) | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-I | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-II |  | 400kv LINES of ER-1 in NR-III Availability |  | NR-I Additional ICT from NR-II |  |  | UPPCL | 220KV SOHAWAL(PG) - SOHAWAL(UP)
400KV KABULPR-BAHADURGRH | 1 | 400KV SASARAM-BIHARSHRF-I | 1 | 315MVA ICT-I BAHADURGARH |  | NR-III HVDC SYSTEM / SVC | UPPCL | 220KV UNCHR-RBRLY-I
400KV KABULPR-BHIWANI | 2 | 400KV SASARAM-BIHARSHRF-II | 2 | 500MVA ICT-II BAHADURGARH | 1 | 500KV HVDC R-D POLE-I | UPPCL | 220KV UNCHR-RBRLY-II
|  |  | 3 | 315MVA ICT-I HISAR | 2 | 500KV HVDC R-D POLE-II | PTCUL | 220KV ROORKI-HARDWAR
|  |  | 4 | 315MVA ICT-II HISAR | 3 | 500KV HVDC BALIA-BHWD POLE-I | PTCUL | 220KV ROORKI--RAMNAGAR
|  | 765 KV TRANS LINES NR-III | 5 | 315MVA ICT-III HISAR | 4 | 500KV HVDC BALIA-BHWD POLE-II | PTCUL | 132KV SITARGNJ(PG)-SITARGNJ(PTCUL)
765 KV TRANS LINES NR-I | 1 | 765KV AGRA-FATEHPUR-I | 6 | 315MVA ICT-I SONIPAT | 5 | 800KV HVDC AGRA-BNC POLE-I | PTCUL | 132KV PITHORAGRH-CHANDOK
765KV AGRA-JHATIKALA | 2 | 765KV AGRA-FATEHPUR-II | 7 | 315MVA ICT-II SONIPAT | 6 | 800KV HVDC AGRA-BNC POLE-II | PTCUL | 132KV PITHORAGRH-ALMORA
765KV BHIWANI-PHAGI(JPR)-I | 3 | 765KV AGRA-GR.NOIDA | 8 | 315MVA ICT-I BHIWANI | 7 | VINDH HVDC B/B BLOCK-I | PTCUL | 132KV PTRGRH-PTRGRH(PTCUL)
765KV MEERUT-GR.NOIDA | 4 | 765KV FATEHPUR-SASARAM | 9 | 315MVA ICT-II BHIWANI | 8 | VINDH HVDC B/B BLOCK-II | POWERLINK
765KV MOGA-BHIWANI | 5 | 765KV LUCKNOW-BALIA | 10 | 500MVA ICT-I JIND | 9 | SASARAM HVDC B/B | PLINK | 400KV LUCKNOW-GORAKH-I (PL)
765KV JHATIKALA-BHIWANI | 6 | 765KV LUCKNOW-BAREILLY | 11 | 500MVA ICT-II JIND | 10 | +/-140MVAR SVC-I KANPUR | PLINK | 400KV LUCKNOW-GORAKH-II (PL)
765KV MEERUT-BHIWANI | 7 | 765KV VARANASI-BALIA |  |  | 11 | +/-140MVAR SVC-II KANPUR | PLINK | 400KV GRKHPR-MZFRPR-I (PL)
765KV BHIWANI-PHAGI(JPR)-II | 8 | 765KV VARANASI-FATEHPUR |  |  |  |  | PLINK | 400KV GRKHPR-MZFRPR-II (PL)
| 9 | 765KV VARANASI-GAYA-I |  | 765KV ICT NR-I
| 10 | 765KV VARANASI-KANPUR(GIS)-I | 1 | 765/400KV ICT-I JHATIKALA
BUS REACTORS NR-I | 11 | 765KV VARANASI-KANPUR(GIS)-II | 2 | 765/400KV ICT-II JHATIKALA |  | SWITCABLE LINE REACTORS NR-III | NR-II | 400KV DAD-M'KOTLA
125MVAR B/Reactor-I BAGPAT | 12 | 765KV KANPUR(GIS)-JHATIKRA-I | 3 | 765/400KV ICT-III JHATIKALA | 1 | AGRA 240MVAR S/R FATEHPR line | NR-II | 400KV BAGHPAT-KAITHAL-I
50MVAR B/Reactor-I BASSI |  |  | 4 | 765/400KV ICT-IV JHATIKALA | 2 | AGRA 50MVAR S/R BHIWADI-I LINE | NR-II | 400KV BAGHPAT-KAITHAL-II
50MVAR B/Reactor-II BASSI |  |  | 5 | 765/400KV ICT-I MEERUT | 3 | ALLHBD 50MVAR S/R MNPR-I LINE | NR-II | 765KV MEERUT-MOGA
50MVAR B/Reactor-III BASSI |  | BUS REACTORS NR-III | 6 | 765/400KV ICT-II MEERUT | 4 | ALLHBD 50MVAR S/R MNPR-II LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-I | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
125MVAR B/Reactor-IV BASSI | 1 | 125MVAR B/Reactor-I AGRA | 7 | 765/400KV ICT-I BHIWANI | 5 | BARLLY 50MVAR S/R MND-I LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-II | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
80MVAR B/Reactor BHINMAL | 2 | 125MVAR B/Reactor-II AGRA | 8 | 765/400KV ICT-II BHIWANI | 6 | BARLLY 50MVAR S/R MND-II LINE | NR-II | 400KV HISAR-MOGA-I
80MVAR B/Reactor BHIWADI | 3 | 240MVAR B/Reactor-II AGRA-765 |  |  | 7 | BALIA 240MVAR S/R LUCKNW Ckt-I | NR-II | 400KV HISAR-MOGA-II
80MVAR B/Reactor BLBGARH | 4 | 240MVAR B/Reactor-1 AGRA-765 |  |  | 8 | BALIA 240MVAR S/R GAYA Line | NR-II | 400KV HISAR-MOGA-III
125MVAR B/Reactor-I JAIPUR(S) | 5 | 80MVAR B/Reactor ALLAHABAD |  |  | 9 | FATEHPR 330MVAR S/R AGRA line
125MVAR B/Reactor-II JAIPUR(S) | 6 | 125MVAR B/Reactor-II ALLAHABAD |  |  | 10 | GORAKH 50MVAR S/R LKO-I LINE
240MVAR B/Reactor-I JHATIKALA-765 | 7 | 80MVAR B/Reactor-I BALIA |  |  | 11 | GORAKH 50MVAR S/R LKO-II LINE
240MVAR B/Reactor-II JHATIKALA-765 | 8 | 125MVAR B/Reactor-II BALIA |  |  | 12 | GORAKH 63MVAR S/R LKO-III LINE
50MVAR B/Reactor KANKROLI | 9 | 125MVAR B/Reactor-III BALIA |  | SWITCABLE LINE REACTORS NR-I | 13 | GORAKH 63MVAR S/R LKO-IV LINE | ER-I | 400KV BALIA-SASARAM
125MVAR B/Reactor-II KANKROLI | 10 | 125MVAR B/Reactor-IV BALIA | 1 | BHINML 50MVAR S/R KANKROLI | 14 | GORAKH 80MVAR S/R Barh-I line | ER-I | 765KV BALIA-GAYA
80MVAR B/Reactor-I KOTA | 11 | 240MVAR B/Reactor-I BALIA-765 | 2 | MEERUT 50MVAR S/R Kotesh-I LINE | 15 | GORAKH 80MVAR S/R Barh-II line | ER-I | 400KV BARH- GRKHPR-I
50MVAR B/Reactor-II KOTA | 12 | 240MVAR B/Reactor-II BALIA-765 | 3 | MEERUT 50MVAR S/R Kotesh-II LINE | 16 | LUCKNW 240MVAR S/R BRLY Line | ER-I | 400KV BARH- GRKHPR-II
80MVAR B/Reactor-I KOTPUTLI | 13 | 80MVAR B/Reactor BAREILLY | 4 | JHATIKALA 240MVAR S/R AGRA Line | 17 | LUCKNW 63MVAR S/R GKP-III LINE | ER-I | 765KV VARANASI-GAYA-II
50MVAR B/Reactor MANDOLA | 14 | 2x50MVAR B/Reactor BAREILLY | 5 | MEERUT 240MVAR S/R AGRA line | 18 | LUCKNW 63MVAR S/R GKP-IV LINE | ER-I | 400KV VARANASI-BIHARSHRF-I
240MVAR B/Reactor-I MEERUT-765 | 15 | 240MVAR B/Reactor-I BAREILLY-765 | 6 | SIKAR 50MVAR S/R AGRA Ckt-I | 19 | LUCKNW 240MVAR S/R BALIA Ckt-I | ER-I | 400KV VARANASI-BIHARSHRF-II
125MVAR B/Reactor MANESAR | 16 | 80MVAR B/Reactor BIHARSHRF | 7 | SIKAR 50MVAR S/R AGRA Ckt-II | 20 | VARANASI 240MVAR S/R KNP(GIS) ckt-1
50MVAR B/Reactor MURADNGR | 17 | 125MVAR B/Reactor-I FATEHPUR | 8 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | 21 | VARANASI 240MVAR S/R KNP(GIS) ckt-2
80MVAR B/Reactor NIMRANA | 18 | 125MVAR B/Reactor-II FATEHPUR | 9 | BHIWANI 240MVAR S/R MEERUT line | 22 | KNP(GIS) 330MVAR S/R JHATIKRA ckt-1 | WR | 765KV AGRA-GWALIOR-I
240MVAR B/Reactor-I PHAGI(JPR)-765 | 19 | 330MVAR B/Reactor-III FTHPR-765 | 10 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line |  |  | WR | 765KV AGRA-GWALIOR-II
125MVAR B/Reactor ROORKEE | 20 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | WR | 765KV GWALIOR-PHAGI-I
125MVAR B/Reactor-I RATANGRH(RJ) | 21 | 125MVAR B/Reactor-II LUCKNOW |  | SVC NR-I |  |  | WR | 765KV GWALIOR-PHAGI-II
80MVAR B/Reactor SIKAR | 22 | 125MVAR B/Reactor-III LUCKNOW | 1 | +400/-300MVAR SVC KANKROLI
50MVAR B/Reactor-I SAHARANPUR | 23 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-I
50MVAR B/Reactor-II SAHARANPUR | 24 | 125MVAR B/Reactor-I VINDH |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-II
125MVAR B/Reactor-II SONIPAT | 25 | 125MVAR B/Reactor-II VINDH
| 26 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - I
BUS REACTORS NR-I From NR2 | 27 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - II
240MVAR B/Reactor-I BHIWANI | 28 | 125MVAR B/Reactor-1 Mainpuri
240MVAR B/Reactor-II BHIWANI | 29 | 125MVAR B/Reactor Gorakhpur-I
50MVAR B/Reactor HISAR | 30 | 125MVAR B/Reactor-II Gorakhpur
125MVAR B/Reactor HISAR | 31 | 125MVAR B/Reactor-I SHAHJHNPR
125MVAR Bus/eactor JIND | 32 | 240MVAR B/Reactor-I KANPUR(GIS)
125MVAR B/Reactor SONIPAT | 33 | 240MVAR B/Reactor-II KANPUR(GIS)
| 34 | 125MVAR B/Reactor-III KANPUR(GIS)
| 35 | 125MVAR B/Reactor-I VARANASI
| 36 | 330MVAR B/Reactor-I VARANASI
| 37 | 330MVAR B/Reactor-II VARANASI
| 38 | 125MVAR B/Reactor KANPUR
Note on E50: a: DOC-01.04.12
Note on I83: 220KV M'PURI-M'PURI(UP)-I LILO at SIRSAGANJ
Note on E84: a: DOC-01.04.12
Note on I86: '400KV M'PURI-PARICHA-I LILO at URI
Note on A96: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on A97: Total-45.6km, PG-26.64km, HVPN-19km.
Note on I98: DELL: 220KV ROORKI-SIDKUL
Note on C108: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C109: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on I112: LILO of 400KV MEERUT-KAITHAL-I at Baghpat
Note on I113: LILO of 400KV MEERUT-KAITHAL-II at Baghpat
Note on I128: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet4
SL.NO. | ELEMENT | Element Name |  | ELEMENT ID | Element name | Total LINE length | 765KV AGRA-JHATIKARA | 253.147
| ID | [5 empty] | 765KV AGRA-Gr Noida | 148.034
|  |  |  | NR176502 | 765KV AGRA-FATEHPUR-I | 8025:36 | 765KV BALLIA-VARANASI | 165.98
A |  | 765 KV TRANS LINES |  | NR176501 | 765KV LUCKNOW-BALIA | 7653:43 | 765KV FATEHPUR-SASARAM | 355.008
1 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR140001 | 400KV AGRA-AGRA(UP)-I | 719:34 | 765KV FATEHPUR-AGRA-1 | 334.52
2 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR140002 | 400KV AGRA-AGRA(UP)-II | 719:34 | 765KV FATEHPUR-AGRA-2 | 334.8
3 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR140003 | 400KV AGRA-AURAIYA-I | 3980:02 | 765KV GAYA-VARANASI-I (OLD FTP-GAYA) | 263.94
4 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR140004 | 400KV AGRA-AURAIYA-II | 0:00 | 765KV GWALIOR-AGRA I | 129.435
5 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR140005 | 400KV AGRA-BASSI-I | 5093:31 | 765KV GWALIOR-AGRA II | 127.934
6 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR140008 | 400KV AGRA-BHIWADI-I | 5023:55 | 765KV KANPUR-JHATIKARA | 465.8
7 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR140009 | 400KV AGRA-BHIWADI-II | 5023:55 | 765KV KANPUR-VARANASI-I | 326.172
8 | NR176513 | 765KV VARANASI-FATEHPUR | 224.963 | NR140010 | 400KV AGRA-BLBGRH | 4347:22 | 765KV KANPUR-VARANASI-II
9 | NR176514 | 765KV VARANASI-GAYA-I | 80.925 | NR140122 | 400KV ALLD-FATEHPUR-I | 3353:31 | 765KV LUCKNOW-BALIA | 318.919
10 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR140123 | 400KV ALLD-FATEHPUR-II | 3353:31 | 765KV LUCKNOW-BAREILLY | 251.613
11 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR140104 | 400KV ALLD-FATEHPUR-III | 3574:19 | 765KV VARANASI-FATEHPUR | 224.963
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR140012 | 400KV ALLD-KNP-II | 5260:24 | 765KV GAYA-VARANASI-II | 80.925
| NR376504 | 765KV ALIGARH-JHATIKARA |  | NR140016 | 400KV ALLD-SASARAM | 4548:43 | 765KV GAYA-BALIA | 238
| NR376505 | 765KV KANPUR(GIS)-ALIGARH | 29.982 | NR140017 | 400KV BALIA-BIHARSHRF-I | 5802:43 | Total 17 765KV Lines | 4019.19
| NR376506 | 765KV AGRA-ALIGARH | 167.2 | NR140018 | 400KV BALIA-BIHARSHRF-II | 5802:43 | AGRA-FATEHABAD(UP)-I | 43.013
| NR376507 | 765KV ALIGARH-GR.NOIDA | 167.2 | NR140019 | 400KV BALIA-MAU-I | 221:10 | FATEHABAD(UP)-AGRA(UP)-I | 57.159
| NR376508 | 765KV ORAI-ALIGARH-II | 212.23 | NR140020 | 400KV BALIA-MAU-II | 221:10 | AGRA-AGRA-(UP)-II | 29.969
| NR376509 | 765KV ORAI-ALIGARH-I | 209.33 | NR140021 | 400KV BALIA-PATNA-I | 4685:34 | AURAIYA-AGRA-I | 167.2
|  |  | 209.33 | NR140022 | 400KV BALIA-PATNA-II | 4685:34 | AURAIYA-AGRA-II
|  |  | 181.14 | NR140136 | 400KV BALIA-PATNA-III | 4440:00 | AGRA-BASSI | 211.433
B |  | 400 KV TRANS LINES | 139.73 | NR140137 | 400KV BALIA-PATNA-IV | 4440:00 | AGRA-BHIWADI-I | 208.98
1 | NR140002 | 400KV AGRA-AGRA(UP)-II | 139.73 | NR140140 | 400KV BALIA-SOHAWAL-I | 5499:55 | AGRA-BHIWADI-II | 209.51
2 | NR140003 | 400KV AGRA-AURAIYA-I | 148.93 | NR140120 | 400KV BALIA-SOHAWAL-II | 5499:55 | AGRA-BLB | 181.137
3 | NR140004 | 400KV AGRA-AURAIYA-II | 219.183 |  | 400KV BLBGRH-MAINPURI-I | 5662:51 | AGRA-JAIPUR(S)-I | 254.41
4 | NR140005 | 400KV AGRA-BASSI-I | 98.791 |  | 400KV BLBGRH-MAINPURI-II | 5662:51 | AGRA-JAIPUR(S)-II
5 | NR140008 | 400KV AGRA-BHIWADI-I | 189.53 | NR140025 | 400KV BAREILLY-LKO(UP) | 6691:12 | AGRA-SIKAR-I | 393.9
6 | NR140009 | 400KV AGRA-BHIWADI-II | 241.78 | NR140026 | 400KV BAREILLY-MBAD-I | 2226:43 | AGRA-SIKAR-II
7 | NR140010 | 400KV AGRA-BLBGRH | 241.78 | NR140027 | 400KV BAREILLY-MBAD-II | 2210:54 | ALLD-FATEHPUR-I | 139.73
8 | NR140122 | 400KV ALLD-FATEHPUR-I | 9.215 |  | 400KV BAREILLY-MEERUT-I | 5899:12 | ALLD-FATEHPUR-II
9 | NR140123 | 400KV ALLD-FATEHPUR-II | 9.215 |  | 400KV BAREILLY-MEERUT-II | 5899:12 | ALLD-FATEHPUR-III | 148.934
10 | NR140104 | 400KV ALLD-FATEHPUR-III | 195.232 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 6241:13 | ALLD-KNP-II | 0
11 | NR140012 | 400KV ALLD-KNP-II | 195.232 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 6241:13 | BALIA-MAU-I | 13
12 | NR140163 | 400KV ALLD-VARANASI | 185 | NR140046 | 400KV GORKH-GORAKH-I | 1102:35 | BALIA-MAU-II
13 | NR140016 | 400KV ALLD-SASARAM | 185 | NR140047 | 400KV GORKH-GORAKH-II | 1102:35 | BALIA-SOHAWAL-I | 229.163
14 | NR140017 | 400KV BALIA-BIHARSHRF-I | 229.163 | NR140052 | 400KV KNP-AGRA | 5760:00 | BALIA-SOHAWAL-II
15 | NR140018 | 400KV BALIA-BIHARSHRF-II | 229.163 | NR140053 | 400KV KNP-AURAIYA-I | 1754:55 | BAREILLY(400)-BAREILLY(765)-I | 1.559
16 | NR140019 | 400KV BALIA-MAU-I | 1.559 | NR140054 | 400KV KNP-AURAIYA-II | 1754:55 | BAREILLY(400)-BAREILLY(765)-II
17 | NR140020 | 400KV BALIA-MAU-II | 1.559 | NR140055 | 400KV KNP-BLBGARH-I | 9256:48 | BAREILLY-BLY(UP)-I | 14.3
18 | NR140021 | 400KV BALIA-PATNA-I | 14.3 | NR140056 | 400KV KNP-BLBGARH-II | 8898:32 | BAREILLY-BLY(UP)-II | 14.3
19 | NR140022 | 400KV BALIA-PATNA-II | 14.3 | NR140057 | 400KV KNP-BLBGARH-III | 8898:32 | BAREILLY-MEERUT-I | 249.52
20 | NR140136 | 400KV BALIA-PATNA-III | 278.8 | NR140110 | 400KV KNP-FATEHPUR-I | 2569:54 | BAREILLY-MEERUT-II | 249.52
21 | NR140137 | 400KV BALIA-PATNA-IV | 92.78 | NR140105 | 400KV KNP-FATEHPUR-II | 2570:24 | LKO(UP)-BAREILLY | 278.76
22 | NR140140 | 400KV BALIA-SOHAWAL-I | 92.121 | NR140058 | 400KV KNP-PANKI-I | 141:36 | BAREILLY-MORADABAD-I | 92.68
23 | NR140120 | 400KV BALIA-SOHAWAL-II | 116.917 | NR140059 | 400KV KNP-PANKI-II | 141:36 | BAREILLY-MORADABAD-II | 92.121
24 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 116.917 | NR140070 | 400KV LUCKNOW-GORAKH-III | 6294:14 | SHAHJAHANPUR-BAREILLY-I | 116.917
25 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 100.659 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 6294:14 | SHAHJAHANPUR-BAREILLY-II | 116.917
26 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 100.659 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 68:41 | B'GARH-M'PURI-I | 235.952
27 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 235.952 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 68:41 | B'GARH-M'PURI-II
28 | NR140025 | 400KV BAREILLY-LKO(UP) | 235.952 | NR140072 | 400KV LUCKNOW-LKO(UP) | 1518:29 | FATEHPUR-MAINPURI-I | 260.051
29 | NR140026 | 400KV BAREILLY-MBAD-I | 260.051 | NR140114 | 400KV LUCKNOW-ROSA-I | 4248:00 | FATEHPUR-MAINPURI-II
30 | NR140027 | 400KV BAREILLY-MBAD-II | 260.051 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 2359:09 | GORAKH-GORAKH-I | 45.941
31 | NR340010 | 400KV BAREILLY-SHAHJHNPR-I | 45.941 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 2359:09 | GORAKH-GORAKH-II
32 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 45.941 | NR140073 | 400KV LUCKNOW-SULTANPR | 3926:24 |  | 240
33 | NR140158 | 400KV BARLY(765)-KASHIPUR-I | 240 | NR140074 | 400KV LUCKNOW-UNNAO-I | 1771:49 | KANPUR-AURAIYA-I | 0
34 | NR140159 | 400KV BARLY(765)-KASHIPUR-II | 73.1212 | NR140075 | 400KV LUCKNOW-UNNAO-II | 1771:49 | KANPUR-AURAIYA-II
35 | NR140037 | 400KV BLBGRH-MAINPURI-I | 73.1212 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 747:48 | KNP-B'GARH-I | 385.69
36 | NR140038 | 400KV BLBGRH-MAINPURI-II | 385.7 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 747:48 | KNP-B'GARH-II | 370.772
37 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 370.772 | NR140084 | 400KV RIHAND-ALLD-I | 6685:47 | KNP-B'GARH-III
38 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 370.772 | NR140085 | 400KV RIHAND-ALLD-II | 6685:47 | KNP-FATEHPUR-II | 107.1
39 | NR140046 | 400KV GORAKH-GORAKH-I | 107.079 | NR140088 | 400KV VARANASI-BIHARSHRF-I | 3420:00 | KNP-FATEHPUR-I | 107.079
40 | NR140047 | 400KV GORAKH-GORAKH-II | 107.1 | NR140089 | 400KV VARANASI-BIHARSHRF-II | 3420:00 | KNP-PANKI-I | 5.924
41 | NR140052 | 400KV KNP-AGRA | 5.9 | NR140090 | 400KV SASARAM-VARANASI | 1140:29 | KNP-PANKI-II | 5.863
42 | NR140053 | 400KV KNP-AURAIYA-I | 5.9 | NR140091 | 400KV SING-ALLD-I | 5422:28 | KASHIPUR-BAREILLY-I | 100.659
43 | NR140054 | 400KV KNP-AURAIYA-II | 262.26 | NR140092 | 400KV SING-ALLD-II | 4829:02 | KASHIPUR-BAREILLY-II
44 | NR140055 | 400KV KNP-BLBGARH-I | 262.26 | NR140093 | 400KV SING-ANPARA | 724:38 | KANPUR(400)-KANPUR(765)-I | 21.32
45 | NR140056 | 400KV KNP-BLBGARH-II | 2.862 | NR140111 | 400KV SING-FATEHPUR | 7942:52 | KANPUR(400)-KANPUR(765)-II
46 | NR140057 | 400KV KNP-BLBGARH-III | 2.862 | NR140095 | 400KV SING-LKO(UP) | 7920:00 | LUCKNOW-GORAKHPUR-III | 263.933
47 | NR140110 | 400KV KNP-FATEHPUR-I | 63.27 | NR140096 | 400KV SING-RIHAND-I | 1008:00 | LUCKNOW-GORAKHPUR-IV
48 | NR140105 | 400KV KNP-FATEHPUR-II | 177 | NR140097 | 400KV SING-RIHAND-II | 1008:00 | LUCKNOW(765)-LUCKNOW(400)-I | 2.862
49 | NR140058 | 400KV KNP-PANKI-I | 169.729 | N-W40001 | 400KV SING-VINDH-I | 80:11 | LUCKNOW(765)-LUCKNOW(400)-II
50 | NR140059 | 400KV KNP-PANKI-II | 98.298 | N-W40002 | 400KV SING-VINDH-II | 40:05 | LUCKNOW-LUCKNOW (UP) | 63.27
51 | NR140070 | 400KV LUCKNOW-GORAKH-III | 98.298 | NR140164 | 400KV VARANASI-SARNATH-I | 1289:31 | LUCKNOW-SULTANPUR | 163.6
52 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 163.6 | NR140165 | 400KV VARANASI-SARNATH-II | 1289:31 | LUCKNOW-SHAHJHNPR-I | 169.729
53 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 73.826 |  |  |  | LUCKNOW-SHAHJHNPR-II
54 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 73.826 |  | 220 KV TRANS LINES |  | LUCKNOW-SOHAWAL-I | 98.281
55 | NR140072 | 400KV LUCKNOW-LKO(UP) | 31.158 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | LUCKNOW-SOHAWAL-II
56 | NR140114 | 400KV LUCKNOW-ROSA-I | 31.158 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 405:27 | LUCKNOW-UNNAO-I | 73.826
57 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 278.574 | BILUP2202 | 220KV ALLD-REWA RD-I | 71:02 | LUCKNOW-UNNAO-II
58 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 278.574 | BILUP2203 | 220KV ALLD-REWA RD-II | 71:02 | RIHAND-ALLD-I | 279.245
59 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 142.5 | NR122006 | 220KV AUR-SIKANDARA-I | 4380:46 | RIHAND-ALLD-II
60 | NR140073 | 400KV LUCKNOW-SULTANPR | 142.5 | NR122007 | 220KV AUR-SIKANDARA-II | 4380:46 | RIHAND-VINDHYACHAL Pooling-I | 31.158
61 | NR140074 | 400KV LUCKNOW-UNNAO-I | 225.936 | NR122012 | 220KV DGANGA-BLY(UP)-II | 5630:10 | RIHAND-VINDHYACHAL Pooling-II
62 | NR140075 | 400KV LUCKNOW-UNNAO-II | 201.21 | NR122013 | 220KV DGANGA-PITHORAGRH | 1416:14 | SING-ALLD-I | 224
63 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.193 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 148:05 | SING-ALLD-II | 202
64 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 330.953 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 148:05 | SING-ANPARA | 25.057
65 | NR140084 | 400KV RIHAND-ALLD-I | 330 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 126:52 | SING-FATEHPUR | 330.953
66 | NR140085 | 400KV RIHAND-ALLD-II | 42 | NR122041 | 220KV FATEHPUR-NAUBASTA | 126:52 | SING-LUCKNOW(UP) | 408.6
67 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 42 | NR122016 | 220KV KNP-MAINPURI | 3624:00 | SING-RIHAND-I | 42.026
68 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 3.341 | NR122017 | 220KV KNP-NAUBASTA | 463:41 | SING-RIHAND-II
69 | NR140091 | 400KV SING-ALLD-I | 1.67 | NR122018 | 220KV KNP-PANKI-I | 374:24 | SING-VINDH-I | 3.341
70 | NR140092 | 400KV SING-ALLD-II | 21.32 | NR122019 | 220KV KNP-PANKI-II | 572:38 | SING-VINDH-II
71 | NR140093 | 400KV SING-ANPARA | 21.32 | NR122020 | 220KV KNP-UNCHR-I | 3445:16 | HVDC Feeder I | 1.25
72 | NR140111 | 400KV SING-FATEHPUR | 139.482 | NR122021 | 220KV KNP-UNCHR-II | 3445:16 | HVDC Feeder I
73 | NR140095 | 400KV SING-LKO(UP)-I | 106.7 | NR122022 | 220KV KNP-UNCHR-III | 3471:07 | HVDC Feeder II | 1.25
74 | NR140096 | 400KV SING-RIHAND-I | 106.7 | NR122023 | 220KV KNP-UNCHR-IV | 3471:07 | HVDC Feeder II
75 | NR140097 | 400KV SING-RIHAND-II | 43.013 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | VINDHYACHAL POOLING-SASAN | 6.02
76 | N-W40001 | 400KV SING-VINDH-I | 43.013 | NR122025 | 220KV RAIBRLY-CHINHAT |  | BIHARSHARIF-VARANASI-I | 285
77 | N-W40002 | 400KV SING-VINDH-II | 28.19 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1026:03 | BIHARSHARIF-VARANASI-II
78 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 28.19 | NR122032 | 220KV SITARGANJ-BLY(UP) | 2534:47 | VARANASI-SARNATH-I | 106.7
79 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 249.52 | NR122033 | 220KV TNKPR-BLY(UP) | 2544:00 | VARANASI-SARNATH-II | 106.7
80 | NR340003 | 400KV VARANASI-SASARAM(ER) | 249.52 | NR122034 | 220KV TNKPR-SITARGANJ | 1026:03 | SASARAM-ALLAHABAD | 213.729
81 | NR340004 | 400KV VARANASI-SARNATH-I | 159.7 | NR122035 | 220KV UNCHR-RAIBRLY-I | 1025:02 | SASARAM-VARANASI | 139.482
82 | NR340005 | 400KV VARANASI-SARNATH-II | 159.7 | NR122036 | 220KV UNCHR-RAIBRLY-II | 1025:02 | VARANASI-ALLAHABAD | 98.791
83 | NR340006 | 400KV AGRA-FATEHABD(UP)-I |  | NR122037 | 220KV UNCHR-RAIBRLY-III | 1048:48 | BARH-GORAKHPUR-I | 353
84 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II |  |  | 220 KV KNP(400KV)-RANIA(UP) | 18.372 | BARH-GORAKHPUR-II
85 | NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 21.879 |  | 220 KV RANIA(UP)-PANKI(UP) | 30.39 | BIHARSHARIF-BALIA-I | 242
86 | NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 16.894 |  | 132 KV TRANS LINES |  | BIHARSHARIF-BALIA-I
87 | NR140142 | 400KV MEERUT-BAREILLY-I | 2.96 | BILUP13201 | 132KV MAU-BALIA | 57.825 | ALLAHABAD-MEJA-I | 28.19
88 | NR140130 | 400KV MEERUT-BAREILLY-II | 2.96 |  | 132 KV Tankpur - Mahendranagar | 3.06 | ALLAHABAD-MEJA-II
89 | NR340011 | 400KV LUCKNOW-SHAHJHNPR-I | 182.532 |  |  |  | UCHAHAR-FATEHPUR-I | 53.7
90 | NR340012 | 400KV Lucknow(765)-Kanpur(GIS)-I | 182.532 |  | 220KV ALLD-JHUSI(UP) | 21.879 | UCHAHAR-FATEHPUR-II
91 | NR340013 | 400KV Lucknow(765)-Kanpur(GIS)-II | 234.59 |  | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | PATNA-BALIA-I | 195
92 | NR340014 | 400KV Kanpur(GIS)-Allahabad-I | 59.01 |  | 220KV ALLD-REWA RD-I&II | 2.96 | PATNA-BALIA-II
93 | NR340015 | 400KV Kanpur(GIS)-Allahabad-II | 6.17 |  | 220KV ALLD-REWA RD-II |  | PATNA-BALIA-III | 185
94 | NR340016 | 400KV ORAI-ORAI(UP)-I | 6.17 |  | 220KV AURAIYA-SIKANDARA-I | 182.532 | PATNA-BALIA-IV
95 | NR340017 | 400KV ORAI-ORAI(UP)-II | 5.286 |  | 220KV AURAIYA-SIKANDARA-II |  | LUCKNOW-KANPUR-I | 159.7
|  |  | 5.286 |  | 220KV D'GANGA-BRLY(UP)-II | 234.59 | LUCKNOW-KANPUR-II
|  |  | 151 |  | 220KV D'GANGA-PITHORAGRH | 59.01 | ALLAHABAD-KANPUR(GIS)-I | 240.39
|  |  | 19.32 |  | 220KV PITHORAGRH-BRLY(UP)-I | 177.88 | ALLAHABAD-KANPUR(GIS)-II
|  |  | 23.86 |  | 220KV FATEHPUR-FTHPR(UP)-I | 6.169 | Total 105 400KV Lines | 10198.266
|  |  | 143.553 |  | 220KV FATEHPUR-FTHPR(UP)-II | 6.169 | HVDC R-D POLE-I | 815
|  |  | 143.553 |  | 220KV FATEHPUR-KNP SOUTH | 5.286 | HVDC R-D POLE-II
|  |  | 144.63 |  | 220KV FATEHPUR-NAUBASTA | 5.286 | HVDC B-B POLE-I | 789.786
|  |  | 144.63 |  | 220KV KNP-MAINPURI | 151 | HVDC B-B POLE-II
|  |  | 177.88 |  | 220KV KNP-RANIA(UP) | 18.372 | BNC-AGRA POLE-I | 1734
|  |  | 93.61 |  | 220KV RANIA(UP)-PANKI(UP) | 30.39 | BNC-AGRA POLE-II
|  |  | 42.752 |  | 220KV KNP-NAUBASTA | 19.32 | CHAMPA-KURUKSHETRA-I | 1305
|  |  | 105.616 |  | 220KV KNP-PANKI-II | 23.86 | CHAMPA-KURUKSHETRA-II
|  |  | 106 |  | 220KV KNP-UNCHAHAR-I | 143.553
|  |  | 42.752 |  | 220KV KNP-UNCHAHAR-II
|  |  | 42.71 |  | 220KV KNP-UNCHAHAR-III | 144.63
|  |  | 42.71 |  | 220KV KNP-UNCHAHAR-IV
C |  | 220 KV TRANS LINES | 43.7 |  | 220KV SITARGANJ-BLY(UP) | 105.72
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 18.372 |  | 220KV TNKPR-BLY(UP) | 106
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 30.39 |  | 220KV TNKPR-SITARGANJ | 42.55
3 | BILUP2202 | 220KV ALLD-REWA RD-I |  |  | 220KV RBRLY-CHINHAT | 93.61
4 | BILUP2203 | 220KV ALLD-REWA RD-II |  |  | 220KV UNCHR-RBRLY-I | 42.71
5 | NR122006 | 220KV AUR-SIKANDARA-I |  |  | 220KV RBRLY-LKO(UP) | 1.19
6 | NR122007 | 220KV AUR-SIKANDARA-II | 57.825 |  | 220KV UNCHR-RBRLY-II | 42.71
7 | NR122012 | 220KV DGANGA-BLY(UP)-II |  |  | 220KV UNCHR-RBRLY-III | 43.7
8 | NR122013 | 220KV DGANGA-PITHORAGRH |  |  | TOTAL 30 Lines
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I |  |  | 132KV LINES
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II |  |  | 132KV MAU-BALIA | 57.825
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH |  |  | 132KV TNKPR-MHNDRNGR | 3.06
12 | NR122041 | 220KV FATEHPUR-NAUBASTA
13 | NR122016 | 220KV KNP-MAINPURI
14 | NR122017 | 220KV KNP-NAUBASTA
15 | NR122019 | 220KV KNP-PANKI-II
16 | NR122020 | 220KV KNP-UNCHR-I
17 | NR122021 | 220KV KNP-UNCHR-II
18 | NR122022 | 220KV KNP-UNCHR-III
19 | NR122023 | 220KV KNP-UNCHR-IV
20 | NR122024 | 220KV PITHORAGRH-BRLY(UP)
21 | NR122025 | 220KV RAIBRLY-CHINHAT
22 | NR122026 | 220KV RAIBRLY-LKO(UP)
23 | NR122032 | 220KV SITARGANJ-BLY(UP)
24 | NR122033 | 220KV TNKPR-BLY(UP)
25 | NR122034 | 220KV TNKPR-SITARGANJ
26 | NR122035 | 220KV UNCHR-RAIBRLY-I
27 | NR122036 | 220KV UNCHR-RAIBRLY-II
28 | NR122037 | 220KV UNCHR-RAIBRLY-III
29 | NR320001 | 220 KV KANPUR(PG) - RANIYA( UP)
30 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)
| NR320003 | 220KV RAIBRLY-CG CITY(UP)
132 KV TRANS LINES
D | BILUP13201 | 132KV MAU-BALIA
1
| Lines | TOTAL FOR T/LS
#REF! |  | OVERALL SYSTEM AVAILABILITY=
E |  | 765/400 KV ICT'S
1 | NR1ICT707 | 765/400KV ICT-I AGRA
2 | NR1ICT708 | 765/400KV ICT-II AGRA
3 | NR1ICT701 | 765/400KV ICT-I BALIA
4 | NR1ICT702 | 765/400KV ICT-II BALIA
5 | NR1ICT715 | 765/400KV ICT-I BAREILLY
6 | NR1ICT716 | 765/400KV ICT-II BAREILLY
7 | NR1ICT705 | 765/400KV ICT-I FATEHPUR
8 | NR1ICT706 | 765/400KV ICT-II FATEHPUR
9 | NR1ICT703 | 765/400KV ICT-I LUCKNOW
10 | NR1ICT704 | 765/400KV ICT-II LUCKNOW
11 | NR1ICT717 | 765/400KV ICT-I VARANASI
12 | NR1ICT718 | 765/400KV ICT-II VARANASI
13 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS)
14 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS)
| NR3ICT703 | 1000MVA ICT-I ORAI(GIS)
| NR3ICT704 | 1000MVA ICT-II ORAI(GIS)
815
F |  | 400/220 KV ICT'S
1 | NR1ICT70 | 315MVA ICT-I AGRA
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 815
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 789.786
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 789.786
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 1734
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 1734
10 | NR1ICT20 | 315MVA ICT-II KANPUR
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW
13 | NR1ICT26 | 315MVA ICT-I MAINPURI
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 0
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 0
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL
| NR3ICT01 | 315MVA ICT-2 at Agra
| NR3ICT02 | 500MVA ICT-3 at Mainpuri
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 100MVA ICT-I PITHORAGRH
2 | NR1ICT44 | 100MVA ICT-II PITHORAGRH
3 | NR1ICT47 | 100MVA ICT-I RAIBAREILLY
4 | NR1ICT38 | 100MVA ICT-II RAIBAREILLY
5 | NR1ICT39 | 200MVA ICT-III RAIBAREILLY
6 | NR1ICT40 | 100MVA ICT-I SITARGANJ
7 | NR1ICT41 | 100MVA ICT-II SITARGANJ
| NR3ICT03 | 200MVA ICT-3 at Raibareilly
| NR3ICT04 | 200MVA ICT-2 at Raibareilly
TOTAL FOR ICTs
39 |  | HVDC RIHAND-DADRI
H | NR1DCP01 | 500KV HVDC R-D POLE-I
1 | NR1DCP02 | 500KV HVDC R-D POLE-II
2 | NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I
3 | NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II
4 |  | TOTAL FOR HVDC line
HVDC AGRA-BNC
J | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I
1 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II
| NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III
| NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV
2 |  | TOTAL of HVDC POLE-I
HVDC BTB VINDHYACHAL
K | NR1DCB01 | VINDH HVDC B/B BLOCK-I
1 | NR1DCB02 | VINDH HVDC B/B BLOCK-II
2 |  | TOTAL FOR HVDC VINDHYACHAL
HVDC BTB SASARAM
L | NEDCB01 | +/-500MW HVDC B/B SASARAM
1 |  | TOTAL FOR HVDC SASARAM
SVC, KANPUR
M | NR1SVC01 | +/-140MVAR SVC-I KANPUR
1 | NR1SVC02 | +/-140MVAR SVC-II KANPUR
2 |  | TOTAL FOR SVC
N |  | Bus & Switch Line Reactor
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA
3 | NR1BRT36 | 240MVAR B/Reactor-I AGRA-765
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD
6 | NR1BRT33 | 125MVAR B/Reactor-II ALLAHABAD
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY
14 | NR1BRT44 | 2x50MVAR B/Reactor BAREILLY
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR
20 | NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI
28 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR
29 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W
30 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N
31 | NR1BRT42 | 125MVAR B/Reactor-I VINDH
32 | NR1BRT43 | 125MVAR B/Reactor-II VINDH
33 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI
34 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI
35 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I
36 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line
37 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I
38 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II
39 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line
40 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 393.9
41 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 393.9
42 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 213.729
43 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 285
44 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 285
45 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 238
46 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 263.94
47 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 139.482
48 | NR1SRT24 | GORAKH 80MVAR S/R Barh-I line
49 | NR1SRT25 | GORAKH 80MVAR S/R Barh-II line
50 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE
51 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE
52 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I
53 | NR1SRT26 | LUCKNW 240MVAR S/R Bareilly Line
54 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS)
55 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS)
56 | NR3SRT01 | VARANASI 240MVAR S/R KNP(GIS)-1
57 | NR3SRT02 | VARANASI 240MVAR S/R KNP(GIS)-2
58 | NR3SRT03 | KNP(GIS) 330MVAR S/R JHATIKRA-1
59 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS)
60 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI
61 | NR3BRT05 | 125MVAR B/Reactor-I KANPUR
62 | NR3BRT06 | 330MVAR B/Reactor-III VARANASI-765
| NR3BRT08 | 330MVAR Bus Reactor-II AT ALIGARH GIS |  |  | 400KV AGRA-SIKAR-I
| NR3SLRT06 | ALIGARH 330MVAR Switachable Line Reactor KANPUR LINE |  |  | 400KV AGRA-SIKAR-II
| NR3BRT09 | 330MVAR B/Reactor-I ALIGARH |  |  | 400KV ALLAHABAD-SASARAM
| NR3LRT07 | ORAI 240MVAR Non Switchable Line Reactor ALIGARH-II LINE |  |  | 400KV VARANASI-BIHARSHRF-I
| NR3LRT08 | ALIGARH 240MVAR Non Switchable Line Reactor ORAI-II LINE |  |  | 400KV VARANASI-BIHARSHRF-II
| NR3BRT10 | 330MVAR Bus Reactor-I ORAI |  |  | 765KV BALIA-GAYA
| NR3LRT09 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-I LINE |  |  | 765KV VARANASI-GAYA
| NR3LRT10 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-II LINE |  |  | 400KV SASARAM-VARANASI
| NR3BRT11 | 330MVAR Bus Reactor-II ORAI |  |  | 400KV MOTIHARI-GRKHPR-I
| NR3LRT11 | ORAI 240MVAR Non-Switchable Line Reactor SATNA LINE |  |  | 400KV MOTIHARI-GRKHPR-II
| NR3LRT12 | ORAI 240MVAR Non-Switchable Line Reactor ALIGARH-I LINE
| NR3LRT13 | ALIGARH 240MVAR Non-Switchable Line Reactor ORAI-I LINE
| NR3BRT07 | 63MVAR B/Reactor-I SOHAWAL
Note on C7: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C12: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C13: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C17: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C18: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C19: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C20: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C37: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16
Note on F76: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on F77: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C82: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C108: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C109: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C169: LILO of KNP-PANKI-II at RANIA by UPPCL. DOC-03-04-17
Note on C279: DOC-26/05/2014
Note on F325: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet5
220KV ALLD-JHUSI(UP)
220KV JHUSI(UP)-PHULPUR(UP)
220KV ALLD-REWA RD-I
220KV ALLD-REWA RD-II
220KV AUR-SIKANDARA-I
220KV AUR-SIKANDARA-II
220KV DGANGA-BLY(UP)-II
220KV DGANGA-PITHORAGRH
220KV FATEHPUR-FTHPR(UP)-I
220KV FATEHPUR-FTHPR(UP)-II
220KV FATEHPUR-KNP SOUTH
220KV FATEHPUR-NAUBASTA
220KV KNP-MAINPURI
220KV KNP-NAUBASTA
220KV KNP-PANKI-I
220KV KNP-PANKI-II
220KV KNP-UNCHR-I
220KV KNP-UNCHR-II
220KV KNP-UNCHR-III
220KV KNP-UNCHR-IV
220KV PITHORAGRH-BRLY(UP)
220KV RAIBRLY-CHINHAT
220KV RAIBRLY-LKO(UP)
220KV SITARGANJ-BLY(UP)
220KV TNKPR-BLY(UP)
220KV TNKPR-SITARGANJ
220KV UNCHR-RAIBRLY-I
220KV UNCHR-RAIBRLY-II
220KV UNCHR-RAIBRLY-III
220KV KNP-RANIA
132 KV TRANS LINES
Note on A31: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Sheet2 (hidden)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
125MVAR B/Reactor-1 Mainpuri | 2017-05-27 22:42 | 2017-05-28 06:46 | 0 | 0 | 0 | 0.33611 | N-2790 | SVRD | H-T for voltage regulation as per NRLDC instruction. Mainpuri=386KV
125MVAR B/Reactor-I GORAKHPUR | 2017-05-22 21:55 | 2017-06-01 | 0 | 0 | 0 | 1900-01-08 02:05 | N-2235 | SVRD | H-T for voltage regulation as per NRLDC instruction. Gorakhpur=393KV
125MVAR B/Reactor-III KANPUR(GIS) | 2017-05-25 23:46 | 2017-05-26 06:58 | 0 | 0 | 0 | 0.3 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. Kanpur=395KV
240MVAR B/Reactor-I BALIA-765 | 2017-05-13 21:25 | 2017-05-27 01:23 | 0 | 0 | 0 | 1900-01-12 03:58 | N-1003 | SVRD | H-T for voltage regulation as per NRLDC instruction. Ballia=744KV
240MVAR B/Reactor-I BAREILLY-765 | 2017-05-25 09:56 | 2017-05-28 05:20 | 0 | 0 | 0 | 1900-01-01 19:24 | N-2455 | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-13 21:24 | 2017-05-14 06:52 | 0 | 0 | 0 | 0.39444 | N-1002 | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-16 20:01 | 2017-05-17 07:40 | 0 | 0 | 0 | 0.48542 | N-1534 | SVRD | H-T for voltage regulation as per NRLDC instruction. Lucknow=749KV
330MVAR B/Reactor-II VARANASI | 2017-05-19 15:05 | 2017-05-19 22:00 | 0 | 0 | 0 | 0.28819 | N-1850 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=751KV
330MVAR B/Reactor-II VARANASI | 2017-05-22 21:34 | 2017-05-24 06:25 | 0 | 0 | 0 | 1899-12-31 08:51 | N-2234 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=761KV
80MVAR B/Reactor BAREILLY | 2017-05-25 23:41 | 2017-05-26 07:02 | 0 | 0 | 0 | 0.30625 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=395KV
80MVAR B/Reactor LUCKNOW | 2017-05-25 23:35 | 2017-05-26 06:53 | 0 | 0 | 0 | 0.30417 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=396KV
Note on A9: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1
Note on A10: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1