## SOP DATA NR3 July
Standard of Performance data for the month of July-2018 Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD, NORTHERN REGION - III | [18 empty] | ANNEXTURE- A
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES
1 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 744
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1327 | 148.034 | 196441.118 | 196441.118 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2018-07-01 | 2018-07-02 15:24 |  |  |  | 0 | 0 | 0 | 1899-12-31 15:24 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
[6 empty] | 2018-07-03 02:56 | 2018-07-04 00:08 |  |  |  | 0 | 0 | 0 | 0.88333 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[6 empty] | 2018-07-05 09:00 | 2018-07-05 13:01 |  |  |  | 0 | 0 | 0 | 0.16736 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=435kV
[6 empty] | 2018-07-12 06:10 | 2018-07-12 11:47 |  |  |  | 0 | 0 | 0 | 0.23403 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[6 empty] | 2018-07-14 07:18 | 2018-07-14 11:17 |  |  |  | 0 | 0 | 0 | 0.16597 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[6 empty] | 2018-07-19 05:41 | 2018-07-19 15:24 |  |  |  | 0 | 0 | 0 | 0.40486 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2018-07-20 06:05 | 2018-07-20 14:42 |  |  |  | 0 | 0 | 0 | 0.35903 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
[6 empty] | 2018-07-24 07:44 | 2018-07-25 11:20 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:36 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2018-07-27 00:06 | 2018-07-27 07:58 |  |  |  | 0 | 0 | 0 | 0.32778 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2018-07-30 02:03 | 2018-07-30 08:35 |  |  |  | 0 | 0 | 0 | 0.27222 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 14:33 | [6 empty] | 744 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2018-07-02 02:37 | 2018-07-02 02:37 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on B-N fault. F.D.= 17.7KM from Fatehpur & 304.9KM from Agra. F.C.= 8.71KA at Fatehpur & 2.67KA at Agra. The fault was in Kanpur jurisdiction.
[6 empty] | 2018-07-04 01:55 | 2018-07-04 20:18 |  |  |  | 0 | 0 | 0 | 0.76597 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
[6 empty] | 2018-07-13 04:30 | 2018-07-17 21:08 |  |  |  | 0 | 0 | 0 | 1900-01-03 16:38 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[6 empty] | 2018-07-21 02:53 | 2018-07-23 12:26 |  |  |  | 0 | 0 | 0 | 1900-01-01 09:33 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
[6 empty] | 2018-07-25 07:50 | 2018-07-26 19:17 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:27 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
[6 empty] | 2018-07-27 02:07 | 2018-07-27 20:08 |  |  |  | 0 | 0 | 0 | 0.75069 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2018-07-28 01:09 | 2018-07-28 19:51 |  |  |  | 0 | 0 | 0 | 0.77917 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2018-07-29 03:21 | 2018-07-29 20:03 |  |  |  | 0 | 0 | 0 | 0.69583 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2018-07-30 04:17 | 2018-07-30 09:53 |  |  |  | 0 | 0 | 0 | 0.23333 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
[6 empty] | 2018-07-31 02:49 | 2018-07-31 19:31 |  |  |  | 0 | 0 | 0 | 0.69583 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-11 11:44 | [6 empty] | 744 | 1210 | 334.8 | 405108 | 405108 | 100
4 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
5 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 256393.647 | 100
6 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1419 | 165.98 | 235525.62 | 235525.62 | 100
7 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | 2018-07-29 11:50 | 2018-07-29 19:55 |  |  |  | 0 | 0 | 0 | 0.33681 |  |  |  | LCSD | S/D availed for attending the tower strengthening work
[6 empty] | 2018-07-30 09:04 | 2018-07-30 20:28 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | LCSD | S/D availed for attending the tower strengthening work
[6 empty] | 2018-07-31 08:41 | 2018-07-31 19:45 |  |  |  | 0 | 0 | 0 | 0.46111 |  |  |  | LCSD | S/D availed for tower strengthening work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 06:33 | [6 empty] | 744 | 1393 | 223 | 310639 | 310639 | 100
8 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1440 | 465.8 | 670752 | 670752 | 100
9 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
10 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
11 | NR376504 | 765KV ALIGARH-JHATIKARA | 158 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 158 | 220094 | 220094 | 100
12 | NR376505 | 765KV KANPUR(GIS)-ALIGARH | 327 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 327 | 455511 | 455511 | 100
13 | NR376506 | 765KV AGRA-ALIGARH | 122.5 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 122.5 | 170642.5 | 170642.5 | 100
14 | NR376507 | 765KV ALIGARH-GR.NOIDA | 51 | NR3 | -- | 2018-07-18 07:10 | 2018-07-18 09:03 |  |  |  | 0.078472 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for rectification of hanging jumper string at loc no 304.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.078472 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 51 | 71043 | 70863.1644 | 99.7469
15 | NR376508 | 765KV ORAI-ALIGARH-II | 331.958 | NR3 | -- | 2018-07-18 07:18 | 2018-07-18 18:45 |  |  |  | 0.47708 | 0 | 0 | 0 |  |  |  | OSFT | Emergency H/T due to sparking in R Ph reactor jumper at Aligarh
[6 empty] | 2018-07-27 10:51 | 2018-07-27 10:51 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto-reclosed successfully at both end on Y-N fault(Top phase). FD: 155.3kM(M1), 162.9kM(M2) from Aligarh end and 149.8kM(M1), 153.6kM(M2) from Orai end. FC: 4.3kA(M1), 4.4(M2) at Aligarh and 4.2kA(M1), 4.287kA(M2) at Orai. Fault in Mainpuri jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.47708 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 331.958 | 462417.494 | 455300.9882 | 98.461
16 | NR376509 | 765KV ORAI-ALIGARH-I | 331.958 | NR3 | -- | 2018-07-26 11:22 | 2018-07-26 20:14 |  |  |  | 0.36944 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed to check & rectify the clearance between conductor and earth wire
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.36944 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 331.958 | 462417.494 | 456906.6045 | 98.8082
B |  | 400 KV TRANS LINES |  |  | --
1 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 29.982 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- | 2018-07-25 11:36 | 2018-07-25 17:03 | -- | -- |  | 0 | 0 | 0 | 0.22708 |  |  |  | OSPD | S/D availed by UPPCL for CT jumper work at their end.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.22708 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 57.159 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 57.159 | 29436.885 | 29436.885 | 100
4 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2018-07-02 08:08 | 2018-07-02 15:22 | -- | -- | -- | 0 | 0 | 0 | 0.30139 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2018-07-04 03:32 | 2018-07-05 14:50 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:18 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-07-10 21:47 | 2018-07-17 17:43 |  |  |  | 0 | 0 | 0 | 1900-01-05 19:56 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=421kV
[6 empty] | 2018-07-20 08:05 | 2018-07-27 11:27 |  |  |  | 0 | 0 | 0 | 1900-01-06 03:22 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-07-28 05:20 | 2018-07-30 12:41 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:21 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-17 01:11 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2018-07-01 | 2018-07-03 16:05 |  |  |  | 0 | 0 | 0 | 1900-01-01 16:05 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2018-07-05 07:58 | 2018-07-06 10:16 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:18 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-07-27 01:58 | 2018-07-27 11:15 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-07-30 03:53 | 2018-08-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 20:07 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 23:47 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 | 100
6 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 245 | 211.433 | 51801.085 | 51801.085 | 100
7 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2018-07-01 07:55 | 2018-07-01 21:14 | -- | -- | -- | 0 | 0 | 0 | 0.55486 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=435kV
[6 empty] | 2018-07-11 16:45 | 2018-07-11 17:23 |  |  |  | 0 | 0 | 0.026389 | 0 |  |  |  | LNCC | Tripped only from Bhiwadi end due to heavy rain & thunderstorm in Bhiwadi
[6 empty] | 2018-07-23 13:51 | 2018-07-28 20:29 |  |  |  | 0 | 0 | 0 | 1900-01-04 06:38 |  |  |  | LCSD | S/D availed for retro-fittment work of line & SCADA integration work with HVDC Agra
[6 empty] | 2018-07-29 04:09 | 2018-07-29 22:40 |  |  |  | 0 | 0 | 0 | 0.77153 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-07-30 04:12 | 2018-08-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 19:48 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.026389 | 1900-01-07 10:16 | [6 empty] | 743.3667 | 402 | 208.98 | 84009.96 | 84009.96 | 100
8 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2018-07-04 03:12 | 2018-07-05 12:03 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 08:51 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-07-16 16:49 | 2018-07-18 10:46 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:57 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2018-07-20 03:52 | 2018-07-20 12:41 |  |  |  | 0 | 0 | 0 | 0.36736 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2018-07-21 06:08 | 2018-07-22 20:43 |  |  |  | 0 | 0 | 0 | 1899-12-31 14:35 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
[6 empty] | 2018-07-23 03:58 | 2018-07-23 09:47 |  |  |  | 0 | 0 | 0 | 0.24236 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-04 08:01 | [6 empty] | 744 | 515 | 209.51 | 107897.65 | 107897.65 | 100
9 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 382 | 181.137 | 69194.334 | 69194.334 | 100
10 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
11 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | 2018-07-26 08:25 | 2018-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-04 15:35 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=430kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 15:35 | [6 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 | 100
12 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- | 2018-07-31 21:13 | 2018-07-31 21:13 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to R-N fault,M1:F.D.=53.9km from FTP,F.C.=5.71KA, M2:F.D.=53.7km from FTP,F.C.=5.8KA ,M1:F.D.=85.3km from ALLD,F.C.=3.346KA, M2:F.D.=79.73km from ALLD,F.C.=4.146KA.(Kanpur and Allahabad jurisdiction)
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 155.932 | 80304.98 | 80304.98 | 100
13 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 224 | 115360 | 115360 | 100
14 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.792 | 50877.88 | 50877.88 | 100
15 | NR140016 | 400KV ALLD-SASARAM | 212 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 15:35 | [6 empty] | 744 | 369 | 212 | 78228 | 78228 | 100
16 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- | 2018-07-12 09:05 | 2018-07-12 18:31 | -- | -- |  | 0 | 0 | 0 | 0.39306 |  |  |  | OSPD | S/D availed by UPPCL for General maintenance at their end.
[6 empty] | 2018-07-23 14:38 | 2018-07-23 17:13 |  |  |  | 0 | 0.10764 | 0 | 0 |  |  |  | OMSU | Tripped only from Mau(UP) end due to PLCC mal-operation at their end.
[6 empty] | 2018-07-23 23:09 | 2018-07-24 01:44 |  |  |  | 0 | 0.10764 | 0 | 0 |  |  |  | OMSU | Tripped only from Mau(UP) end due to due to problem at their end at their end.
[6 empty] | 2018-07-24 13:38 | 2018-07-24 19:16 |  |  |  | 0 | 0.23472 | 0 | 0 |  |  |  | OMSU | Tripped only from Mau(UP) end due to DC earth fault in 86 relay at Mau end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.45 | 0 | 0.39306 | [6 empty] | 744 | 515 | 13 | 6695 | 6695 | 100
17 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- | 2018-07-13 12:31 | 2018-07-13 19:58 | -- | -- | -- | 0 | 0 | 0 | 0.23472 |  |  |  | OSPD | S/D availed by UPPCL for General maintenance at their end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.23472 | [6 empty] | 744 | 515 | 13 | 6695 | 6695 | 100
18 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 227 | 229.163 | 52020.001 | 52020.001 | 100
19 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 227 | 229.163 | 52020.001 | 52020.001 | 100
20 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
21 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
22 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 9.2 | 4738 | 4738 | 100
23 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 9.2 | 4738 | 4738 | 100
24 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- | 2018-07-10 11:43 | 2018-07-10 14:08 | -- | -- | -- | 0.10069 | 0 | 0 | 0 |  |  |  | OSFT | Emergency H/T due to heavy sparking in R Ph of non switchable L/R at Bareilly end
[6 empty] | 2018-07-17 10:55 | 2018-07-17 11:00 |  |  |  | 0.0034722 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for isolation of L/R at Bareilly end for canopy work
[6 empty] | 2018-07-17 13:02 | 2018-07-17 13:06 |  |  |  | 0.0027778 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed to take L/R in service at Bareilly after canopy work
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.10694 | 0 | 0 | 0 | [6 empty] | 744 | 331 | 278.76 | 92269.56 | 91951.2466 | 99.655
25 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
26 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 | 100
27 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR3
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
28 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 115.926 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 115.926 | 59701.89 | 59701.89 | 100
29 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 | 100
30 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 |  | 2018-07-08 14:33 | 2018-07-08 15:07 |  |  |  | 0.023611 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault. F.D.= 16.8KM from Bareilly, F.C.= 11.9KAmp, The fault was in Bareilly jurisdiction.
[6 empty] | 2018-07-21 12:57 | 2018-07-21 16:09 |  |  |  | 0.13333 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault(bottom phase). FD: 33.17kM(M1), 32.7kM(M2) at Bareilly and 40.9kM from kashipur. FC: 8.537kA(M1), 8.4kA (M2) at bareilly and 4.9kA at Kashipur. Fault in Bareilly jurisdiction. Charging attempt taken at 1312 hrs fron bareilly but line immediately tripped on SOTF on B-N fault.
[6 empty] | 2018-07-25 12:24 | 2018-07-25 12:24 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on R-N fault. F.D.= 1.65KM (M1), 3.0KM (M2) from Bareilly. F.C.= 19.6KA(M1), 18.1KA(M2) at Bareilly & 1.861KA at Kashipur. The fault was in Bareilly jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.15694 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69610.5547 | 99.4937
31 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 |  | 2018-07-24 14:00 | 2018-07-24 14:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully on B-N fault. F.D.= 30.8KM from Bareilly & 83.2KM from Kashipur. The fault was in Bareilly jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 | 100
32 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2018-07-02 06:08 | 2018-07-02 14:10 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LEFT | Tripped on Y-N fault. F.D.= 50.32KM from Mainpuri & 166KM from Ballabhgarh. F.C.= 5.71KA at Mainpuri & 2.3KA at Ballabhgarh. The fault is in Mainpuri jurisdiction.
[6 empty] | 2018-07-03 03:07 | 2018-07-03 22:18 |  |  |  | 0 | 0 | 0 | 0.79931 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2018-07-04 03:31 | 2018-07-04 09:40 |  |  |  | 0 | 0 | 0 | 0.25625 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-11 06:32 | 2018-07-11 17:12 |  |  |  | 0 | 0 | 0 | 0.44444 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2018-07-12 14:03 | 2018-07-12 15:28 |  |  |  | 0 | 0 | 0 | 0.059028 |  |  |  | LCSD | Tripped due to Y-N(middle phase) fault during OPGW laying work. FD: 50.52kM(M1), 47.67Km(M2) at Mainpuri and 158kM from Ballabgarh. FC: 5.69kA(M1) at MNPR. Fault in Mainpuri jurisdiction.
[6 empty] | 2018-07-13 14:00 | 2018-07-13 17:11 |  |  |  | 0 | 0 | 0 | 0.13264 |  |  |  | LCSD | Tripped due to R-B fault(Top and middle phase). FD: 135.79kM(M1), 104.16kM(M2) at Mainpuri and 89.7kM(M1) and 90.08kM(M2) from Ballabgarh. FC: 3.566kA(M1) at MNPR. Fault in NR-1 jurisdiction. ** Due to heavy rain at between location No 382 to 396 resulting all 5kM Pilot wire and PP rope burnt during the OPGW work was going on NR-1(Ballabgarh) jurisdcition.**
[6 empty] | 2018-07-13 18:12 | 2018-07-13 18:31 |  |  |  | 0.013194 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to Y-N(middle phase) fault. FD: 51.27kM(M1), 48.84Km(M2) from Mainpuri and 160.4kM from Ballabgarh. FC: 5.473kA(M1) at MNPR. Fault in Mainpuri jurisdiction.
[6 empty] | 2018-07-14 12:06 | 2018-07-14 12:52 |  |  |  | 0 | 0 | 0 | 0.031944 |  |  |  | LCSD | E/S/D taken to remove hanging OPGW rope at Location no. 162, which was left hanging during OPGW work.
[6 empty] | 2018-07-21 06:56 | 2018-07-21 12:54 |  |  |  | 0 | 0 | 0 | 0.24861 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-22 05:42 | 2018-07-22 13:50 |  |  |  | 0 | 0 | 0 | 0.33889 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-27 00:09 | 2018-07-27 19:31 |  |  |  | 0 | 0 | 0 | 0.80694 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=424kV
[6 empty] | 2018-07-28 01:05 | 2018-07-28 19:44 |  |  |  | 0 | 0 | 0 | 0.77708 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-29 04:10 | 2018-07-29 21:19 |  |  |  | 0 | 0 | 0 | 0.71458 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-30 01:44 | 2018-07-30 21:23 |  |  |  | 0 | 0 | 0 | 0.81875 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.013194 | 0 | 0 | 1900-01-04 10:17 | [6 empty] | 744 | 515 | 235.952 | 121515.28 | 121463.5598 | 99.9574
33 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- | 2018-07-05 08:05 | 2018-07-05 11:34 | -- | -- |  | 0 | 0 | 0 | 0.14514 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-13 17:19 | 2018-07-14 11:27 |  |  |  | 0 | 0 | 0 | 0.75556 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2018-07-26 03:02 | 2018-07-26 15:29 |  |  |  | 0 | 0 | 0 | 0.51875 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[6 empty] | 2018-07-31 02:44 | 2018-07-31 10:41 |  |  |  | 0 | 0 | 0 | 0.33125 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 18:01 | [6 empty] | 744 | 515 | 235.952 | 121515.28 | 121515.28 | 100
34 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2018-07-03 02:58 | 2018-07-03 22:13 | -- | -- | -- | 0 | 0 | 0 | 0.80208 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
[6 empty] | 2018-07-04 03:31 | 2018-07-04 19:47 |  |  |  | 0 | 0 | 0 | 0.67778 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-05 08:04 | 2018-07-05 11:32 |  |  |  | 0 | 0 | 0 | 0.14444 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-11 06:29 | 2018-07-11 17:05 |  |  |  | 0 | 0 | 0 | 0.44167 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
[6 empty] | 2018-07-13 17:16 | 2018-07-15 13:40 |  |  |  | 0 | 0 | 0 | 1899-12-31 20:24 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
[6 empty] | 2018-07-21 06:58 | 2018-07-21 12:54 |  |  |  | 0 | 0 | 0 | 0.24722 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-22 05:46 | 2018-07-23 10:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 04:41 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-25 05:15 | 2018-07-26 15:26 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:11 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
[6 empty] | 2018-07-27 00:09 | 2018-07-27 20:12 |  |  |  | 0 | 0 | 0 | 0.83542 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=424kV
[5 empty] | -- | 2018-07-30 01:42 | 2018-07-30 21:24 | -- | -- | -- | 0 | 0 | 0 | 0.82083 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-31 02:42 | 2018-07-31 10:37 |  |  |  | 0 | 0 | 0 | 0.32986 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 18:27 | [6 empty] | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
35 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- | 2018-07-28 01:06 | 2018-07-28 20:00 | -- | -- | -- | 0 | 0 | 0 | 0.7875 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[6 empty] | 2018-07-29 04:11 | 2018-07-29 21:12 |  |  |  | 0 | 0 | 0 | 0.70903 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:55 | [6 empty] | 744 | 469 | 260.051 | 121963.919 | 121963.919 | 100
36 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
37 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | 2018-07-31 15:28 | 2018-07-31 16:48 |  |  |  | 0 | 0.055556 | 0 | 0 |  |  |  | OMSU | Tripped only from Gorakhpur(UPPCL) end due to problem at their end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.055556 | 0 | 0 | [6 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 | 100
38 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 291 | 240 | 69840 | 69840 | 100
39 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 72.6 | 37389 | 37389 | 100
40 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 73.2 | 37698 | 37698 | 100
41 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2018-07-02 14:40 | 2018-07-02 19:00 | -- | -- |  | 0.18056 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to facilitate rectification of snapped conductor of spare ckt at loc no 925 and refixing of the bundle spacer in place of broken spacer in adjacent span of spare ckt at loc no 929 (Yamuna river crossing tower)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.18056 | 0 | 0 | 0 | [6 empty] | 744 | 342 | 385.69 | 131905.98 | 131137.7104 | 99.4176
42 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
43 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- | 2018-07-21 15:19 | 2018-07-21 15:19 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed successfully at both end on B-N fault(bottom phase). FD: 364.3kM from Kanpur and 5.9kM from Ballabgarh end. FC: 1.3kA at Kanpur and 26kA at BLBGH. Fault in NR-1 jurisdcition.
[6 empty] | 2018-07-22 05:51 | 2018-07-23 14:53 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:02 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
[6 empty] | 2018-07-26 05:24 | 2018-07-29 22:56 |  |  |  | 0 | 0 | 0 | 1900-01-02 17:32 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=428kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-04 02:34 | [6 empty] | 744 | 361 | 370.772 | 133848.692 | 133848.692 | 100
44 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 107.079 | 55145.685 | 55145.685 | 100
45 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 107.1 | 55156.5 | 55156.5 | 100
46 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | 2018-07-26 02:38 | 2018-07-26 07:19 |  |  |  | 0 | 0.19514 | 0 | 0 |  |  |  | OMSU | Tripped only from Panki (UP) end due to fault at Panki(UP) S/S. Panki(UP) S/S become dead.
[6 empty] | 2018-07-26 08:32 | 2018-07-27 09:04 |  |  |  | 0 | 1899-12-31 00:32 | 0 | 0 |  |  |  | OMSU | Tripped due to DC earth fault at Panki(UP) S/S
[6 empty] | 2018-07-27 10:31 | 2018-07-27 20:03 |  |  |  | 0 | 0.39722 | 0 | 0 |  |  |  | OMSU | Tripped only from Panki(UP) end due to DC earth fault at Panki(UP) S/S. line was charged from kanpur end.
[5 empty] | -- | 2018-07-27 20:55 | 2018-07-28 11:51 |  |  |  | 0 | 0.62222 | 0 | 0 |  |  |  | OMSU | Tripped only from Panki(UP) end due to DC earth fault at Panki(UP) S/S. line was charged from kanpur end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 1900-01-01 05:41 | 0 | 0 | [6 empty] | 744 | 515 | 5.922 | 3049.83 | 3049.83 | 100
47 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | 2018-07-26 02:38 | 2018-08-01 |  |  |  | 0 | 1900-01-04 21:22 | 0 | 0 |  |  |  | OMSU | Tripped due to fault at Panki(UP) S/S. Panki(UP) S/S become dead.
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 1900-01-04 21:22 | 0 | 0 | [6 empty] | 744 | 515 | 5.86 | 3017.9 | 3017.9 | 100
48 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- | 2018-07-04 12:11 | 2018-07-04 12:11 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully from both end due to Y-N fault (Top phase). F.D.= 41.04kM from Lucknow and 207.53kM from Gorakhpur. FC:7.536kA at Lucknow and 1.535kA at Gorakhpur. Fault in Lucknow jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 289 | 263.933 | 76276.637 | 76276.637 | 100
49 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- | 2018-07-21 09:32 | 2018-07-21 18:07 | -- | -- | -- | 0.35764 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for Relay testing work at Gorakhpur end
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.35764 | 0 | 0 | 0 | [6 empty] | 744 | 289 | 263.933 | 76276.637 | 75396.6534 | 98.8463
50 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
51 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 | 100
52 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | 2018-07-28 11:30 | 2018-07-28 19:08 |  |  |  | 0 | 0 | 0 | 0.31806 |  |  |  | OSPD | S/D availed by NHAI for girder lauching at Faizabad Road 93.955 (LHS). (LILOED at Lucknow(PG))
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.31806 | [6 empty] | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
53 | NR140114 | 400KV LUCKNOW-SHAHJHNPR-I | 169.785 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 371 | 169.785 | 62990.235 | 62990.235 | 100
54 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 169.729 | 87410.435 | 87410.435 | 100
55 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
56 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 | 100
57 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- | 2018-07-08 20:46 | 2018-07-08 22:10 | -- | -- | -- | 0 | 0.058333 | 0 | 0 |  |  |  | OMSU | Tripped due to Y-B fault, Zone-3, Sultanpur (UP) S/S become dead. F.D.=464KM from Lucknow, F.C.=> Iy=1.154KA & Ib= 1.332KA at Lucknow.
[6 empty] | 2018-07-28 11:30 | 2018-07-28 18:59 |  |  |  | 0 | 0 | 0 | 0.31181 |  |  |  | OSPD | S/D availed by NHAI for girder lauching at Faizabad Road 93.955 (LHS). (LILOED at Lucknow(PG))
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.058333 | 0 | 0.31181 | [6 empty] | 744 | 515 | 41.743 | 21497.645 | 21497.645 | 100
58 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 73.826 | 38020.39 | 38020.39 | 100
59 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- | 2018-07-05 11:18 | 2018-07-05 16:37 | -- | -- | -- | 0 | 0 | 0 | 0.22153 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending hot spot at connector clamp between y-phase CB and Line side isolator at Unnao(UP) end.
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.22153 | [6 empty] | 734.52 | 515 | 73.826 | 38020.39 | 38020.39 | 100
60 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 691 | 30.703 | 21215.773 | 21215.773 | 100
61 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 691 | 31.159 | 21530.869 | 21530.869 | 100
62 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
63 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 616 | 66.009 | 40661.544 | 40661.544 | 100
64 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- | 2018-07-05 12:12 | 2018-07-05 16:19 | -- | -- | -- | 0.17153 | 0 | 0 | 0 |  |  |  | SRMT | Tripped due to main MCB short circuit due to DC positive and negative mix cause main-1 relay REL 521 internal short circuit resulting differential protection operated at Allahabad.
[6 empty] | 2018-07-21 03:42 | 2018-07-21 21:34 |  |  |  | 0 | 0 | 0.74444 | 0 |  |  |  | LNCC | Tripped due to B-N(Top phase) fault due to bad weather condition in fault area. FD: 169kM(M1), 173.1kM(M2) from Allahabad and 125.5kM from Rihand end. FC: 2.333kA(M1), 2.6kA(M2) from Allahabad. Fault in Mirzapur jurisdiction. Charging attempt taken at 0413 hrs from Rihand end but tripped immediately on B-N fault.118kM from Rihand end. again Charging attempt taken at 0435 hrs from Alld end but tripped immediately on SOTF on B-N fault.ALLD: 137kM , 2.735kA. Agrain Charging attempt taken at 1711 hrs dtd 21.07.18 hrs from Rihand end but tripped immediately on B-N fault.120kM from Rihand end.
[6 empty] | 2018-07-21 21:34 | 2018-07-23 10:19 |  |  |  | 1899-12-31 12:45 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for replacement of faulty porcelain disc insulator string at location No 343 and 344. charging attempt taken at 1514hrs on 22.07.2018 from Rihand end but line could not hold due to B-N fault. Fault distance =120KM from Rihand. During patrolling insulator De-capping found at Loc. No. 356 (Mirzapur jurisdiction)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 1899-12-31 16:52 | 0 | 0.74444 | 0 | [6 empty] | 726.1333 | 433 | 279.245 | 120913.085 | 114108.1161 | 94.372
65 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | 2018-07-09 10:45 | 2018-07-09 17:47 |  |  |  | 0.29306 | 0 | 0 | 0 |  |  |  | OSPT | E/S/D availed for attending hot spot in R-phase Line side jumper T connector at Allahabad.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.29306 | 0 | 0 | 0 | [6 empty] | 744 | 433 | 279.245 | 120913.085 | 119770.0446 | 99.0547
66 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 332 | 224 | 74368 | 74368 | 100
67 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 306 | 202 | 61812 | 61812 | 100
68 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 25.057 | 12904.355 | 12904.355 | 100
69 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | 2018-07-13 13:25 | 2018-07-13 13:25 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto-reclosed successfully at both end on Y-N fault(left phase). FD: 222.17kM(M1), 222.18kM(M2) from Fatehpur and 127.1kM from Singrauli. FC: 1.52kA(M1), 1.57kA(M2) at Fatehpur and 2.81kA at Singrauli. Fault in Mirzapur jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 236 | 330.953 | 78104.908 | 78104.908 | 100
70 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- | 2018-07-04 10:20 | 2018-07-04 15:51 | -- | -- |  | 0 | 0 | 0 | 0.22986 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending hot spot in line isolator and 4th IPS pipe clamp of Y & B phase of Bus-1 isolator at Lucknow(UP) end. CPCC code was not taken by UPPCL.
[6 empty] | 2018-07-05 13:18 | 2018-07-05 14:45 |  |  |  | 0.060417 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault. FD: 270.5kM(M2) from Lucknow(UP). FC:0.95kA at Lucknow(UP). Singrauli: No distance display in relay. Line was auto-reclosed(M1) from Lucknow(UP) but A/R lockout(Main 2) protection operated at Lucknow(UP) end but tripped from Singrauli end. Fault in Mirzapur jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.060417 | 0 | 0 | 0.22986 | [6 empty] | 744 | 337 | 408.6 | 137698.2 | 137429.8366 | 99.8051
71 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 42.026 | 21643.39 | 21643.39 | 100
72 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 43.952 | 22635.28 | 22635.28 | 100
73 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | 2018-07-11 12:03 | 2018-07-11 18:11 |  |  |  | 0.25556 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to attend hot spot in main bay R Ph isolator AWL-3 trapezee contact at Vindhyachal
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.25556 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 3.341 | 1720.615 | 1706.4307 | 99.1756
74 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 3.317 | 1708.255 | 1708.255 | 100
75 | NR140164 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | 2018-07-10 08:10 | 2018-07-11 23:37 |  |  |  | 0 | 0 | 0 | 1899-12-31 15:27 |  |  |  | OSPD | S/D availed by UPPCL for general maintenance work at their end.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 15:27 | [6 empty] | 744 | 515 | 69.677 | 35883.655 | 35883.655 | 100
76 | NR140165 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | 2018-07-06 08:32 | 2018-07-08 02:03 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:31 |  |  |  | OSPD | S/D availed by UPPCL for general maintenanace work
[6 empty] | 2018-07-10 19:15 | 2018-07-10 20:01 |  |  |  | 0 | 0.031944 | 0 | 0 |  |  |  | OMSU | Tripped only from Sarnath end due to some problem at Sarnath(UP) end. No replay indication at Varanasi end. Sarnath- O/V Stage-1, Y Ph, 3 Ph alarm
[6 empty] | 2018-07-17 12:03 | 2018-07-17 14:47 |  |  |  | 0 | 0 | 0 | 0.11389 |  |  |  | OSPD | S/D availed by UPPCL to PLCC problem at their end Sarnath (UP)
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.031944 | 0 | 1899-12-31 20:15 | [6 empty] | 744 | 515 | 69.677 | 35883.655 | 35883.655 | 100
77 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
78 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 | 100
79 | NR340013 | 400KV LKO(765)-KANPUR(GIS)-I | 159.7 | NR3 | -- | 2018-07-02 22:20 | 2018-07-02 23:46 |  |  |  | 0.059722 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to TC2 faulty alarm of tie CB at Kanpur & DT received at Lucknow.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.059722 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 159.7 | 109713.9 | 109502.5336 | 99.8073
80 | NR340009 | 400KV LKO(765)-KANPUR(GIS)-II | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 159.7 | 109713.9 | 109713.9 | 100
81 | NR340010 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR3 | -- | 2018-07-28 18:25 | 2018-07-28 18:40 |  |  |  | 0.010417 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to attend lockout Tie CB 426-52 at ALLD
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.010417 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 28.19 | 19366.53 | 19360.0224 | 99.9664
82 | NR340011 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 28.19 | 14517.85 | 14517.85 | 100
83 |  | 400KV Kanpur(GIS)-Allahabad-1 | 239.5 | NR3 | -- | 2018-07-01 09:13 | 2018-07-01 14:24 |  |  |  | 0.21597 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for lowering of earth-wire of UPPTCL 400 KV D/C Banda-Rewa Road to maintain electrical clearance with bottom conductor of 400 KV D/C Allahabad-Kanpur TL at loc. no. 37-38
| NR340014 |  |  |  |  | 2018-07-12 10:31 | 2018-07-12 11:03 |  |  |  | 0.022222 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for attending oil leakage from top of Line reactor at Kanpur(GIS) end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.23819 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 239.5 | 123342.5 | 122394.7742 | 99.2316
84 | NR340015 | 400KV Kanpur(GIS)-Allahabad-2 | 239.5 | NR3 | -- | 2018-07-01 09:13 | 2018-07-01 13:58 |  |  |  | 0.19792 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for lowering of earth-wire of UPPTCL 400 KV D/C Banda-Rewa Road to maintain electrical clearance with bottom conductor of 400 KV D/C Allahabad-Kanpur TL at loc. no. 37-39
[6 empty] | 2018-07-28 18:27 | 2018-07-28 18:53 |  |  |  | 0.018056 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to attend lockout Tie CB 426-52 at ALLD
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.21597 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 239.5 | 123342.5 | 122483.1918 | 99.3033
85 |  | 400KV ORAI-ORAI(UP)-I | 41.832 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 41.832 | 21543.48 | 21543.48 | 100
86 |  | 400KV ORAI-ORAI(UP)-II | 41.832 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 41.832 | 21543.48 | 21543.48 | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- | 2018-07-16 10:59 | 2018-07-16 19:23 | -- | -- |  | 0 | 0 | 0 | 0.35 |  |  |  | OSFD | E/S/D availed by UPPCL for replacement of bunt Bus isolator jaw at Rewa Road(UP) end
[6 empty] | 2018-07-14 19:52 | 2018-07-14 20:35 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | OMSU | Line tripped from Rewa road(UP) end only due to problem at UPPCL end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.029861 | 0 | 0.35 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | 2018-07-16 10:59 | 2018-07-16 19:23 |  |  |  | 0 | 0 | 0 | 0.35 |  |  |  | OSFD | E/S/D availed by UPPCL for replacement of bunt Bus isolator jaw at Rewa Road(UP) end
[6 empty] | 2018-07-14 19:52 | 2018-07-14 20:35 |  |  |  | 0 | 0.029861 | 0 | 0 |  |  |  | OMSU | Line tripped from Rewa road(UP) end only due to problem at UPPCL end
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.029861 | 0 | 0.35 | [6 empty] | 744 | 132 | 3 | 396 | 396 | 100
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | 2018-07-30 00:05 | 2018-07-30 04:15 |  |  |  | 0 | 0.17361 | 0 | 0 |  |  |  | OMSU | Tripped only from Auraiya(NTPC) end due to B-N fault.Z1. Due to some problem at NTPC, Auraiya end.
[6 empty] | 2018-07-30 04:15 | 2018-07-30 13:13 |  |  |  | 0 | 0 | 0 | 0.37361 |  |  |  | OSFD | Emergency S/D availed by NTPC, Auraiya to attend relay problem at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.17361 | 0 | 0.37361 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 24047.232 | 100
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | 2018-07-03 14:33 | 2018-07-03 23:45 |  |  |  | 0.38333 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault. FD: Sikandra- 114.5km, FC: Sikandra- 7.978km. After patrolling by Auraiya group, R Ph jumper found opened at loc no 190.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.38333 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 23749.8738 | 98.7634
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- | 2018-07-25 14:49 | 2018-07-25 17:24 | -- | -- |  | 0 | 0.10764 | 0 | 0 |  |  |  | OMSU | Tripped due to fault at Dhauliganaga(NHPC) S/S. Dhauliganga (NHPC) S/S become dead.
[6 empty] | 2018-07-02 13:10 | 2018-07-02 15:05 |  |  |  | 0 | 0 | 0 | 0.079861 |  |  |  | OSFD | Emergency S/D availed by Dhauliganga(NHPC) for CB rectification work at Dhauliganga
[6 empty] | 2018-07-29 16:57 | 2018-07-29 17:52 |  |  |  | 0 | 0 | 0.038194 | 0 |  |  |  | GGDC | Tripped due to Power swing block at Dhauliganga as reported by Dhauliganga. All generation unit tripped at Dhauliganga. Heavy rain and thunder storm reported at Dhauliganga.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.10764 | 0.038194 | 0.079861 | [6 empty] | 743.0833 | 109 | 234.59 | 25570.31 | 25570.31 | 100
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- | 2018-07-25 14:49 | 2018-07-25 17:26 | -- | -- | -- | 0 | 0.10903 | 0 | 0 |  |  |  | OMSU | Tripped due to fault at Dhauliganaga(NHPC) S/S. Dhauliganga (NHPC) S/S become dead.
[6 empty] | 2018-07-29 16:56 | 2018-07-30 14:51 |  |  |  | 0 | 0 | 0.91319 | 0 |  |  |  | LNCC | Tripped due to R-N fault due to heavy rain and thunder storm reported at faulty area. FD: 52.15kM(M1), 41.01kM from Pithoragarh and 7kM from Dhauliganga. FC: 1.336kA at Pithoragarh. Fault in Pithoragarh jurisdiction. Charging attempt taken at 1726 hrs but line tripped immediately on R-N fault. 52.15kM from Pithoragarh. R phase jumper snapped at location No-21.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.10903 | 0.91319 | 0 | [6 empty] | 722.0833 | 156 | 59.01 | 9205.56 | 9205.56 | 100
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- | 2018-07-19 11:58 | 2018-07-19 13:20 | -- | -- |  | 0 | 0 | 0 | 0.056944 |  |  |  | OSFD | Emergency S/D availed by UPPCL for maintenance work at their end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.056944 | [6 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 | 100
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | 2018-07-02 07:25 | 2018-07-02 13:26 |  |  |  | 0 | 0.25069 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault. FD: FTPR-55.7km, FC: FTPR-3.159KA. Fault in UPPCL jurisdiction
[6 empty] | 2018-07-30 23:12 | 2018-07-31 00:01 |  |  |  | 0 | 0.034028 | 0 | 0 |  |  |  | OMSU | Tripped only from UPPCL/Kanpur(South) end due to B-N fault,F.D.=25km from Fatehpur,F.C.=5.5KA (UPPCL Jurisdiction)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.28472 | 0 | 0 | [6 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 | 100
13 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- |  |  |  |  | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 10.4 | 1362.4 | 1362.4 | 100
14 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
15 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)-1 | 8.717 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.34167
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.34167 | [6 empty] | 744 | 131 | 8.717 | 1141.927 | 1141.927 | 100
16 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 | 100
17 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
18 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 143.553 | 18805.443 | 18805.443 | 100
19 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
20 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 144.63 | 18946.53 | 18946.53 | 100
21 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 156 | 177.88 | 27749.28 | 27749.28 | 100
22 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
23 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 1.19 | 157.08 | 157.08 | 100
24 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 105.72 | 13955.04 | 13955.04 | 100
25 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | 2018-07-31 12:20 | 2018-07-31 14:06 |  |  |  | 0 | 0.073611 | 0 | 0 |  |  |  | OMSU | Tripped only from UPPCL/BLY(UP) end due to problem at their end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.073611 | 0 | 0 | [6 empty] | 744 | 132 | 106 | 13992 | 13992 | 100
26 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 42.55 | 5616.6 | 5616.6 | 100
27 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- | 2018-07-13 12:17 | 2018-07-13 19:22 | -- | -- |  | 0 | 0 | 0 | 0.29514 |  |  |  | OSFD | Emergency S/D availed by Unchahar(NTPC) for rectification of CB problem at Unchahar(NTPC) end.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.29514 | [6 empty] | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
28 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 0.92 | 121.44 | 121.44 | 100
29 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 42.5 | 5610 | 5610 | 100
30 | NR320001 | 220KV KNP-RANIA | 1.683 | NR3 | -- | 2018-07-26 05:57 | 2018-07-26 14:09 | -- | -- |  | 0 | 0 | 0 | 0.34167 |  |  |  | OSFD | Emergency H/T from Rania(UP) end only due to problem at Rania(UP)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.34167 | [6 empty] | 744 | 132 | 18.372 | 2425.104 | 2425.104 | 100
31 | NR320003 | 220KV RAIBRLY-CG CITY(UP) | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 18.372 | 2425.104 | 2425.104 | 100
31 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP) | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 18.372 | 2425.104 | 2425.104 | 100
[5 empty] | -- | [17 empty] | 2420.56
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 | 58 | 2900 | 2900 | 100
134 | Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-03 23:02 | 1900-01-08 12:45 | 1899-12-31 17:20 | 1900-04-04 19:24 | [8 empty] | 19614.664 | 10651442.852 | 10625710.2989 | 99.7584 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.8693 | % (HVDC) | 89.1368
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
17 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
18 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
19 | NR3ICT701 | 765/400KV ICT-I Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
20 | NR3ICT702 | 765/400KV ICT-II Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
21 | NR3ICT05 | 1000MVA ICT-1 ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1000 |  | 1000 | 1000 | 100
22 | NR3ICT06 | 1000MVA ICT-2 ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1000 |  | 1000 | 1000 | 100
F |  | 400/220 KV ICT'S |  | NR3 | --
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | 2018-07-18 14:29 | 2018-07-18 20:12 |  |  |  | 0.23819 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for commissioning of CSD relay
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.23819 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 312.5796 | 99.2316
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | 2018-07-03 08:23 | 2018-07-03 17:36 |  |  |  | 0.38403 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for application of insulator sleeve on 33KV tertiary conductor |  | 744 | 315 |  | 315 | 311.0978 | 98.7612
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500 | 100
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
[11 empty] | 0 | 0 | 0 | 0
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR3 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | 2018-07-11 13:38 | 2018-07-11 16:00 |  |  |  | 0.098611 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for installation of rain canopy in RPD/OSR and Buccholz relay to avoid any moisture ingress
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.098611 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 99.6819 | 99.6819
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 200 | NR3 | -- | 2018-07-16 13:28 | 2018-07-16 16:37 |  |  |  | 0.13125 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for application of sealants and rain canopy over the PRD/OSR and buchholtz relay to avoid any moisture ingress.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.13125 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 99.5766 | 99.5766
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 200 | NR3 | -- | 2018-07-18 11:37 | 2018-07-18 15:30 |  |  |  | 0.16181 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for installation of rain canopy over the Buccholz/PRD/OSR
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.16181 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 99.478 | 99.478
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
--
45 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 0.82187 | 0 | 0 | 0 | [7 empty] | 31425 |  | 31425 | 31417.414 | 99.9759 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2018-07-07 04:59 | 2018-07-07 04:59 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully due to DC transient earth fault,F.D.=738.57km from Rihand, F.D.=76.43km from Dadri(NR-1 jurisdiction)
[6 empty] | 2018-07-08 03:29 | 2018-07-08 03:29 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully due to DC transient earth fault,F.D.=738.5km from Rihand, F.D.=76.5km from Dadri(NR-1 jurisdiction)
[6 empty] | 2018-07-27 05:20 | 2018-07-27 05:20 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD:Rihand-780.1km, Dadri-34.9km. Fault in NR-1 jurisdiction
[6 empty] | 2018-07-27 13:50 | 2018-07-27 13:50 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient DC earth Fault. FD: 697.2kM from Rihand end and 117.8kM from Dadri end. Fault in Mainpuri jurisdiction.
[6 empty] | 2018-07-28 02:17 | 2018-07-28 02:17 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient DC earth Fault. FD: 549.59kM from Rihand end and 265.41kM from Dadri end. Fault in Mainpuri jurisdiction.
[6 empty] | 2018-07-30 10:15 | 2018-07-30 10:15 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC Transient earth Fault, FD= 717.14kM from Rihand and F.D.= 97.86kM from Dadri. Fault in NR-1 jurisdiction.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2018-07-03 04:29 | 2018-07-03 04:29 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient Fault. FD: Rihand-334.41, Dadri-480.59km. Fault in Kanpur TL jurisdiction.
[6 empty] | 2018-07-04 17:09 | 2018-07-04 17:09 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient Fault. FD: Rihand-151.20kM , Dadri-663.8km. Fault in Mirzapur jurisdiction.
[6 empty] | 2018-07-04 19:14 | 2018-07-04 19:14 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient Fault. FD: Rihand-744.84kM, Dadri-70.16km. Fault in NR-1 jurisdiction.
[6 empty] | 2018-07-07 09:54 | 2018-07-07 21:07 |  |  |  | 0.46736 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for checking of PEX tubing of all the three quadruple valves inside valve hall and rectification after fault finding work by Rihand
[6 empty] | 2018-07-09 20:04 | 2018-07-10 00:36 |  |  |  | 0.18889 | 0 | 0 | 0 |  |  |  | OSPT | E/S/D availed for attending sparking in Neutral bushing of R- phase converter transformer at Rihand.
[6 empty] | 2018-07-11 15:38 | 2018-07-11 15:38 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Rihand-152.14km, Dadri-662.86km. Fault in Mirzapur TL jurisdiction
[6 empty] | 2018-07-29 23:05 | 2018-07-29 23:05 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient Fault. FD: 725.5kM from Rihand and 89.5kM from Dadri. Fault in NR-1 jurisdiction.
[6 empty] | 2018-07-31 05:34 | 2018-07-31 05:34 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to DC Transient earth Fault, FD= 744.8kM from Rihand and F.D.= 70.2kM from Dadri. Fault in NR-1 jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.65625 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 598310.2319 | 97.8831
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | 2018-07-13 04:26 | 2018-07-13 05:30 |  |  |  | 0.044444 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to Water tank Expansion Level Low alarm operated at Balia end.
[6 empty] | 2018-07-21 00:07 | 2018-07-21 00:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: 694.261kM from Balia and 95.539kM from Bhiwadi end. Tower No 1894. Fault in NR-1 jurisdiction.
[6 empty] | 2018-07-21 05:33 | 2018-07-21 05:33 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: 584.836kM from Balia and 204.954kM from Bhiwadi end. Tower No 1597. Fault in NR-1 jurisdiction.
[6 empty] | 2018-07-21 07:41 | 2018-07-21 09:13 |  |  |  | 0.063889 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to change over logic failure at Balia end.
[6 empty] | 2018-07-22 22:16 | 2018-07-22 22:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R on DC transient E/F. F.D.= 614.397KM from Balia & 175.393KM from Bhiwadi end. Loc. No.= 1676, The fault was in NR-1 jurisdiction.
[6 empty] | 2018-07-26 17:37 | 2018-07-26 17:37 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Ballia-641.839km, Bhiwadi-147.95km (Tower no. 1752). Fault in NR-1 jurisdiction
[6 empty] | 2018-07-28 09:16 | 2018-07-28 19:49 |  |  |  | 0.43958 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed by NR-1 for replacement of DC filters at Bhiwadi.
[6 empty] | 2018-07-29 08:59 | 2018-07-29 19:45 |  |  |  | 0.44861 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed by NR-1 for replacement of DC filters at Bhiwadi.
[6 empty] | 2018-07-30 08:34 | 2018-07-30 19:35 |  |  |  | 0.45903 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed by NR-1 for replacement of DC filters at Bhiwadi.
[6 empty] | 2018-07-31 09:44 | 2018-08-01 |  |  |  | 0.59444 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed by Balia for balance replacement work of DC filters at Balia
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-01 01:12 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 921947.7702 | 93.3871
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2018-07-12 04:49 | 2018-07-12 04:49 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Ballia- 513.704km, Bhiwadi- 276.086km (Tower No. 1403). Fault in Mainpuri TL group jurisdiction.
[6 empty] | 2018-07-29 21:05 | 2018-07-29 21:05 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient Fault. FD: 66.665kM from Balia and 723.125kM from Bhiwadi. Tower No-185. Fault in Balia jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
5 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2018-07-26 03:32 | 2018-07-28 10:10 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:38 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[6 empty] | 2018-07-31 02:08 | 2018-07-31 05:05 |  |  |  | 0.12292 | 0 | 0 | 0 |  |  |  | OMST | tripped due to mal operation of R ph converter transformer OLTC 2 pressure trip relay caused by ingress of water(heavy rain at Agra).
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.12292 | 0 | 0 | 1900-01-01 06:38 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2581722.5806 | 99.6035
6 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | 2018-07-02 12:02 | 2018-07-02 13:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to operation of converter T/F protection of Pole-2(Delta side R Ph pressure relay trip. Charging readiness sent to NRLDC/NLDC at 1342 hrs on 02/07/18 by mail.
[6 empty] | 2018-07-02 13:42 | 2018-07-02 14:56 |  |  |  | 0 | 0 | 0 | 0.051389 |  |  |  | GOMD | After tripping at 1202 hrs on 02/07/18, charging readiness sent to NRLDC/NLDC at 1342 hrs on 02/07/18 by mail but charging code was not issued by NRLDC/NLDC.
[6 empty] | 2018-07-20 08:07 | 2018-07-23 09:55 |  |  |  | 0 | 0 | 0 | 1900-01-02 01:48 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[6 empty] | 2018-07-30 04:03 | 2018-07-30 05:58 |  |  |  | 0 | 0.079861 | 0 | 0 |  |  |  | OMSU | Tripped due to protection indication received from BNC end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.079861 | 0 | 1900-01-02 03:02 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2592000 | 100
7 | NR1DCP03 | 800KV HVDC AGRA-APD POLE-III | 789.786 | NR3 | -- | 2018-07-31 16:37 | 2018-07-31 21:06 |  |  |  | 0.18681 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to mal operation of VESDA at Agra end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.18681 | 0 | 0 | 0 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2576380.6452 | 99.3974
8 | NR1DCP04 | 800KV HVDC AGRA-APD POLE-IV | 789.786 | NR3 | -- | 2018-07-01 08:13 | 2018-07-02 12:45 |  |  |  | 0 | 0 | 0 | 1899-12-31 04:32 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[6 empty] | 2018-07-03 05:15 | 2018-07-03 10:32 |  |  |  | 0 | 0 | 0 | 0.22014 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[6 empty] | 2018-07-12 07:38 | 2018-07-15 13:16 |  |  |  | 0 | 0 | 0 | 1900-01-02 05:38 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[6 empty] | 2018-07-17 06:59 | 2018-07-17 21:12 |  |  |  | 0 | 0 | 0 | 0.59236 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[6 empty] | 2018-07-25 04:31 | 2018-07-29 09:25 |  |  |  | 0 | 0 | 0 | 1900-01-03 04:54 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[6 empty] | 2018-07-30 06:15 | 2018-08-01 |  |  |  | 1899-12-31 17:45 | 0 | 0 | 0 |  |  |  | OSFT | Hand tripped due to water drop was accumulaing on floor due to heavy rain at Agra.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 17:45 | 0 | 0 | 1900-01-08 10:34 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2446548.3871 | 94.3884
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 1900-01-02 00:23 | 0.079861 | 0 | 1900-01-04 09:40 | [8 empty] | 10121.572 | 13564965 | 13315392.1149 | 98.1602 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2018-07-10 12:36 | 2018-07-10 20:38 |  |  |  | 0.33472 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to attend hot spot in 400KV north side Bus-1A gantry jumper
[6 empty] | 2018-07-11 12:54 | 2018-07-11 23:13 |  |  |  | 0.42986 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to DC over current protection operated
[6 empty] | 2018-07-23 19:57 | 2018-07-24 13:08 |  |  |  | 0.71597 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to DC over current protection operated
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1899-12-31 11:32 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 238.06 | 95.224
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | 2018-07-01 | 2018-08-01 |  |  |  | 1900-01-30 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-30 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 0 | 0
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-31 11:32 | 0 | 0 | 0 | [9 empty] | 500 | 238.06 | 47.612 | %
3 | NR1DCB02 | Sasaram HVDC B/B BLOCK-I | 250 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
|  | HVDC BTB TOTAL |  |  | -- | [5 empty] | 1900-01-31 11:32 | 0 | 0 | 0 | [7 empty] | RC
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 530 | 530 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- | 2018-07-01 | 2018-07-09 16:33 | -- | -- |  | 0 | 0 | 0 | 1900-01-07 16:33 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
[6 empty] | 2018-07-21 20:03 | 2018-07-25 07:33 |  |  |  | 0 | 0 | 0 | 1900-01-02 11:30 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=395kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-11 04:03 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- | 2018-07-01 | 2018-08-01 | -- | -- |  | 0 | 0 | 0 | 1900-01-30 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-30 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- | 2018-07-04 19:52 | 2018-07-21 07:00 | -- | -- | -- | 0 | 0 | 0 | 1900-01-15 11:08 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=745kV
[6 empty] | 2018-07-04 19:52 | 2018-07-21 07:00 |  |  |  | 0 | 0 | 0 | 1900-01-15 11:08 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=745kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-31 22:16 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- | 2018-07-01 | 2018-07-25 07:30 | -- | -- |  | 0 | 0 | 0 | 1900-01-23 07:30 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=398kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-23 07:30 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 2X50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- | 2018-07-01 | 2018-07-25 07:30 | -- | -- |  | 0 | 0 | 0 | 1900-01-23 07:30 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=392kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-23 07:30 | [6 empty] | 744 | 100 |  | 100 | 100 | 100
15 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
16 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
17 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
18 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | 2018-07-09 14:45 | 2018-07-11 06:24 |  |  |  | 0 | 0 | 0 | 1899-12-31 15:39 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=749kV
[6 empty] | 2018-07-31 10:04 | 2018-08-01 |  |  |  | 0 | 0 | 0 | 0.58056 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=747kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 05:35 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
19 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | 2018-07-01 | 2018-07-21 08:10 |  |  |  | 0 | 0 | 0 | 1900-01-19 08:10 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=395kV
[6 empty] | 2018-07-22 00:33 | 2018-07-26 05:46 |  |  |  | 0 | 0 | 0 | 1900-01-03 05:13 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=385kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-23 13:23 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
20 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | 2018-07-10 19:50 | 2018-07-21 08:10 |  |  |  | 0 | 0 | 0 | 1900-01-09 12:20 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=383kV
[6 empty] | 2018-07-22 00:33 | 2018-07-26 09:10 |  |  |  | 0 | 0 | 0 | 1900-01-03 08:37 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=385kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-13 20:57 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
21 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | 2018-07-19 01:18 | 2018-07-25 08:54 |  |  |  | 0 | 0 | 0 | 1900-01-05 07:36 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Low voltage at Sitarganj-190KV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-05 07:36 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
22 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | 2018-07-19 01:20 | 2018-07-25 08:45 |  |  |  | 0 | 0 | 0 | 1900-01-05 07:25 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Low voltage at Sitarganj-190KV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-05 07:25 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
23 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | 2018-07-23 22:53 | 2018-07-24 10:51 |  |  |  | 0 | 0 | 0 | 0.49861 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV |  | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.49861 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
24 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | 2018-07-04 19:53 | 2018-07-14 07:17 |  |  |  | 0 | 0 | 0 | 1900-01-08 11:24 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=756kV
[6 empty] | 2018-07-15 23:28 | 2018-07-21 07:16 |  |  |  | 0 | 0 | 0 | 1900-01-04 07:48 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=753kV
[6 empty] | 2018-07-22 20:28 | 2018-07-23 07:27 |  |  |  | 0 | 0 | 0 | 0.45764 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV
[6 empty] | 2018-07-23 22:51 | 2018-07-24 10:49 |  |  |  | 0 | 0 | 0 | 0.49861 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV
[6 empty] | 2018-07-28 23:32 | 2018-08-01 |  |  |  | 0 | 0 | 0 | 1900-01-02 00:28 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=748kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
25 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
26 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | 2018-07-17 00:22 | 2018-07-17 10:41 |  |  |  | 0 | 0 | 0 | 0.42986 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Shahjahanpur=388kV
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.42986 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
27 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80 | 100
28 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
29 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
30 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
31 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
32 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
33 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
34 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
35 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
36 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
37 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
38 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
39 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
40 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
41 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
42 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
43 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
44 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
45 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
46 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
47 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100
48 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50 | 100
49 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | 2018-07-01 | 2018-07-02 09:10 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:10 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=755kV
[6 empty] | 2018-07-04 19:52 | 2018-07-10 06:29 |  |  |  | 0 | 0 | 0 | 1900-01-04 10:37 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=759kV
[6 empty] | 2018-07-11 19:45 | 2018-07-12 05:45 |  |  |  | 0 | 0 | 0 | 0.41667 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=753kV
[6 empty] | 2018-07-17 00:43 | 2018-07-21 05:26 |  |  |  | 0 | 0 | 0 | 1900-01-03 04:43 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=745kV
[6 empty] | 2018-07-22 20:25 | 2018-07-23 07:24 |  |  |  | 0 | 0 | 0 | 0.45764 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=750kV
[6 empty] | 2018-07-23 19:04 | 2018-07-24 06:00 |  |  |  | 0 | 0 | 0 | 0.45556 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=755kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-11 08:25 | [6 empty] | 744 | 240 |  | 240 | 240 | 100
50 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 330 | NR3 | -- | 2018-07-08 10:38 | 2018-07-08 17:59 |  |  |  | 0.30625 | 0 | 0 | 0 |  |  |  | OSPT | Taken under S/D for VFTO test.
[6 empty] | 2018-07-10 19:55 | 2018-07-11 06:18 |  |  |  | 0 | 0 | 0 | 0.43264 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=772kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.30625 | 0 | 0 | 0.43264 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
51 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100
52 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100 | %
53 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100 | %
54 |  | 125MVAR B/Reactor-III KANPUR(GIS) | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 | 100 | %
55 |  | 240MVAR B/Reactor-I KANPUR(GIS) | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 | 100 | %
56 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH | 330 | NR3 | -- | 2018-07-09 14:14 | 2018-07-09 18:09 |  |  |  | 0 | 0 | 0 | 0.16319 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=753kV
[6 empty] | 2018-07-10 09:18 | 2018-07-11 06:20 |  |  |  | 0 | 0 | 0 | 0.87639 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=760kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 00:57 | [6 empty] | 744 | 330 |  | 330 | 330 | 100 | %
56 |  | 330MVAR B/Reactor-II ALIGARH | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100 | %
57 |  | 63MVAR B/Reactor-II SOHAWAL | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 | 100 | %
57 |  | TOTAL FOR Reactor |  |  | -- | [5 empty] | 0.6125 | 0 | 0 | 1900-07-21 03:36 | [7 empty] | 12048.4 |  | 12048.4 | 12048.4 | 100
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L11:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M11:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N11:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O11:[Deemed Available, row above])
Note on C11: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C89: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C93: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C107: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C116: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C125: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C132: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C136: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C141: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C305: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C308: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C580: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C583: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C778: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C783: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Sheet1
POWER GRID CORPORATION OF INDIA LTD.
CPCC, LUCKNOW
DOC No: NR-III-CPCC- |  | DOC No: NR-III-CPCC-
MONTH –July LINE- ICT OUTAGE DETAILS
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | NRLDC CODE | Classification- Category Code | REASON OF OUTAGE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint- Natural calamity- Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  | Code
[5 empty] | 1900-02-11 22:05 | 1900-01-08 14:40 | 1899-12-31 17:20 | 1900-11-18 09:42
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 11 | 12
NR1DCP03 | 307073 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-13 04:26 | 2018-07-13 05:30 | 0.044444 | 0 | 0 | 0 | **** | OMST | Tripped due to Water tank Expansion Level Low alarm operated at Balia end.
NR1DCP03 | 307110 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-21 00:07 | 2018-07-21 00:07 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: 694.261kM from Balia and 95.539kM from Bhiwadi end. Tower No 1894. Fault in NR-1 jurisdiction.
NR1DCP03 | 307112 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-21 05:33 | 2018-07-21 05:33 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: 584.836kM from Balia and 204.954kM from Bhiwadi end. Tower No 1597. Fault in NR-1 jurisdiction.
NR1DCP03 | 307117 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-21 07:41 | 2018-07-21 09:13 | 0.063889 | 0 | 0 | 0 | **** | OMST | Tripped due to change over logic failure at Balia end.
NR1DCP03 | 307130 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-22 22:16 | 2018-07-22 22:16 | 0 | 0 | 0 | 0 | **** | LART | A/R on DC transient E/F. F.D.= 614.397KM from Balia & 175.393KM from Bhiwadi end. Loc. No.= 1676, The fault was in NR-1 jurisdiction.
NR1DCP03 | 307158 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-26 17:37 | 2018-07-26 17:37 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Ballia-641.839km, Bhiwadi-147.95km (Tower no. 1752). Fault in NR-1 jurisdiction
NR1DCP03 | 307176 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-28 09:16 | 2018-07-28 19:49 | 0.43958 | 0 | 0 | 0 | N-1736 | OSPT | S/D availed by NR-1 for replacement of DC filters at Bhiwadi.
NR1DCP03 | 307186 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-29 08:59 | 2018-07-29 19:45 | 0.44861 | 0 | 0 | 0 | N-1801 | OSPT | S/D availed by NR-1 for replacement of DC filters at Bhiwadi.
NR1DCP03 | 307202 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-30 08:34 | 2018-07-30 19:35 | 0.45903 | 0 | 0 | 0 | N-1851 | OSPT | S/D availed by NR-1 for replacement of DC filters at Bhiwadi.
NR1DCP03 | 307212 | 500KV HVDC BALIA-BHWD POLE-I | 2018-07-31 09:44 | 2018-08-01 | 0.59444 | 0 | 0 | 0 | N-1913 | OSPT | S/D availed by Balia for balance replacement work of DC filters at Balia
NR1DCP04 | 307067 | 500KV HVDC BALIA-BHWD POLE-II | 2018-07-12 04:49 | 2018-07-12 04:49 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Ballia- 513.704km, Bhiwadi- 276.086km (Tower No. 1403). Fault in Mainpuri TL group jurisdiction.
NR1DCP04 | 307190 | 500KV HVDC BALIA-BHWD POLE-II | 2018-07-29 21:05 | 2018-07-29 21:05 | 0 | 0 | 0 | 0 | **** | LART | Transient Fault. FD: 66.665kM from Balia and 723.125kM from Bhiwadi. Tower No-185. Fault in Balia jurisdiction.
NR1DCP01 | 307041 | 500KV HVDC R-D POLE-I | 2018-07-07 04:59 | 2018-07-07 04:59 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully due to DC transient earth fault,F.D.=738.57km from Rihand, F.D.=76.43km from Dadri(NR-1 jurisdiction)
NR1DCP01 | 307043 | 500KV HVDC R-D POLE-I | 2018-07-08 03:29 | 2018-07-08 03:29 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully due to DC transient earth fault,F.D.=738.5km from Rihand, F.D.=76.5km from Dadri(NR-1 jurisdiction)
NR1DCP01 | 307166 | 500KV HVDC R-D POLE-I | 2018-07-27 05:20 | 2018-07-27 05:20 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD:Rihand-780.1km, Dadri-34.9km. Fault in NR-1 jurisdiction
NR1DCP01 | 307169 | 500KV HVDC R-D POLE-I | 2018-07-27 13:50 | 2018-07-27 13:50 | 0 | 0 | 0 | 0 | **** | LART | Transient DC earth Fault. FD: 697.2kM from Rihand end and 117.8kM from Dadri end. Fault in Mainpuri jurisdiction.
NR1DCP01 | 307170 | 500KV HVDC R-D POLE-I | 2018-07-28 02:17 | 2018-07-28 02:17 | 0 | 0 | 0 | 0 | **** | LART | Transient DC earth Fault. FD: 549.59kM from Rihand end and 265.41kM from Dadri end. Fault in Mainpuri jurisdiction.
NR1DCP01 | 307204 | 500KV HVDC R-D POLE-I | 2018-07-30 10:15 | 2018-07-30 10:15 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to DC Transient earth Fault, FD= 717.14kM from Rihand and F.D.= 97.86kM from Dadri. Fault in NR-1 jurisdiction.
NR1DCP02 | 307017 | 500KV HVDC R-D POLE-II | 2018-07-03 04:29 | 2018-07-03 04:29 | 0 | 0 | 0 | 0 | **** | LART | Transient Fault. FD: Rihand-334.41, Dadri-480.59km. Fault in Kanpur TL jurisdiction.
NR1DCP02 | 307028 | 500KV HVDC R-D POLE-II | 2018-07-04 17:09 | 2018-07-04 17:09 | 0 | 0 | 0 | 0 | **** | LART | Transient Fault. FD: Rihand-151.20kM , Dadri-663.8km. Fault in Mirzapur jurisdiction.
NR1DCP02 | 307029 | 500KV HVDC R-D POLE-II | 2018-07-04 19:14 | 2018-07-04 19:14 | 0 | 0 | 0 | 0 | **** | LART | Transient Fault. FD: Rihand-744.84kM, Dadri-70.16km. Fault in NR-1 jurisdiction.
NR1DCP02 | 307042 | 500KV HVDC R-D POLE-II | 2018-07-07 09:54 | 2018-07-07 21:07 | 0.46736 | 0 | 0 | 0 | N-401 | OSPT | S/D availed for checking of PEX tubing of all the three quadruple valves inside valve hall and rectification after fault finding work by Rihand
NR1DCP02 | 307050 | 500KV HVDC R-D POLE-II | 2018-07-09 20:04 | 2018-07-10 00:36 | 0.18889 | 0 | 0 | 0 | N-528 | OSPT | E/S/D availed for attending sparking in Neutral bushing of R- phase converter transformer at Rihand.
NR1DCP02 | 307064 | 500KV HVDC R-D POLE-II | 2018-07-11 15:38 | 2018-07-11 15:38 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand-152.14km, Dadri-662.86km. Fault in Mirzapur TL jurisdiction
NR1DCP02 | 307191 | 500KV HVDC R-D POLE-II | 2018-07-29 23:05 | 2018-07-29 23:05 | 0 | 0 | 0 | 0 | **** | LART | Transient Fault. FD: 725.5kM from Rihand and 89.5kM from Dadri. Fault in NR-1 jurisdiction.
NR1DCP02 | 307207 | 500KV HVDC R-D POLE-II | 2018-07-31 05:34 | 2018-07-31 05:34 | 0 | 0 | 0 | 0 |  | LART | A/R operated successfully from both end due to DC Transient earth Fault, FD= 744.8kM from Rihand and F.D.= 70.2kM from Dadri. Fault in NR-1 jurisdiction.
NRNEDCP03 | 307215 | 800KV HVDC AGRA-APD POLE-III | 2018-07-31 16:37 | 2018-07-31 21:06 | 0.18681 | 0 | 0 | 0 | **** | OMST | Tripped due to mal operation of VESDA at Agra end
NRNEDCP04 | 307002 | 800KV HVDC AGRA-APD POLE-IV | 2018-07-01 08:13 | 2018-07-02 12:45 | 0 | 0 | 0 | 1899-12-31 04:32 | NL-08 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP04 | 307018 | 800KV HVDC AGRA-APD POLE-IV | 2018-07-03 05:15 | 2018-07-03 10:32 | 0 | 0 | 0 | 0.22014 | NL-60 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP04 | 307069 | 800KV HVDC AGRA-APD POLE-IV | 2018-07-12 07:38 | 2018-07-15 13:16 | 0 | 0 | 0 | 1900-01-02 05:38 | NL-463 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP04 | 307090 | 800KV HVDC AGRA-APD POLE-IV | 2018-07-17 06:59 | 2018-07-17 21:12 | 0 | 0 | 0 | 0.59236 | N-1010 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NRNEDCP04 | 307142 | 800KV HVDC AGRA-APD POLE-IV | 2018-07-25 04:31 | 2018-07-29 09:25 | 0 | 0 | 0 | 1900-01-03 04:54 | N-1504 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP04 | 307194 | 800KV HVDC AGRA-APD POLE-IV | 2018-07-30 06:15 | 2018-08-01 | 1899-12-31 17:45 | 0 | 0 | 0 | **** | OSFT | Hand tripped due to water drop was accumulaing on floor due to heavy rain at Agra.
NRNEDCP01 | 307127 | 800KV HVDC AGRA-BNC POLE-I | 2018-07-22 09:26 | 2018-07-25 16:47 | 0 | 0 | 0 | 1900-01-02 07:21 | N-1239 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP01 | 307152 | 800KV HVDC AGRA-BNC POLE-I | 2018-07-26 03:32 | 2018-07-28 10:10 | 0 | 0 | 0 | 1900-01-01 06:38 | N-1577 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP01 | 307206 | 800KV HVDC AGRA-BNC POLE-I | 2018-07-31 02:08 | 2018-07-31 05:05 | 0.12292 | 0 | 0 | 0 |  | OMST | tripped due to mal operation of R ph converter transformer OLTC 2 pressure trip relay caused by ingress of water(heavy rain at Agra).
NRNEDCP02 | 307009 | 800KV HVDC AGRA-BNC POLE-II | 2018-07-02 12:02 | 2018-07-02 13:42 | 0.069444 | 0 | 0 | 0 | **** | OMST | Tripped due to operation of converter T/F protection of Pole-2(Delta side R Ph pressure relay trip. Charging readiness sent to NRLDC/NLDC at 1342 hrs on 02/07/18 by mail.
NRNEDCP02 | 307010 | 800KV HVDC AGRA-BNC POLE-II | 2018-07-02 13:42 | 2018-07-02 14:56 | 0 | 0 | 0 | 0.051389 | **** | GOMD | After tripping at 1202 hrs on 02/07/18, charging readiness sent to NRLDC/NLDC at 1342 hrs on 02/07/18 by mail but charging code was not issued by NRLDC/NLDC.
NRNEDCP02 | 307109 | 800KV HVDC AGRA-BNC POLE-II | 2018-07-20 08:07 | 2018-07-23 09:55 | 0 | 0 | 0 | 1900-01-02 01:48 | NL-745 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP02 | 307193 | 800KV HVDC AGRA-BNC POLE-II | 2018-07-30 04:03 | 2018-07-30 05:58 | 0 | 0.079861 | 0 | 0 | **** | OMSU | Tripped due to protection indication received from BNC end.
NR1DCB01 | 307054 | VINDH HVDC B/B BLOCK-I | 2018-07-10 12:36 | 2018-07-10 20:38 | 0.33472 | 0 | 0 | 0 | N-573 | OSFT | Emergency S/D availed to attend hot spot in 400KV north side Bus-1A gantry jumper
NR1DCB01 | 307063 | VINDH HVDC B/B BLOCK-I | 2018-07-11 12:54 | 2018-07-11 23:13 | 0.42986 | 0 | 0 | 0 | **** | OMST | Tripped due to DC over current protection operated
NR1DCB01 | 307135 | VINDH HVDC B/B BLOCK-I | 2018-07-23 19:57 | 2018-07-24 13:08 | 0.71597 | 0 | 0 | 0 | **** | OMST | Tripped due to DC over current protection operated
NR1DCB02 | 311198 | VINDH HVDC B/B BLOCK-II | 2018-07-01 | 2018-08-01 | 1900-01-30 | 0 | 0 | 0 | **** | OMST | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL. | Time not mentioned.
NR176502 | 306187 | 765KV AGRA-FATEHPUR-I | 2018-07-01 | 2018-07-02 15:24 | 0 | 0 | 0 | 1899-12-31 15:24 | N-2190 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
NR176502 | 307014 | 765KV AGRA-FATEHPUR-I | 2018-07-03 02:56 | 2018-07-04 00:08 | 0 | 0 | 0 | 0.88333 | N-93 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR176502 | 307036 | 765KV AGRA-FATEHPUR-I | 2018-07-05 09:00 | 2018-07-05 13:01 | 0 | 0 | 0 | 0.16736 | N-268 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=435kV
NR176502 | 307068 | 765KV AGRA-FATEHPUR-I | 2018-07-12 06:10 | 2018-07-12 11:47 | 0 | 0 | 0 | 0.23403 | N-691 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR176502 | 307082 | 765KV AGRA-FATEHPUR-I | 2018-07-14 07:18 | 2018-07-14 11:17 | 0 | 0 | 0 | 0.16597 | N-830 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR176502 | 307100 | 765KV AGRA-FATEHPUR-I | 2018-07-19 05:41 | 2018-07-19 15:24 | 0 | 0 | 0 | 0.40486 | N-1120 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176502 | 307107 | 765KV AGRA-FATEHPUR-I | 2018-07-20 06:05 | 2018-07-20 14:42 | 0 | 0 | 0 | 0.35903 | N-1200 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
NR176502 | 307139 | 765KV AGRA-FATEHPUR-I | 2018-07-24 07:44 | 2018-07-25 11:20 | 0 | 0 | 0 | 1899-12-31 03:36 | N-1455 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176502 | 307161 | 765KV AGRA-FATEHPUR-I | 2018-07-27 00:06 | 2018-07-27 07:58 | 0 | 0 | 0 | 0.32778 | N-1658 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176502 | 307197 | 765KV AGRA-FATEHPUR-I | 2018-07-30 02:03 | 2018-07-30 08:35 | 0 | 0 | 0 | 0.27222 | N-1837 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176507 | 307005 | 765KV AGRA-FATEHPUR-II | 2018-07-02 02:37 | 2018-07-02 02:37 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on B-N fault. F.D.= 17.7KM from Fatehpur & 304.9KM from Agra. F.C.= 8.71KA at Fatehpur & 2.67KA at Agra. The fault was in Kanpur jurisdiction.
NR176507 | 307021 | 765KV AGRA-FATEHPUR-II | 2018-07-04 01:55 | 2018-07-04 20:18 | 0 | 0 | 0 | 0.76597 | N-163 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
NR176507 | 307074 | 765KV AGRA-FATEHPUR-II | 2018-07-13 04:30 | 2018-07-17 21:08 | 0 | 0 | 0 | 1900-01-03 16:38 | N-754 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR176507 | 307113 | 765KV AGRA-FATEHPUR-II | 2018-07-21 02:53 | 2018-07-23 12:26 | 0 | 0 | 0 | 1900-01-01 09:33 | N-1263 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=794kV
NR176507 | 307144 | 765KV AGRA-FATEHPUR-II | 2018-07-25 07:50 | 2018-07-26 19:17 | 0 | 0 | 0 | 1899-12-31 11:27 | N-1510 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=793kV
NR176507 | 307165 | 765KV AGRA-FATEHPUR-II | 2018-07-27 02:07 | 2018-07-27 20:08 | 0 | 0 | 0 | 0.75069 | N-1662 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176507 | 307173 | 765KV AGRA-FATEHPUR-II | 2018-07-28 01:09 | 2018-07-28 19:51 | 0 | 0 | 0 | 0.77917 | N-1723 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176507 | 307182 | 765KV AGRA-FATEHPUR-II | 2018-07-29 03:21 | 2018-07-29 20:03 | 0 | 0 | 0 | 0.69583 | N-1795 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176507 | 307200 | 765KV AGRA-FATEHPUR-II | 2018-07-30 04:17 | 2018-07-30 09:53 | 0 | 0 | 0 | 0.23333 | N-1843 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176507 | 307208 | 765KV AGRA-FATEHPUR-II | 2018-07-31 02:49 | 2018-07-31 19:31 | 0 | 0 | 0 | 0.69583 | N-1900 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=789kV
NR376507 | 307094 | 765KV ALIGARH-GR.NOIDA | 2018-07-18 07:10 | 2018-07-18 09:03 | 0.078472 | 0 | 0 | 0 | N-1068 | OSFT | Emergency S/D availed for rectification of hanging jumper string at loc no 304.
NR376509 | 307157 | 765KV ORAI-ALIGARH-I | 2018-07-26 11:22 | 2018-07-26 20:14 | 0.36944 | 0 | 0 | 0 | N-1617 | OSPT | S/D availed to check & rectify the clearance between conductor and earth wire
NR376508 | 307095 | 765KV ORAI-ALIGARH-II | 2018-07-18 07:18 | 2018-07-18 18:45 | 0.47708 | 0 | 0 | 0 | **** | OSFT | Emergency H/T due to sparking in R Ph reactor jumper at Aligarh
NR376508 | 307168 | 765KV ORAI-ALIGARH-II | 2018-07-27 10:51 | 2018-07-27 10:51 | 0 | 0 | 0 | 0 | **** | LART | Auto-reclosed successfully at both end on Y-N fault(Top phase). FD: 155.3kM(M1), 162.9kM(M2) from Aligarh end and 149.8kM(M1), 153.6kM(M2) from Orai end. FC: 4.3kA(M1), 4.4(M2) at Aligarh and 4.2kA(M1), 4.287kA(M2) at Orai. Fault in Mainpuri jurisdiction.
NR176513 | 307187 | 765KV VARANASI-FATEHPUR | 2018-07-29 11:50 | 2018-07-29 19:55 | 0 | 0 | 0 | 0.33681 | N-1811 | LCSD | S/D availed for attending the tower strengthening work
NR176513 | 307203 | 765KV VARANASI-FATEHPUR | 2018-07-30 09:04 | 2018-07-30 20:28 | 0 | 0 | 0 | 0.475 | N-1853 | LCSD | S/D availed for attending the tower strengthening work
NR176513 | 307211 | 765KV VARANASI-FATEHPUR | 2018-07-31 08:41 | 2018-07-31 19:45 | 0 | 0 | 0 | 0.46111 | N-1907 | LCSD | S/D availed for tower strengthening work
NR140002 | 307145 | 400KV AGRA-AGRA(UP)-II | 2018-07-25 11:36 | 2018-07-25 17:03 | 0 | 0 | 0 | 0.22708 | N-1524 | OSPD | S/D availed by UPPCL for CT jumper work at their end.
NR140003 | 307008 | 400KV AGRA-AURAIYA-I | 2018-07-02 08:08 | 2018-07-02 15:22 | 0 | 0 | 0 | 0.30139 | N-47 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
| 307023 | 400KV AGRA-AURAIYA-I | 2018-07-04 03:32 | 2018-07-05 14:50 | 0 | 0 | 0 | 1899-12-31 11:18 | N-169 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
| 307058 | 400KV AGRA-AURAIYA-I | 2018-07-10 21:47 | 2018-07-17 17:43 | 0 | 0 | 0 | 1900-01-05 19:56 | N-609 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=421kV
NR140003 | 307108 | 400KV AGRA-AURAIYA-I | 2018-07-20 08:05 | 2018-07-27 11:27 | 0 | 0 | 0 | 1900-01-06 03:22 | N-1202 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140003 | 307174 | 400KV AGRA-AURAIYA-I | 2018-07-28 05:20 | 2018-07-30 12:41 | 0 | 0 | 0 | 1900-01-01 07:21 | N-1727 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140004 | 306168 | 400KV AGRA-AURAIYA-II | 2018-07-01 | 2018-07-03 16:05 | 0 | 0 | 0 | 1900-01-01 16:05 | N-2020 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140004 | 307033 | 400KV AGRA-AURAIYA-II | 2018-07-05 07:58 | 2018-07-06 10:16 | 0 | 0 | 0 | 1899-12-31 02:18 | N-266 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140004 | 307164 | 400KV AGRA-AURAIYA-II | 2018-07-27 01:58 | 2018-07-27 11:15 | 0 | 0 | 0 | 0.38681 | N-1661 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140004 | 307198 | 400KV AGRA-AURAIYA-II | 2018-07-30 03:53 | 2018-08-01 | 0 | 0 | 0 | 1899-12-31 20:07 | N-1839 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140008 | 307001 | 400KV AGRA-BHIWADI-I | 2018-07-01 07:55 | 2018-07-01 21:14 | 0 | 0 | 0 | 0.55486 | N-10 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=435kV
NR140008 | 307065 | 400KV AGRA-BHIWADI-I | 2018-07-11 16:45 | 2018-07-11 17:23 | 0 | 0 | 0.026389 | 0 | **** | LNCC | Tripped only from Bhiwadi end due to heavy rain & thunderstorm in Bhiwadi
NR140008 | 307132 | 400KV AGRA-BHIWADI-I | 2018-07-23 13:51 | 2018-07-28 20:29 | 0 | 0 | 0 | 1900-01-04 06:38 | N-1410 | LCSD | S/D availed for retro-fittment work of line & SCADA integration work with HVDC Agra
NR140008 | 307183 | 400KV AGRA-BHIWADI-I | 2018-07-29 04:09 | 2018-07-29 22:40 | 0 | 0 | 0 | 0.77153 | N-1797 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140008 | 307199 | 400KV AGRA-BHIWADI-I | 2018-07-30 04:12 | 2018-08-01 | 0 | 0 | 0 | 1899-12-31 19:48 | N-1841 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140009 | 307022 | 400KV AGRA-BHIWADI-II | 2018-07-04 03:12 | 2018-07-05 12:03 | 0 | 0 | 0 | 1899-12-31 08:51 | N-168 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140009 | 307087 | 400KV AGRA-BHIWADI-II | 2018-07-16 16:49 | 2018-07-18 10:46 | 0 | 0 | 0 | 1899-12-31 17:57 | N-987 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140009 | 307106 | 400KV AGRA-BHIWADI-II | 2018-07-20 03:52 | 2018-07-20 12:41 | 0 | 0 | 0 | 0.36736 | N-1198 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140009 | 307114 | 400KV AGRA-BHIWADI-II | 2018-07-21 06:08 | 2018-07-22 20:43 | 0 | 0 | 0 | 1899-12-31 14:35 | N-1270 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=433kV
NR140009 | 307131 | 400KV AGRA-BHIWADI-II | 2018-07-23 03:58 | 2018-07-23 09:47 | 0 | 0 | 0 | 0.24236 | N-1372 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR340008 | 307179 | 400KV ALLAHABAD-MEJA(NTPC)-I | 2018-07-28 18:25 | 2018-07-28 18:40 | 0.010417 | 0 | 0 | 0 | N-1764 | OSFT | Emergency S/D availed to attend lockout Tie CB 426-52 at ALLD
NR140123 | 307155 | 400KV ALLD-FATEHPUR-II | 2018-07-26 08:25 | 2018-08-01 | 0 | 0 | 0 | 1900-01-04 15:35 | N-1601 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=430kV
NR140104 | 307216 | 400KV ALLD-FATEHPUR-III | 2018-07-31 21:13 | 2018-07-31 21:13 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to R-N fault,M1:F.D.=53.9km from FTP,F.C.=5.71KA, M2:F.D.=53.7km from FTP,F.C.=5.8KA ,M1:F.D.=85.3km from ALLD,F.C.=3.346KA, M2:F.D.=79.73km from ALLD,F.C.=4.146KA.(Kanpur and Allahabad jurisdiction)
NR140019 | 307070 | 400KV BALIA-MAU-I | 2018-07-12 09:05 | 2018-07-12 18:31 | 0 | 0 | 0 | 0.39306 | N-697 | OSPD | S/D availed by UPPCL for General maintenance at their end.
NR140019 | 307133 | 400KV BALIA-MAU-I | 2018-07-23 14:38 | 2018-07-23 17:13 | 0 | 0.10764 | 0 | 0 | **** | OMSU | Tripped only from Mau(UP) end due to PLCC mal-operation at their end.
NR140019 | 307138 | 400KV BALIA-MAU-I | 2018-07-23 23:09 | 2018-07-24 01:44 | 0 | 0.10764 | 0 | 0 | **** | OMSU | Tripped only from Mau(UP) end due to due to problem at their end at their end.
NR140019 | 307141 | 400KV BALIA-MAU-I | 2018-07-24 13:38 | 2018-07-24 19:16 | 0 | 0.23472 | 0 | 0 | **** | OMSU | Tripped only from Mau(UP) end due to DC earth fault in 86 relay at Mau end.
NR140020 | 307076 | 400KV BALIA-MAU-II | 2018-07-13 12:31 | 2018-07-13 19:58 | 0 | 0 | 0 | 0.31042 | N-780 | OSPD | S/D availed by UPPCL for General maintenance at their end.
NR140025 | 307053 | 400KV BAREILLY-LKO(UP) | 2018-07-10 11:43 | 2018-07-10 14:08 | 0.10069 | 0 | 0 | 0 | **** | OSFT | Emergency H/T due to heavy sparking in R Ph of non switchable L/R at Bareilly end
NR140025 | 307091 | 400KV BAREILLY-LKO(UP) | 2018-07-17 10:55 | 2018-07-17 11:00 | 0.0034722 | 0 | 0 | 0 | N-1016 | OSPT | S/D availed for isolation of L/R at Bareilly end for canopy work
NR140025 | 307091 | 400KV BAREILLY-LKO(UP) | 2018-07-17 13:02 | 2018-07-17 13:06 | 0.0027778 | 0 | 0 | 0 | N-1029 | OSPT | S/D availed to take L/R in service at Bareilly after canopy work
NR140158 | 307045 | 400KV BARLY(765)-KASHIPUR-I | 2018-07-08 14:33 | 2018-07-08 15:07 | 0.023611 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault. F.D.= 16.8KM from Bareilly, F.C.= 11.9KAmp, The fault was in Bareilly jurisdiction.
NR140158 | 307118 | 400KV BARLY(765)-KASHIPUR-I | 2018-07-21 12:57 | 2018-07-21 16:09 | 0.13333 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault(bottom phase). FD: 33.17kM(M1), 32.7kM(M2) at Bareilly and 40.9kM from kashipur. FC: 8.537kA(M1), 8.4kA (M2) at bareilly and 4.9kA at Kashipur. Fault in Bareilly jurisdiction. Charging attempt taken at 1312 hrs fron bareilly but line immediately tripped on SOTF on B-N fault.
NR140158 | 307146 | 400KV BARLY(765)-KASHIPUR-I | 2018-07-25 12:24 | 2018-07-25 12:24 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on R-N fault. F.D.= 1.65KM (M1), 3.0KM (M2) from Bareilly. F.C.= 19.6KA(M1), 18.1KA(M2) at Bareilly & 1.861KA at Kashipur. The fault was in Bareilly jurisdiction.
NR140159 | 307140 | 400KV BARLY(765)-KASHIPUR-II | 2018-07-24 14:00 | 2018-07-24 14:00 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully on B-N fault. F.D.= 30.8KM from Bareilly & 83.2KM from Kashipur. The fault was in Bareilly jurisdiction.
NR140037 | 307006 | 400KV BLBGRH-MAINPURI-I | 2018-07-02 06:08 | 2018-07-02 14:10 | 0.33472 | 0 | 0 | 0 | **** | LEFT | Tripped on Y-N fault. F.D.= 50.32KM from Mainpuri & 166KM from Ballabhgarh. F.C.= 5.71KA at Mainpuri & 2.3KA at Ballabhgarh. The fault is in Mainpuri jurisdiction.
NR140037 | 307016 | 400KV BLBGRH-MAINPURI-I | 2018-07-03 03:07 | 2018-07-03 22:18 | 0 | 0 | 0 | 0.79931 | N-94 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
| 307025 | 400KV BLBGRH-MAINPURI-I | 2018-07-04 03:31 | 2018-07-04 09:40 | 0 | 0 | 0 | 0.25625 | N-170 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 307060 | 400KV BLBGRH-MAINPURI-I | 2018-07-11 06:32 | 2018-07-11 17:12 | 0 | 0 | 0 | 0.44444 | N-618 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140037 | 307072 | 400KV BLBGRH-MAINPURI-I | 2018-07-12 14:03 | 2018-07-12 15:28 | 0 | 0 | 0 | 0.059028 | **** | LCSD | Tripped due to Y-N(middle phase) fault during OPGW laying work. FD: 50.52kM(M1), 47.67Km(M2) at Mainpuri and 158kM from Ballabgarh. FC: 5.69kA(M1) at MNPR. Fault in Mainpuri jurisdiction.
NR140037 | 307080 | 400KV BLBGRH-MAINPURI-I | 2018-07-13 14:00 | 2018-07-13 17:11 | 0 | 0 | 0 | 0.13264 | **** | LCSD | Tripped due to R-B fault(Top and middle phase). FD: 135.79kM(M1), 104.16kM(M2) at Mainpuri and 89.7kM(M1) and 90.08kM(M2) from Ballabgarh. FC: 3.566kA(M1) at MNPR. Fault in NR-1 jurisdiction. ** Due to heavy rain at between location No 382 to 396 resulting all 5kM Pilot wire and PP rope burnt during the OPGW work was going on NR-1(Ballabgarh) jurisdcition.**
NR140037 | 307081 | 400KV BLBGRH-MAINPURI-I | 2018-07-13 18:12 | 2018-07-13 18:31 | 0.013194 | 0 | 0 | 0 | **** | LEFT | Tripped due to Y-N(middle phase) fault. FD: 51.27kM(M1), 48.84Km(M2) from Mainpuri and 160.4kM from Ballabgarh. FC: 5.473kA(M1) at MNPR. Fault in Mainpuri jurisdiction.
NR140037 | 307083 | 400KV BLBGRH-MAINPURI-I | 2018-07-14 12:06 | 2018-07-14 12:52 | 0 | 0 | 0 | 0.031944 | N-846 | LCSD | E/S/D taken to remove hanging OPGW rope at Location no. 162, which was left hanging during OPGW work.
NR140037 | 307115 | 400KV BLBGRH-MAINPURI-I | 2018-07-21 06:56 | 2018-07-21 12:54 | 0 | 0 | 0 | 0.24861 | N-1271 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 307125 | 400KV BLBGRH-MAINPURI-I | 2018-07-22 05:42 | 2018-07-22 13:50 | 0 | 0 | 0 | 0.33889 | N-1321 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 307163 | 400KV BLBGRH-MAINPURI-I | 2018-07-27 00:09 | 2018-07-27 19:31 | 0 | 0 | 0 | 0.80694 | N-1657 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=424kV
NR140037 | 307171 | 400KV BLBGRH-MAINPURI-I | 2018-07-28 01:05 | 2018-07-28 19:44 | 0 | 0 | 0 | 0.77708 | N-1722 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 307184 | 400KV BLBGRH-MAINPURI-I | 2018-07-29 04:10 | 2018-07-29 21:19 | 0 | 0 | 0 | 0.71458 | N-1797 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140037 | 307196 | 400KV BLBGRH-MAINPURI-I | 2018-07-30 01:44 | 2018-07-30 21:23 | 0 | 0 | 0 | 0.81875 | N-1836 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140038 | 307035 | 400KV BLBGRH-MAINPURI-II | 2018-07-05 08:05 | 2018-07-05 11:34 | 0 | 0 | 0 | 0.14514 | N-267 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140038 | 307078 | 400KV BLBGRH-MAINPURI-II | 2018-07-13 17:19 | 2018-07-14 11:27 | 0 | 0 | 0 | 0.75556 | N-799 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140038 | 307151 | 400KV BLBGRH-MAINPURI-II | 2018-07-26 03:02 | 2018-07-26 15:29 | 0 | 0 | 0 | 0.51875 | N-1576 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140038 | 307209 | 400KV BLBGRH-MAINPURI-II | 2018-07-31 02:44 | 2018-07-31 10:41 | 0 | 0 | 0 | 0.33125 | N-1901 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140124 | 307015 | 400KV FATEHPUR-MAINPURI-I | 2018-07-03 02:58 | 2018-07-03 22:13 | 0 | 0 | 0 | 0.80208 | N-94 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=426kV
| 307024 | 400KV FATEHPUR-MAINPURI-I | 2018-07-04 03:31 | 2018-07-04 19:47 | 0 | 0 | 0 | 0.67778 | N-170 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140124 | 307034 | 400KV FATEHPUR-MAINPURI-I | 2018-07-05 08:04 | 2018-07-05 11:32 | 0 | 0 | 0 | 0.14444 | N-267 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140124 | 307059 | 400KV FATEHPUR-MAINPURI-I | 2018-07-11 06:29 | 2018-07-11 17:05 | 0 | 0 | 0 | 0.44167 | N-618 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=430kV
NR140124 | 307077 | 400KV FATEHPUR-MAINPURI-I | 2018-07-13 17:16 | 2018-07-15 13:40 | 0 | 0 | 0 | 1899-12-31 20:24 | N-799 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=429kV
NR140124 | 307116 | 400KV FATEHPUR-MAINPURI-I | 2018-07-21 06:58 | 2018-07-21 12:54 | 0 | 0 | 0 | 0.24722 | N-1271 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140124 | 307126 | 400KV FATEHPUR-MAINPURI-I | 2018-07-22 05:46 | 2018-07-23 10:27 | 0 | 0 | 0 | 1899-12-31 04:41 | N-1321 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140124 | 307143 | 400KV FATEHPUR-MAINPURI-I | 2018-07-25 05:15 | 2018-07-26 15:26 | 0 | 0 | 0 | 1899-12-31 10:11 | N-1505 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140124 | 307162 | 400KV FATEHPUR-MAINPURI-I | 2018-07-27 00:09 | 2018-07-27 20:12 | 0 | 0 | 0 | 0.83542 | N-1657 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=424kV
NR140124 | 307195 | 400KV FATEHPUR-MAINPURI-I | 2018-07-30 01:42 | 2018-07-30 21:24 | 0 | 0 | 0 | 0.82083 | N-1836 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140124 | 307210 | 400KV FATEHPUR-MAINPURI-I | 2018-07-31 02:42 | 2018-07-31 10:37 | 0 | 0 | 0 | 0.32986 | N-1901 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427kV
NR140125 | 307172 | 400KV FATEHPUR-MAINPURI-II | 2018-07-28 01:06 | 2018-07-28 20:00 | 0 | 0 | 0 | 0.7875 | N-1722 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140125 | 307185 | 400KV FATEHPUR-MAINPURI-II | 2018-07-29 04:11 | 2018-07-29 21:12 | 0 | 0 | 0 | 0.70903 | N-1797 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=428kV
NR140047 | 307214 | 400KV GORAKH-GORAKH-II | 2018-07-31 15:28 | 2018-07-31 16:48 | 0 | 0.055556 | 0 | 0 | **** | OMSU | Tripped only from Gorakhpur(UPPCL) end due to problem at their end
NR340014 | 307003 | 400KV KANPUR(GIS) - ALLAHABAD - I | 2018-07-01 09:13 | 2018-07-01 14:24 | 0.21597 | 0 | 0 | 0 | N-07 | OSPT | S/D availed for lowering of earth-wire of UPPTCL 400 KV D/C Banda-Rewa Road to maintain electrical clearance with bottom conductor of 400 KV D/C Allahabad-Kanpur TL at loc. no. 37-38
NR340014 | 307071 | 400KV KANPUR(GIS) - ALLAHABAD - I | 2018-07-12 10:31 | 2018-07-12 11:03 | 0.022222 | 0 | 0 | 0 | N-706 | OSFT | Emergency S/D availed for attending oil leakage from top of Line reactor at Kanpur(GIS) end.
NR340015 | 307004 | 400KV KANPUR(GIS) - ALLAHABAD - II | 2018-07-01 09:13 | 2018-07-01 13:58 | 0.19792 | 0 | 0 | 0 | N-07 | OSPT | S/D availed for lowering of earth-wire of UPPTCL 400 KV D/C Banda-Rewa Road to maintain electrical clearance with bottom conductor of 400 KV D/C Allahabad-Kanpur TL at loc. no. 37-39
NR340015 | 307180 | 400KV KANPUR(GIS) - ALLAHABAD - II | 2018-07-28 18:27 | 2018-07-28 18:53 | 0.018056 | 0 | 0 | 0 | N-1764 | OSFT | Emergency S/D availed to attend lockout Tie CB 426-52 at ALLD
NR140055 | 307012 | 400KV KNP-BLBGARH-I | 2018-07-02 14:40 | 2018-07-02 19:00 | 0.18056 | 0 | 0 | 0 | N-71 | OSFT | Emergency S/D availed to facilitate rectification of snapped conductor of spare ckt at loc no 925 and refixing of the bundle spacer in place of broken spacer in adjacent span of spare ckt at loc no 929 (Yamuna river crossing tower)
NR140057 | 307119 | 400KV KNP-BLBGARH-III | 2018-07-21 15:19 | 2018-07-21 15:19 | 0 | 0 | 0 | 0 | **** | LART | Auto reclosed successfully at both end on B-N fault(bottom phase). FD: 364.3kM from Kanpur and 5.9kM from Ballabgarh end. FC: 1.3kA at Kanpur and 26kA at BLBGH. Fault in NR-1 jurisdcition.
NR140057 | 307126A | 400KV KNP-BLBGARH-III | 2018-07-22 05:51 | 2018-07-23 14:53 | 0 | 0 | 0 | 1899-12-31 09:02 | N-1321 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.
NR140057 | 307153 | 400KV KNP-BLBGARH-III | 2018-07-26 05:24 | 2018-07-29 22:56 | 0 | 0 | 0 | 1900-01-02 17:32 | N-1583 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=428kV
NR140058 | 307149 | 400KV KNP-PANKI-I | 2018-07-26 02:38 | 2018-07-26 07:19 | 0 | 0.19514 | 0 | 0 | **** | OMSU | Tripped only from Panki (UP) end due to fault at Panki(UP) S/S. Panki(UP) S/S become dead.
NR140058 | 307156 | 400KV KNP-PANKI-I | 2018-07-26 08:32 | 2018-07-27 09:04 | 0 | 1899-12-31 00:32 | 0 | 0 | **** | OMSU | Tripped due to DC earth fault at Panki(UP) S/S
NR140058 | 307167 | 400KV KNP-PANKI-I | 2018-07-27 10:31 | 2018-07-27 20:03 | 0 | 0.39722 | 0 | 0 | **** | OMSU | Tripped only from Panki(UP) end due to DC earth fault at Panki(UP) S/S. line was charged from kanpur end.
NR140058 | 307175 | 400KV KNP-PANKI-I | 2018-07-27 20:55 | 2018-07-28 11:51 | 0 | 0.62222 | 0 | 0 | **** | OMSU | Tripped only from Panki(UP) end due to DC earth fault at Panki(UP) S/S. line was charged from kanpur end.
NR140059 | 307150 | 400KV KNP-PANKI-II | 2018-07-26 02:38 | 2018-08-01 | 0 | 1900-01-04 21:22 | 0 | 0 | **** | OMSU | Tripped due to fault at Panki(UP) S/S. Panki(UP) S/S become dead.
NR340013 | 307013 | 400KV Lucknow(765)-Kanpur(GIS)-II | 2018-07-02 22:20 | 2018-07-02 23:46 | 0.059722 | 0 | 0 | 0 | **** | OMST | Tripped due to TC2 faulty alarm of tie CB at Kanpur & DT received at Lucknow.
NR140070 | 307027 | 400KV LUCKNOW-GORAKH-III | 2018-07-04 12:11 | 2018-07-04 12:11 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully from both end due to Y-N fault (Top phase). F.D.= 41.04kM from Lucknow and 207.53kM from Gorakhpur. FC:7.536kA at Lucknow and 1.535kA at Gorakhpur. Fault in Lucknow jurisdiction.
NR140071 | 307120 | 400KV LUCKNOW-GORAKH-IV | 2018-07-21 09:32 | 2018-07-21 18:07 | 0.35764 | 0 | 0 | 0 | N-1282 | OSPT | S/D availed for Relay testing work at Gorakhpur end
NR140072 | 307178 | 400KV LUCKNOW-LKO(UP) | 2018-07-28 11:30 | 2018-07-28 19:08 | 0 | 0 | 0 | 0.31806 | N-1740 | OSPD | S/D availed by NHAI for girder lauching at Faizabad Road 93.955 (LHS). (LILOED at Lucknow(PG))
NR140073 | 307046 | 400KV LUCKNOW-SULTANPR | 2018-07-08 20:46 | 2018-07-08 22:10 | 0 | 0.058333 | 0 | 0 | **** | OMSU | Tripped due to Y-B fault, Zone-3, Sultanpur (UP) S/S become dead. F.D.=464KM from Lucknow, F.C.=> Iy=1.154KA & Ib= 1.332KA at Lucknow.
NR140073 | 307177 | 400KV LUCKNOW-SULTANPR | 2018-07-28 11:30 | 2018-07-28 18:59 | 0 | 0 | 0 | 0.31181 | N-1740 | OSPD | S/D availed by NHAI for girder lauching at Faizabad Road 93.955 (LHS). (LILOED at Lucknow(PG))
NR140075 | 307037 | 400KV LUCKNOW-UNNAO-II | 2018-07-05 11:18 | 2018-07-05 16:37 | 0 | 0 | 0 | 0.22153 | N-286 | OSFD | Emergency S/D availed by UPPCL for attending hot spot at connector clamp between y-phase CB and Line side isolator at Unnao(UP) end.
NR140084 | 307038 | 400KV RIHAND-ALLD-I | 2018-07-05 12:12 | 2018-07-05 16:19 | 0.17153 | 0 | 0 | 0 | **** | SRMT | Tripped due to main MCB short circuit due to DC positive and negative mix cause main-1 relay REL 521 internal short circuit resulting differential protection operated at Allahabad.
NR140084 | 307111 | 400KV RIHAND-ALLD-I | 2018-07-21 03:42 | 2018-07-21 21:34 | 0 | 0 | 0.74444 | 0 | **** | LNCC | Tripped due to B-N(Top phase) fault due to bad weather condition in fault area. FD: 169kM(M1), 173.1kM(M2) from Allahabad and 125.5kM from Rihand end. FC: 2.333kA(M1), 2.6kA(M2) from Allahabad. Fault in Mirzapur jurisdiction. Charging attempt taken at 0413 hrs from Rihand end but tripped immediately on B-N fault.118kM from Rihand end. again Charging attempt taken at 0435 hrs from Alld end but tripped immediately on SOTF on B-N fault.ALLD: 137kM , 2.735kA. Agrain Charging attempt taken at 1711 hrs dtd 21.07.18 hrs from Rihand end but tripped immediately on B-N fault.120kM from Rihand end.
NR140084 | 307122 | 400KV RIHAND-ALLD-I | 2018-07-21 21:34 | 2018-07-23 10:19 | 1899-12-31 12:45 | 0 | 0 | 0 | N-1317 | OSFT | Emergency S/D availed for replacement of faulty porcelain disc insulator string at location No 343 and 344. charging attempt taken at 1514hrs on 22.07.2018 from Rihand end but line could not hold due to B-N fault. Fault distance =120KM from Rihand. During patrolling insulator De-capping found at Loc. No. 356 (Mirzapur jurisdiction)
NR140085 | 307047 | 400KV RIHAND-ALLD-II | 2018-07-09 10:45 | 2018-07-09 17:47 | 0.29306 | 0 | 0 | 0 | N-488 | OSPT | E/S/D availed for attending hot spot in R-phase Line side jumper T connector at Allahabad.
NR140111 | 307079 | 400KV SING-FATEHPUR | 2018-07-13 13:25 | 2018-07-13 13:25 | 0 | 0 | 0 | 0 | **** | LART | Auto-reclosed successfully at both end on Y-N fault(left phase). FD: 222.17kM(M1), 222.18kM(M2) from Fatehpur and 127.1kM from Singrauli. FC: 1.52kA(M1), 1.57kA(M2) at Fatehpur and 2.81kA at Singrauli. Fault in Mirzapur jurisdiction.
NR140095 | 307026 | 400KV SING-LKO(UP)-I | 2018-07-04 10:20 | 2018-07-04 15:51 | 0 | 0 | 0 | 0.22986 | N-195 | OSFD | Emergency S/D availed by UPPCL for attending hot spot in line isolator and 4th IPS pipe clamp of Y & B phase of Bus-1 isolator at Lucknow(UP) end. CPCC code was not taken by UPPCL.
NR140095 | 307039 | 400KV SING-LKO(UP)-I | 2018-07-05 13:18 | 2018-07-05 14:45 | 0.060417 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault. FD: 270.5kM(M2) from Lucknow(UP). FC:0.95kA at Lucknow(UP). Singrauli: No distance display in relay. Line was auto-reclosed(M1) from Lucknow(UP) but A/R lockout(Main 2) protection operated at Lucknow(UP) end but tripped from Singrauli end. Fault in Mirzapur jurisdiction.
N-W40001 | 307061 | 400KV SING-VINDH-I | 2018-07-11 12:03 | 2018-07-11 18:11 | 0.25556 | 0 | 0 | 0 | N-639 | OSFT | Emergency S/D availed to attend hot spot in main bay R Ph isolator AWL-3 trapezee contact at Vindhyachal
NR340004 | 307051 | 400KV VARANASI-SARNATH-I | 2018-07-10 08:10 | 2018-07-11 23:37 | 0 | 0 | 0 | 1899-12-31 15:27 | N-545 | OSPD | S/D availed by UPPCL for general maintenance work at their end.
NR340005 | 307040 | 400KV VARANASI-SARNATH-II | 2018-07-06 08:32 | 2018-07-08 02:03 | 0 | 0 | 0 | 1899-12-31 17:31 | N-344 | OSPD | S/D availed by UPPCL for general maintenanace work
NR340005 | 307057 | 400KV VARANASI-SARNATH-II | 2018-07-10 19:15 | 2018-07-10 20:01 | 0 | 0.031944 | 0 | 0 | **** | OMSU | Tripped only from Sarnath end due to some problem at Sarnath(UP) end. No replay indication at Varanasi end. Sarnath- O/V Stage-1, Y Ph, 3 Ph alarm
NR340005 | 307092 | 400KV VARANASI-SARNATH-II | 2018-07-17 12:03 | 2018-07-17 14:47 | 0 | 0 | 0 | 0.11389 | N-1024 | OSPD | S/D availed by UPPCL to PLCC problem at their end Sarnath (UP)
BILUP2202 | 307084 | 220KV ALLD-REWA RD-I | 2018-07-16 10:59 | 2018-07-16 19:23 | 0 | 0 | 0 | 0.35 | N-967 | OSFD | E/S/D availed by UPPCL for replacement of bunt Bus isolator jaw at Rewa Road(UP) end
BILUP2202 | 307084 | 220KV ALLD-REWA RD-I | 2018-07-14 19:52 | 2018-07-14 20:35 | 0 | 0.029861 | 0 | 0 | **** | OMSU | Line tripped from Rewa road(UP) end only due to problem at UPPCL end
BILUP2203 | 307085 | 220KV ALLD-REWA RD-II | 2018-07-16 10:59 | 2018-07-16 19:23 | 0 | 0 | 0 | 0.35 | N-967 | OSFD | E/S/D availed by UPPCL for replacement of bunt Bus isolator jaw at Rewa Road(UP) end
BILUP2203 | 307085 | 220KV ALLD-REWA RD-II | 2018-07-14 19:52 | 2018-07-14 20:35 | 0 | 0.029861 | 0 | 0 | **** | OMSU | Line tripped from Rewa road(UP) end only due to problem at UPPCL end
NR122006 | 307192 | 220KV AUR-SIKANDARA-I | 2018-07-30 00:05 | 2018-07-30 04:15 | 0 | 0.17361 | 0 | 0 | **** | OMSU | Tripped only from Auraiya(NTPC) end due to B-N fault.Z1. Due to some problem at NTPC, Auraiya end.
NR122006 | 307201 | 220KV AUR-SIKANDARA-I | 2018-07-30 04:15 | 2018-07-30 13:13 | 0 | 0 | 0 | 0.37361 | N-1842 | OSFD | Emergency S/D availed by NTPC, Auraiya to attend relay problem at their end.
NR122007 | 307020 | 220KV AUR-SIKANDARA-II | 2018-07-03 14:33 | 2018-07-03 23:45 | 0.38333 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault. FD: Sikandra- 114.5km, FC: Sikandra- 7.978km. After patrolling by Auraiya group, R Ph jumper found opened at loc no 190.
NR122012 | 307147 | 220KV DGANGA-BLY(UP)-II | 2018-07-25 14:49 | 2018-07-25 17:24 | 0 | 0.10764 | 0 | 0 | **** | OMSU | Tripped due to fault at Dhauliganaga(NHPC) S/S. Dhauliganga (NHPC) S/S become dead.
NR122012 | 307011 | 220KV DGANGA-BLY(UP)-II | 2018-07-02 13:10 | 2018-07-02 15:05 | 0 | 0 | 0 | 0.079861 | N-66 | OSFD | Emergency S/D availed by Dhauliganga(NHPC) for CB rectification work at Dhauliganga
NR122012 | 307189 | 220KV DGANGA-BLY(UP)-II | 2018-07-29 16:57 | 2018-07-29 17:52 | 0 | 0 | 0.038194 | 0 | **** | GGDC | Tripped due to Power swing block at Dhauliganga as reported by Dhauliganga. All generation unit tripped at Dhauliganga. Heavy rain and thunder storm reported at Dhauliganga.
NR122013 | 307148 | 220KV DGANGA-PITHORAGRH | 2018-07-25 14:49 | 2018-07-25 17:26 | 0 | 0.10903 | 0 | 0 | **** | OMSU | Tripped due to fault at Dhauliganaga(NHPC) S/S. Dhauliganga (NHPC) S/S become dead.
NR122013 | 307188 | 220KV DGANGA-PITHORAGRH | 2018-07-29 16:56 | 2018-07-30 14:51 | 0 | 0 | 0.91319 | 0 | **** | LNCC | Tripped due to R-N fault due to heavy rain and thunder storm reported at faulty area. FD: 52.15kM(M1), 41.01kM from Pithoragarh and 7kM from Dhauliganga. FC: 1.336kA at Pithoragarh. Fault in Pithoragarh jurisdiction. Charging attempt taken at 1726 hrs but line tripped immediately on R-N fault. 52.15kM from Pithoragarh. R phase jumper snapped at location No-21.
NR122038 | 307104 | 220KV FATEHPUR-FTHPR(UP)-I | 2018-07-19 11:58 | 2018-07-19 13:20 | 0 | 0 | 0 | 0.056944 | N-1149 | OSFD | Emergency S/D availed by UPPCL for maintenance work at their end.
NR122040 | 307007 | 220KV FATEHPUR-KNP SOUTH | 2018-07-02 07:25 | 2018-07-02 13:26 | 0 | 0.25069 | 0 | 0 | **** | OMSU | Tripped due to R-N fault. FD: FTPR-55.7km, FC: FTPR-3.159KA. Fault in UPPCL jurisdiction
NR122040 | 307205 | 220KV FATEHPUR-KNP SOUTH | 2018-07-30 23:12 | 2018-07-31 00:01 | 0 | 0.034028 | 0 | 0 |  | OMSU | Tripped only from UPPCL/Kanpur(South) end due to B-N fault,F.D.=25km from Fatehpur,F.C.=5.5KA (UPPCL Jurisdiction)
NR320001 | 307154 | 220KV KANPUR(PG) - RANIYA( UP)-1 | 2018-07-26 05:57 | 2018-07-26 14:09 | 0 | 0 | 0 | 0.34167 | **** | OSFD | Emergency H/T from Rania(UP) end only due to problem at Rania(UP)
NR122033 | 307213 | 220KV TNKPR-BLY(UP) | 2018-07-31 12:20 | 2018-07-31 14:06 | 0 | 0.073611 | 0 | 0 | **** | OMSU | Tripped only from UPPCL/BLY(UP) end due to problem at their end
NR122035 | 307075 | 220KV UNCHR-RAIBRLY-I | 2018-07-13 12:17 | 2018-07-13 19:22 | 0 | 0 | 0 | 0.29514 | N-776 | OSFD | Emergency S/D availed by Unchahar(NTPC) for rectification of CB problem at Unchahar(NTPC) ned.
NR3ICT01 | 307097 | 315MVA ICT-2 Agra | 2018-07-18 14:29 | 2018-07-18 20:12 | 0.23819 | 0 | 0 | 0 | N-1088 | OSPT | S/D availed for commissioning of CSD relay
NR1ICT01 | 307019 | 315MVA ICT-I ALLAHABAD | 2018-07-03 08:23 | 2018-07-03 17:36 | 0.38403 | 0 | 0 | 0 | N-103 | OSPT | S/D availed for application of insulator sleeve on 33KV tertiary conductor
NR3ICT04 | 307086 | 200MVA ICT-II RAIBAREILLY | 2018-07-16 13:28 | 2018-07-16 16:37 | 0.13125 | 0 | 0 | 0 | N-975 | OSPT | S/D availed for application of sealants and rain canopy over the PRD/OSR and buchholtz relay to avoid any moisture ingress.
NR1ICT39 | 307096 | 200MVA ICT-III RAIBAREILLY | 2018-07-18 11:37 | 2018-07-18 15:30 | 0.16181 | 0 | 0 | 0 | N-1083 | OSFT | Emergency S/D availed for installation of rain canopy over the Buccholz/PRD/OSR
NR1ICT47 | 307062 | 100MVA ICT-I RAIBAREILLY | 2018-07-11 13:38 | 2018-07-11 16:00 | 0.098611 | 0 | 0 | 0 | N-647 | OSPT | S/D availed for installation of rain canopy in RPD/OSR and Buccholz relay to avoid any moisture ingress
NR3BRT09 | 307048 | 330MVAR B/Reactor-I ALIGARH | 2018-07-09 14:14 | 2018-07-09 18:09 | 0 | 0 | 0 | 0.16319 | N-501 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=753kV
NR3BRT09 | 307052 | 330MVAR B/Reactor-I ALIGARH | 2018-07-10 09:18 | 2018-07-11 06:20 | 0 | 0 | 0 | 0.87639 | N-554 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=760kV
NR1BRT55 | 307044 | 330MVAR B/Reactor-I VARANASI | 2018-07-08 10:38 | 2018-07-08 17:59 | 0.30625 | 0 | 0 | 0 | N-453 | OSPT | Taken under S/D for VFTO test.
NR1BRT55 | 307056 | 330MVAR B/Reactor-I VARANASI | 2018-07-10 19:55 | 2018-07-11 06:18 | 0 | 0 | 0 | 0.43264 | N-599 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=772kV
NR1BRT23 | 307049 | 330MVAR B/Reactor-III FTHPR-765 | 2018-07-09 14:45 | 2018-07-11 06:24 | 0 | 0 | 0 | 1899-12-31 15:39 | N-505 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=749kV
NR1BRT23 | 307217 | 330MVAR B/Reactor-III FTHPR-765 | 2018-07-31 10:04 | 2018-08-01 | 0 | 0 | 0 | 0.58056 | N-1917 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=747kV
NR1BRT32 | 307031 | 240MVAR B/Reactor-I BALIA-765 | 2018-07-04 19:52 | 2018-07-21 07:00 | 0 | 0 | 0 | 1900-01-15 11:08 | N-245 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=745kV
NR1BRT32 | 307031 | 240MVAR B/Reactor-I BALIA-765 | 2018-07-04 19:52 | 2018-07-21 07:00 | 0 | 0 | 0 | 1900-01-15 11:08 | N-245 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=745kV
NR1BRT50 | 306192 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-07-01 | 2018-07-02 09:10 | 0 | 0 | 0 | 1899-12-31 09:10 | N-2265 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=755kV
NR1BRT50 | 307030 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-07-04 19:52 | 2018-07-10 06:29 | 0 | 0 | 0 | 1900-01-04 10:37 | N-243 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=759kV
NR1BRT50 | 307066 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-07-11 19:45 | 2018-07-12 05:45 | 0 | 0 | 0 | 0.41667 | N-669 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=753kV
NR1BRT50 | 307089 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-07-17 00:43 | 2018-07-21 05:26 | 0 | 0 | 0 | 1900-01-03 04:43 | N-1002 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=745kV
NR1BRT50 | 307128 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-07-22 20:25 | 2018-07-23 07:24 | 0 | 0 | 0 | 0.45764 | N-1351 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=750kV
NR1BRT50 | 307134 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-07-23 19:04 | 2018-07-24 06:00 | 0 | 0 | 0 | 0.45556 | N-1428 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=755kV
NR1BRT28 | 307032 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2018-07-04 19:53 | 2018-07-14 07:17 | 0 | 0 | 0 | 1900-01-08 11:24 | N-244 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=756kV
NR1BRT28 | 307083 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2018-07-15 23:28 | 2018-07-21 07:16 | 0 | 0 | 0 | 1900-01-04 07:48 | N-900 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=753kV
NR1BRT28 | 307129 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2018-07-22 20:28 | 2018-07-23 07:27 | 0 | 0 | 0 | 0.45764 | N-1352 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV
NR1BRT28 | 307136 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2018-07-23 22:51 | 2018-07-24 10:49 | 0 | 0 | 0 | 0.49861 | N-1442 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV
NR1BRT28 | 307181 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2018-07-28 23:32 | 2018-08-01 | 0 | 0 | 0 | 1900-01-02 00:28 | N-1792 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=748kV
NR1BRT21 | 307137 | 125MVAR B/Reactor LUCKNOW-765 | 2018-07-23 22:53 | 2018-07-24 10:51 | 0 | 0 | 0 | 0.49861 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV
NR1BRT39 | 306184 | 125MVAR B/Reactor-I Gorakhpur | 2018-07-01 | 2018-07-21 08:10 | 0 | 0 | 0 | 1900-01-19 08:10 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=395kV
NR1BRT39 | 307123 | 125MVAR B/Reactor-I Gorakhpur | 2018-07-22 00:33 | 2018-07-26 05:46 | 0 | 0 | 0 | 1900-01-03 05:13 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=385kV
| 307088 | 125MVAR B/Reactor-I SHAHJHNPR | 2018-07-17 00:22 | 2018-07-17 10:41 | 0 | 0 | 0 | 0.42986 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Shahjahanpur=388kV
NR1BRT17 | 306135 | 125MVAR B/Reactor-II BALIA | 2018-07-01 | 2018-07-09 16:33 | 0 | 0 | 0 | 1900-01-07 16:33 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
NR1BRT17 | 307121 | 125MVAR B/Reactor-II BALIA | 2018-07-21 20:03 | 2018-07-25 07:33 | 0 | 0 | 0 | 1900-01-02 11:30 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=395kV
NR1BRT46 | 307055 | 125MVAR B/Reactor-II Gorakhpur | 2018-07-10 19:50 | 2018-07-21 08:10 | 0 | 0 | 0 | 1900-01-09 12:20 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=383kV
NR1BRT46 | 307124 | 125MVAR B/Reactor-II Gorakhpur | 2018-07-22 00:33 | 2018-07-26 09:10 | 0 | 0 | 0 | 1900-01-03 08:37 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=385kV
NR1BRT16 | 307099 | 125MVAR B/Reactor-II LUCKNOW | 2018-07-19 01:20 | 2018-07-25 08:45 | 0 | 0 | 0 | 1900-01-05 07:25 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Low voltage at Sitarganj-190KV
NR1BRT27 | 306134 | 125MVAR B/Reactor-III BALIA | 2018-07-01 | 2018-08-01 | 0 | 0 | 0 | 1900-01-30 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
NR1BRT03 | 306183 | 80MVAR B/Reactor BAREILLY | 2018-07-01 | 2018-07-25 07:30 | 0 | 0 | 0 | 1900-01-23 07:30 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=398kV
NR1BRT10 | 307098 | 80MVAR B/Reactor LUCKNOW | 2018-07-19 01:18 | 2018-07-25 08:54 | 0 | 0 | 0 | 1900-01-05 07:36 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Low voltage at Sitarganj-190KV
NR1BRT44 | 306100 | 2x50MVAR B/Reactor BAREILLY | 2018-07-01 | 2018-07-25 07:30 | 0 | 0 | 0 | 1900-01-23 07:30 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=392kV
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="T",(+[RESTORATION]-[OUTAGE]),0))
OTHERS = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="U",(+[RESTORATION]-[OUTAGE]),0))
Hrs:Min = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="C",(+[RESTORATION]-[OUTAGE]),0))
Deemed Available = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="D",(+[RESTORATION]-[OUTAGE]),0))

## Sheet3 (hidden)
400kv LINES |  |  |  | 220kv LINES |  | ICTs,HVDC & SVC. |  | OTHER LINES
400kv LINES NR-I |  | 400kv LINES NR-III |  | 220kv LINES & ICT & Reactor NR-I |  | 220kv LINES & ICT & Reactor NR-III
400KV AGRA-JAIPUR(S)-I | 1 | 400KV AGRA-FATEHABD(UP)-I | 1 | 220KV ANTA-BHIL-I | 1 | 220KV ALLD-JHUSI(UP) | RRVPNL | 220KV BASSI-KUKAS-I
400KV AGRA-JAIPUR(S)-II | 2 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2 | 220KV ANTA-BHIL-II | 2 | 220KV ALLD-REWA RD-I | RRVPNL | 220KV BASSI-KUNDA KI DHANI
400KV AGRA-SIKAR-I | 3 | 400KV AGRA-AGRA(UP)-II | 3 | 220KV ANTA-LALSOT | 3 | 220KV ALLD-REWA RD-II | RRVPNL | 220KV BHIWADI(PG)-BHIWADI
400KV AGRA-SIKAR-II | 4 | 400KV AGRA-AURAIYA-I | 4 | 220KV ANTA-RAPPC | 4 | 220KV AUR-SIKANDARA-I | RRVPNL | 220KV BHIWADI-KHUSHKHERA-I
400KV BASSI-BHIWADI-I | 5 | 400KV AGRA-AURAIYA-II | 5 | 220KV ANTA-S.MDHPR | 5 | 220KV AUR-SIKANDARA-II | RRVPNL | 220KV BHIWADI-KHUSHKHERA-II
400KV BASSI-HIRAPURA-I | 6 | 400KV AGRA-BASSI-I | 6 | 220KV BASSI-BAGRU | 6 | 220KV DGANGA-BLY(UP)-II | RRVPNL | 220KV BHIWADI-NIMRANA(RJ)
400KV BASSI-HIRAPURA-II | 7 | 400KV AGRA-BHIWADI-I | 7 | 220KV BASSI-DAUSA-I | 7 | 220KV DGANGA-PITHORAGRH | RRVPNL | 220KV BHINMAL-BHINMAL-I
400KV BASSI-JAIPUR(S)-I | 8 | 400KV AGRA-BHIWADI-II | 8 | 220KV BASSI-DAUSA-II | 8 | 220KV FATEHPUR-FTHPR(UP)-I | RRVPNL | 220KV BHINMAL-BHINMAL-II
400KV BASSI-JAIPUR(S)-II | 9 | 400KV AGRA-BLBGRH | 9 | 220KV BASSI-IG NAGAR | 9 | 220KV FATEHPUR-FTHPR(UP)-II | RRVPNL | 220KV BHINMAL-SANCHORE
400KV BASSI-KOTPUTLI | 10 | 400KV ALLD-FATEHPUR-I | 10 | 220KV FGPP-PALLA-I | 10 | 220KV FATEHPUR-KNP SOUTH | RRVPNL | 220KV BHINMAL-SIROHI
400KV BASSI-PHAGI-I | 11 | 400KV ALLD-FATEHPUR-II | 11 | 220KV FGPP-PALLA-II | 11 | 220KV FATEHPUR-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-CHAKSU-I |  | LEGENDS
400KV BASSI-PHAGI-II | 12 | 400KV ALLD-FATEHPUR-III | 12 | 220KV FGPP-SPUR-I | 12 | 220KV JHUSI(UP)-PHULPUR(UP) | RRVPNL | 220KV JAIPUR(S)-CHAKSU-II
400KV BHINMAL-ZERDA | 13 | 400KV ALLD-KNP-II | 13 | 220KV FGPP-SPUR-II | 13 | 220KV KNP-MAINPURI | RRVPNL | 220KV JAIPUR(S)-SEZ |  |  | Lines maintained by ER
400KV BHIWADI-GURGAON | 14 | 400KV ALLD-VARANASI | 14 | 220KV HIRAPURA-IG NAGAR | 14 | 220KV KNP-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-DOONI
400KV BHIWADI-HISAR-I | 15 | 400KV BALIA-MAU-I | 15 | 220KV HIRAPURA-SANGANER | 15 | 220 KV KANPUR(PG) - RANIYA( UP)-1 | RRVPNL | 220KV KANKROLI(PG)-BHILWARA
400KV BHIWADI-KOTPUTLI | 16 | 400KV BALIA-MAU-II | 16 | 220KV LALSOT-DAUSA | 16 | 220 KV RANIYA( UP) - PANKI (UP)-1 | RRVPNL | 220KV KANKROLI(PG)-KANK-I
400KV BHIWADI-NIMRANA-I | 17 | 400KV BALIA-SOHAWAL-I | 17 | 220KV MEERUT-MPURAM-I | 17 | 220KV KNP-PANKI-II | RRVPNL | 220KV KANKROLI(PG)-KANK-II
400KV BHIWADI-NIMRANA-II | 18 | 400KV BALIA-SOHAWAL-II | 18 | 220KV MEERUT-MPURAM-II | 18 | 220KV KNP-UNCHR-I | RRVPNL | 220KV KANKROLI-DEBARI |  |  | lines maintained by WR
400KV BLBGRH-GURGAON | 19 | 400KV BAREILLY-BRLY(765)-I | 19 | 220KV MEERUT-NARA | 19 | 220KV KNP-UNCHR-II | RRVPNL | 220KV KOTA-KTPS-1
400KV BLBGRH-MAHRANIBG | 20 | 400KV BAREILLY-BRLY(765)-II | 20 | 220KV MEERUT-SHTBDNGR | 20 | 220KV KNP-UNCHR-III | RRVPNL | 220KV KOTA-KTPS-2 |  |  | LILO portions only of POWERGRID
400KV BLBGRH-NAVADA(HVPN) | 21 | 400KV BAREILLY-BRLY(UP)-I | 21 | 220KV MEERUT-SIMBHOLI | 21 | 220KV KNP-UNCHR-IV | RRVPNL | 220KV KOTA-BHILWARA
400KV DAD-GR.NOIDA | 22 | 400KV BAREILLY-BRLY(UP)-II | 22 | 220KV RAPPB-CHITT-I | 22 | 220KV PITHORAGRH-BRLY(UP) | RRVPNL | 220KV KOTA-DHUNI |  |  | LILO portion maintained by constituents
400KV DAD-MAHRANIBG | 23 | 400KV BAREILLY-LKO(UP) | 23 | 220KV RAPPB-CHITT-II | 23 | 220KV RAIBRLY-CHINHAT | RRVPNL | 220KV KOTPUTLI-KOTPUTLI
400KV DAD-MANDOLA-I | 24 | 400KV BAREILLY-MBAD-I | 24 | 220KV RAPPB-RAPPC | 24 | 220KV RAIBRLY-LKO(UP) | RRVPNL | 220KV KOTPUTLI-MANOHARPUR
400KV DAD-MANDOLA-II | 25 | 400KV BAREILLY-MBAD-II | 25 | 220KV RAPPB-UDAIPUR | 25 | 220KV SITARGANJ-BLY(UP) | RRVPNL | 220KV NIMRANA-NIMRANA
400KV DAD-MURADNGR | 26 | 400KV BAREILLY-ROSA-I | 26 | 220KV S.MDHPR-DAUSA-I | 26 | 220KV TNKPR-BLY(UP) | RRVPNL | 220KV NIMRANA-KHUSHKHERA |  |  | Maintained by NR-1 & NR-II
400KV DAD-PANIPAT-I | 27 | 400KV BAREILLY-SHAHJHNPR-I | 27 | 220KV SIKAR-RATANGARH-I | 27 | 220KV TNKPR-SITARGANJ | HVPNL | 220KV BHIWADI-MAU
400KV DAD-PANIPAT-II | 28 | 400KV BAREILLY-SHAHJHNPR-II | 28 | 220KV SIKAR-RATANGARH-II | 28 | 220KV UNCHR-RAIBRLY-I | HVPNL | 220KV BHIWADI-REWARI-I
400KV GURGAON-MANESAR-I | 29 | 400KV BARLY(765)-KASHIPUR-I | 29 | 220KV SIKAR-SIKAR(RJ)-I | 29 | 220KV UNCHR-RAIBRLY-II | HVPNL | 220KV BHIWADI-REWARI-II
400KV GURGAON-MANESAR-II | 30 | 400KV BARLY(765)-KASHIPUR-II | 30 | 220KV SIKAR-SIKAR(RJ)-II | 30 | 220KV UNCHR-RAIBRLY-III | HVPNL | 220KV BHIWADI-BAWAL
400KV JHATIKALA-BAMNOLI-I | 31 | 400KV BLBGRH-MAINPURI-I | 31 | 220KV HISAR-HISAR I/A-I |  |  | HVPNL | 220KV GURGAON-GURGAON-I
400KV JHATIKALA-BAMNOLI-II | 32 | 400KV BLBGRH-MAINPURI-II | 32 | 220KV HISAR-HISAR I/A-II |  |  | HVPNL | 220KV GURGAON-GURGAON-II
400KV JHATIKALA-MUNDKA-I | 33 | 400KV FATEHPUR-MAINPURI-I |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-III
400KV JHATIKALA-MUNDKA-II | 34 | 400KV FATEHPUR-MAINPURI-II |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-IV
400KV KANKROLI-BHINMAL | 35 | 400KV GORAKH-GORAKH-I |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-I
400KV KANKROLI-JODHPUR | 36 | 400KV GORAKH-GORAKH-II |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-II
400KV KANKROLI-CHITTOR(RJ)-I | 37 | 400KV KNP-AGRA |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-I
400KV KANKROLI-RAPPC-II | 38 | 400KV KNP-AURAIYA-I |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-II
400KV KANKROLI-ZERDA-I | 39 | 400KV KNP-AURAIYA-II |  | 400KV & 220KV ICT NR-I |  |  | HVPNL | 220 KV MANESAR-BADSHAHPUR-I
400KV KOTA-BEAWAR | 40 | 400KV KNP-BLBGARH-I | 1 | 315MVA ICT-I BASSI |  | 400KV & 220KV ICT NR-III | HVPNL | 220 KV MANESAR-BADSHAHPUR-II
400KV KOTA-MERTA-I | 41 | 400KV KNP-BLBGARH-II | 2 | 315MVA ICT-II BASSI | 1 | 315MVA ICT-I AGRA | HVPNL | 220 KV MANESAR-MAU-I
400KV KOTA-RAPPC | 42 | 400KV KNP-BLBGARH-III | 3 | 500MVA ICT-III BASSI | 2 | 315MVA ICT-I ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-II
400KV KOTESHWR-KHEP-I | 43 | 400KV KNP-FATEHPUR-I | 4 | 315MVA ICT-III BAWANA | 3 | 315MVA ICT-II ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-III
400KV KOTESHWR-KHEP-II | 44 | 400KV KNP-FATEHPUR-II | 5 | 315MVA ICT-I BHINMAL | 4 | 315MVA ICT-III ALLAHABAD | HVPNL | 220 KV SONIPAT-MOHANA-I
400KV KOTESHWR-TEHRI-I | 45 | 400KV KNP-PANKI-I | 6 | 315MVA ICT-II BHINMAL | 5 | 315MVA ICT-I FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-I
400KV KOTESHWR-TEHRI-II | 46 | 400KV KNP-PANKI-II | 7 | 315MVA ICT-I BHIWADI | 6 | 315MVA ICT-II FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-II
400KV MBAD-MURADNGR | 47 | 400KV LUCKNOW-GORAKH-III | 8 | 315MVA ICT-II BHIWADI | 7 | 315MVA ICT-I GORAKHPR | HVPNL | 220KV HISAR-SRWL-I
400KV MEERUT-BAGPAT-I | 48 | 400KV LUCKNOW-GORAKH-IV | 9 | 315MVA ICT-III BHIWADI | 8 | 315MVA ICT-II GORAKHPR | HVPNL | 220KV HISAR-SRWL-II
400KV MEERUT-BAREILLY-I | 49 | 400KV LUCKNOW-LKO(765)-I | 10 | 500MVA ICT-I BLBGARH | 9 | 315MVA ICT-I KANPUR | HVPNL | 220KV HISAR-FATEHABAD-I
400KV MEERUT-BAREILLY-II | 50 | 400KV LUCKNOW-LKO(765)-II | 11 | 315MVA ICT-II BLBGARH | 10 | 315MVA ICT-II KANPUR | HVPNL | 220KV HISAR-FATEHABAD-II
400KV MEERUT-KOTESHWR-I | 51 | 400KV LUCKNOW-LKO(UP) | 12 | 315MVA ICT-III BLBGARH | 11 | 315MVA ICT-I LUCKNOW | NTPC | 132KV SING-VINDH-RIH
400KV MEERUT-KOTESHWR-II | 52 | 400KV LUCKNOW-ROSA-I | 13 | 315MVA ICT-IV BLBGARH | 12 | 500MVA ICT-II LUCKNOW | NTPC | 132KV SING-RENUSAGAR-PIPRI
400KV MEERUT-MND-I | 53 | 400KV LUCKNOW-SHAHJHNPR-I | 14 | 315MVA ICT-I GURGAON | 13 | 315MVA ICT-I MAINPURI | DTL | 400KV B'GARH-BAMNOLI-I
400KV MEERUT-MND-II | 54 | 400KV LUCKNOW-SHAHJHNPR-II | 15 | 315MVA ICT-II GURGAON | 14 | 315MVA ICT-II MAINPURI | DTL | 400KV B'GARH-BAMNOLI-II
400KV MEERUT-MND-III | 55 | 400KV LUCKNOW-SOHAWAL-I | 16 | 500MVA ICT-I JAIPUR(S) | 15 | 100MVA ICT-I PITHORAGRH | DTL | 400KV MND-BAWANA-I
400KV MEERUT-MND-IV | 56 | 400KV LUCKNOW-SOHAWAL-II | 17 | 500MVA ICT-II JAIPUR(S) | 16 | 100MVA ICT-II PITHORAGRH | DTL | 400KV MND-BAWANA-II
400KV MEERUT-MUZFRNGR | 57 | 400KV LUCKNOW-SULTANPR | 18 | 315MVA ICT-I KANKROLI | 17 | 100MVA ICT-I RAIBAREILLY | DTL | 220KV MND-S.WZRBD-I
400KV MERTA-BEAWAR | 58 | 400KV LUCKNOW-UNNAO-I | 19 | 315MVA ICT-II KANKROLI | 18 | 100MVA ICT-II RAIBAREILLY | DTL | 220KV MND-S.WZRBD-II
400KV NAVADA(HVPN)-GR.NOIDA | 59 | 400KV LUCKNOW-UNNAO-II | 20 | 315MVA ICT-III KANKROLI | 19 | 100MVA ICT-III RAIBAREILLY | DTL | 220KV MND-S.WZRBD-III
400KV NIMRANA-MANESAR-I | 60 | 400KV MEERUT-BAREILLY-I | 21 | 315MVA ICT-I KOTA | 20 | 500MVA ICT-I SHAHJHNPR | DTL | 220KV MND-S.WZRBD-IV
400KV NIMRANA-MANESAR-II | 61 | 400KV MEERUT-BAREILLY-II | 22 | 315MVA ICT-II KOTA | 21 | 500MVA ICT-II SHAHJHNPR | DTL | 220KV MND-NARELA-I
400KV NIMRANA-SIKAR-I | 62 | 400KV RIHAND-ALLD-I | 23 | 315MVA ICT-I KOTPUTLI | 22 | 100MVA ICT-I SITARGANJ | DTL | 220KV MND-NARELA-II
400KV NIMRANA-SIKAR-II | 63 | 400KV RIHAND-ALLD-II | 24 | 315MVA ICT-II KOTPUTLI | 23 | 100MVA ICT-II SITARGANJ | DTL | 220KV MND-GOPALPUR-I
400KV ROORKI-KASHIPUR-I | 64 | 400KV RIHAND3-VINDH(Pool)-I | 25 | 315MVA ICT-I MAHRANIBAG | 24 | 315MVA ICT-I SOHAWAL | DTL | 220KV MND-GOPALPUR-II
400KV ROORKI-KASHIPUR-II | 65 | 400KV RIHAND3-VINDH(Pool)-II | 26 | 315MVA ICT-II MAHRANIBAG | 25 | 315MVA ICT-II SOHAWAL | DTL | 220KV MBAG-SARITAVIHAR
400KV ROORKI-MUZFRNGR | 66 | 400KV SING-ALLD-I | 27 | 500MVA ICT-III MAHRANIBAG | 26 |  | DTL | 220KV MBAG-LODHIROAD-I
400KV ROORKI-RISHIKESH | 67 | 400KV SING-ALLD-II | 28 | 500MVA ICT-IV MAHRANIBAG | 27 |  | DTL | 220KV MBAG-LODHIROAD-II
400KV SIKAR-RATANGARH-I | 68 | 400KV SING(NTPC)-ANPARA(UP) | 29 | 500MVA ICT-I MANDOLA | 28 |  | DTL | 220KV MBAG-I P EXTN
400KV SIKAR-RATANGARH-II | 69 | 400KV SING-FATEHPUR | 30 | 500MVA ICT-II MANDOLA | 29 |  | UPPCL | 220KV AGRA-SHAMSABD-I
400KV MEERUT-BAGPAT-II | 70 | 400KV SING-LKO(UP)-I | 31 | 500MVA ICT-III MANDOLA | 30 |  | UPPCL | 220KV AGRA-FEROZABAD
400KV ROORKI-SAHARANPUR-I | 71 | 400KV SING-RIHAND-I | 32 | 500MVA ICT-IV MANDOLA |  |  | UPPCL | 220KV BAGHPAT(PG)-BAGHPAT(UP)
400KV ROORKI-SAHARANPUR-II | 72 | 400KV SING-RIHAND-II | 33 | 500MVA ICT-I MANESAR |  |  | UPPCL | 220KV BAGHPAT-MURADNGR
400KV RAPPC-CHITTOR(RJ)-I | 73 | 400KV SING-VINDH-I | 34 | 500MVA ICT-II MANESAR |  |  | UPPCL | 220KV BAGHPAT-SHAMLI
| 74 | 400KV SING-VINDH-II | 35 | 315MVA ICT-I MEERUT |  |  | UPPCL | 220KV GORAKH-BARHUA
| 75 | 400KV KANPUR-KANPUR(GIS)-I | 36 | 315MVA ICT-II MEERUT |  | 765KV ICT NR-III | UPPCL | 220KV GORAKH-BASTI
| 76 | 400KV KANPUR-KANPUR(GIS)-II | 37 | 315MVA ICT-III MEERUT | 1 | 765/400KV ICT-I BALIA | UPPCL | 220KV LKO(PG)-Bakhsi Ka Talab
| 77 | 400KV VARANASI-SASARAM(ER) | 38 | 500MVA ICT-IV MEERUT | 2 | 765/400KV ICT-II BALIA | UPPCL | 220KV LKO(PG)-CHINHAT
400KV BAHADURGRH-BAWANA | 78 | 400KV VARANASI-SARNATH-I | 39 | 315MVA ICT-III MUZFRNGR | 3 | 765/400KV ICT-I LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-I
400KV BAHADURGRH-SONIPAT-I | 79 | 400KV VARANASI-SARNATH-II | 40 | 315MVA ICT-II NIMRANA | 4 | 765/400KV ICT-II LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-II
400KV BAHADURGRH-SONIPAT-II | 80 | 400KV ALLAHABAD-MEJA(NTPC)-I | 41 | 315MVA ICT-I ROORKI | 5 | 765/400KV ICT-I FATEHPUR | UPPCL | 220KV M'PURI-ETAH
400KV BHIWANI-BAWANA | 81 | 400KV BALIA-BIHARSHRF-I | 42 | 315MVA ICT-II ROORKI | 6 | 765/400KV ICT-II FATEHPUR | UPPCL | 220KV M'PURI-SIRSAGANJ-I
400KV BHIWANI-BHIWANI(BBMB) | 82 | 400KV BALIA-BIHARSHRF-II | 43 | 315MVA ICT-I SIKAR | 7 | 765/400KV ICT-I AGRA | UPPCL | 220KV M'PURI-M'PURI(UP)-II
400KV BHIWANI-HISAR-I | 83 | 400KV ALLD-SASARAM | 44 | 315MVA ICT-II SIKAR | 8 | 765/400KV ICT-II AGRA | UPPCL | 220KV M'PURI-FEROZBD
400KV BHIWANI-HISAR-II | 84 | 400KV BALIA-PATNA-I | 45 | 500MVA ICT-I BAGPAT | 9 | 765/400KV ICT-I BAREILLY | UPPCL | 400KV M'PURI-ORAI-I
400KV BHIWANI-HISAR-III | 85 | 400KV BALIA-PATNA-II | 46 | 500MVA ICT-II BAGPAT | 10 | 765/400KV ICT-II BAREILLY | UPPCL | 400KV M'PURI-PARICHA-II
400KV BHIWANI-JIND-I | 86 | 400KV BALIA-PATNA-III | 47 | 315MVA ICT-I SAHARANPUR | 11 | 765/400KV ICT-I VARANASI | UPPCL | 220KV MEERUT-GAJRAULA
400KV BHIWANI-JIND-II | 87 | 400KV BALIA-PATNA-IV | 48 | 315MVA ICT-II SAHARANPUR | 12 | 765/400KV ICT-II VARANASI | UPPCL | 220KV MEERUT-NEHTAUR
400KV FATEHABAD-HISAR | 88 | 400KV LKO(765)-KANPUR(GIS)-I |  |  | 13 | 765/400KV ICT-I KANPUR(GIS) | UPPCL | 220KV ORAI-KANPUR
400KV BHIWADI-HISAR-II | 89 | 400KV LKO(765)-KANPUR(GIS)-II |  |  | 14 | 765/400KV ICT-II KANPUR(GIS) | UPPCL | 400KV PANKI-MURADNGR
400KV BHIWADI-HISAR-III | [6 empty] | UPPCL | 220KV SHAHJHNP-HARDOI
400KV HISAR-BHIWANI(BBMB) | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-I | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-II |  | 400kv LINES of ER-1 in NR-III Availability |  | NR-I Additional ICT from NR-II |  |  | UPPCL | 220KV SOHAWAL(PG) - SOHAWAL(UP)
400KV KABULPR-BAHADURGRH | 1 | 400KV SASARAM-BIHARSHRF-I | 1 | 315MVA ICT-I BAHADURGARH |  | NR-III HVDC SYSTEM / SVC | UPPCL | 220KV UNCHR-RBRLY-I
400KV KABULPR-BHIWANI | 2 | 400KV SASARAM-BIHARSHRF-II | 2 | 500MVA ICT-II BAHADURGARH | 1 | 500KV HVDC R-D POLE-I | UPPCL | 220KV UNCHR-RBRLY-II
|  |  | 3 | 315MVA ICT-I HISAR | 2 | 500KV HVDC R-D POLE-II | PTCUL | 220KV ROORKI-HARDWAR
|  |  | 4 | 315MVA ICT-II HISAR | 3 | 500KV HVDC BALIA-BHWD POLE-I | PTCUL | 220KV ROORKI--RAMNAGAR
|  | 765 KV TRANS LINES NR-III | 5 | 315MVA ICT-III HISAR | 4 | 500KV HVDC BALIA-BHWD POLE-II | PTCUL | 132KV SITARGNJ(PG)-SITARGNJ(PTCUL)
765 KV TRANS LINES NR-I | 1 | 765KV AGRA-FATEHPUR-I | 6 | 315MVA ICT-I SONIPAT | 5 | 800KV HVDC AGRA-BNC POLE-I | PTCUL | 132KV PITHORAGRH-CHANDOK
765KV AGRA-JHATIKALA | 2 | 765KV AGRA-FATEHPUR-II | 7 | 315MVA ICT-II SONIPAT | 6 | 800KV HVDC AGRA-BNC POLE-II | PTCUL | 132KV PITHORAGRH-ALMORA
765KV BHIWANI-PHAGI(JPR)-I | 3 | 765KV AGRA-GR.NOIDA | 8 | 315MVA ICT-I BHIWANI | 7 | VINDH HVDC B/B BLOCK-I | PTCUL | 132KV PTRGRH-PTRGRH(PTCUL)
765KV MEERUT-GR.NOIDA | 4 | 765KV FATEHPUR-SASARAM | 9 | 315MVA ICT-II BHIWANI | 8 | VINDH HVDC B/B BLOCK-II | POWERLINK
765KV MOGA-BHIWANI | 5 | 765KV LUCKNOW-BALIA | 10 | 500MVA ICT-I JIND | 9 | SASARAM HVDC B/B | PLINK | 400KV LUCKNOW-GORAKH-I (PL)
765KV JHATIKALA-BHIWANI | 6 | 765KV LUCKNOW-BAREILLY | 11 | 500MVA ICT-II JIND | 10 | +/-140MVAR SVC-I KANPUR | PLINK | 400KV LUCKNOW-GORAKH-II (PL)
765KV MEERUT-BHIWANI | 7 | 765KV VARANASI-BALIA |  |  | 11 | +/-140MVAR SVC-II KANPUR | PLINK | 400KV GRKHPR-MZFRPR-I (PL)
765KV BHIWANI-PHAGI(JPR)-II | 8 | 765KV VARANASI-FATEHPUR |  |  |  |  | PLINK | 400KV GRKHPR-MZFRPR-II (PL)
| 9 | 765KV VARANASI-GAYA-I |  | 765KV ICT NR-I
| 10 | 765KV VARANASI-KANPUR(GIS)-I | 1 | 765/400KV ICT-I JHATIKALA
BUS REACTORS NR-I | 11 | 765KV VARANASI-KANPUR(GIS)-II | 2 | 765/400KV ICT-II JHATIKALA |  | SWITCABLE LINE REACTORS NR-III | NR-II | 400KV DAD-M'KOTLA
125MVAR B/Reactor-I BAGPAT | 12 | 765KV KANPUR(GIS)-JHATIKRA-I | 3 | 765/400KV ICT-III JHATIKALA | 1 | AGRA 240MVAR S/R FATEHPR line | NR-II | 400KV BAGHPAT-KAITHAL-I
50MVAR B/Reactor-I BASSI |  |  | 4 | 765/400KV ICT-IV JHATIKALA | 2 | AGRA 50MVAR S/R BHIWADI-I LINE | NR-II | 400KV BAGHPAT-KAITHAL-II
50MVAR B/Reactor-II BASSI |  |  | 5 | 765/400KV ICT-I MEERUT | 3 | ALLHBD 50MVAR S/R MNPR-I LINE | NR-II | 765KV MEERUT-MOGA
50MVAR B/Reactor-III BASSI |  | BUS REACTORS NR-III | 6 | 765/400KV ICT-II MEERUT | 4 | ALLHBD 50MVAR S/R MNPR-II LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-I | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
125MVAR B/Reactor-IV BASSI | 1 | 125MVAR B/Reactor-I AGRA | 7 | 765/400KV ICT-I BHIWANI | 5 | BARLLY 50MVAR S/R MND-I LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-II | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
80MVAR B/Reactor BHINMAL | 2 | 125MVAR B/Reactor-II AGRA | 8 | 765/400KV ICT-II BHIWANI | 6 | BARLLY 50MVAR S/R MND-II LINE | NR-II | 400KV HISAR-MOGA-I
80MVAR B/Reactor BHIWADI | 3 | 240MVAR B/Reactor-II AGRA-765 |  |  | 7 | BALIA 240MVAR S/R LUCKNW Ckt-I | NR-II | 400KV HISAR-MOGA-II
80MVAR B/Reactor BLBGARH | 4 | 240MVAR B/Reactor-1 AGRA-765 |  |  | 8 | BALIA 240MVAR S/R GAYA Line | NR-II | 400KV HISAR-MOGA-III
125MVAR B/Reactor-I JAIPUR(S) | 5 | 80MVAR B/Reactor ALLAHABAD |  |  | 9 | FATEHPR 330MVAR S/R AGRA line
125MVAR B/Reactor-II JAIPUR(S) | 6 | 125MVAR B/Reactor-II ALLAHABAD |  |  | 10 | GORAKH 50MVAR S/R LKO-I LINE
240MVAR B/Reactor-I JHATIKALA-765 | 7 | 80MVAR B/Reactor-I BALIA |  |  | 11 | GORAKH 50MVAR S/R LKO-II LINE
240MVAR B/Reactor-II JHATIKALA-765 | 8 | 125MVAR B/Reactor-II BALIA |  |  | 12 | GORAKH 63MVAR S/R LKO-III LINE
50MVAR B/Reactor KANKROLI | 9 | 125MVAR B/Reactor-III BALIA |  | SWITCABLE LINE REACTORS NR-I | 13 | GORAKH 63MVAR S/R LKO-IV LINE | ER-I | 400KV BALIA-SASARAM
125MVAR B/Reactor-II KANKROLI | 10 | 125MVAR B/Reactor-IV BALIA | 1 | BHINML 50MVAR S/R KANKROLI | 14 | GORAKH 80MVAR S/R Barh-I line | ER-I | 765KV BALIA-GAYA
80MVAR B/Reactor-I KOTA | 11 | 240MVAR B/Reactor-I BALIA-765 | 2 | MEERUT 50MVAR S/R Kotesh-I LINE | 15 | GORAKH 80MVAR S/R Barh-II line | ER-I | 400KV BARH- GRKHPR-I
50MVAR B/Reactor-II KOTA | 12 | 240MVAR B/Reactor-II BALIA-765 | 3 | MEERUT 50MVAR S/R Kotesh-II LINE | 16 | LUCKNW 240MVAR S/R BRLY Line | ER-I | 400KV BARH- GRKHPR-II
80MVAR B/Reactor-I KOTPUTLI | 13 | 80MVAR B/Reactor BAREILLY | 4 | JHATIKALA 240MVAR S/R AGRA Line | 17 | LUCKNW 63MVAR S/R GKP-III LINE | ER-I | 765KV VARANASI-GAYA-II
50MVAR B/Reactor MANDOLA | 14 | 2x50MVAR B/Reactor BAREILLY | 5 | MEERUT 240MVAR S/R AGRA line | 18 | LUCKNW 63MVAR S/R GKP-IV LINE | ER-I | 400KV VARANASI-BIHARSHRF-I
240MVAR B/Reactor-I MEERUT-765 | 15 | 240MVAR B/Reactor-I BAREILLY-765 | 6 | SIKAR 50MVAR S/R AGRA Ckt-I | 19 | LUCKNW 240MVAR S/R BALIA Ckt-I | ER-I | 400KV VARANASI-BIHARSHRF-II
125MVAR B/Reactor MANESAR | 16 | 80MVAR B/Reactor BIHARSHRF | 7 | SIKAR 50MVAR S/R AGRA Ckt-II | 20 | VARANASI 240MVAR S/R KNP(GIS) ckt-1
50MVAR B/Reactor MURADNGR | 17 | 125MVAR B/Reactor-I FATEHPUR | 8 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | 21 | VARANASI 240MVAR S/R KNP(GIS) ckt-2
80MVAR B/Reactor NIMRANA | 18 | 125MVAR B/Reactor-II FATEHPUR | 9 | BHIWANI 240MVAR S/R MEERUT line | 22 | KNP(GIS) 330MVAR S/R JHATIKRA ckt-1 | WR | 765KV AGRA-GWALIOR-I
240MVAR B/Reactor-I PHAGI(JPR)-765 | 19 | 330MVAR B/Reactor-III FTHPR-765 | 10 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line |  |  | WR | 765KV AGRA-GWALIOR-II
125MVAR B/Reactor ROORKEE | 20 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | WR | 765KV GWALIOR-PHAGI-I
125MVAR B/Reactor-I RATANGRH(RJ) | 21 | 125MVAR B/Reactor-II LUCKNOW |  | SVC NR-I |  |  | WR | 765KV GWALIOR-PHAGI-II
80MVAR B/Reactor SIKAR | 22 | 125MVAR B/Reactor-III LUCKNOW | 1 | +400/-300MVAR SVC KANKROLI
50MVAR B/Reactor-I SAHARANPUR | 23 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-I
50MVAR B/Reactor-II SAHARANPUR | 24 | 125MVAR B/Reactor-I VINDH |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-II
125MVAR B/Reactor-II SONIPAT | 25 | 125MVAR B/Reactor-II VINDH
| 26 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - I
BUS REACTORS NR-I From NR2 | 27 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - II
240MVAR B/Reactor-I BHIWANI | 28 | 125MVAR B/Reactor-1 Mainpuri
240MVAR B/Reactor-II BHIWANI | 29 | 125MVAR B/Reactor Gorakhpur-I
50MVAR B/Reactor HISAR | 30 | 125MVAR B/Reactor-II Gorakhpur
125MVAR B/Reactor HISAR | 31 | 125MVAR B/Reactor-I SHAHJHNPR
125MVAR Bus/eactor JIND | 32 | 240MVAR B/Reactor-I KANPUR(GIS)
125MVAR B/Reactor SONIPAT | 33 | 240MVAR B/Reactor-II KANPUR(GIS)
| 34 | 125MVAR B/Reactor-III KANPUR(GIS)
| 35 | 125MVAR B/Reactor-I VARANASI
| 36 | 330MVAR B/Reactor-I VARANASI
| 37 | 330MVAR B/Reactor-II VARANASI
| 38 | 125MVAR B/Reactor KANPUR
Note on E50: a: DOC-01.04.12
Note on I83: 220KV M'PURI-M'PURI(UP)-I LILO at SIRSAGANJ
Note on E84: a: DOC-01.04.12
Note on I86: '400KV M'PURI-PARICHA-I LILO at URI
Note on A96: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on A97: Total-45.6km, PG-26.64km, HVPN-19km.
Note on I98: DELL: 220KV ROORKI-SIDKUL
Note on C108: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C109: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on I112: LILO of 400KV MEERUT-KAITHAL-I at Baghpat
Note on I113: LILO of 400KV MEERUT-KAITHAL-II at Baghpat
Note on I128: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet4
SL.NO. | ELEMENT | Element Name |  | ELEMENT ID | Element name | Total LINE length | 765KV AGRA-JHATIKARA | 253.147
| ID | [5 empty] | 765KV AGRA-Gr Noida | 148.034
|  |  |  | NR176502 | 765KV AGRA-FATEHPUR-I | 8025:36 | 765KV BALLIA-VARANASI | 165.98
A |  | 765 KV TRANS LINES |  | NR176501 | 765KV LUCKNOW-BALIA | 7653:43 | 765KV FATEHPUR-SASARAM | 355.008
1 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR140001 | 400KV AGRA-AGRA(UP)-I | 719:34 | 765KV FATEHPUR-AGRA-1 | 334.52
2 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR140002 | 400KV AGRA-AGRA(UP)-II | 719:34 | 765KV FATEHPUR-AGRA-2 | 334.8
3 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR140003 | 400KV AGRA-AURAIYA-I | 3980:02 | 765KV GAYA-VARANASI-I (OLD FTP-GAYA) | 263.94
4 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR140004 | 400KV AGRA-AURAIYA-II | 0:00 | 765KV GWALIOR-AGRA I | 129.435
5 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR140005 | 400KV AGRA-BASSI-I | 5093:31 | 765KV GWALIOR-AGRA II | 127.934
6 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR140008 | 400KV AGRA-BHIWADI-I | 5023:55 | 765KV KANPUR-JHATIKARA | 465.8
7 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR140009 | 400KV AGRA-BHIWADI-II | 5023:55 | 765KV KANPUR-VARANASI-I | 326.172
8 | NR176513 | 765KV VARANASI-FATEHPUR | 224.963 | NR140010 | 400KV AGRA-BLBGRH | 4347:22 | 765KV KANPUR-VARANASI-II
9 | NR176514 | 765KV VARANASI-GAYA-I | 80.925 | NR140122 | 400KV ALLD-FATEHPUR-I | 3353:31 | 765KV LUCKNOW-BALIA | 318.919
10 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR140123 | 400KV ALLD-FATEHPUR-II | 3353:31 | 765KV LUCKNOW-BAREILLY | 251.613
11 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR140104 | 400KV ALLD-FATEHPUR-III | 3574:19 | 765KV VARANASI-FATEHPUR | 224.963
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR140012 | 400KV ALLD-KNP-II | 5260:24 | 765KV GAYA-VARANASI-II | 80.925
13 | NR376504 | 765KV ALIGARH-JHATIKARA |  | NR140016 | 400KV ALLD-SASARAM | 4548:43 | 765KV GAYA-BALIA | 238
14 | NR376505 | 765KV KANPUR(GIS)-ALIGARH |  | NR140017 | 400KV BALIA-BIHARSHRF-I | 5802:43 | Total 17 765KV Lines | 4019.19
15 | NR376506 | 765KV AGRA-ALIGARH |  | NR140018 | 400KV BALIA-BIHARSHRF-II | 5802:43 | AGRA-FATEHABAD(UP)-I | 43.013
16 | NR376507 | 765KV ALIGARH-GR.NOIDA |  | NR140019 | 400KV BALIA-MAU-I | 221:10 | FATEHABAD(UP)-AGRA(UP)-I | 57.159
17 | NR376508 | 765KV ORAI-ALIGARH-II |  | NR140020 | 400KV BALIA-MAU-II | 221:10 | AGRA-AGRA-(UP)-II | 29.969
18 | NR376509 | 765KV ORAI-ALIGARH-I |  | NR140021 | 400KV BALIA-PATNA-I | 4685:34 | AURAIYA-AGRA-I | 167.2
|  |  |  | NR140022 | 400KV BALIA-PATNA-II | 4685:34 | AURAIYA-AGRA-II
|  |  |  | NR140136 | 400KV BALIA-PATNA-III | 4440:00 | AGRA-BASSI | 211.433
B |  | 400 KV TRANS LINES |  | NR140137 | 400KV BALIA-PATNA-IV | 4440:00 | AGRA-BHIWADI-I | 208.98
1 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR140140 | 400KV BALIA-SOHAWAL-I | 5499:55 | AGRA-BHIWADI-II | 209.51
2 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR140120 | 400KV BALIA-SOHAWAL-II | 5499:55 | AGRA-BLB | 181.137
3 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 |  | 400KV BLBGRH-MAINPURI-I | 5662:51 | AGRA-JAIPUR(S)-I | 254.41
4 | NR140005 | 400KV AGRA-BASSI-I | 212.23 |  | 400KV BLBGRH-MAINPURI-II | 5662:51 | AGRA-JAIPUR(S)-II
5 | NR140008 | 400KV AGRA-BHIWADI-I | 209.33 | NR140025 | 400KV BAREILLY-LKO(UP) | 6691:12 | AGRA-SIKAR-I | 393.9
6 | NR140009 | 400KV AGRA-BHIWADI-II | 209.33 | NR140026 | 400KV BAREILLY-MBAD-I | 2226:43 | AGRA-SIKAR-II
7 | NR140010 | 400KV AGRA-BLBGRH | 181.14 | NR140027 | 400KV BAREILLY-MBAD-II | 2210:54 | ALLD-FATEHPUR-I | 139.73
8 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 |  | 400KV BAREILLY-MEERUT-I | 5899:12 | ALLD-FATEHPUR-II
9 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 |  | 400KV BAREILLY-MEERUT-II | 5899:12 | ALLD-FATEHPUR-III | 148.934
10 | NR140104 | 400KV ALLD-FATEHPUR-III | 148.93 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 6241:13 | ALLD-KNP-II | 0
11 | NR140012 | 400KV ALLD-KNP-II | 219.183 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 6241:13 | BALIA-MAU-I | 13
12 | NR140163 | 400KV ALLD-VARANASI | 98.791 | NR140046 | 400KV GORKH-GORAKH-I | 1102:35 | BALIA-MAU-II
13 | NR140016 | 400KV ALLD-SASARAM | 189.53 | NR140047 | 400KV GORKH-GORAKH-II | 1102:35 | BALIA-SOHAWAL-I | 229.163
14 | NR140017 | 400KV BALIA-BIHARSHRF-I | 241.78 | NR140052 | 400KV KNP-AGRA | 5760:00 | BALIA-SOHAWAL-II
15 | NR140018 | 400KV BALIA-BIHARSHRF-II | 241.78 | NR140053 | 400KV KNP-AURAIYA-I | 1754:55 | BAREILLY(400)-BAREILLY(765)-I | 1.559
16 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR140054 | 400KV KNP-AURAIYA-II | 1754:55 | BAREILLY(400)-BAREILLY(765)-II
17 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR140055 | 400KV KNP-BLBGARH-I | 9256:48 | BAREILLY-BLY(UP)-I | 14.3
18 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR140056 | 400KV KNP-BLBGARH-II | 8898:32 | BAREILLY-BLY(UP)-II | 14.3
19 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR140057 | 400KV KNP-BLBGARH-III | 8898:32 | BAREILLY-MEERUT-I | 249.52
20 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 14.3 | NR140110 | 400KV KNP-FATEHPUR-I | 2569:54 | BAREILLY-MEERUT-II | 249.52
21 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 14.3 | NR140105 | 400KV KNP-FATEHPUR-II | 2570:24 | LKO(UP)-BAREILLY | 278.76
22 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.8 | NR140058 | 400KV KNP-PANKI-I | 141:36 | BAREILLY-MORADABAD-I | 92.68
23 | NR140026 | 400KV BAREILLY-MBAD-I | 92.78 | NR140059 | 400KV KNP-PANKI-II | 141:36 | BAREILLY-MORADABAD-II | 92.121
24 | NR140027 | 400KV BAREILLY-MBAD-II | 92.121 | NR140070 | 400KV LUCKNOW-GORAKH-III | 6294:14 | SHAHJAHANPUR-BAREILLY-I | 116.917
25 | NR340010 | 400KV BAREILLY-SHAHJHNPR-I | 116.917 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 6294:14 | SHAHJAHANPUR-BAREILLY-II | 116.917
26 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.917 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 68:41 | B'GARH-M'PURI-I | 235.952
27 | NR140158 | 400KV BARLY(765)-KASHIPUR-I | 100.659 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 68:41 | B'GARH-M'PURI-II
28 | NR140159 | 400KV BARLY(765)-KASHIPUR-II | 100.659 | NR140072 | 400KV LUCKNOW-LKO(UP) | 1518:29 | FATEHPUR-MAINPURI-I | 260.051
29 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR140114 | 400KV LUCKNOW-ROSA-I | 4248:00 | FATEHPUR-MAINPURI-II
30 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 2359:09 | GORAKH-GORAKH-I | 45.941
31 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 2359:09 | GORAKH-GORAKH-II
32 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR140073 | 400KV LUCKNOW-SULTANPR | 3926:24 |  | 240
33 | NR140046 | 400KV GORAKH-GORAKH-I | 45.941 | NR140074 | 400KV LUCKNOW-UNNAO-I | 1771:49 | KANPUR-AURAIYA-I | 0
34 | NR140047 | 400KV GORAKH-GORAKH-II | 45.941 | NR140075 | 400KV LUCKNOW-UNNAO-II | 1771:49 | KANPUR-AURAIYA-II
35 | NR140052 | 400KV KNP-AGRA | 240 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 747:48 | KNP-B'GARH-I | 385.69
36 | NR140053 | 400KV KNP-AURAIYA-I | 73.1212 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 747:48 | KNP-B'GARH-II | 370.772
37 | NR140054 | 400KV KNP-AURAIYA-II | 73.1212 | NR140084 | 400KV RIHAND-ALLD-I | 6685:47 | KNP-B'GARH-III
38 | NR140055 | 400KV KNP-BLBGARH-I | 385.7 | NR140085 | 400KV RIHAND-ALLD-II | 6685:47 | KNP-FATEHPUR-II | 107.1
39 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR140088 | 400KV VARANASI-BIHARSHRF-I | 3420:00 | KNP-FATEHPUR-I | 107.079
40 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR140089 | 400KV VARANASI-BIHARSHRF-II | 3420:00 | KNP-PANKI-I | 5.924
41 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR140090 | 400KV SASARAM-VARANASI | 1140:29 | KNP-PANKI-II | 5.863
42 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR140091 | 400KV SING-ALLD-I | 5422:28 | KASHIPUR-BAREILLY-I | 100.659
43 | NR140058 | 400KV KNP-PANKI-I | 5.9 | NR140092 | 400KV SING-ALLD-II | 4829:02 | KASHIPUR-BAREILLY-II
44 | NR140059 | 400KV KNP-PANKI-II | 5.9 | NR140093 | 400KV SING-ANPARA | 724:38 | KANPUR(400)-KANPUR(765)-I | 21.32
45 | NR140070 | 400KV LUCKNOW-GORAKH-III | 262.26 | NR140111 | 400KV SING-FATEHPUR | 7942:52 | KANPUR(400)-KANPUR(765)-II
46 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 262.26 | NR140095 | 400KV SING-LKO(UP) | 7920:00 | LUCKNOW-GORAKHPUR-III | 263.933
47 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.862 | NR140096 | 400KV SING-RIHAND-I | 1008:00 | LUCKNOW-GORAKHPUR-IV
48 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.862 | NR140097 | 400KV SING-RIHAND-II | 1008:00 | LUCKNOW(765)-LUCKNOW(400)-I | 2.862
49 | NR140072 | 400KV LUCKNOW-LKO(UP) | 63.27 | N-W40001 | 400KV SING-VINDH-I | 80:11 | LUCKNOW(765)-LUCKNOW(400)-II
50 | NR140114 | 400KV LUCKNOW-ROSA-I | 177 | N-W40002 | 400KV SING-VINDH-II | 40:05 | LUCKNOW-LUCKNOW (UP) | 63.27
51 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR140164 | 400KV VARANASI-SARNATH-I | 1289:31 | LUCKNOW-SULTANPUR | 163.6
52 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.298 | NR140165 | 400KV VARANASI-SARNATH-II | 1289:31 | LUCKNOW-SHAHJHNPR-I | 169.729
53 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.298 |  |  |  | LUCKNOW-SHAHJHNPR-II
54 | NR140073 | 400KV LUCKNOW-SULTANPR | 163.6 |  | 220 KV TRANS LINES |  | LUCKNOW-SOHAWAL-I | 98.281
55 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | LUCKNOW-SOHAWAL-II
56 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 405:27 | LUCKNOW-UNNAO-I | 73.826
57 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 31.158 | BILUP2202 | 220KV ALLD-REWA RD-I | 71:02 | LUCKNOW-UNNAO-II
58 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.158 | BILUP2203 | 220KV ALLD-REWA RD-II | 71:02 | RIHAND-ALLD-I | 279.245
59 | NR140084 | 400KV RIHAND-ALLD-I | 278.574 | NR122006 | 220KV AUR-SIKANDARA-I | 4380:46 | RIHAND-ALLD-II
60 | NR140085 | 400KV RIHAND-ALLD-II | 278.574 | NR122007 | 220KV AUR-SIKANDARA-II | 4380:46 | RIHAND-VINDHYACHAL Pooling-I | 31.158
61 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 142.5 | NR122012 | 220KV DGANGA-BLY(UP)-II | 5630:10 | RIHAND-VINDHYACHAL Pooling-II
62 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 142.5 | NR122013 | 220KV DGANGA-PITHORAGRH | 1416:14 | SING-ALLD-I | 224
63 | NR140091 | 400KV SING-ALLD-I | 225.936 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 148:05 | SING-ALLD-II | 202
64 | NR140092 | 400KV SING-ALLD-II | 201.21 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 148:05 | SING-ANPARA | 25.057
65 | NR140093 | 400KV SING-ANPARA | 30.193 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 126:52 | SING-FATEHPUR | 330.953
66 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR122041 | 220KV FATEHPUR-NAUBASTA | 126:52 | SING-LUCKNOW(UP) | 408.6
67 | NR140095 | 400KV SING-LKO(UP)-I | 330 | NR122016 | 220KV KNP-MAINPURI | 3624:00 | SING-RIHAND-I | 42.026
68 | NR140096 | 400KV SING-RIHAND-I | 42 | NR122017 | 220KV KNP-NAUBASTA | 463:41 | SING-RIHAND-II
69 | NR140097 | 400KV SING-RIHAND-II | 42 | NR122018 | 220KV KNP-PANKI-I | 374:24 | SING-VINDH-I | 3.341
70 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR122019 | 220KV KNP-PANKI-II | 572:38 | SING-VINDH-II
71 | N-W40002 | 400KV SING-VINDH-II | 1.67 | NR122020 | 220KV KNP-UNCHR-I | 3445:16 | HVDC Feeder I | 1.25
72 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.32 | NR122021 | 220KV KNP-UNCHR-II | 3445:16 | HVDC Feeder I
73 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.32 | NR122022 | 220KV KNP-UNCHR-III | 3471:07 | HVDC Feeder II | 1.25
74 | NR340003 | 400KV VARANASI-SASARAM(ER) | 139.482 | NR122023 | 220KV KNP-UNCHR-IV | 3471:07 | HVDC Feeder II
75 | NR340004 | 400KV VARANASI-SARNATH-I | 106.7 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | VINDHYACHAL POOLING-SASAN | 6.02
76 | NR340005 | 400KV VARANASI-SARNATH-II | 106.7 | NR122025 | 220KV RAIBRLY-CHINHAT |  | BIHARSHARIF-VARANASI-I | 285
77 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 43.013 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1026:03 | BIHARSHARIF-VARANASI-II
78 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 43.013 | NR122032 | 220KV SITARGANJ-BLY(UP) | 2534:47 | VARANASI-SARNATH-I | 106.7
79 | NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR122033 | 220KV TNKPR-BLY(UP) | 2544:00 | VARANASI-SARNATH-II | 106.7
80 | NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR122034 | 220KV TNKPR-SITARGANJ | 1026:03 | SASARAM-ALLAHABAD | 213.729
81 | NR140142 | 400KV MEERUT-BAREILLY-I | 249.52 | NR122035 | 220KV UNCHR-RAIBRLY-I | 1025:02 | SASARAM-VARANASI | 139.482
82 | NR140130 | 400KV MEERUT-BAREILLY-II | 249.52 | NR122036 | 220KV UNCHR-RAIBRLY-II | 1025:02 | VARANASI-ALLAHABAD | 98.791
83 | NR340011 | 400KV LUCKNOW-SHAHJHNPR-I | 159.7 | NR122037 | 220KV UNCHR-RAIBRLY-III | 1048:48 | BARH-GORAKHPUR-I | 353
84 | NR340012 | 400KV Lucknow(765)-Kanpur(GIS)-I | 159.7 |  | 220 KV KNP(400KV)-RANIA(UP) | 18.372 | BARH-GORAKHPUR-II
85 | NR340013 | 400KV Lucknow(765)-Kanpur(GIS)-II |  |  | 220 KV RANIA(UP)-PANKI(UP) | 30.39 | BIHARSHARIF-BALIA-I | 242
86 | NR340014 | 400KV Kanpur(GIS)-Allahabad-I |  |  | 132 KV TRANS LINES |  | BIHARSHARIF-BALIA-I
87 | NR340015 | 400KV Kanpur(GIS)-Allahabad-II |  | BILUP13201 | 132KV MAU-BALIA | 57.825 | ALLAHABAD-MEJA-I | 28.19
88 | NR340016 | 400KV ORAI-ORAI(UP)-I |  |  | 132 KV Tankpur - Mahendranagar | 3.06 | ALLAHABAD-MEJA-II
89 | NR340017 | 400KV ORAI-ORAI(UP)-II |  |  |  |  | UCHAHAR-FATEHPUR-I | 53.7
90 | NR140019 | 400KV BALIA-MAU-I | 9.215 |  | 220KV ALLD-JHUSI(UP) | 21.879 | UCHAHAR-FATEHPUR-II
91 | NR140020 | 400KV BALIA-MAU-II | 9.215 |  | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | PATNA-BALIA-I | 195
92 | NR140021 | 400KV BALIA-PATNA-I | 195.232 |  | 220KV ALLD-REWA RD-I&II | 2.96 | PATNA-BALIA-II
93 | NR140022 | 400KV BALIA-PATNA-II | 195.232 |  | 220KV ALLD-REWA RD-II |  | PATNA-BALIA-III | 185
94 | NR140136 | 400KV BALIA-PATNA-III | 185 |  | 220KV AURAIYA-SIKANDARA-I | 182.532 | PATNA-BALIA-IV
95 | NR140137 | 400KV BALIA-PATNA-IV | 185 |  | 220KV AURAIYA-SIKANDARA-II |  | LUCKNOW-KANPUR-I | 159.7
[5 empty] | 220KV D'GANGA-BRLY(UP)-II | 234.59 | LUCKNOW-KANPUR-II
[5 empty] | 220KV D'GANGA-PITHORAGRH | 59.01 | ALLAHABAD-KANPUR(GIS)-I | 240.39
[5 empty] | 220KV PITHORAGRH-BRLY(UP)-I | 177.88 | ALLAHABAD-KANPUR(GIS)-II
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-I | 6.169 | Total 105 400KV Lines | 10198.266
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-II | 6.169 | HVDC R-D POLE-I | 815
[5 empty] | 220KV FATEHPUR-KNP SOUTH | 5.286 | HVDC R-D POLE-II
[5 empty] | 220KV FATEHPUR-NAUBASTA | 5.286 | HVDC B-B POLE-I | 789.786
[5 empty] | 220KV KNP-MAINPURI | 151 | HVDC B-B POLE-II
[5 empty] | 220KV KNP-RANIA(UP) | 18.372 | BNC-AGRA POLE-I | 1734
[5 empty] | 220KV RANIA(UP)-PANKI(UP) | 30.39 | BNC-AGRA POLE-II
[5 empty] | 220KV KNP-NAUBASTA | 19.32 | CHAMPA-KURUKSHETRA-I | 1305
[5 empty] | 220KV KNP-PANKI-II | 23.86 | CHAMPA-KURUKSHETRA-II
[5 empty] | 220KV KNP-UNCHAHAR-I | 143.553
220KV KNP-UNCHAHAR-II
[5 empty] | 220KV KNP-UNCHAHAR-III | 144.63
220KV KNP-UNCHAHAR-IV
C |  | 220 KV TRANS LINES |  |  | 220KV SITARGANJ-BLY(UP) | 105.72
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 |  | 220KV TNKPR-BLY(UP) | 106
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 |  | 220KV TNKPR-SITARGANJ | 42.55
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 2.96 |  | 220KV RBRLY-CHINHAT | 93.61
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 2.96 |  | 220KV UNCHR-RBRLY-I | 42.71
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.532 |  | 220KV RBRLY-LKO(UP) | 1.19
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.532 |  | 220KV UNCHR-RBRLY-II | 42.71
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 |  | 220KV UNCHR-RBRLY-III | 43.7
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 |  | TOTAL 30 Lines
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 6.17 |  | 132KV LINES
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 6.17 |  | 132KV MAU-BALIA | 57.825
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 5.286 |  | 132KV TNKPR-MHNDRNGR | 3.06
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 5.286
13 | NR122016 | 220KV KNP-MAINPURI | 151
14 | NR122017 | 220KV KNP-NAUBASTA | 19.32
15 | NR122019 | 220KV KNP-PANKI-II | 23.86
16 | NR122020 | 220KV KNP-UNCHR-I | 143.553
17 | NR122021 | 220KV KNP-UNCHR-II | 143.553
18 | NR122022 | 220KV KNP-UNCHR-III | 144.63
19 | NR122023 | 220KV KNP-UNCHR-IV | 144.63
20 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88
21 | NR122025 | 220KV RAIBRLY-CHINHAT | 93.61
22 | NR122026 | 220KV RAIBRLY-LKO(UP) | 42.752
23 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.616
24 | NR122033 | 220KV TNKPR-BLY(UP) | 106
25 | NR122034 | 220KV TNKPR-SITARGANJ | 42.752
26 | NR122035 | 220KV UNCHR-RAIBRLY-I | 42.71
27 | NR122036 | 220KV UNCHR-RAIBRLY-II | 42.71
28 | NR122037 | 220KV UNCHR-RAIBRLY-III | 43.7
29 | NR320001 | 220 KV KANPUR(PG) - RANIYA( UP) | 18.372
30 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP) | 30.39
31 | NR320003 | 220KV RAIBRLY-CG CITY(UP)
32 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP)
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA | 57.825
| Lines | TOTAL FOR T/LS
142 |  | OVERALL SYSTEM AVAILABILITY=
E |  | 765/400 KV ICT'S
1 | NR1ICT707 | 765/400KV ICT-I AGRA
2 | NR1ICT708 | 765/400KV ICT-II AGRA
3 | NR1ICT701 | 765/400KV ICT-I BALIA
4 | NR1ICT702 | 765/400KV ICT-II BALIA
5 | NR1ICT715 | 765/400KV ICT-I BAREILLY
6 | NR1ICT716 | 765/400KV ICT-II BAREILLY
7 | NR1ICT705 | 765/400KV ICT-I FATEHPUR
8 | NR1ICT706 | 765/400KV ICT-II FATEHPUR
9 | NR1ICT703 | 765/400KV ICT-I LUCKNOW
10 | NR1ICT704 | 765/400KV ICT-II LUCKNOW
11 | NR1ICT717 | 765/400KV ICT-I VARANASI
12 | NR1ICT718 | 765/400KV ICT-II VARANASI
13 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS)
14 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS)
| NR3ICT703 | 1000MVA ICT-I ORAI(GIS)
| NR3ICT704 | 1000MVA ICT-II ORAI(GIS)
815
F |  | 400/220 KV ICT'S
1 | NR1ICT70 | 315MVA ICT-I AGRA
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 815
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 789.786
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 789.786
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 1734
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 1734
10 | NR1ICT20 | 315MVA ICT-II KANPUR
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW
13 | NR1ICT26 | 315MVA ICT-I MAINPURI
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 0
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 0
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL
| NR3ICT01 | 315MVA ICT-2 at Agra
| NR3ICT02 | 500MVA ICT-3 at Mainpuri
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 100MVA ICT-I PITHORAGRH
2 | NR1ICT44 | 100MVA ICT-II PITHORAGRH
3 | NR1ICT47 | 100MVA ICT-I RAIBAREILLY
4 | NR1ICT38 | 100MVA ICT-II RAIBAREILLY
5 | NR1ICT39 | 200MVA ICT-III RAIBAREILLY
6 | NR1ICT40 | 100MVA ICT-I SITARGANJ
7 | NR1ICT41 | 100MVA ICT-II SITARGANJ
| NR3ICT03 | 200MVA ICT-3 at Raibareilly
| NR3ICT04 | 200MVA ICT-2 at Raibareilly
TOTAL FOR ICTs
39 |  | HVDC RIHAND-DADRI
H | NR1DCP01 | 500KV HVDC R-D POLE-I
1 | NR1DCP02 | 500KV HVDC R-D POLE-II
2 | NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I
3 | NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II
4 |  | TOTAL FOR HVDC line
HVDC AGRA-BNC
J | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I
1 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II
| NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III
| NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV
2 |  | TOTAL of HVDC POLE-I
HVDC BTB VINDHYACHAL
K | NR1DCB01 | VINDH HVDC B/B BLOCK-I
1 | NR1DCB02 | VINDH HVDC B/B BLOCK-II
2 |  | TOTAL FOR HVDC VINDHYACHAL
HVDC BTB SASARAM
L | NEDCB01 | +/-500MW HVDC B/B SASARAM
1 |  | TOTAL FOR HVDC SASARAM
SVC, KANPUR
M | NR1SVC01 | +/-140MVAR SVC-I KANPUR
1 | NR1SVC02 | +/-140MVAR SVC-II KANPUR
2 |  | TOTAL FOR SVC
N |  | Bus & Switch Line Reactor
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA
3 | NR1BRT36 | 240MVAR B/Reactor-I AGRA-765
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD
6 | NR1BRT33 | 125MVAR B/Reactor-II ALLAHABAD
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY
14 | NR1BRT44 | 2x50MVAR B/Reactor BAREILLY
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR
20 | NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI
28 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR
29 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W
30 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N
31 | NR1BRT42 | 125MVAR B/Reactor-I VINDH
32 | NR1BRT43 | 125MVAR B/Reactor-II VINDH
33 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI
34 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI
35 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I
36 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line
37 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I
38 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II
39 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line
40 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 393.9
41 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 393.9
42 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 213.729
43 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 285
44 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 285
45 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 238
46 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 263.94
47 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 139.482
48 | NR1SRT24 | GORAKH 80MVAR S/R Barh-I line
49 | NR1SRT25 | GORAKH 80MVAR S/R Barh-II line
50 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE
51 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE
52 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I
53 | NR1SRT26 | LUCKNW 240MVAR S/R Bareilly Line
54 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS)
55 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS)
56 | NR3SRT01 | VARANASI 240MVAR S/R KNP(GIS)-1
57 | NR3SRT02 | VARANASI 240MVAR S/R KNP(GIS)-2
58 | NR3SRT03 | KNP(GIS) 330MVAR S/R JHATIKRA-1
59 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS)
60 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI
61 | NR3BRT05 | 125MVAR B/Reactor-I KANPUR
62 | NR3BRT06 | 330MVAR B/Reactor-III VARANASI-765
63 | NR3BRT08 | 330MVAR Bus Reactor-II AT ALIGARH GIS |  |  | 400KV AGRA-SIKAR-I
64 | NR3SLRT06 | ALIGARH 330MVAR Switachable Line Reactor KANPUR LINE |  |  | 400KV AGRA-SIKAR-II
65 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH |  |  | 400KV ALLAHABAD-SASARAM
66 | NR3LRT07 | ORAI 240MVAR Non Switchable Line Reactor ALIGARH-II LINE |  |  | 400KV VARANASI-BIHARSHRF-I
67 | NR3LRT08 | ALIGARH 240MVAR Non Switchable Line Reactor ORAI-II LINE |  |  | 400KV VARANASI-BIHARSHRF-II
68 | NR3BRT10 | 330MVAR Bus Reactor-I ORAI |  |  | 765KV BALIA-GAYA
69 | NR3LRT09 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-I LINE |  |  | 765KV VARANASI-GAYA
70 | NR3LRT10 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-II LINE |  |  | 400KV SASARAM-VARANASI
71 | NR3BRT11 | 330MVAR Bus Reactor-II ORAI |  |  | 400KV MOTIHARI-GRKHPR-I
72 | NR3LRT11 | ORAI 240MVAR Non-Switchable Line Reactor SATNA LINE |  |  | 400KV MOTIHARI-GRKHPR-II
73 | NR3LRT12 | ORAI 240MVAR Non-Switchable Line Reactor ALIGARH-I LINE
74 | NR3LRT13 | ALIGARH 240MVAR Non-Switchable Line Reactor ORAI-I LINE
75 | NR3BRT07 | 63MVAR B/Reactor-I SOHAWAL
Note on C7: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C12: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C13: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C17: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C18: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C19: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C20: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C37: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16
Note on C76: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on F76: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on F77: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C102: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C103: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C279: DOC-26/05/2014
Note on F325: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet5
220KV ALLD-JHUSI(UP)
220KV JHUSI(UP)-PHULPUR(UP)
220KV ALLD-REWA RD-I
220KV ALLD-REWA RD-II
220KV AUR-SIKANDARA-I
220KV AUR-SIKANDARA-II
220KV DGANGA-BLY(UP)-II
220KV DGANGA-PITHORAGRH
220KV FATEHPUR-FTHPR(UP)-I
220KV FATEHPUR-FTHPR(UP)-II
220KV FATEHPUR-KNP SOUTH
220KV FATEHPUR-NAUBASTA
220KV KNP-MAINPURI
220KV KNP-NAUBASTA
220KV KNP-PANKI-I
220KV KNP-PANKI-II
220KV KNP-UNCHR-I
220KV KNP-UNCHR-II
220KV KNP-UNCHR-III
220KV KNP-UNCHR-IV
220KV PITHORAGRH-BRLY(UP)
220KV RAIBRLY-CHINHAT
220KV RAIBRLY-LKO(UP)
220KV SITARGANJ-BLY(UP)
220KV TNKPR-BLY(UP)
220KV TNKPR-SITARGANJ
220KV UNCHR-RAIBRLY-I
220KV UNCHR-RAIBRLY-II
220KV UNCHR-RAIBRLY-III
220KV KNP-RANIA
132 KV TRANS LINES
Note on A31: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Sheet2 (hidden)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
125MVAR B/Reactor-1 Mainpuri | 2017-05-27 22:42 | 2017-05-28 06:46 | 0 | 0 | 0 | 0.33611 | N-2790 | SVRD | H-T for voltage regulation as per NRLDC instruction. Mainpuri=386KV
125MVAR B/Reactor-I GORAKHPUR | 2017-05-22 21:55 | 2017-06-01 | 0 | 0 | 0 | 1900-01-08 02:05 | N-2235 | SVRD | H-T for voltage regulation as per NRLDC instruction. Gorakhpur=393KV
125MVAR B/Reactor-III KANPUR(GIS) | 2017-05-25 23:46 | 2017-05-26 06:58 | 0 | 0 | 0 | 0.3 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. Kanpur=395KV
240MVAR B/Reactor-I BALIA-765 | 2017-05-13 21:25 | 2017-05-27 01:23 | 0 | 0 | 0 | 1900-01-12 03:58 | N-1003 | SVRD | H-T for voltage regulation as per NRLDC instruction. Ballia=744KV
240MVAR B/Reactor-I BAREILLY-765 | 2017-05-25 09:56 | 2017-05-28 05:20 | 0 | 0 | 0 | 1900-01-01 19:24 | N-2455 | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-13 21:24 | 2017-05-14 06:52 | 0 | 0 | 0 | 0.39444 | N-1002 | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-16 20:01 | 2017-05-17 07:40 | 0 | 0 | 0 | 0.48542 | N-1534 | SVRD | H-T for voltage regulation as per NRLDC instruction. Lucknow=749KV
330MVAR B/Reactor-II VARANASI | 2017-05-19 15:05 | 2017-05-19 22:00 | 0 | 0 | 0 | 0.28819 | N-1850 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=751KV
330MVAR B/Reactor-II VARANASI | 2017-05-22 21:34 | 2017-05-24 06:25 | 0 | 0 | 0 | 1899-12-31 08:51 | N-2234 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=761KV
80MVAR B/Reactor BAREILLY | 2017-05-25 23:41 | 2017-05-26 07:02 | 0 | 0 | 0 | 0.30625 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=395KV
80MVAR B/Reactor LUCKNOW | 2017-05-25 23:35 | 2017-05-26 06:53 | 0 | 0 | 0 | 0.30417 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=396KV
Note on A9: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1
Note on A10: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1