## SOP DATA NR3 June
Standard of Performance data for the month of June-2018 Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD, NORTHERN REGION - III
ANNEXTURE- A
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
A |  | 765 KV TRANS LINES
1 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [12 empty] | 720
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1327 | 148.034 | 196441.118 | 196441.118 | 100
2 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2018-06-09 17:42 | 2018-06-10 20:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:18 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
[6 empty] | 2018-06-11 06:57 | 2018-06-11 10:55 |  |  |  | 0 | 0 | 0 | 0.16528 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
[6 empty] | 2018-06-12 07:14 | 2018-06-12 12:49 |  |  |  | 0 | 0 | 0 | 0.23264 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2018-06-14 07:46 | 2018-06-14 14:54 |  |  |  | 0 | 0 | 0 | 0.29722 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra =787kV
[6 empty] | 2018-06-17 07:51 | 2018-06-18 14:46 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:55 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796KV
[6 empty] | 2018-06-21 18:18 | 2018-06-24 23:49 |  |  |  | 0 | 0 | 0 | 1900-01-02 05:31 |  |  |  | LCSD | S/D taken for stringing work of 800kV Agra-BNC HVDC line.
[6 empty] | 2018-06-27 05:23 | 2018-06-28 09:47 |  |  |  | 0 | 0 | 0 | 1899-12-31 04:24 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=798kV
[6 empty] | 2018-06-29 06:08 | 2018-07-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:52 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 05:41 | [6 empty] | 720 | 1216 | 334.52 | 406776.32 | 406776.32 | 100
3 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2018-06-13 06:54 | 2018-06-13 14:56 |  |  |  | 0 | 0 | 0 | 0.33472 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
[6 empty] | 2018-06-21 18:21 | 2018-06-21 18:59 |  |  |  | 0.026389 | 0 | 0 | 0 |  |  |  | LEFT | Line Tripped from Agra end at 1821hrs on R-N fault. F.D.= 187.629KM from Fatehpur (RTAMC Data), 207.2KM (M1-Fatehpur), 206.1KM (M2-Fatehpur) & 109KM from Agra, F.C.=2.99KAmp at Fatehpur (RTAMC Data), 2.76KA (M1-Fatehpur), 2.7KA (M2-Fatehpur) & 6.24KA at Agra.
[6 empty] | 2018-06-28 06:45 | 2018-06-29 09:55 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:10 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.026389 | 0 | 0 | 1899-12-31 11:12 | [6 empty] | 720 | 1210 | 334.8 | 405108 | 404751.655 | 99.912
4 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | 2018-06-04 12:28 | 2018-06-04 12:28 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | auto reclosed successfully from both end due to Y-N fault. Ballia: FD-247km, FC-2.6KA. LKO: FD-67.9km, FC-5.1KA. Lucknow jurisdiction
[6 empty] | 2018-06-08 17:03 | 2018-06-08 17:03 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed successfully from both end due to B-N fault. FD: Ballia-172.3km, LKO-117.1km. FC: Ballia-3.512KA, LKO-3.8KA. Fault in Lucknow TL jurisdiction
[6 empty] | 2018-06-09 15:36 | 2018-06-09 20:54 |  |  |  | 0 | 0 | 0.22083 | 0 |  |  |  | LNCC | Emergency S/D availed for insulator cleaning at loc no 503 & 504 which was found polluted due to bird excreta during patrolling
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.22083 | 0 | [6 empty] | 714.7 | 1374 | 318.919 | 438194.706 | 438194.706 | 100
5 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 256393.647 | 100
6 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1419 | 165.98 | 235525.62 | 235525.62 | 100
7 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 223 | 310639 | 310639 | 100
8 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1440 | 465.8 | 670752 | 670752 | 100
9 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | 2018-06-01 | 2018-06-03 19:37 |  |  |  | 0 | 0 | 1900-01-01 19:37 | 0 |  |  |  | LNCC | Opened on emergency basis due to tower bent near Ghatampur caused by heavy storm
[6 empty] | 2018-06-13 11:16 | 2018-06-13 22:01 |  |  |  | 0 | 0 | 0 | 0.44792 |  |  |  | LCSD | Emergency S/D taken to facilitate rectification work of broken earth wire at loc no 701-704 of 765KV D/C Varanasi-Kanpur line-2
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1900-01-01 19:37 | 0.44792 | [6 empty] | 652.3833 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
10 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | 2018-06-01 | 2018-06-03 20:49 |  |  |  | 0 | 0 | 1900-01-01 20:49 | 0 |  |  |  | LNCC | Tripped due to R-N fault due to heavy storm. FD: 22.1kM from KNP and 244.2kM from varanasi. FC: 8.347kA at KNP and 3.053kA at Varanasi. Charging attemp tajken at 0257 hrs dtd 03.05.18 but line didn't hold on SOTF on Y-B fault. 23.7kM from KNP. Fault in KNP jurisdiction.
[6 empty] | 2018-06-13 00:35 | 2018-06-14 12:33 |  |  |  | 0 | 0 | 1899-12-31 11:58 | 0 |  |  |  | LNCC | Tripped due to Y-N fault,M1:F.D.=199.6km from VNS,F.C.=3.63KA, M2:F.D.=206.7km from VNS ,F.C.=2.47KA, M1:F.D.=56.2km from KNP(GIS),F.C.=6.154KA, M2:F.D.=52.7km from KNP(GIS) ,F.C.=6.25KA caused by heavy storm(Kanpur Jurisdiction)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1900-01-03 08:47 | 0 | [6 empty] | 615.2167 | 1447 | 326.172 | 471970.884 | 471970.884 | 100
11 | NR376504 | 765KV ALIGARH-JHATIKARA | 158 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 158 | 220094 | 220094 | 100
12 | NR376505 | 765KV KANPUR(GIS)-ALIGARH | 327 | NR3 | -- | 2018-06-01 20:50 | 2018-06-01 22:35 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | GOVC | Tripped on over voltage protection operated at Aligarh.
[6 empty] | 2018-06-09 17:44 | 2018-06-09 20:06 |  |  |  | 0 | 0 | 0.098611 | 0 |  |  |  | GOVC | Tripped due to over voltage protection operated at Aligrah & DT received at Kanpur. Aligarh-804KV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.098611 | 0 | [6 empty] | 717.6333 | 1393 | 327 | 455511 | 455511 | 100
13 | NR376506 | 765KV AGRA-ALIGARH | 122.5 | NR3 | -- | 2018-06-01 | 2018-06-04 01:21 |  |  |  | 0 | 0 | 1900-01-02 01:21 | 0 |  |  |  | LNCC | Tripped due to heavy storm due to Y-ph WT disloated from its bus. 4Nos tower collapsed (tower no 15, 16,17,18)
[6 empty] | 2018-06-11 11:25 | 2018-06-11 16:52 |  |  |  | 0 | 0 | 0 | 0.22708 |  |  |  | LCSD | Emergency S/D availed for removing hanging OPGW laying rope between loc No 1 to 4.
[6 empty] | 2018-06-12 14:38 | 2018-06-12 16:29 |  |  |  | 0 | 0 | 0 | 0.077083 |  |  |  | LCSD | Tripped due to OPGW work caused by Y-N fault,F.D.=0.2km from Agra,F.C.=20.96KA, F.D.=102km from Aligarh and F.C.=5.2KA(Agra Jurisdiction) .
[6 empty] | 2018-06-27 12:56 | 2018-06-27 16:15 |  |  |  | 0.13819 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for removal of earth-wire twist between location No 20 to 21.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.13819 | 0 | 1900-01-02 01:21 | 0.30417 | [6 empty] | 646.65 | 1393 | 122.5 | 170642.5 | 169767.2749 | 99.4871
14 | NR376507 | 765KV ALIGARH-GR.NOIDA | 51 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 51 | 71043 | 71043 | 100
15 | NR376508 | 765KV ORAI-ALIGARH-II | 331.958 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 331.958 | 462417.494 | 462417.494 | 100
16 | NR376509 | 765KV ORAI-ALIGARH-I | 331.958 | NR3 | -- | 2018-06-09 05:06 | 2018-06-09 09:47 |  |  |  | 0.19514 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for replacement of 765KV R Ph Tie Bay(705) CB at Orai. Charged at 09:47 hrs from Orai end but immidiatly tripped on over voltage protection operated at Orai end
[6 empty] | 2018-06-09 09:47 | 2018-06-09 10:54 |  |  |  | 0 | 0 | 0.046528 | 0 |  |  |  | GOVC | After S/D charged at 09:47 hrs from Orai end but immidiatly tripped on over voltage protection operated at Orai end.
[6 empty] | 2018-06-10 08:13 | 2018-06-10 11:33 |  |  |  | 0 | 0 | 0.13889 | 0 |  |  |  | GOVC | Tripped due to over voltage protection operated (stage-I) at Orai(GIS) and DT received at Aligarh end. Orai=819kV
[6 empty] | 2018-06-18 13:22 | 2018-06-18 14:02 |  |  |  | 0.027778 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault. FD: 59.5kM from Orai end and 200.4kM from Aligarh end (Total line length-331kM). FC:6.59kA at Orai and 3.6kA at Aligarh. Fault in Orai jurisdiction.
[6 empty] | 2018-06-25 18:05 | 2018-06-25 18:24 |  |  |  | 0.013194 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault. FD: Orai-284.1km, Aligarh-43.7km, FC: Orai-2.6KA, Aligarh-9.5KA. Fault in Aligarh TL jurisdiction.
[6 empty] | 2018-06-27 06:06 | 2018-06-27 12:20 |  |  |  | 0.25972 | 0 | 0 | 0 |  |  |  | OSFT | S/D availed to attend oil leakage in B-PH line reactor
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.49583 | 0 | 0.18542 | 0 | [6 empty] | 715.55 | 1393 | 331.958 | 462417.494 | 454727.2303 | 98.3369
B |  | 400 KV TRANS LINES |  |  | --
1 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 29.982 | NR3 | -- | 2018-06-18 14:57 | 2018-06-18 16:46 | -- | -- |  | 0 | 0 | 0 | 0.075694 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending heavy sparking in B phase line isolator at Fatehpur(UPPCL) end.
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.075694 | [6 empty] | 720 | 515 | 29.982 | 15440.73 | 15440.73 | 100
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- | 2018-06-09 17:30 | 2018-06-09 18:37 | -- | -- |  | 0 | 0 | 0.046528 | 0 |  |  |  | GOVC | Tripped due to over voltage protection operated. Agra-436KV
[5 empty] | -- | 2018-06-21 15:13 | 2018-06-21 16:17 | -- | -- |  | 0 | 0.044444 | 0 | 0 |  |  |  | OMSU | Line Tripped only from Agra(UP) end due to Mal-operation of Bus bar protection at Agra(UP) end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.044444 | 0.046528 | 0 | [6 empty] | 718.8833 | 515 | 29.982 | 15440.73 | 15440.73 | 100
3 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 57.159 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 57.159 | 29436.885 | 29436.885 | 100
4 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2018-06-02 04:19 | 2018-06-03 08:14 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 03:55 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430KV
[6 empty] | 2018-06-07 07:15 | 2018-06-11 23:31 |  |  |  | 0 | 0 | 0 | 1900-01-03 16:16 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=423KV
[6 empty] | 2018-06-12 07:07 | 2018-06-16 21:07 |  |  |  | 0 | 0 | 0 | 1900-01-03 14:00 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430KV
[6 empty] | 2018-06-24 18:06 | 2018-06-24 19:25 |  |  |  | 0 | 0 | 0 | 0.054861 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-09 11:30 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 61362.4 | 100
5 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2018-06-11 07:14 | 2018-06-11 23:20 |  |  |  | 0 | 0 | 0 | 0.67083 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430KV
[6 empty] | 2018-06-15 08:13 | 2018-06-20 11:15 |  |  |  | 0 | 0 | 0 | 1900-01-04 03:02 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431KV
[6 empty] | 2018-06-27 07:53 | 2018-07-01 |  |  |  | 0 | 0 | 0 | 1900-01-02 16:07 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 11:15 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 61362.4 | 100
6 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- | 2018-06-08 17:27 | 2018-06-08 18:08 | -- | -- | -- | 0.028472 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for attending SF6 low alarm at Bassi end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.028472 | 0 | 0 | 0 | [6 empty] | 720 | 245 | 211.433 | 51801.085 | 51751.9219 | 99.9051
7 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2018-06-26 05:10 | 2018-06-26 05:59 | -- | -- | -- | 0.034028 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault. Agra: FD-1135km, FC-20.67KA. Fault in Agra TL jurisdiction
[6 empty] | 2018-06-28 01:24 | 2018-06-28 11:11 |  |  |  | 0 | 0 | 0 | 0.40764 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[6 empty] | 2018-06-30 03:51 | 2018-06-30 04:26 |  |  |  | 0.024306 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault. FD: Agra-2.148km, FC: Agra- 31.27KA. Fault in Agra TL jurisdiction. Charged at 04:26 hrs but immidiatly tripped due to over voltage protection operated at Agra & DT received at Bhiwadi.
[6 empty] | 2018-06-30 04:26 | 2018-07-01 |  |  |  | 0 | 0 | 0.81528 | 0 |  |  |  | GOVC | Tripped at 03:51 hrs due to R-N fault. Charged at 04:26 hrs but immidiatly tripped due to over voltage protection operated at Agra & DT received at Bhiwadi.
[6 empty] | 2018-06-26 14:16 | 2018-06-26 16:40 |  |  |  | 0.1 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for removing of kite with metallic thread from R phase of line between location no 8 -9 and 9-10.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.15833 | 0 | 0.81528 | 0.40764 | [6 empty] | 700.4333 | 402 | 208.98 | 84009.96 | 83554.1881 | 99.4575
8 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2018-06-08 09:34 | 2018-06-16 16:43 | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 07:09 |  |  |  | LCSD | Taken under S/D for retrofitting of existing 400KV line and SCADA integration work with HVDC Agra
[6 empty] | 2018-06-29 05:29 | 2018-06-29 10:43 |  |  |  | 0 | 0 | 0 | 0.21806 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-07 12:23 | [6 empty] | 720 | 515 | 209.51 | 107897.65 | 107897.65 | 100
9 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 382 | 181.137 | 69194.334 | 69194.334 | 100
10 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 332 | 139.73 | 46390.36 | 46390.36 | 100
11 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | 2018-06-13 14:33 | 2018-06-13 15:32 |  |  |  | 0 | 0 | 0.040972 | 0 |  |  |  | LNCC | Tripped due to heavy storm caused by R-N fault,F.D.=8.4km from FTP, F.C.=16.91KA, F.D.=140km from ALLD,F.C.=2.401KA(Kanpur Jurisdiction)
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.040972 | 0 | [6 empty] | 719.0167 | 332 | 139.73 | 46390.36 | 46390.36 | 100
12 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- | 2018-06-13 15:03 | 2018-06-13 15:03 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to Y-N fault,F.D.=53.92km from FTP , F.C.=5.49KA, F.D.=96.5km from ALLD,F.C.=3.057KA (Kanpur Jurisdiction)
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 155.932 | 80304.98 | 80304.98 | 100
13 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | 2018-06-08 15:00 | 2018-06-08 17:20 |  |  |  | 0.097222 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for rectification of broken earth wire between loc no 1010 & 1011
[6 empty] | 2018-06-22 16:37 | 2018-06-22 17:02 |  |  |  | 0.017361 | 0 | 0 | 0 |  |  |  | LHWT | Tripped due to B-N fault. F.D.= 173KM from Kanpur & 40.6KM from Allahabad. F.C.= 2.7KA at Kanpur & 8.23KA at Allahabad. The fault was in Allahabad Jurisdiction (Earth wire dead end failed at Loc. No. 635).
[6 empty] | 2018-06-23 10:56 | 2018-06-23 14:09 |  |  |  | 0.13403 | 0 | 0 | 0 |  |  |  | OSFT | E/S/D availed for rectification of broken E/W tension clamp at Loc. No. 635
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.24861 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 224 | 115360 | 114404.0074 | 99.1713
14 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.792 | 50877.88 | 50877.88 | 100
15 | NR140016 | 400KV ALLD-SASARAM | 212 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.040972 | 0 | [6 empty] | 719.0167 | 369 | 212 | 78228 | 78228 | 100
16 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 13 | 6695 | 6695 | 100
17 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 13 | 6695 | 6695 | 100
18 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 227 | 229.163 | 52020.001 | 52020.001 | 100
19 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 227 | 229.163 | 52020.001 | 52020.001 | 100
20 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 1.559 | 1071.033 | 1071.033 | 100
21 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 1.559 | 1071.033 | 1071.033 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
22 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 9.2 | 4738 | 4738 | 100
23 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | 2018-06-01 22:07 | 2018-06-01 23:49 |  |  |  | 0 | 0 | 0.070833 | 0 |  |  |  | LNCC | Tripped on R-N fault due to heavy thunderstorm. Bareilly- FD: 11.7km, FC: 14.11KA
[5 empty] | -- | 2018-06-18 14:07 | 2018-06-18 14:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed successfully at both end on Y-N fault. FD: 11.7kM from BRLY (Total line length-14.3kM). FC: 10.6kA at BRLY. Fault in UPPCL jurisdiction.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.070833 | 0 | [6 empty] | 718.3 | 515 | 9.2 | 4738 | 4738 | 100
24 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- | 2018-06-08 08:17 | 2018-06-08 08:51 | -- | -- | -- | 0.023611 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault. FD=165.4KM from Bareilly, FC= 2.4KAmp at Bareilly. Fault in Shahjahanpur TL jurisdiction
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.023611 | 0 | 0 | 0 | [6 empty] | 720 | 331 | 278.76 | 92269.56 | 92196.9404 | 99.9213
25 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | 2018-06-01 21:30 | 2018-06-01 23:51 |  |  |  | 0 | 0 | 0.097917 | 0 |  |  |  | LNCC | Tripped on R-N fault due to heavy thunderstorm. Bareilly- FD: 51.9km, FC: 5.13KA
[6 empty] | 2018-06-05 16:38 | 2018-06-05 18:34 |  |  |  | 0 | 0 | 0 | 0.080556 |  |  |  | OSFD | E/S/D availed by UPPCL for attending hot spot in line side CT clamp at Moradabad(UPPCL end)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.097917 | 0.080556 | [6 empty] | 717.65 | 515 | 92.68 | 47730.2 | 47730.2 | 100
26 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 92.68 | 47730.2 | 47730.2 | 100
27 | NR140115 | 400KV BAREILLY-ROSA-I | 115.926 | NR3
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 115.926 | 59701.89 | 59701.89 | 100
28 | NR140115 | 400KV BAREILLY-SHAHJHNPR-I | 115.926 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 115.926 | 59701.89 | 59701.89 | 100
29 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 116.03 | 59755.45 | 59755.45 | 100
30 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 101.841 | 69964.767 | 69964.767 | 100
31 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 |  | 2018-06-01 21:55 | 2018-06-01 22:54 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LNCC | Tripped on Y-B fault due to heavy thunderstorm. Bareilly- FD: 10.23km, FC: Y-16.29KA, B-16.62KA.
[6 empty] | 2018-06-30 08:55 | 2018-06-30 08:55 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully from both end due to B-N fault. F.D.= 39.96KM from Bareilly, F.C.= 8.046KA at Bareilly. The fault was in Bareilly jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 101.841 | 69964.767 | 69964.767 | 100
32 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2018-06-01 21:11 | 2018-06-02 09:59 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427KV
[6 empty] | 2018-06-08 08:56 | 2018-06-08 17:21 |  |  |  | 0 | 0 | 0 | 0.35069 |  |  |  | LCSD | Tripped due to Y-N fault during OPGW work. FD=50.66km from Mainpuri, FC=5.649KA, FD=170.2km from BLB, F.C.=2.4KA. Rope found in the line during OPGW work. Fault in Mainpuri TL jurisdiction.
[6 empty] | 2018-06-13 07:59 | 2018-06-13 08:54 |  |  |  | 0 | 0 | 0 | 0.038194 |  |  |  | LCSD | S/D taken for removing hanging OPGW rope at Loc no 100
[6 empty] | 2018-06-17 07:13 | 2018-06-18 08:04 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:51 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=429KV
[6 empty] | 2018-06-27 06:19 | 2018-06-27 09:52 |  |  |  | 0 | 0 | 0 | 0.14792 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=427kV
[6 empty] | 2018-06-28 12:28 | 2018-06-28 12:59 |  |  |  | 0 | 0 | 0 | 0.021528 |  |  |  | LCSD | Tripped due to development of loop of earth wire while removing the same during OPGW work on B-N fault F.D.= 91.19KM from Mainpuri & 118KM from Ballabhgarh, F.C.= 3.595KA at Mainpuri & 3.1KA at Ballabhgarh.. The fault was in Mainpuri jurisdiction.
[6 empty] | 2018-06-28 13:23 | 2018-06-28 20:05 |  |  |  | 0 | 0 | 0 | 0.27917 |  |  |  | LCSD | Tripped due to development of loop of earth wire while removing the same during OPGW work on B-N fault . F.D.= 90.5KM from Mainpuri & 122.72KM from Ballabhgarh, F.C.= 3.653KA at Mainpuri & 3.086KA at Ballabhgarh. The fault was in Mainpuri jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 20:57 | [6 empty] | 720 | 515 | 235.952 | 121515.28 | 121515.28 | 100
33 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- | 2018-06-09 17:48 | 2018-06-10 17:20 | -- | -- |  | 0 | 0 | 0 | 0.98056 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=432kV
[6 empty] | 2018-06-28 02:54 | 2018-06-28 10:56 |  |  |  | 0 | 0 | 0 | 0.33472 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=432kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 07:34 | [6 empty] | 720 | 515 | 235.952 | 121515.28 | 121515.28 | 100
34 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2018-06-01 20:48 | 2018-06-02 10:22 | -- | -- | -- | 0 | 0 | 0 | 0.56528 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427KV
[6 empty] | 2018-06-02 10:22 | 2018-06-02 20:52 |  |  |  | 0 | 0 | 0 | 0.4375 |  |  |  | LCSD | S/D availed for restoration of 765KV Varanasi-Kanpur-2
[6 empty] | 2018-06-09 17:48 | 2018-06-10 17:15 |  |  |  | 0 | 0 | 0 | 0.97708 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=432kV
[6 empty] | 2018-06-13 14:30 | 2018-06-13 15:17 |  |  |  | 0 | 0 | 0.032639 | 0 |  |  |  | LNCC | Tripped due to heavy storm caused by R-N fault,F.D.=8.8km from FTP, F.C.=17.8KA, F.D.=260km from MNP ,F.C.=1.672KA(Kanpur Jurisdiction)
[6 empty] | 2018-06-17 07:14 | 2018-06-18 08:04 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:50 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=429KV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.032639 | 1900-01-02 00:21 | [6 empty] | 719.2167 | 469 | 260.051 | 121963.919 | 121963.919 | 100
35 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- | 2018-06-02 10:22 | 2018-06-02 20:47 | -- | -- | -- | 0 | 0 | 0 | 0.43403 |  |  |  | LCSD | S/D availed for restoration of 765KV Varanasi-Kanpur-2
[6 empty] | 2018-06-27 06:29 | 2018-06-27 09:58 |  |  |  | 0 | 0 | 0 | 0.14514 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=427kV
[6 empty] | 2018-06-28 02:52 | 2018-06-28 10:52 |  |  |  | 0 | 0 | 0 | 0.33333 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=432kV
[6 empty] | 2018-06-09 20:52 | 2018-06-09 20:52 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Auto reclosed successfully from both end due to B-N fault. FTP: FD-260.2km, FC-1.58KA. Fault in Mainpuri TL jurisdiction
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.9125 | [6 empty] | 720 | 469 | 260.051 | 121963.919 | 121963.919 | 100
36 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 45.94 | 23659.1 | 23659.1 | 100
37 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 45.94 | 23659.1 | 23659.1 | 100
38 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | 2018-06-26 08:07 | 2018-06-26 19:15 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LCSD | S/D availed for replacement of CVT under add-cap.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 291 | 240 | 69840 | 69840 | 100
39 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 72.6 | 37389 | 37389 | 100
40 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 73.2 | 37698 | 37698 | 100
41 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2018-06-06 10:37 | 2018-06-06 10:37 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R successfully at both end on Y-N fault. F.D.=205.2KM from Ballabgarh & 145.4KM from Kanpur, F.C.= 1.83KA at Ballabhgarh & 2.8KA at Kanpur. Fault was in Mainpuri jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 342 | 385.69 | 131905.98 | 131905.98 | 100
42 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 361 | 370.772 | 133848.692 | 133848.692 | 100
43 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 361 | 370.772 | 133848.692 | 133848.692 | 100
44 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- | 2018-06-24 16:36 | 2018-06-24 17:18 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to Y-N fault. FD: FTP-67.7km, KNP-84.7km, FC: FTP-2.89KA, KNP-9.568KA. Fault in Kanpur TL jurisdiction
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 107.079 | 55145.685 | 55145.685 | 100
45 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 107.1 | 55156.5 | 55156.5 | 100
46 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | 2018-06-17 18:26 | 2018-06-18 19:36 |  |  |  | 0 | 0 | 0 | 1899-12-31 01:10 |  |  |  | OSFD | Emergency H/T from Panki (UP) end due to blast in 400/220KV ICT-2 at Panki(UP) & fire incident occurred at Panki.
[6 empty] | 2018-06-21 01:24 | 2018-06-21 05:30 |  |  |  | 0 | 0.17083 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault,F.D.=6.8km from Kanpur,F.C.=12KA(UPPCL Jurisdiction) caused by R Ph CT blast in 400KV Bus coupler bay at UPPCL/Panki end.
[6 empty] | 2018-06-25 13:21 | 2018-06-25 14:06 |  |  |  | 0 | 0 | 0 | 0.03125 |  |  |  | OSFD | Emergency S/D availed by UPPCL for shifting of line from Bus-1 to Bus-2 at Panki end
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.17083 | 0 | 1899-12-31 01:55 | [6 empty] | 720 | 515 | 5.922 | 3049.83 | 3049.83 | 100
47 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | 2018-06-17 18:26 | 2018-06-18 19:39 |  |  |  | 0 | 0 | 0 | 1899-12-31 01:13 |  |  |  | OSFD | Emergency H/T from Panki (UP) end due to blast in 400/220KV ICT-2 at Panki(UP) & fire incident occurred at Panki.
[5 empty] | -- | 2018-06-21 01:24 | 2018-06-21 05:30 |  |  |  | 0 | 0.17083 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault,F.D.=6.1km from Kanpur,F.C.=20.7KA(UPPCL Jurisdiction) caused by R Ph CT blast in 400KV Bus coupler bay at UPPCL/Panki end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.17083 | 0 | 1899-12-31 01:13 | [6 empty] | 720 | 515 | 5.86 | 3017.9 | 3017.9 | 100
48 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 289 | 263.933 | 76276.637 | 76276.637 | 100
49 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 289 | 263.933 | 76276.637 | 76276.637 | 100
50 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 | 100
51 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 | 100
52 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | 2018-06-22 01:32 | 2018-06-22 03:23 |  |  |  | 0 | 0.077083 | 0 | 0 |  |  |  | OMSU | Line Tripped because of CT blast at UP end, Busbar protection operated at UP end and DT Received at Lko(PG) end.
[6 empty] | 2018-06-28 03:46 | 2018-06-28 05:59 |  |  |  | 0 | 0.092361 | 0 | 0 |  |  |  | OMSU | Tripped only from Lucknow(UP) end and remain charged from Lucknow(PG) end due to some problem at Lucknow(UP) end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.16944 | 0 | 0 | [6 empty] | 720 | 515 | 41.743 | 21497.645 | 21497.645 | 100
53 | NR140114 | 400KV LUCKNOW-SHAHJHNPR-I | 169.785 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 371 | 169.785 | 62990.235 | 62990.235 | 100
54 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 169.729 | 87410.435 | 87410.435 | 100
55 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.281 | 50614.715 | 50614.715 | 100
56 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[8 empty] | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.281 | 50614.715 | 50614.715 | 100
57 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- | 2018-06-26 20:30 | 2018-06-26 22:01 | -- | -- | -- | 0 | 0.063194 | 0 | 0 |  |  |  | OMSU | Tripped due to bursting of 400kv B phase CT of 240MVA ICT 2 at Sultanpur end(UPPCL).
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.063194 | 0 | 0 | [6 empty] | 720 | 515 | 41.743 | 21497.645 | 21497.645 | 100
58 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 73.826 | 38020.39 | 38020.39 | 100
59 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 734.52 | 515 | 73.826 | 38020.39 | 38020.39 | 100
60 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 691 | 30.703 | 21215.773 | 21215.773 | 100
61 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 691 | 31.159 | 21530.869 | 21530.869 | 100
62 | NR140142 | 400KV MEERUT-BAREILLY-I | 66.009 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
63 | NR140130 | 400KV MEERUT-BAREILLY-II | 66.009 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 616 | 66.009 | 40661.544 | 40661.544 | 100
64 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 433 | 279.245 | 120913.085 | 120913.085 | 100
65 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 433 | 279.245 | 120913.085 | 120913.085 | 100
66 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | 2018-06-19 13:03 | 2018-06-19 18:10 |  |  |  | 0.21319 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for replacement of Y-phase line LA at Allahabad due to high THRC Value(THRC value=155mA, which should be<100mA).
[6 empty] | 2018-06-02 15:24 | 2018-06-02 16:26 |  |  |  | 0 | 0.043056 | 0 | 0 |  |  |  | OMSU | Tripped due to 400kV Bus-1 fault at NTPC, Singrauli due to haevy storm reported by Singrauli.
[6 empty] | 2018-06-19 18:10 | 2018-06-19 18:33 |  |  |  | 0 | 0 | 0 | 0.015972 |  |  |  | OSFD | Emergency S/D availed by NTPC, Singrauli for closing of line isolator which was automatically opened at NTPC,Singrauli end during closing period.
[6 empty] | 2018-06-25 16:06 | 2018-06-25 17:00 |  |  |  | 0 | 0 | 0.0375 | 0 |  |  |  | LNCC | Tripped on B-N fault due to heavy lightning. FD: Allahabad-225km, FC: Allahabad-1.9KA. Fault in Singrauli(NTPC) jurisdiction.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.21319 | 0.043056 | 0.0375 | 0.015972 | [6 empty] | 719.1 | 332 | 224 | 74368 | 73838.8437 | 99.2885
67 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | 2018-06-10 14:43 | 2018-06-10 14:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Tripped only from Singrauli end due to R-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli and Auto-reclosed successful at Allahabad end. FD: 108kM from Allahabad. FC:3.058kA at Allahabad.
[6 empty] | 2018-06-02 15:24 | 2018-06-02 16:38 |  |  |  | 0 | 0.051389 | 0 | 0 |  |  |  | OMSU | Tripped due to 400kV Bus-1 fault at NTPC, Singrauli due to haevy storm reported by Singrauli.
[6 empty] | 2018-06-04 13:42 | 2018-06-04 13:52 |  |  |  | 0 | 0.0069444 | 0 | 0 |  |  |  | OMSU | Tripped only from NTPC/Singrauli end due to problem at their end
[6 empty] | 2018-06-10 14:43 | 2018-06-10 17:00 |  |  |  | 0 | 0.095139 | 0 | 0 |  |  |  | OMSU | Tripped only from Singrauli end due to R-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli and Auto-reclosed successful at Allahabad end. FD: 108kM from Allahabad. FC:3.058kA at Allahabad.
[6 empty] | 2018-06-12 22:16 | 2018-06-12 22:52 |  |  |  | 0.025 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to R-N fault,M1:F.D.=109km from Alld,F.C.=2.99KA, M2:F.D.=102.2km from Alld ,F.C.=2.731KA,F.D.=103.06km from Singrauli( Mirzapur Jurisdiction)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.025 | 0.15347 | 0 | 0 | [6 empty] | 720 | 306 | 202 | 61812 | 61760.49 | 99.9167
68 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- | 2018-06-10 15:05 | 2018-06-10 15:05 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  | LART | Tripped only (unsuccessful A/R) from Anpara end due to Y-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli. FD:2.338kM from Singrauli and 22.2kM from Anpara. Fault in Shaktinagar jurisdiction.
[6 empty] | 2018-06-02 15:24 | 2018-06-03 01:40 |  |  |  | 0 | 0.42778 | 0 | 0 |  |  |  | OMSU | Tripped due to 400kV Bus-1 fault at NTPC, Singrauli due to haevy storm reported by Singrauli.
[6 empty] | 2018-06-10 15:05 | 2018-06-10 18:44 |  |  |  | 0 | 0.15208 | 0 | 0 |  |  |  | OMSU | Tripped only (unsuccessful A/R) from Anpara end due to Y-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli. FD:2.338kM from Singrauli and 22.2kM from Anpara.
[6 empty] | 2018-06-25 16:06 | 2018-06-25 17:20 |  |  |  | 0 | 0 | 0.051389 | 0 |  |  |  | LNCC | Tripped on B-N fault due to heavy lightning. FD: Singrauli-14.43km, Anpara- 10.10km, FC: Singrauli-13KA, Anpara-7.826KA. Fault in Shaktinagar TL jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.57986 | 0.051389 | 0 | [6 empty] | 718.7667 | 515 | 25.057 | 12904.355 | 12904.355 | 100
69 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 236 | 330.953 | 78104.908 | 78104.908 | 100
70 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- | 2018-06-25 18:47 | 2018-06-26 06:28 | -- | -- |  | 0.48681 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault. FD: Singrauli-210.3km, LKO-152.3km, FC: Singrauli-1.64KA, LKO-1.344KA. Charging attempt failed at 2004 hrs on SOTF. Fault in Allahabad & Mirzapur TL jurisdiction
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.48681 | 0 | 0 | 0 | [6 empty] | 720 | 337 | 408.6 | 137698.2 | 135463.7917 | 98.3773
71 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- | 2018-06-11 08:42 | 2018-06-12 01:00 | -- | -- |  | 0 | 0 | 0 | 0.67917 |  |  |  | LCSD | S/D availed for Stringing between 5/0 to 5A/0 of New 400 KV S/C Singrauli-Allahabad T/L and existing tower no 06 to 07 of 400 KV SINGRAULI (NTPC) -RIHAND (NTPC) D/C line
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.67917 | [6 empty] | 720 | 515 | 42.026 | 21643.39 | 21643.39 | 100
72 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- | 2018-06-11 09:23 | 2018-06-12 01:05 | -- | -- |  | 0 | 0 | 0 | 0.65417 |  |  |  | LCSD | S/D availed for Stringing between 5/0 to 5A/0 of New 400 KV S/C Singrauli-Allahabad T/L and existing tower no 06 to 07 of 400 KV SINGRAULI (NTPC) -RIHAND (NTPC) D/C line
[8 empty] | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.65417 | [6 empty] | 720 | 515 | 43.952 | 22635.28 | 22635.28 | 100
73 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 3.341 | 1720.615 | 1720.615 | 100
74 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 3.317 | 1708.255 | 1708.255 | 100
75 | NR140164 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | 2018-06-08 14:48 | 2018-06-08 18:56 |  |  |  | 0.17222 | 0 | 0 | 0 |  |  |  | SEFT | Tripped due to B Ph LA blast at Varanasi end. Details at Varanasi: B-N fault, FD-118Mtrs, FC-23KA.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.17222 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 69.677 | 35883.655 | 35677.6562 | 99.4259
76 | NR140165 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 69.677 | 35883.655 | 35883.655 | 100
77 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 21.233 | 14587.071 | 14587.071 | 100
78 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 21.233 | 14587.071 | 14587.071 | 100
79 | NR340008 | 400KV LKO(765)-KANPUR(GIS)-I | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 159.7 | 109713.9 | 109713.9 | 100
80 | NR340009 | 400KV LKO(765)-KANPUR(GIS)-II | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 159.7 | 109713.9 | 109713.9 | 100
81 | NR340010 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 28.19 | 19366.53 | 19366.53 | 100
82 | NR340011 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 28.19 | 14517.85 | 14517.85 | 100
83 |  | 400KV Kanpur(GIS)-Allahabad-1 | 239.5 | NR3 | -- | 2018-06-04 09:51 | 2018-06-04 20:42 |  |  |  | 0 | 0 | 0 | 0.45208 |  |  |  | LCSD
[6 empty] | 2018-06-05 05:40 | 2018-06-05 21:02 |  |  |  | 0 | 0 | 0 | 0.64028 |  |  |  | LCSD
[6 empty] | 2018-06-14 14:17 | 2018-06-14 20:47 |  |  |  | 0 | 0 | 0 | 0.27083 |  |  |  | LCSD
[6 empty] | 2018-06-22 08:08 | 2018-06-22 08:08 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 08:43 | [6 empty] | 720 | 515 | 239.5 | 123342.5 | 123342.5 | 100
84 |  | 400KV Kanpur(GIS)-Allahabad-2 | 239.5 | NR3 | -- | 2018-06-04 09:52 | 2018-06-04 20:43 |  |  |  | 0 | 0 | 0 | 0.45208 |  |  |  | LCSD | S/D availed for stringing of multi circuit portion of 400KV Allahabad-Singrauli line
[6 empty] | 2018-06-05 05:40 | 2018-06-05 21:03 |  |  |  | 0 | 0 | 0 | 0.64097 |  |  |  | LCSD | S/D availed for stringing of multi circuit portion of 400KV Allahabad-Singrauli line
[6 empty] | 2018-06-14 14:17 | 2018-06-14 20:50 |  |  |  | 0 | 0 | 0 | 0.27292 |  |  |  | LCSD | S/D availed for balance completion of stringing of multi circuit portion of 400KV Allahabad-Singrauli line
[6 empty] | 2018-06-22 08:03 | 2018-06-22 08:48 |  |  |  | 0.03125 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to B-N fault. F.D.= 229.4KM from Kanpur(GIS) & 13.92KM from Allahabad. F.C.= 1.5KA at Kanpur(GIS) & 15.81KA at Allahabad. The fault was in Allahabad Jurisdiction.
[6 empty] | 2018-06-13 16:11 | 2018-06-13 16:11 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to B-N fault,F.D.=250km from Kanpur GIS , F.C.=2.5KA, F.D.=12.49km from ALLD, F.C.=16.19KA (Allahabad Jurisdiction)
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.03125 | 0 | 0 | 1899-12-31 08:47 | [6 empty] | 720 | 515 | 239.5 | 123342.5 | 123214.0182 | 99.8958
85 |  | 400KV ORAI-ORAI(UP)-I | 41.832 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 41.832 | 21543.48 | 21543.48 | 100
86 |  | 400KV ORAI-ORAI(UP)-II | 41.832 | NR3 | -- | 2018-06-02 04:45 | 2018-06-02 06:24 |  |  |  | 0 | 0 | 0.06875 | 0 |  |  |  | GOVC | Tripped on over voltage protection operated at Orai.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0.06875 | 0 | [6 empty] | 718.35 | 515 | 41.832 | 21543.48 | 21543.48 | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 21.879 | 2888.028 | 2888.028 | 100
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 16.894 | 2230.008 | 2230.008 | 100
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- | 2018-06-06 18:42 | 2018-06-06 19:45 | -- | -- |  | 0 | 0.04375 | 0 | 0 |  |  |  | OMSU | Tripped only from Rewa Road (UP) end due to problem at Rewa Road (UP).
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.04375 | 0 | 0 | [6 empty] | 720 | 132 | 3 | 396 | 396 | 100
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | 2018-06-06 18:42 | 2018-06-06 19:45 |  |  |  | 0 | 0.04375 | 0 | 0 |  |  |  | OMSU | Tripped only from Rewa Road (UP) end due to problem at Rewa Road (UP).
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.04375 | 0 | 0 | [6 empty] | 720 | 132 | 3 | 396 | 396 | 100
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | 2018-06-01 17:11 | 2018-06-01 21:02 |  |  |  | 0 | 0 | 0 | 0.16042 |  |  |  | LCSD | S/D availed for balance rectification work on collapsed tower caused by heavy storm
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.16042 | [6 empty] | 720 | 132 | 182.176 | 24047.232 | 24047.232 | 100
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | 2018-06-01 10:36 | 2018-06-01 16:48 |  |  |  | 0 | 0 | 0 | 0.25833 |  |  |  | LCSD | S/D availed for balance rectification work on collapsed tower caused by heavy storm
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.25833 | [6 empty] | 720 | 132 | 182.176 | 24047.232 | 24047.232 | 100
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 109 | 234.59 | 25570.31 | 25570.31 | 100
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 156 | 59.01 | 9205.56 | 9205.56 | 100
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 5.284 | 692.204 | 692.204 | 100
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- | 2018-06-08 15:11 | 2018-06-08 18:05 | -- | -- |  | 0 | 0 | 0 | 0.12083 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending hot spot in R Ph line isolator at UP end
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.12083 | [6 empty] | 720 | 131 | 5.284 | 692.204 | 692.204 | 100
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | 2018-06-18 12:00 | 2018-06-18 12:28 |  |  |  | 0 | 0.019444 | 0 | 0 |  |  |  | OMSU | Tripped only from UPPCL (Kanpur South) end on R-N fault and autoreclosed successfully at Fatehpur end. FD: 51.5kM from Fatehpur (Total line length-65kM). FC:2.9kA at Fatehpur. Fault in UPPCL jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.019444 | 0 | 0 | [6 empty] | 720 | 131 | 6.17 | 808.27 | 808.27 | 100
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 6.17 | 808.27 | 808.27 | 100
13 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- |  |  |  |  | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 10.4 | 1362.4 | 1362.4 | 100
14 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 14.86 | 1946.66 | 1946.66 | 100
15 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)-1 | 8.717 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.37778
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.37778 | [6 empty] | 720 | 131 | 8.717 | 1141.927 | 1141.927 | 100
16 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- | 2018-06-17 18:13 | 2018-06-17 21:29 | -- | -- | -- | 0 | 0.13611 | 0 | 0 |  |  |  | OMSU | Tripped on R-Y fault due to blast in 400/220KV ICT-2 at Panki(UP) & fire incident occurred at Panki. FD: KNP-23.8KM, FC: R-5.826KA, Y-5.390KA. Fault at UPPCL end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.13611 | 0 | 0 | [6 empty] | 720 | 131 | 14.86 | 1946.66 | 1946.66 | 100
17 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 143.553 | 18805.443 | 18805.443 | 100
18 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 143.553 | 18805.443 | 18805.443 | 100
19 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | 2018-06-12 09:04 | 2018-06-14 22:42 |  |  |  | 0 | 0 | 0 | 1900-01-01 13:38 |  |  |  | OSPD | S/D availed by NTPC/Unchahar for AMP work at their end
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-01 13:38 | [6 empty] | 720 | 131 | 144.63 | 18946.53 | 18946.53 | 100
20 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | 2018-06-18 09:28 | 2018-06-19 19:19 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:51 |  |  |  | OSPD | S/D availed by NTPC/Unchahar for AMP work at their end
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:51 | [6 empty] | 720 | 131 | 144.63 | 18946.53 | 18946.53 | 100
21 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 156 | 177.88 | 27749.28 | 27749.28 | 100
22 | NR122025 | 220KV RAIBRLY-CHINHAT | 1.19 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 1.19 | 157.08 | 157.08 | 100
23 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 1.19 | 157.08 | 157.08 | 100
24 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- | 2018-06-01 22:14 | 2018-06-01 23:16 | -- | -- | -- | 0 | 0 | 0.043056 | 0 |  |  |  | LNCC | Tripped on Y-B fault due to heavy thunderstorm. Sitarganj- FD: 88.93km, FC: Iy=1.44KA,Ib=1.43KA
[6 empty] | 2018-06-11 12:34 | 2018-06-11 15:52 |  |  |  | 0.1375 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for attending hot spot in Y phase line isolator at Sitarganj end.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.1375 | 0 | 0.043056 | 0 | [6 empty] | 718.9667 | 132 | 105.72 | 13955.04 | 13890.9875 | 99.541
25 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | 2018-06-07 12:48 | 2018-06-07 13:54 |  |  |  | 0 | 0.045833 | 0 | 0 |  |  |  | OMSU | Tripped due to over voltage protection operated at Tanakpur(NHPC) end & Bus -B tripped at Bareilly(UP).
[6 empty] | 2018-06-13 16:16 | 2018-06-13 18:02 |  |  |  | 0.073611 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D taken for attending hot spot in B ph wave trap at Bareily(UP) end by Powergrid
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.073611 | 0.045833 | 0 | 0 | [6 empty] | 720 | 132 | 106 | 13992 | 13957.6678 | 99.7546
26 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | 2018-06-23 15:16 | 2018-06-23 15:30 |  |  |  | 0 | 0.0097222 | 0 | 0 |  |  |  | SRMU | Tripped only from Tanakpur(NHPC) due to Mal operation of E/F protection relay at Tanakpur(NHPC) end.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.0097222 | 0 | 0 | [6 empty] | 720 | 132 | 42.55 | 5616.6 | 5616.6 | 100
27 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 0.92 | 121.44 | 121.44 | 100
28 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 0.92 | 121.44 | 121.44 | 100
29 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 42.5 | 5610 | 5610 | 100
30 | NR320001 | 220KV KNP-RANIA | 1.683 | NR3 | -- | 2018-06-06 10:00 | 2018-06-06 19:04 | -- | -- |  | 0 | 0 | 0 | 0.37778 |  |  |  | OSPD | S/D availed by UPPCL for maintenance work at their end
[6 empty] | 2018-06-07 08:53 | 2018-06-07 15:58 |  |  |  | 0 | 0 | 0 | 0.29514 |  |  |  | OSPD | S/D availed by UPPCL for maintenance work at their end
[6 empty] | 2018-06-28 12:58 | 2018-06-28 19:25 |  |  |  | 0 | 0 | 0 | 0.26875 |  |  |  | OSFD | Emergency hand tripped by UPPCL to attend R- phase broken jumper at Tower No. 20. (UPPCL jurisdiction)
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.94167 | [6 empty] | 720 | 132 | 18.372 | 2425.104 | 2425.104 | 100
31 | NR320003 | 220KV RAIBRLY-CG CITY(UP) | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 18.372 | 2425.104 | 2425.104 | 100
31 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP) | 1.683 | NR3 | -- | 2018-06-10 15:09 | 2018-06-10 22:50 | -- | -- |  | 0 | 0.32014 | 0 | 0 |  |  |  | OMSU | Tripped due to B-N fault due to heavy wind and rain. FD:1.646Km from Raibareilly FC:11.01kA at Raibareilly. Fault in UPPCL jurisdiction.
[6 empty] | 2018-06-10 22:50 | 2018-06-11 02:25 |  |  |  | 0.14931 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for attending B-phase broken jumper at Loc. No 09.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.14931 | 0.32014 | 0 | 0 | [6 empty] | 720 | 132 | 18.372 | 2425.104 | 2413.0346 | 99.5023
[5 empty] | -- | [17 empty] | 2420.56
D |  | 132 KV TRANS LINES |  |  | --
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 | 58 | 2900 | 2900 | 100
134 | Lines | TOTAL FOR T/LS | [8 empty] | 1900-01-01 09:48 | 1900-01-01 00:20 | 1900-01-11 01:41 | 1900-02-27 15:29 | [8 empty] | 19614.664 | 10651442.852 | 10637727.4619 | 99.8712 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.857 | % (HVDC) | 90.6761
E |  | 765/400 KV ICT'S |  |  | -- | [16 empty] | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | 2018-06-05 10:06 | 2018-06-05 15:15 |  |  |  | 0.21458 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for Twin jumper modification work in spare ICT and its AMP.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.21458 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1489.2708 | 99.2847
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | 2018-06-06 10:09 | 2018-06-06 17:41 |  |  |  | 0.31389 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for Twin jumper modification work in spare ICT and its AMP.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.31389 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1484.3056 | 98.9537
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | 2018-06-01 08:20 | 2018-06-01 17:22 |  |  |  | 0.37639 | 0 | 0 | 0 |  |  |  | OSFT | Emergency H/T due to heavy sparking in IPS tube which are connected between 02 isolators of B Ph at 765KV side.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.37639 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1481.1806 | 98.7454
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
17 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
18 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
19 | NR3ICT701 | 765/400KV ICT-I Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
20 | NR3ICT702 | 765/400KV ICT-II Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
21 | NR3ICT05 | 1000MVA ICT-1 ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1000 |  | 1000 | 1000 | 100
22 | NR3ICT06 | 1000MVA ICT-2 ORAI(GIS) | 1000 | NR3 |  | 2018-06-09 05:13 | 2018-06-09 09:26 |  |  |  | 0.17569 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for replacement of 765KV R Ph Tie Bay(705) CB at Orai
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.17569 | 0 | 0 | 0 | [6 empty] | 720 | 1000 |  | 1000 | 994.1435 | 99.4144
F |  | 400/220 KV ICT'S |  | NR3 | --
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500 | 100
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | 2018-06-01 | 2018-06-09 00:04 |  |  |  | 1900-01-07 00:04 | 0 | 0 | 0 |  |  |  | SICT | Tripped due to buchholz relay operation.Replacement is under progress and expected to restore on 08.06.18.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-07 00:04 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 230.9708 | 73.3241
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500 | 100
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
[11 empty] | 0 | 0 | 0 | 0
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315 | 100
G |  | 220/132 KV ICT'S |  | NR3 | --
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | 2018-06-09 09:57 | 2018-06-09 11:55 |  |  |  | 0 | 0 | 0 | 0.081944 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending hot spot in 132KV Main Bus at 132KV Raebareilly(UP) S/S
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.081944 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
4 | NR1ICT38 | 220/132KV ICT-II RAIBAREILLY | 200 | NR3 | -- | 2018-06-09 09:57 | 2018-06-09 11:55 |  |  |  | 0 | 0 | 0 | 0.081944 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending hot spot in 132KV Main Bus at 132KV Raebareilly(UP) S/S
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.081944 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 200 | NR3 | -- | 2018-06-09 09:57 | 2018-06-09 12:14 |  |  |  | 0 | 0 | 0 | 0.095139 |  |  |  | OSFD | Emergency S/D availed by UPPCL for attending hot spot in 132KV Main Bus at 132KV Raebareilly(UP) S/S
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.095139 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
--
45 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 1900-01-08 02:00 | 0 | 0 | 0.25903 | [7 empty] | 31425 |  | 31425 | 31289.8713 | 99.57 | %
H |  | HVDC RIHAND-DADRI |  |  | -- | [16 empty] | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2018-06-02 05:05 | 2018-06-02 05:05 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Rihand-773.23km, Dadri-41.77km. Fault in NR-1 jurisdiction.
[6 empty] | 2018-06-18 01:00 | 2018-06-18 01:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Rihand-758.98km, Dadri-56.02km. Fault in NR-1 jurisdiction.
[6 empty] | 2018-06-29 20:57 | 2018-06-29 20:57 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Rihand- 767.83km, Dadri-47.17km. Fault in NR-1 jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 611250 | 100
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2018-06-14 01:05 | 2018-06-14 01:05 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | A/R operated successfully from both end due to dc transient earth fault, F.D.=137.23km from Rihand, F.D.=677.77km from Dadri.(Mirzapur jurisdiction)
[6 empty] | 2018-06-25 16:53 | 2018-06-25 16:53 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Rihand-523.83km, Dadri-291.17km. Fault in Kanpur TL jurisdiction
[6 empty] | 2018-06-26 11:14 | 2018-06-26 11:14 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD: Rihand-717.4km, Dadri-97.6km. Fault in NR-1 jurisdiction
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 611250 | 100
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | 2018-06-27 22:52 | 2018-06-27 23:20 |  |  |  | 0.019444 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to change over logic failure at Bhiwadi end.
[6 empty] | 2018-06-28 00:56 | 2018-06-28 01:38 |  |  |  | 0.029167 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to transformer isolator configuration status missing to pole 1 control at Bhiwadi and Continuous rain at Bhiwadi.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.048611 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 985632.8177 | 99.838
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2018-06-18 23:35 | 2018-06-18 23:35 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LART | Transient fault. FD:731.561kM from Balia and 58.229kM from Bhiwadi. Tower No 1993. Fault in NR-1 jurisdiction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 987232.5 | 100
5 | NR1DCP04 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2018-06-01 | 2018-06-25 01:25 |  |  |  | 0 | 0 | 1900-01-23 01:25 | 0 |  |  |  | LNCC | Tripped due to heavy storm due to 3 Nos. Tower(4328,4347,4428) damaged.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 1900-01-23 01:25 | 0 | [6 empty] | 142.5833 | 1500 | 1728 | 2592000 | 2592000 | 100
6 | NR1DCP03 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | 2018-06-10 06:25 | 2018-06-10 15:54 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LVRD | Blocked for voltage regulation as per NLDC instruction
[6 empty] | 2018-06-20 06:02 | 2018-06-25 11:51 |  |  |  | 0 | 0 | 0 | 1900-01-04 05:49 |  |  |  | LCSD | S/D availed for restoration of HVDC line to normal tower at two separate locations.
[6 empty] | 2018-06-28 01:53 | 2018-06-29 09:52 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:59 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 13:48 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000 | 100
7 | NR1DCP03 | 800KV HVDC AGRA-APD POLE-III | 789.786 | NR3 | -- | 2018-06-01 | 2018-06-25 01:42 |  |  |  | 0 | 0 | 1900-01-23 01:42 | 0 |  |  |  | LNCC | Tripped due to heavy storm due to 3 Nos. Tower(4328,4347,4428) damaged.
[6 empty] | 2018-06-26 05:10 | 2018-06-26 06:42 |  |  |  | 0.063889 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to converter T/F Differential Protection Operated at HVDC Agra.
[6 empty] | 2018-06-28 03:12 | 2018-06-30 16:16 |  |  |  | 0 | 0 | 0 | 1900-01-01 13:04 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.063889 | 0 | 1900-01-23 01:42 | 1900-01-01 13:04 | [6 empty] | 142.3 | 1500 | 1728 | 2592000 | 2564070.2741 | 98.9225
8 | NR1DCP04 | 800KV HVDC AGRA-APD POLE-IV | 789.786 | NR3 | -- | 2018-06-15 16:09 | 2018-06-15 18:14 |  |  |  | 0.086806 | 0 | 0 | 0 |  |  |  | OSFT | S/D availed to attend hot spot in P4.WT.Q11.Q11 B-phase isolator at Agra.
[6 empty] | 2018-06-01 | 2018-06-07 23:08 |  |  |  | 0 | 0 | 1900-01-05 23:08 | 0 |  |  |  | LNCC | Tripped due to heavy storm due to 3 Nos. Tower(4328,4347,4428) damaged.
[6 empty] | 2018-06-09 17:54 | 2018-06-10 |  |  |  | 0 | 0 | 0 | 0.25417 |  |  |  | LVRD | Blocked for voltage regulation as per NLDC instruction
[6 empty] | 2018-06-20 05:49 | 2018-06-25 12:22 |  |  |  | 0 | 0 | 0 | 1900-01-04 06:33 |  |  |  | LCSD | S/D availed for restoration of HVDC line to normal tower at two separate locations.
[6 empty] | 2018-06-27 04:41 | 2018-06-27 11:48 |  |  |  | 0 | 0 | 0 | 0.29653 |  |  |  | LVRD | Blocked on Voltage regulation as per NRLDC instruction.
[6 empty] | 2018-06-28 03:09 | 2018-06-28 21:54 |  |  |  | 0 | 0 | 0 | 0.78125 |  |  |  | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
[6 empty] | 2018-06-29 | 2018-06-29 00:36 |  |  |  | 0.025 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to Zone-1 Fire in VESDA system (Mal functioning) at Alipuduar.
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.11181 | 0 | 1900-01-05 23:08 | 1900-01-05 14:31 | [6 empty] | 552.8667 | 1500 | 1728 | 2592000 | 2579419.7516 | 99.5147
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0.1125 | 0 | 1900-02-16 03:07 | 1900-01-08 02:52 | [8 empty] | 10121.572 | 13564965 | 13522855.3434 | 99.6896 | %
J |  | HVDC BTB VINDH |  |  | -- | [16 empty] | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2018-06-26 15:21 | 2018-06-26 15:55 |  |  |  | 0.023611 | 0 | 0 | 0 |  |  |  | OSFT | Emergency Hand Tripped due to attend sparking in R phase of 400kV filter bank.
[6 empty] | 2018-06-02 15:23 | 2018-06-02 17:30 |  |  |  | 0 | 0 | 0.088194 | 0 |  |  |  | SNCC | Tripped due to DC Over current protection operated due to heavy storm at Vindhyachal.
[6 empty] | 2018-06-10 15:05 | 2018-06-10 18:04 |  |  |  | 0 | 0.12431 | 0 | 0 |  |  |  | OMSU | Tripped due to DC over current protection due to external disturbance at NTPC, Singrauli due to heavy wind pressure and rain.
[6 empty] | 2018-06-12 20:00 | 2018-06-12 22:03 |  |  |  | 0 | 0.085417 | 0 | 0 |  |  |  | OMSU | Tripped due to DC over current protection caused by external disturbance in western system at VSTPP/NTPC
[6 empty] | 2018-06-25 16:06 | 2018-06-25 17:44 |  |  |  | 0 | 0.068056 | 0 | 0 |  |  |  | OMSU | Tripped on DC over current protection operated due to external disturbance in north side system at NTPC due to lightning & heavy rain.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.023611 | 0.27778 | 0.088194 | 0 | [6 empty] | 717.8833 | 250 |  | 250 | 249.8027 | 99.9211
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | 2018-06-01 | 2018-07-01 |  |  |  | 1900-01-29 | 0 | 0 | 0 |  |  |  | OMST | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL.
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 1900-01-29 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 0 | 0
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 1900-01-29 00:34 | 0.27778 | 0.088194 | 0 | [9 empty] | 500 | 249.8027 | 49.9605 | %
3 | NR1DCB02 | Sasaram HVDC B/B BLOCK-I | 250 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250 | 100
|  | HVDC BTB TOTAL |  |  | -- | [5 empty] | 1900-01-29 00:34 | 0.27778 | 0.088194 | 0 | [7 empty] | RC
L |  | SVC, KANPUR |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250 | 100
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 280 |  | 280 | 280 | 100
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 530 | 530 | 100 | %
M |  | Bus & Switch Line Reactor |  |  | -- | [16 empty] | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- | 2018-06-09 22:01 | 2018-06-10 04:30 | -- | -- |  | 0 | 0 | 0 | 0.27014 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=756kV
[6 empty] | 2018-06-01 | 2018-06-01 17:08 |  |  |  | 0 | 0 | 0 | 0.71389 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=747kV
[6 empty] | 2018-06-22 11:16 | 2018-06-24 18:35 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:19 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=755kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 06:56 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- | 2018-06-01 | 2018-06-01 18:55 | -- | -- |  | 0 | 0 | 0 | 0.78819 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=748kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.78819 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- | 2018-06-06 21:16 | 2018-06-08 17:05 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 19:49 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=393kV
[6 empty] | 2018-06-21 19:27 | 2018-07-01 |  |  |  | 0 | 0 | 0 | 1900-01-08 04:33 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 00:22 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- | 2018-06-06 21:17 | 2018-06-08 17:05 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 19:48 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=393kV
[5 empty] | -- | 2018-06-21 19:24 | 2018-07-01 | -- | -- |  | 0 | 0 | 0 | 1900-01-08 04:36 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 00:24 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- | 2018-06-02 22:52 | 2018-06-09 07:26 | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 08:34 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=752kV
[6 empty] | 2018-06-13 18:56 | 2018-06-17 07:03 |  |  |  | 0 | 0 | 0 | 1900-01-02 12:07 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=742kV
[6 empty] | 2018-06-20 11:01 | 2018-06-28 03:13 |  |  |  | 0 | 0 | 0 | 1900-01-06 16:12 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=740kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-16 12:53 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- | 2018-06-01 | 2018-06-02 01:15 | -- | -- |  | 0 | 0 | 0 | 1899-12-31 01:15 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=748kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 01:15 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- | 2018-06-13 18:58 | 2018-06-28 03:38 | -- | -- |  | 0 | 0 | 0 | 1900-01-13 08:40 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=392kV
[6 empty] | 2018-06-28 16:49 | 2018-07-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:11 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=398kV
[6 empty] | 2018-06-01 | 2018-06-01 20:16 |  |  |  | 0 | 0 | 0 | 0.84444 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-16 12:07 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
14 | NR1BRT44 | 2X50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- | 2018-06-13 19:08 | 2018-07-01 | -- | -- |  | 0 | 0 | 0 | 1900-01-16 04:52 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=392kV
[6 empty] | 2018-06-01 | 2018-06-01 20:17 |  |  |  | 0 | 0 | 0 | 0.84514 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[5 empty] | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-17 01:09 | [6 empty] | 720 | 100 |  | 100 | 100 | 100
15 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
16 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
17 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
18 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | 2018-06-02 22:36 | 2018-06-04 07:57 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:21 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTHPR=747kV
[6 empty] | 2018-06-14 20:16 | 2018-06-15 08:23 |  |  |  | 0 | 0 | 0 | 0.50486 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=754kV
[6 empty] | 2018-06-23 00:16 | 2018-06-24 17:50 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:34 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=745kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-02 15:02 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
19 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | 2018-06-01 | 2018-06-01 20:32 |  |  |  | 0 | 0 | 0 | 0.85556 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=389kV
[6 empty] | 2018-06-02 19:07 | 2018-06-09 07:20 |  |  |  | 0 | 0 | 0 | 1900-01-05 12:13 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=385kV
[6 empty] | 2018-06-09 18:59 | 2018-06-14 07:37 |  |  |  | 0 | 0 | 0 | 1900-01-03 12:38 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=387kV
[6 empty] | 2018-06-18 20:12 | 2018-06-27 08:45 |  |  |  | 0 | 0 | 0 | 1900-01-07 12:33 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=387kV
[6 empty] | 2018-06-28 21:58 | 2018-07-01 |  |  |  | 0 | 0 | 0 | 1900-01-01 02:02 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=395kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-21 11:58 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
20 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | 2018-06-02 19:07 | 2018-06-09 07:22 |  |  |  | 0 | 0 | 0 | 1900-01-05 12:15 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=385kV
[6 empty] | 2018-06-09 18:59 | 2018-06-14 07:37 |  |  |  | 0 | 0 | 0 | 1900-01-03 12:38 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=387kV
[6 empty] | 2018-06-22 20:06 | 2018-06-27 08:45 |  |  |  | 0 | 0 | 0 | 1900-01-03 12:39 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=396kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-14 13:32 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
21 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
22 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
23 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
24 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | 2018-06-14 20:16 | 2018-06-15 08:12 |  |  |  | 0 | 0 | 0 | 0.49722 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=755kV
[6 empty] | 2018-06-23 13:01 | 2018-06-25 17:34 |  |  |  | 0 | 0 | 0 | 1900-01-01 04:33 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow = 762kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
25 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
26 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | 2018-06-02 19:38 | 2018-06-03 08:24 |  |  |  | 0 | 0 | 0 | 0.53194 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Shahajahanpur=386kV
[5 empty] | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.53194 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
27 | NR1BRT29 | 80MVAR B/Reactor SIKAR | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80 | 100
28 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
29 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
30 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
31 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
32 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
33 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
34 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
35 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
36 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
37 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
38 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
39 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
40 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
41 | NR1SRT19 | JHATIKALA 240MVAR S/R AGRA Line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
42 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
43 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
44 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
45 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
46 | NR1SRT21 | MEERUT 240MVAR S/R AGRA line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
47 | NR1SRT22 | SIKAR 50MVAR S/R AGRA Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100
48 | NR1SRT23 | SIKAR 50MVAR S/R AGRA Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50 | 100
49 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | 2018-06-05 14:47 | 2018-06-06 07:44 |  |  |  | 0 | 0 | 0 | 0.70625 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=756kV
[6 empty] | 2018-06-14 20:10 | 2018-06-17 06:56 |  |  |  | 0 | 0 | 0 | 1900-01-01 10:46 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=753kV
[6 empty] | 2018-06-01 | 2018-06-01 20:23 |  |  |  | 0 | 0 | 0 | 0.84931 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=758kV
[6 empty] | 2018-06-22 12:25 | 2018-06-27 06:13 |  |  |  | 0 | 0 | 0 | 1900-01-03 17:48 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=754kV
[6 empty] | 2018-06-30 09:26 | 2018-07-01 |  |  |  | 0 | 0 | 0 | 0.60694 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=755kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-08 08:28 | [6 empty] | 720 | 240 |  | 240 | 240 | 100
50 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 330 | NR3 | -- | 2018-06-01 | 2018-06-02 01:02 |  |  |  | 0 | 0 | 0 | 1899-12-31 01:02 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=748kV
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 01:02 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
51 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100
52 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100 | %
53 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100 | %
54 |  | 125MVAR B/Reactor-III KANPUR(GIS) | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 | 100 | %
55 |  | 240MVAR B/Reactor-I KANPUR(GIS) | 240 | NR3 | -- | 2018-06-02 19:45 | 2018-06-06 07:33 |  |  |  | 0 | 0 | 0 | 1900-01-02 11:48 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=735kV
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 11:48 | [6 empty] | 720 | 240 |  | 240 | 240 | 100 | %
56 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100 | %
56 |  | 330MVAR B/Reactor-II ALIGARH | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100 | %
57 |  | 63MVAR B/Reactor-II SOHAWAL | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 | 100 | %
57 |  | TOTAL FOR Reactor |  |  | -- | [5 empty] | 0 | 0 | 0 | 1900-05-16 16:51 | 0 | 0 | 0 |  |  |  |  | 12048.4 |  | 12048.4 | 12048.4 | 100
Formulas:
ISTS Licensee = IF(RIGHT([Code])="T",(+[DATE TIME]-[DATE TIME]),0)
ISTS Licensee = SUM(L11:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Code])="U",(+[DATE TIME]-[DATE TIME]),0)
OTHERS = SUM(M11:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Code])="C",(+[DATE TIME]-[DATE TIME]),0)
Hrs:Min = SUM(N11:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Code])="D",(+[DATE TIME]-[DATE TIME]),0)
Deemed Available = SUM(O11:[Deemed Available, row above])
Note on C11: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C89: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C93: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C107: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C116: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C125: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C132: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C136: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C141: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C305: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C308: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C578: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C581: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C776: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C781: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Sheet1
POWER GRID CORPORATION OF INDIA LTD.
CPCC, LUCKNOW
| DOC No: NR-III-CPCC- |  | DOC No: NR-III-CPCC-
MONTH –June LINE- ICT OUTAGE DETAILS
CODE | CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | NRLDC CODE | Classification- Category Code | REASON OF OUTAGE
|  |  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint- Natural calamity- Militancy | Deemed Available
[6 empty] | @ (T) | # (U) | & ( C ) | * (D)
[6 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  | Code
[6 empty] | 1900-02-09 18:27 | 1900-01-01 07:00 | 1900-03-07 08:17 | 1900-08-03 12:23
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 11 | 12
NR3ICT704 | NR3ICT704 | 306054 | 1000MVA ICT-II ORAI(GIS) | 2018-06-09 05:13 | 2018-06-09 09:26 | 0.17569 | 0 | 0 | 0 | N-730 | OSPT | S/D availed for replacement of 765KV R Ph Tie Bay(705) CB at Orai
NR1ICT47 | NR1ICT47 | 306056 | 100MVA ICT-I RAIBAREILLY | 2018-06-09 09:57 | 2018-06-09 11:55 | 0 | 0 | 0 | 0.081944 | N-748 | OSFD | Emergency S/D availed by UPPCL for attending hot spot in 132KV Main Bus at 132KV Raebareilly(UP) S/S
NR1BRT39 | NR1BRT39 | 305245 | 125MVAR B/Reactor-I GORAKHPUR | 2018-06-01 | 2018-06-01 20:32 | 0 | 0 | 0 | 0.85556 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=389kV
NR1BRT39 | NR1BRT39 | 306020 | 125MVAR B/Reactor-I GORAKHPUR | 2018-06-02 19:07 | 2018-06-09 07:20 | 0 | 0 | 0 | 1900-01-05 12:13 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=385kV
NR1BRT39 | NR1BRT39 | 306066 | 125MVAR B/Reactor-I GORAKHPUR | 2018-06-09 18:59 | 2018-06-14 07:37 | 0 | 0 | 0 | 1900-01-03 12:38 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=387kV
NR1BRT39 | NR1BRT39 | 306119 | 125MVAR B/Reactor-I Gorakhpur | 2018-06-18 20:12 | 2018-06-27 08:45 | 0 | 0 | 0 | 1900-01-07 12:33 | N-1475 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=387kV
NR1BRT39 | NR1BRT39 | 306184 | 125MVAR B/Reactor-I Gorakhpur | 2018-06-28 21:58 | 2018-07-01 | 0 | 0 | 0 | 1900-01-01 02:02 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Gorakhpur=395kV
NR1BRT49 | NR1BRT49 | 306022 | 125MVAR B/Reactor-I SHAHJHNPR | 2018-06-02 19:38 | 2018-06-03 08:24 | 0 | 0 | 0 | 0.53194 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Shahajahanpur=386kV
NR1BRT17 | NR1BRT17 | 306040 | 125MVAR B/Reactor-II BALIA | 2018-06-06 21:16 | 2018-06-08 17:05 | 0 | 0 | 0 | 1899-12-31 19:49 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=393kV
NR1BRT17 | NR1BRT17 | 306135 | 125MVAR B/Reactor-II BALIA | 2018-06-21 19:27 | 2018-07-01 | 0 | 0 | 0 | 1900-01-08 04:33 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
NR1BRT46 | NR1BRT46 | 306021 | 125MVAR B/Reactor-II GORAKHPUR | 2018-06-02 19:07 | 2018-06-09 07:22 | 0 | 0 | 0 | 1900-01-05 12:15 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=385kV
NR1BRT46 | NR1BRT46 | 306067 | 125MVAR B/Reactor-II GORAKHPUR | 2018-06-09 18:59 | 2018-06-14 07:37 | 0 | 0 | 0 | 1900-01-03 12:38 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=387kV
NR1BRT46 | NR1BRT46 | 306142 | 125MVAR B/Reactor-II Gorakhpur | 2018-06-22 20:06 | 2018-06-27 08:45 | 0 | 0 | 0 | 1900-01-03 12:39 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Gorakhpur=396kV
NR1BRT27 | NR1BRT27 | 306041 | 125MVAR B/Reactor-III BALIA | 2018-06-06 21:17 | 2018-06-08 17:05 | 0 | 0 | 0 | 1899-12-31 19:48 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=393kV
NR1BRT27 | NR1BRT27 | 306134 | 125MVAR B/Reactor-III BALIA | 2018-06-21 19:24 | 2018-07-01 | 0 | 0 | 0 | 1900-01-08 04:36 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=393kV
NR3ICT04 | NR3ICT04 | 306057 | 200MVA ICT-II RAIBAREILLY | 2018-06-09 09:57 | 2018-06-09 11:55 | 0 | 0 | 0 | 0.081944 | N-748 | OSFD | Emergency S/D availed by UPPCL for attending hot spot in 132KV Main Bus at 132KV Raebareilly(UP) S/S
NR1ICT39 | NR1ICT39 | 306058 | 200MVA ICT-III RAIBAREILLY | 2018-06-09 09:57 | 2018-06-09 12:14 | 0 | 0 | 0 | 0.095139 | N-748 | OSFD | Emergency S/D availed by UPPCL for attending hot spot in 132KV Main Bus at 132KV Raebareilly(UP) S/S
NR320001 | NR320001 | 306035 | 220 KV KANPUR(PG) - RANIYA( UP) | 2018-06-06 10:00 | 2018-06-06 19:04 | 0 | 0 | 0 | 0.37778 | N-473 | OSPD | S/D availed by UPPCL for maintenance work at their end
NR320001 | NR320001 | 306043 | 220 KV KANPUR(PG) - RANIYA( UP) | 2018-06-07 08:53 | 2018-06-07 15:58 | 0 | 0 | 0 | 0.29514 | N-565 | OSPD | S/D availed by UPPCL for maintenance work at their end
NR320001 | NR320001 | 306182 | 220 KV KANPUR(PG) - RANIYA( UP) | 2018-06-28 12:58 | 2018-06-28 19:25 | 0 | 0 | 0 | 0.26875 | N-2150 | OSFD | Emergency hand tripped by UPPCL to attend R- phase broken jumper at Tower No. 20. (UPPCL jurisdiction)
BILUP2202 | BILUP2202 | 306038 | 220KV ALLD-REWA RD-I | 2018-06-06 18:42 | 2018-06-06 19:45 | 0 | 0.04375 | 0 | 0 | **** | OMSU | Tripped only from Rewa Road (UP) end due to problem at Rewa Road (UP).
BILUP2203 | BILUP2203 | 306039 | 220KV ALLD-REWA RD-II | 2018-06-06 18:42 | 2018-06-06 19:45 | 0 | 0.04375 | 0 | 0 | **** | OMSU | Tripped only from Rewa Road (UP) end due to problem at Rewa Road (UP).
NR122006 | NR122006 | 306003 | 220KV AUR-SIKANDARA-I | 2018-06-01 17:11 | 2018-06-01 21:02 | 0 | 0 | 0 | 0.16042 | N-55 | LCSD | S/D availed for balance rectification work on collapsed tower caused by heavy storm
NR122007 | NR122007 | 306002 | 220KV AUR-SIKANDARA-II | 2018-06-01 10:36 | 2018-06-01 16:48 | 0 | 0 | 0 | 0.25833 | N-16 | LCSD | S/D availed for balance rectification work on collapsed tower caused by heavy storm
NR122039 | NR122039 | 306049 | 220KV FATEHPUR-FTHPR(UP)-II | 2018-06-08 15:11 | 2018-06-08 18:05 | 0 | 0 | 0 | 0.12083 | N-678 | OSFD | Emergency S/D availed by UPPCL for attending hot spot in R Ph line isolator at UP end
NR122040 | NR122040 | 305120 | 220KV FATEHPUR-KNP SOUTH | 2018-06-18 12:00 | 2018-06-18 12:28 | 0 | 0.019444 | 0 | 0 | **** | OMSU | Tripped only from UPPCL (Kanpur South) end on R-N fault and autoreclosed successfully at Fatehpur end. FD: 51.5kM from Fatehpur (Total line length-65kM). FC:2.9kA at Fatehpur. Fault in UPPCL jurisdiction.
NR122019 | NR122019 | 306113 | 220KV KNP-PANKI-II | 2018-06-17 18:13 | 2018-06-17 21:29 | 0 | 0.13611 | 0 | 0 | **** | OMSU | Tripped on R-Y fault due to blast in 400/220KV ICT-2 at Panki(UP) & fire incident occurred at Panki. FD: KNP-23.8KM, FC: R-5.826KA, Y-5.390KA. Fault at UPPCL end.
NR122022 | NR122022 | 306085 | 220KV KNP-UNCHR-III | 2018-06-12 09:04 | 2018-06-14 22:42 | 0 | 0 | 0 | 1900-01-01 13:38 | N-1036 | OSPD | S/D availed by NTPC/Unchahar for AMP work at their end
NR122023 | NR122023 | 306117 | 220KV KNP-UNCHR-IV | 2018-06-18 09:28 | 2018-06-19 19:19 | 0 | 0 | 0 | 1899-12-31 09:51 | N-1430 | OSPD | S/D availed by NTPC/Unchahar for AMP work at their end
NR320004 | NR320004 | 306076 | 220KV RAIBRLY-BACHHRAWAN(UP) | 2018-06-10 15:09 | 2018-06-10 22:50 | 0 | 0.32014 | 0 | 0 | **** | OMSU | Tripped due to B-N fault due to heavy wind and rain. FD:1.646Km from Raibareilly FC:11.01kA at Raibareilly. Fault in UPPCL jurisdiction.
NR320004 | NR320004 | 306071 | 220KV RAIBRLY-BACHHRAWAN(UP) | 2018-06-10 22:50 | 2018-06-11 02:25 | 0.14931 | 0 | 0 | 0 | N-927 | OSFT | Emergency S/D availed for attending B-phase broken jumper at Loc. No 09.
NR122032 | NR122032 | 306009 | 220KV SITARGANJ-BLY(UP) | 2018-06-01 22:14 | 2018-06-01 23:16 | 0 | 0 | 0.043056 | 0 | **** | LNCC | Tripped on Y-B fault due to heavy thunderstorm. Sitarganj- FD: 88.93km, FC: Iy=1.44KA,Ib=1.43KA
NR122032 | NR122032 | 306082 | 220KV SITARGANJ-BLY(UP) | 2018-06-11 12:34 | 2018-06-11 15:52 | 0.1375 | 0 | 0 | 0 | N-975 | OSFT | Emergency S/D availed for attending hot spot in Y phase line isolator at Sitarganj end.
NR122033 | NR122033 | 306044 | 220KV TNKPR-BLY(UP) | 2018-06-07 12:48 | 2018-06-07 13:54 | 0 | 0.045833 | 0 | 0 | **** | OMSU | Tripped due to over voltage protection operated at Tanakpur(NHPC) end & Bus -B tripped at Bareilly(UP).
NR122033 | NR122033 | 306097 | 220KV TNKPR-BLY(UP) | 2018-06-13 16:16 | 2018-06-13 18:02 | 0.073611 | 0 | 0 | 0 | N-1125 | OSFT | Emergency S/D taken for attending hot spot in B ph wave trap at Bareily(UP) end by Powergrid
NR122034 | NR122034 | 306146 | 220KV TNKPR-SITARGANJ | 2018-06-23 15:16 | 2018-06-23 15:30 | 0 | 0.0097222 | 0 | 0 | **** | SRMU | Tripped only from Tanakpur(NHPC) due to Mal operation of E/F protection relay at Tanakpur(NHPC) end.
NR3BRT01 | NR3BRT01 | 305156 | 240MVAR B/Reactor-I KANPUR(GIS) | 2018-06-01 | 2018-06-01 20:36 | 0 | 0 | 0 | 0.85833 | N-1458 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=735kV
NR1BRT36 | NR1BRT36 | 306069 | 240MVAR B/Reactor-I AGRA-765 | 2018-06-09 22:01 | 2018-06-10 04:30 | 0 | 0 | 0 | 0.27014 | N-852 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=756kV
NR1BRT36 | NR1BRT36 | 305196 | 240MVAR B/Reactor-I AGRA-765 | 2018-06-01 | 2018-06-01 17:08 | 0 | 0 | 0 | 0.71389 | N-1981 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=747kV
NR1BRT36 | NR1BRT36 | 306139 | 240MVAR B/Reactor-I AGRA-765 | 2018-06-22 11:16 | 2018-06-24 18:35 | 0 | 0 | 0 | 1900-01-01 07:19 | N-1698 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=755kV
NR1BRT32 | NR1BRT32 | 306025 | 240MVAR B/Reactor-I BALIA-765 | 2018-06-02 22:52 | 2018-06-09 07:26 | 0 | 0 | 0 | 1900-01-05 08:34 | N-233 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=752kV
NR1BRT32 | NR1BRT32 | 306098 | 240MVAR B/Reactor-I BALIA-765 | 2018-06-13 18:56 | 2018-06-17 07:03 | 0 | 0 | 0 | 1900-01-02 12:07 | N-1172 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=742kV
NR1BRT32 | NR1BRT32 | 306128 | 240MVAR B/Reactor-I BALIA-765 | 2018-06-20 11:01 | 2018-06-28 03:13 | 0 | 0 | 0 | 1900-01-06 16:12 | N-1576 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=740kV
NR1BRT50 | NR1BRT50 | 306033 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-06-05 14:47 | 2018-06-06 07:44 | 0 | 0 | 0 | 0.70625 | N-387 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=756kV
NR1BRT50 | NR1BRT50 | 306105 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-06-14 20:10 | 2018-06-17 06:56 | 0 | 0 | 0 | 1900-01-01 10:46 | N-1248 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=753kV
NR1BRT50 | NR1BRT50 | 305261 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-06-01 | 2018-06-01 20:23 | 0 | 0 | 0 | 0.84931 | N-2692 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=758kV
NR1BRT50 | NR1BRT50 | 306140 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-06-22 12:25 | 2018-06-27 06:13 | 0 | 0 | 0 | 1900-01-03 17:48 | N-1705 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=754kV
NR1BRT50 | NR1BRT50 | 306192 | 240MVAR B/Reactor-I BAREILLY-765 | 2018-06-30 09:26 | 2018-07-01 | 0 | 0 | 0 | 0.60694 | N-2265 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=755kV
NR1BRT35 | NR1BRT35 | 305258 | 240MVAR B/Reactor-II AGRA-765 | 2018-06-01 | 2018-06-01 18:55 | 0 | 0 | 0 | 0.78819 | N-2651 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=748kV
NR1BRT22 | NR1BRT22 | 305203 | 240MVAR B/Reactor-II BALIA-765 | 2018-06-01 | 2018-06-02 01:15 | 0 | 0 | 0 | 1899-12-31 01:15 | N-2073 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=748kV
NR3BRT02 | NR3BRT02 | 306023 | 240MVAR B/Reactor-II KANPUR(GIS) | 2018-06-02 19:45 | 2018-06-06 07:33 | 0 | 0 | 0 | 1900-01-02 11:48 | N-219 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=735kV
NR1BRT28 | NR1BRT28 | 306106 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2018-06-14 20:16 | 2018-06-15 08:12 | 0 | 0 | 0 | 0.49722 | N-1249 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=755kV
NR1BRT28 | NR1BRT28 | 306145 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2018-06-23 13:01 | 2018-06-25 17:34 | 0 | 0 | 0 | 1900-01-01 04:33 | N-1767 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow = 762kV
NR1BRT44 | NR1BRT44 | 306100 | 2x50MVAR B/Reactor BAREILLY | 2018-06-13 19:08 | 2018-07-01 | 0 | 0 | 0 | 1900-01-16 04:52 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=392kV
NR1BRT44 | NR1BRT44 | 305259 | 2x50MVAR B/Reactor BAREILLY | 2018-06-01 | 2018-06-01 20:17 | 0 | 0 | 0 | 0.84514 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
NR1ICT23 | NR1ICT23 | 304218 | 315MVA ICT-I LUCKNOW | 2018-06-01 | 2018-06-09 00:04 | 1900-01-07 00:04 | 0 | 0 | 0 | **** | SICT | Tripped due to buchholz relay operation.Replacement is under progress and expected to restore on 08.06.18.
NR1BRT55 | NR1BRT55 | 305188 | 330MVAR B/Reactor-I VARANASI | 2018-06-01 | 2018-06-02 01:02 | 0 | 0 | 0 | 1899-12-31 01:02 | N-1857 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Varanasi=748kV
NR1BRT23 | NR1BRT23 | 306024 | 330MVAR B/Reactor-III FTHPR-765 | 2018-06-02 22:36 | 2018-06-04 07:57 | 0 | 0 | 0 | 1899-12-31 09:21 | N-232 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTHPR=747kV
NR1BRT23 | NR1BRT23 | 306107 | 330MVAR B/Reactor-III FTHPR-765 | 2018-06-14 20:16 | 2018-06-15 08:23 | 0 | 0 | 0 | 0.50486 | N-1250 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=754kV
NR1BRT23 | NR1BRT23 | 306143 | 330MVAR B/Reactor-III FTHPR-765 | 2018-06-23 00:16 | 2018-06-24 17:50 | 0 | 0 | 0 | 1899-12-31 17:34 | N-1743 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=745kV
NR140002 | NR140002 | 306060 | 400KV AGRA-AGRA(UP)-II | 2018-06-09 17:30 | 2018-06-09 18:37 | 0 | 0 | 0.046528 | 0 | **** | GOVC | Tripped due to over voltage protection operated. Agra-436KV
NR140002 | NR140002 | 306131 | 400KV AGRA-AGRA(UP)-II | 2018-06-21 15:13 | 2018-06-21 16:17 | 0 | 0.044444 | 0 | 0 | **** | OMSU | Line Tripped only from Agra(UP) end due to Mal-operation of Bus bar protection at Agra(UP) end
NR140003 | NR140003 | 306011 | 400KV AGRA-AURAIYA-I | 2018-06-02 04:19 | 2018-06-03 08:14 | 0 | 0 | 0 | 1899-12-31 03:55 | N-146 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430KV
NR140003 | NR140003 | 306042 | 400KV AGRA-AURAIYA-I | 2018-06-07 07:15 | 2018-06-11 23:31 | 0 | 0 | 0 | 1900-01-03 16:16 | N-561 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=423KV
NR140003 | NR140003 | 306083 | 400KV AGRA-AURAIYA-I | 2018-06-12 07:07 | 2018-06-16 21:07 | 0 | 0 | 0 | 1900-01-03 14:00 | N-1021 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430KV
NR140003 | NR140003 | 306148 | 400KV AGRA-AURAIYA-I | 2018-06-24 18:06 | 2018-06-24 19:25 | 0 | 0 | 0 | 0.054861 | N-1827 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140004 | NR140004 | 306078 | 400KV AGRA-AURAIYA-II | 2018-06-11 07:14 | 2018-06-11 23:20 | 0 | 0 | 0 | 0.67083 | N-937 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430KV
NR140004 | NR140004 | 306108 | 400KV AGRA-AURAIYA-II | 2018-06-15 08:13 | 2018-06-20 11:15 | 0 | 0 | 0 | 1900-01-04 03:02 | N-1269 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431KV
NR140004 | NR140004 | 306168 | 400KV AGRA-AURAIYA-II | 2018-06-27 07:53 | 2018-07-01 | 0 | 0 | 0 | 1900-01-02 16:07 | N-2020 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140005 | NR140005 | 306052 | 400KV AGRA-BASSI-I | 2018-06-08 17:27 | 2018-06-08 18:08 | 0.028472 | 0 | 0 | 0 | N-702 | OSFT | Emergency S/D availed for attending SF6 low alarm at Bassi end
NR140008 | NR140008 | 306156 | 400KV AGRA-BHIWADI-I | 2018-06-26 05:10 | 2018-06-26 05:59 | 0.034028 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault. Agra: FD-1135km, FC-20.67KA. Fault in Agra TL jurisdiction
NR140008 | NR140008 | 306172 | 400KV AGRA-BHIWADI-I | 2018-06-28 01:24 | 2018-06-28 11:11 | 0 | 0 | 0 | 0.40764 | N-2080 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR140008 | NR140008 | 306189 | 400KV AGRA-BHIWADI-I | 2018-06-30 03:51 | 2018-06-30 04:26 | 0.024306 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault. FD: Agra-2.148km, FC: Agra- 31.27KA. Fault in Agra TL jurisdiction. Charged at 04:26 hrs but immidiatly tripped due to over voltage protection operated at Agra & DT received at Bhiwadi.
NR140008 | NR140008 | 306190 | 400KV AGRA-BHIWADI-I | 2018-06-30 04:26 | 2018-07-01 | 0 | 0 | 0.81528 | 0 | **** | GOVC | Tripped at 03:51 hrs due to R-N fault. Charged at 04:26 hrs but immidiatly tripped due to over voltage protection operated at Agra & DT received at Bhiwadi.
NR140008 | NR140008 | 306159 | 400KV AGRA-BHIWADI-I | 2018-06-26 14:16 | 2018-06-26 16:40 | 0.1 | 0 | 0 | 0 | N-1960 | OSFT | Emergency S/D availed for removing of kite with metallic thread from R phase of line between location no 8 -9 and 9-10.
NR140009 | NR140009 | 306047 | 400KV AGRA-BHIWADI-II | 2018-06-08 09:34 | 2018-06-16 16:43 | 0 | 0 | 0 | 1900-01-07 07:09 | N-661 | LCSD | Taken under S/D for retrofitting of existing 400KV line and SCADA integration work with HVDC Agra
NR140009 | NR140009 | 306186 | 400KV AGRA-BHIWADI-II | 2018-06-29 05:29 | 2018-06-29 10:43 | 0 | 0 | 0 | 0.21806 | N-2187 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR340006 | NR340006 | 306118 | 400KV AGRA-FATEHABD(UP)-I | 2018-06-18 14:57 | 2018-06-18 16:46 | 0 | 0 | 0 | 0.075694 | N-1452 | OSFD | Emergency S/D availed by UPPCL for attending heavy sparking in B phase line isolator at Fatehpur(UPPCL) end.
NR140123 | NR140123 | 306094 | 400KV ALLD-FATEHPUR-II | 2018-06-13 14:33 | 2018-06-13 15:32 | 0 | 0 | 0.040972 | 0 | **** | LNCC | Tripped due to heavy storm caused by R-N fault,F.D.=8.4km from FTP, F.C.=16.91KA, F.D.=140km from ALLD,F.C.=2.401KA(Kanpur Jurisdiction)
NR140104 | NR140104 | 306095 | 400KV ALLD-FATEHPUR-III | 2018-06-13 15:03 | 2018-06-13 15:03 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to Y-N fault,F.D.=53.92km from FTP , F.C.=5.49KA, F.D.=96.5km from ALLD,F.C.=3.057KA (Kanpur Jurisdiction)
NR140012 | NR140012 | 306048 | 400KV ALLD-KNP-II | 2018-06-08 15:00 | 2018-06-08 17:20 | 0.097222 | 0 | 0 | 0 | N-686 | OSFT | Emergency S/D availed for rectification of broken earth wire between loc no 1010 & 1011
NR140012 | NR140012 | 306141 | 400KV ALLD-KNP-II | 2018-06-22 16:37 | 2018-06-22 17:02 | 0.017361 | 0 | 0 | 0 | **** | LHWT | Tripped due to B-N fault. F.D.= 173KM from Kanpur & 40.6KM from Allahabad. F.C.= 2.7KA at Kanpur & 8.23KA at Allahabad. The fault was in Allahabad Jurisdiction (Earth wire dead end failed at Loc. No. 635).
NR140012 | NR140012 | 306144 | 400KV ALLD-KNP-II | 2018-06-23 10:56 | 2018-06-23 14:09 | 0.13403 | 0 | 0 | 0 | N-1760 | OSFT | E/S/D availed for rectification of broken E/W tension clamp at Loc. No. 635
NR140024 | NR140024 | 306010 | 400KV BAREILLY-BRLY(UP)-II | 2018-06-01 22:07 | 2018-06-01 23:49 | 0 | 0 | 0.070833 | 0 | **** | LNCC | Tripped on R-N fault due to heavy thunderstorm. Bareilly- FD: 11.7km, FC: 14.11KA
NR140024 | NR140024 | 305122 | 400KV BAREILLY-BRLY(UP)-II | 2018-06-18 14:07 | 2018-06-18 14:07 | 0 | 0 | 0 | 0 | **** | LART | Auto reclosed successfully at both end on Y-N fault. FD: 11.7kM from BRLY (Total line length-14.3kM). FC: 10.6kA at BRLY. Fault in UPPCL jurisdiction.
NR140025 | NR140025 | 306045 | 400KV BAREILLY-LKO(UP) | 2018-06-08 08:17 | 2018-06-08 08:51 | 0.023611 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault. FD=165.4KM from Bareilly, FC= 2.4KAmp at Bareilly. Fault in Shahjahanpur TL jurisdiction
NR140026 | NR140026 | 306007 | 400KV BAREILLY-MBAD-I | 2018-06-01 21:30 | 2018-06-01 23:51 | 0 | 0 | 0.097917 | 0 | **** | LNCC | Tripped on R-N fault due to heavy thunderstorm. Bareilly- FD: 51.9km, FC: 5.13KA
NR140026 | NR140026 | 306034 | 400KV BAREILLY-MBAD-I | 2018-06-05 16:38 | 2018-06-05 18:34 | 0 | 0 | 0 | 0.080556 | N-395 | OSFD | E/S/D availed by UPPCL for attending hot spot in line side CT clamp at Moradabad(UPPCL end)
NR140159 | NR140159 | 306008 | 400KV BARLY(765)-KASHIPUR-II | 2018-06-01 21:55 | 2018-06-01 22:54 | 0 | 0 | 0.040972 | 0 | **** | LNCC | Tripped on Y-B fault due to heavy thunderstorm. Bareilly- FD: 10.23km, FC: Y-16.29KA, B-16.62KA.
NR140159 | NR140159 | 306191 | 400KV BARLY(765)-KASHIPUR-II | 2018-06-30 08:55 | 2018-06-30 08:55 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully from both end due to B-N fault. F.D.= 39.96KM from Bareilly, F.C.= 8.046KA at Bareilly. The fault was in Bareilly jurisdiction.
NR140037 | NR140037 | 306005 | 400KV BLBGRH-MAINPURI-I | 2018-06-01 21:11 | 2018-06-02 09:59 | 0 | 0 | 0 | 0.53333 | N-91 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427KV
NR140037 | NR140037 | 306046 | 400KV BLBGRH-MAINPURI-I | 2018-06-08 08:56 | 2018-06-08 17:21 | 0 | 0 | 0 | 0.35069 | **** | LCSD | Tripped due to Y-N fault during OPGW work. FD=50.66km from Mainpuri, FC=5.649KA, FD=170.2km from BLB, F.C.=2.4KA. Rope found in the line during OPGW work. Fault in Mainpuri TL jurisdiction.
NR140037 | NR140037 | 306091 | 400KV BLBGRH-MAINPURI-I | 2018-06-13 07:59 | 2018-06-13 08:54 | 0 | 0 | 0 | 0.038194 | N-1106 | LCSD | S/D taken for removing hanging OPGW rope at Loc no 100
NR140037 | NR140037 | 306110 | 400KV BLBGRH-MAINPURI-I | 2018-06-17 07:13 | 2018-06-18 08:04 | 0 | 0 | 0 | 1899-12-31 00:51 | N-1372 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=429KV
NR140037 | NR140037 | 306166 | 400KV BLBGRH-MAINPURI-I | 2018-06-27 06:19 | 2018-06-27 09:52 | 0 | 0 | 0 | 0.14792 | N-2012 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=427kV
NR140037 | NR140037 | 306180 | 400KV BLBGRH-MAINPURI-I | 2018-06-28 12:28 | 2018-06-28 12:59 | 0 | 0 | 0 | 0.021528 | **** | LCSD | Tripped due to development of loop of earth wire while removing the same during OPGW work on B-N fault F.D.= 91.19KM from Mainpuri & 118KM from Ballabhgarh, F.C.= 3.595KA at Mainpuri & 3.1KA at Ballabhgarh.. The fault was in Mainpuri jurisdiction.
NR140037 | NR140037 | 306181 | 400KV BLBGRH-MAINPURI-I | 2018-06-28 13:23 | 2018-06-28 20:05 | 0 | 0 | 0 | 0.27917 | **** | LCSD | Tripped due to development of loop of earth wire while removing the same during OPGW work on B-N fault . F.D.= 90.5KM from Mainpuri & 122.72KM from Ballabhgarh, F.C.= 3.653KA at Mainpuri & 3.086KA at Ballabhgarh. The fault was in Mainpuri jurisdiction.
NR140038 | NR140038 | 306063 | 400KV BLBGRH-MAINPURI-II | 2018-06-09 17:48 | 2018-06-10 17:20 | 0 | 0 | 0 | 0.98056 | N-797 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=432kV
NR140038 | NR140038 | 306174 | 400KV BLBGRH-MAINPURI-II | 2018-06-28 02:54 | 2018-06-28 10:56 | 0 | 0 | 0 | 0.33472 | N-2087 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=432kV
NR140124 | NR140124 | 306004 | 400KV FATEHPUR-MAINPURI-I | 2018-06-01 20:48 | 2018-06-02 10:22 | 0 | 0 | 0 | 0.56528 | N-91 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=427KV
NR140124 | NR140124 | 306014 | 400KV FATEHPUR-MAINPURI-I | 2018-06-02 10:22 | 2018-06-02 20:52 | 0 | 0 | 0 | 0.4375 | N-176 | LCSD | S/D availed for restoration of 765KV Varanasi-Kanpur-2
NR140124 | NR140124 | 306064 | 400KV FATEHPUR-MAINPURI-I | 2018-06-09 17:48 | 2018-06-10 17:15 | 0 | 0 | 0 | 0.97708 | N-797 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri=432kV
NR140124 | NR140124 | 306093 | 400KV FATEHPUR-MAINPURI-I | 2018-06-13 14:30 | 2018-06-13 15:17 | 0 | 0 | 0.032639 | 0 | **** | LNCC | Tripped due to heavy storm caused by R-N fault,F.D.=8.8km from FTP, F.C.=17.8KA, F.D.=260km from MNP ,F.C.=1.672KA(Kanpur Jurisdiction)
NR140124 | NR140124 | 306111 | 400KV FATEHPUR-MAINPURI-I | 2018-06-17 07:14 | 2018-06-18 08:04 | 0 | 0 | 0 | 1899-12-31 00:50 | N-1372 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. MNP=429KV
NR140125 | NR140125 | 306015 | 400KV FATEHPUR-MAINPURI-II | 2018-06-02 10:22 | 2018-06-02 20:47 | 0 | 0 | 0 | 0.43403 | N-176 | LCSD | S/D availed for restoration of 765KV Varanasi-Kanpur-2
NR140125 | NR140125 | 306167 | 400KV FATEHPUR-MAINPURI-II | 2018-06-27 06:29 | 2018-06-27 09:58 | 0 | 0 | 0 | 0.14514 | N-2012 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=427kV
NR140125 | NR140125 | 306175 | 400KV FATEHPUR-MAINPURI-II | 2018-06-28 02:52 | 2018-06-28 10:52 | 0 | 0 | 0 | 0.33333 | N-2087 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.MNPR=432kV
NR140125 | NR140125 | 306068 | 400KV FATEHPUR-MAINPURI-II | 2018-06-09 20:52 | 2018-06-09 20:52 | 0 | 0 | 0 | 0 | **** | LART | Auto reclosed successfully from both end due to B-N fault. FTP: FD-260.2km, FC-1.58KA. Fault in Mainpuri TL jurisdiction
NR340014 | NR340014 | 306026 | 400KV Kanpur(GIS)-Allahabad-I | 2018-06-04 09:51 | 2018-06-04 20:42 | 0 | 0 | 0 | 0.45208 | N-293 | LCSD | S/D availed for stringing of multi circuit portion of 400KV Allahabad-Singrauli line
NR340014 | NR340014 | 306030 | 400KV Kanpur(GIS)-Allahabad-I | 2018-06-05 05:40 | 2018-06-05 21:02 | 0 | 0 | 0 | 0.64028 | N-343 | LCSD | S/D availed for stringing of multi circuit portion of 400KV Allahabad-Singrauli line
NR340014 | NR340014 | 306103 | 400KV Kanpur(GIS)-Allahabad-I | 2018-06-14 14:17 | 2018-06-14 20:47 | 0 | 0 | 0 | 0.27083 | N-1219 | LCSD | S/D availed for balance completion of stringing of multi circuit portion of 400KV Allahabad-Singrauli line
NR340014 | NR340014 | 306138 | 400KV Kanpur(GIS)-Allahabad-I | 2018-06-22 08:08 | 2018-06-22 08:08 | 0 | 0 | 0 | 0 | **** | LART | A/R succesfully on B-N fault. F.D.= 221.5KM from Kanpur(GIS) & 11.26KM from Allahabad. F.C.= 1.6KA at Kanpur(GIS) & 15.42KA at Allahabad. The fault was in Allahabad Jurisdiction.
NR340015 | NR340015 | 306027 | 400KV Kanpur(GIS)-Allahabad-II | 2018-06-04 09:52 | 2018-06-04 20:43 | 0 | 0 | 0 | 0.45208 | N-294 | LCSD | S/D availed for stringing of multi circuit portion of 400KV Allahabad-Singrauli line
NR340015 | NR340015 | 306031 | 400KV Kanpur(GIS)-Allahabad-II | 2018-06-05 05:40 | 2018-06-05 21:03 | 0 | 0 | 0 | 0.64097 | N-343 | LCSD | S/D availed for stringing of multi circuit portion of 400KV Allahabad-Singrauli line
NR340015 | NR340015 | 306104 | 400KV Kanpur(GIS)-Allahabad-II | 2018-06-14 14:17 | 2018-06-14 20:50 | 0 | 0 | 0 | 0.27292 | N-1219 | LCSD | S/D availed for balance completion of stringing of multi circuit portion of 400KV Allahabad-Singrauli line
NR340015 | NR340015 | 306137 | 400KV Kanpur(GIS)-Allahabad-II | 2018-06-22 08:03 | 2018-06-22 08:48 | 0.03125 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault. F.D.= 229.4KM from Kanpur(GIS) & 13.92KM from Allahabad. F.C.= 1.5KA at Kanpur(GIS) & 15.81KA at Allahabad. The fault was in Allahabad Jurisdiction.
NR340015 | NR340015 | 306096 | 400KV Kanpur(GIS)-Allahabad-II | 2018-06-13 16:11 | 2018-06-13 16:11 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to B-N fault,F.D.=250km from Kanpur GIS , F.C.=2.5KA, F.D.=12.49km from ALLD, F.C.=16.19KA (Allahabad Jurisdiction)
NR140052 | NR140052 | 306158 | 400KV KNP-AGRA | 2018-06-26 08:07 | 2018-06-26 19:15 | 0 | 0 | 0 | 0.46389 | N-1928 | LCSD | S/D availed for replacement of CVT under add-cap.
NR140055 | NR140055 | 306037 | 400KV KNP-BLBGARH-I | 2018-06-06 10:37 | 2018-06-06 10:37 | 0 | 0 | 0 | 0 | **** | LART | A/R successfully at both end on Y-N fault. F.D.=205.2KM from Ballabgarh & 145.4KM from Kanpur, F.C.= 1.83KA at Ballabhgarh & 2.8KA at Kanpur. Fault was in Mainpuri jurisdiction.
NR140110 | NR140110 | 306147 | 400KV KNP-FATEHPUR-I | 2018-06-24 16:36 | 2018-06-24 17:18 | 0.029167 | 0 | 0 | 0 | **** | LEFT | Tripped due to Y-N fault. FD: FTP-67.7km, KNP-84.7km, FC: FTP-2.89KA, KNP-9.568KA. Fault in Kanpur TL jurisdiction
NR140058 | NR140058 | 306114 | 400KV KNP-PANKI-I | 2018-06-17 18:26 | 2018-06-18 19:36 | 0 | 0 | 0 | 1899-12-31 01:10 | **** | OSFD | Emergency H/T from Panki (UP) end due to blast in 400/220KV ICT-2 at Panki(UP) & fire incident occurred at Panki.
NR140058 | NR140058 | 306129 | 400KV KNP-PANKI-I | 2018-06-21 01:24 | 2018-06-21 05:30 | 0 | 0.17083 | 0 | 0 | **** | OMSU | Tripped due to R-N fault,F.D.=6.8km from Kanpur,F.C.=12KA(UPPCL Jurisdiction) caused by R Ph CT blast in 400KV Bus coupler bay at UPPCL/Panki end.
NR140058 | NR140058 | 2: 306149; 3: 400KV KNP-PANKI-I; 4: 2018-06-25 13:21; 5: 2018-06-25 14:06 | N-1868 | OSFD | Emergency S/D availed by UPPCL for shifting of line from Bus-1 to Bus-2 at Panki end
NR140059 | NR140059 | 306115 | 400KV KNP-PANKI-II | 2018-06-17 18:26 | 2018-06-18 19:39 | 0 | 0 | 0 | 1899-12-31 01:13 | **** | OSFD | Emergency H/T from Panki (UP) end due to blast in 400/220KV ICT-2 at Panki(UP) & fire incident occurred at Panki.
NR140059 | NR140059 | 306130 | 400KV KNP-PANKI-II | 2018-06-21 01:24 | 2018-06-21 05:30 | 0 | 0.17083 | 0 | 0 | **** | OMSU | Tripped due to R-N fault,F.D.=6.1km from Kanpur,F.C.=20.7KA(UPPCL Jurisdiction) caused by R Ph CT blast in 400KV Bus coupler bay at UPPCL/Panki end.
NR140072 | NR140072 | 306136 | 400KV LUCKNOW-LKO(UP) | 2018-06-22 01:32 | 2018-06-22 03:23 | 0 | 0.077083 | 0 | 0 | NR-1678 | OMSU | Line Tripped because of CT blast at UP end, Busbar protection operated at UP end and DT Received at Lko(PG) end.
NR140072 | NR140072 | 306179 | 400KV LUCKNOW-LKO(UP) | 2018-06-28 03:46 | 2018-06-28 05:59 | 0 | 0.092361 | 0 | 0 | **** | OMSU | Tripped only from Lucknow(UP) end and remain charged from Lucknow(PG) end due to some problem at Lucknow(UP) end.
NR140073 | NR140073 | 306162 | 400KV LUCKNOW-SULTANPR | 2018-06-26 20:30 | 2018-06-26 22:01 | 0 | 0.063194 | 0 | 0 | **** | OMSU | Tripped due to bursting of 400kv B phase CT of 240MVA ICT 2 at Sultanpur end(UPPCL).
NR340017 | NR340017 | 306012 | 400KV ORAI-ORAI(UP)-II | 2018-06-02 04:45 | 2018-06-02 06:24 | 0 | 0 | 0.06875 | 0 | **** | GOVC | Tripped on over voltage protection operated at Orai.
NR140091 |  | 306124 | 400KV SING-ALLD-I | 2018-06-19 13:03 | 2018-06-19 18:10 | 0.21319 | 0 | 0 | 0 | N-1506 | OSFT | Emergency S/D availed for replacement of Y-phase line LA at Allahabad due to high THRC Value(THRC value=155mA, which should be<100mA).
NR140091 | NR140091 | 306019 | 400KV SING-ALLD-I | 2018-06-02 15:24 | 2018-06-02 16:26 | 0 | 0.043056 | 0 | 0 | **** | OMSU | Tripped due to 400kV Bus-1 fault at NTPC, Singrauli due to haevy storm reported by Singrauli.
NR140091 | NR140091 | 306125 | 400KV SING-ALLD-I | 2018-06-19 18:10 | 2018-06-19 18:33 | 0 | 0 | 0 | 0.015972 | N-1529 | OSFD | Emergency S/D availed by NTPC, Singrauli for closing of line isolator which was automatically opened at NTPC,Singrauli end during closing period.
NR140091 | NR140091 | 306150 | 400KV SING-ALLD-I | 2018-06-25 16:06 | 2018-06-25 17:00 | 0 | 0 | 0.0375 | 0 | **** | LNCC | Tripped on B-N fault due to heavy lightning. FD: Allahabad-225km, FC: Allahabad-1.9KA. Fault in Singrauli(NTPC) jurisdiction.
NR140092 | NR140092 | 306073 | 400KV SING-ALLD-II | 2018-06-10 14:43 | 2018-06-10 14:43 | 0 | 0 | 0 | 0 | **** | LART | Tripped only from Singrauli end due to R-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli and Auto-reclosed successful at Allahabad end. FD: 108kM from Allahabad. FC:3.058kA at Allahabad.
NR140092 | NR140092 | 306017 | 400KV SING-ALLD-II | 2018-06-02 15:24 | 2018-06-02 16:38 | 0 | 0.051389 | 0 | 0 | **** | OMSU | Tripped due to 400kV Bus-1 fault at NTPC, Singrauli due to haevy storm reported by Singrauli.
NR140092 | NR140092 | 306029 | 400KV SING-ALLD-II | 2018-06-04 13:42 | 2018-06-04 13:52 | 0 | 0.0069444 | 0 | 0 | **** | OMSU | Tripped only from NTPC/Singrauli end due to problem at their end
NR140092 | NR140092 | 306073A | 400KV SING-ALLD-II | 2018-06-10 14:43 | 2018-06-10 17:00 | 0 | 0.095139 | 0 | 0 | **** | OMSU | Tripped only from Singrauli end due to R-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli and Auto-reclosed successful at Allahabad end. FD: 108kM from Allahabad. FC:3.058kA at Allahabad.
NR140092 | NR140092 | 306088 | 400KV SING-ALLD-II | 2018-06-12 22:16 | 2018-06-12 22:52 | 0.025 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault,M1:F.D.=109km from Alld,F.C.=2.99KA, M2:F.D.=102.2km from Alld ,F.C.=2.731KA,F.D.=103.06km from Singrauli( Mirzapur Jurisdiction)
NR140093 | NR140093 | 306075 | 400KV SING-ANPARA | 2018-06-10 15:05 | 2018-06-10 15:05 | 0 | 0 | 0 | 0 | **** | LART | Tripped only (unsuccessful A/R) from Anpara end due to Y-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli. FD:2.338kM from Singrauli and 22.2kM from Anpara. Fault in Shaktinagar jurisdiction.
NR140093 | NR140093 | 306018 | 400KV SING-ANPARA | 2018-06-02 15:24 | 2018-06-03 01:40 | 0 | 0.42778 | 0 | 0 | **** | OMSU | Tripped due to 400kV Bus-1 fault at NTPC, Singrauli due to haevy storm reported by Singrauli.
NR140093 | NR140093 | 306075A | 400KV SING-ANPARA | 2018-06-10 15:05 | 2018-06-10 18:44 | 0 | 0.15208 | 0 | 0 | **** | OMSU | Tripped only (unsuccessful A/R) from Anpara end due to Y-N fault due to heavy wind pressure and rain as reported by NTPC, Singrauli. FD:2.338kM from Singrauli and 22.2kM from Anpara.
NR140093 | NR140093 | 306151 | 400KV SING-ANPARA | 2018-06-25 16:06 | 2018-06-25 17:20 | 0 | 0 | 0.051389 | 0 | **** | LNCC | Tripped on B-N fault due to heavy lightning. FD: Singrauli-14.43km, Anpara- 10.10km, FC: Singrauli-13KA, Anpara-7.826KA. Fault in Shaktinagar TL jurisdiction.
NR140095 | NR140095 | 306155 | 400KV SING-LKO(UP)-I | 2018-06-25 18:47 | 2018-06-26 06:28 | 0.48681 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault. FD: Singrauli-210.3km, LKO-152.3km, FC: Singrauli-1.64KA, LKO-1.344KA. Charging attempt failed at 2004 hrs on SOTF. Fault in Allahabad & Mirzapur TL jurisdiction
NR140096 | NR140096 | 306079 | 400KV SING-RIHAND-I | 2018-06-11 08:42 | 2018-06-12 01:00 | 0 | 0 | 0 | 0.67917 | N-939 | LCSD | S/D availed for Stringing between 5/0 to 5A/0 of New 400 KV S/C Singrauli-Allahabad T/L and existing tower no 06 to 07 of 400 KV SINGRAULI (NTPC) -RIHAND (NTPC) D/C line
NR140097 | NR140097 | 306080 | 400KV SING-RIHAND-II | 2018-06-11 09:23 | 2018-06-12 01:05 | 0 | 0 | 0 | 0.65417 | N-946 | LCSD | S/D availed for Stringing between 5/0 to 5A/0 of New 400 KV S/C Singrauli-Allahabad T/L and existing tower no 06 to 07 of 400 KV SINGRAULI (NTPC) -RIHAND (NTPC) D/C line
NR340004 | NR340004 | 306050 | 400KV VARANASI-SARNATH-I | 2018-06-08 14:48 | 2018-06-08 18:56 | 0.17222 | 0 | 0 | 0 | **** | SEFT | Tripped due to B Ph LA blast at Varanasi end. Details at Varanasi: B-N fault, FD-118Mtrs, FC-23KA.
NR1DCP03 | NR1DCP03 | 306170 | 500KV HVDC BALIA-BHWD POLE-I | 2018-06-27 22:52 | 2018-06-27 23:20 | 0.019444 | 0 | 0 | 0 | **** | OMST | Tripped due to change over logic failure at Bhiwadi end.
NR1DCP03 | NR1DCP03 | 306171 | 500KV HVDC BALIA-BHWD POLE-I | 2018-06-28 00:56 | 2018-06-28 01:38 | 0.029167 | 0 | 0 | 0 | **** | OMST | Tripped due to transformer isolator configuration status missing to pole 1 control at Bhiwadi and Continuous rain at Bhiwadi.
NR1DCP04 | NR1DCP04 | 305123 | 500KV HVDC BALIA-BHWD POLE-II | 2018-06-18 23:35 | 2018-06-18 23:35 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD:731.561kM from Balia and 58.229kM from Bhiwadi. Tower No 1993. Fault in NR-1 jurisdiction.
NR1DCP01 | NR1DCP01 | 306013 | 500KV HVDC R-D POLE-I | 2018-06-02 05:05 | 2018-06-02 05:05 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand-773.23km, Dadri-41.77km. Fault in NR-1 jurisdiction.
NR1DCP01 | NR1DCP01 | 306116 | 500KV HVDC R-D POLE-I | 2018-06-18 01:00 | 2018-06-18 01:00 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand-758.98km, Dadri-56.02km. Fault in NR-1 jurisdiction.
NR1DCP01 | NR1DCP01 | 306188 | 500KV HVDC R-D POLE-I | 2018-06-29 20:57 | 2018-06-29 20:57 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand- 767.83km, Dadri-47.17km. Fault in NR-1 jurisdiction.
NR1DCP02 | NR1DCP02 | 306101 | 500KV HVDC R-D POLE-II | 2018-06-14 01:05 | 2018-06-14 01:05 | 0 | 0 | 0 | 0 | **** | LART | A/R operated successfully from both end due to dc transient earth fault, F.D.=137.23km from Rihand, F.D.=677.77km from Dadri.(Mirzapur jurisdiction)
NR1DCP02 | NR1DCP02 | 306153 | 500KV HVDC R-D POLE-II | 2018-06-25 16:53 | 2018-06-25 16:53 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand-523.83km, Dadri-291.17km. Fault in Kanpur TL jurisdiction
NR1DCP02 | NR1DCP02 | 306161 | 500KV HVDC R-D POLE-II | 2018-06-26 11:14 | 2018-06-26 11:14 | 0 | 0 | 0 | 0 | **** | LART | Transient fault. FD: Rihand-717.4km, Dadri-97.6km. Fault in NR-1 jurisdiction
NR1ICT705 | NR1ICT705 | 306032 | 765/400KV ICT-I FATEHPUR | 2018-06-05 10:06 | 2018-06-05 15:15 | 0.21458 | 0 | 0 | 0 | N-360 | OSPT | S/D availed for Twin jumper modification work in spare ICT and its AMP.
NR1ICT703 | NR1ICT703 | 306001 | 765/400KV ICT-I LUCKNOW | 2018-06-01 08:20 | 2018-06-01 17:22 | 0.37639 | 0 | 0 | 0 | **** | OSFT | Emergency H/T due to heavy sparking in IPS tube which are connected between 02 isolators of B Ph at 765KV side.
NR1ICT706 | NR1ICT706 | 306036 | 765/400KV ICT-II FATEHPUR | 2018-06-06 10:09 | 2018-06-06 17:41 | 0.31389 | 0 | 0 | 0 | N-479 | OSPT | S/D availed for Twin jumper modification work in spare ICT and its AMP.
NR376506 | NR376506 | 305025 | 765KV AGRA-ALIGARH | 2018-06-01 | 2018-06-04 01:21 | 0 | 0 | 1900-01-02 01:21 | 0 | **** | LNCC | Tripped due to heavy storm due to Y-ph WT disloated from its bus. 4Nos tower collapsed (tower no 15, 16,17,18)
NR376506 | NR376506 | 306081 | 765KV AGRA-ALIGARH | 2018-06-11 11:25 | 2018-06-11 16:52 | 0 | 0 | 0 | 0.22708 | N-972 | LCSD | Emergency S/D availed for removing hanging OPGW laying rope between loc No 1 to 4.
NR376506 | NR376506 | 306086 | 765KV AGRA-ALIGARH | 2018-06-12 14:38 | 2018-06-12 16:29 | 0 | 0 | 0 | 0.077083 | **** | LCSD | Tripped due to OPGW work caused by Y-N fault,F.D.=0.2km from Agra,F.C.=20.96KA, F.D.=102km from Aligarh and F.C.=5.2KA(Agra Jurisdiction) .
NR376506 | NR376506 | 306169 | 765KV AGRA-ALIGARH | 2018-06-27 12:56 | 2018-06-27 16:15 | 0.13819 | 0 | 0 | 0 | N-2046 | OSFT | Emergency S/D availed for removal of earth-wire twist between location No 20 to 21.
NR176502 | NR176502 | 306062 | 765KV AGRA-FATEHPUR-I | 2018-06-09 17:42 | 2018-06-10 20:00 | 0 | 0 | 0 | 1899-12-31 02:18 | N-790 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
NR176502 | NR176502 | 306077 | 765KV AGRA-FATEHPUR-I | 2018-06-11 06:57 | 2018-06-11 10:55 | 0 | 0 | 0 | 0.16528 | N-936 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
NR176502 | NR176502 | 306084 | 765KV AGRA-FATEHPUR-I | 2018-06-12 07:14 | 2018-06-12 12:49 | 0 | 0 | 0 | 0.23264 | N-1022 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176502 | NR176502 | 306102 | 765KV AGRA-FATEHPUR-I | 2018-06-14 07:46 | 2018-06-14 14:54 | 0 | 0 | 0 | 0.29722 | N-1190 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra =787kV
NR176502 | NR176502 | 306112 | 765KV AGRA-FATEHPUR-I | 2018-06-17 07:51 | 2018-06-18 14:46 | 0 | 0 | 0 | 1899-12-31 06:55 | N-1377 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796KV
NR176502 | NR176502 | 306133 | 765KV AGRA-FATEHPUR-I | 2018-06-21 18:18 | 2018-06-24 23:49 | 0 | 0 | 0 | 1900-01-02 05:31 | N-1656 | LCSD | S/D taken for stringing work of 800kV Agra-BNC HVDC line.
NR176502 | NR176502 | 306164 | 765KV AGRA-FATEHPUR-I | 2018-06-27 05:23 | 2018-06-28 09:47 | 0 | 0 | 0 | 1899-12-31 04:24 | N-2009 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=798kV
NR176502 | NR176502 | 306187 | 765KV AGRA-FATEHPUR-I | 2018-06-29 06:08 | 2018-07-01 | 0 | 0 | 0 | 1899-12-31 17:52 | N-2190 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
NR176507 | NR176507 | 306090 | 765KV AGRA-FATEHPUR-II | 2018-06-13 06:54 | 2018-06-13 14:56 | 0 | 0 | 0 | 0.33472 | N-1103 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=786kV
NR176507 | NR176507 | 306132 | 765KV AGRA-FATEHPUR-II | 2018-06-21 18:21 | 2018-06-21 18:59 | 0.026389 | 0 | 0 | 0 |  | LEFT | Line Tripped from Agra end at 1821hrs on R-N fault. F.D.= 187.629KM from Fatehpur (RTAMC Data), 207.2KM (M1-Fatehpur), 206.1KM (M2-Fatehpur) & 109KM from Agra, F.C.=2.99KAmp at Fatehpur (RTAMC Data), 2.76KA (M1-Fatehpur), 2.7KA (M2-Fatehpur) & 6.24KA at Agra.
NR176507 | NR176507 | 306178 | 765KV AGRA-FATEHPUR-II | 2018-06-28 06:45 | 2018-06-29 09:55 | 0 | 0 | 0 | 1899-12-31 03:10 | N-2099 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
NR376505 | NR376505 | 306006 | 765KV KANPUR(GIS)-ALIGARH | 2018-06-01 20:50 | 2018-06-01 22:35 | 0 | 0 | 0.072917 | 0 | **** | GOVC | Tripped on over voltage protection operated at Aligarh.
NR376505 | NR376505 | 306061 | 765KV KANPUR(GIS)-ALIGARH | 2018-06-09 17:44 | 2018-06-09 20:06 | 0 | 0 | 0.098611 | 0 | **** | GOVC | Tripped due to over voltage protection operated at Aligrah & DT received at Kanpur. Aligarh-804KV
NR176501 | NR176501 | 306028 | 765KV LUCKNOW-BALIA | 2018-06-04 12:28 | 2018-06-04 12:28 | 0 | 0 | 0 | 0 | **** | LART | auto reclosed successfully from both end due to Y-N fault. Ballia: FD-247km, FC-2.6KA. LKO: FD-67.9km, FC-5.1KA. Lucknow jurisdiction
NR176501 | NR176501 | 306051 | 765KV LUCKNOW-BALIA | 2018-06-08 17:03 | 2018-06-08 17:03 | 0 | 0 | 0 | 0 | **** | LART | Auto reclosed successfully from both end due to B-N fault. FD: Ballia-172.3km, LKO-117.1km. FC: Ballia-3.512KA, LKO-3.8KA. Fault in Lucknow TL jurisdiction
NR176501 | NR176501 | 306059 | 765KV LUCKNOW-BALIA | 2018-06-09 15:36 | 2018-06-09 20:54 | 0 | 0 | 0.22083 | 0 | N-768 | LNCC | Emergency S/D availed for insulator cleaning at loc no 503 & 504 which was found polluted due to bird excreta during patrolling
NR376509 | NR376509 | 306053 | 765KV ORAI-ALIGARH-I | 2018-06-09 05:06 | 2018-06-09 09:47 | 0.19514 | 0 | 0 | 0 | N-729 | OSPT | S/D availed for replacement of 765KV R Ph Tie Bay(705) CB at Orai. Charged at 09:47 hrs from Orai end but immidiatly tripped on over voltage protection operated at Orai end
NR376509 | NR376509 | 306055 | 765KV ORAI-ALIGARH-I | 2018-06-09 09:47 | 2018-06-09 10:54 | 0 | 0 | 0.046528 | 0 | **** | GOVC | After S/D charged at 09:47 hrs from Orai end but immidiatly tripped on over voltage protection operated at Orai end.
NR376509 | NR376509 | 306072 | 765KV ORAI-ALIGARH-I | 2018-06-10 08:13 | 2018-06-10 11:33 | 0 | 0 | 0.13889 | 0 | **** | GOVC | Tripped due to over voltage protection operated (stage-I) at Orai(GIS) and DT received at Aligarh end. Orai=819kV
NR376509 | NR376509 | 305121 | 765KV ORAI-ALIGARH-I | 2018-06-18 13:22 | 2018-06-18 14:02 | 0.027778 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault. FD: 59.5kM from Orai end and 200.4kM from Aligarh end (Total line length-331kM). FC:6.59kA at Orai and 3.6kA at Aligarh. Fault in Orai jurisdiction.
NR376509 | NR376509 | 306154 | 765KV ORAI-ALIGARH-I | 2018-06-25 18:05 | 2018-06-25 18:24 | 0.013194 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault. FD: Orai-284.1km, Aligarh-43.7km, FC: Orai-2.6KA, Aligarh-9.5KA. Fault in Aligarh TL jurisdiction.
NR376509 | NR376509 | 306165 | 765KV ORAI-ALIGARH-I | 2018-06-27 06:06 | 2018-06-27 12:20 | 0.25972 | 0 | 0 | 0 | N-2011 | OSFT | S/D availed to attend oil leakage in B-PH line reactor
NR376501 | NR376501 | 305048 | 765KV VARANASI-KANPUR(GIS)-I | 2018-06-01 | 2018-06-03 19:37 | 0 | 0 | 1900-01-01 19:37 | 0 | N-285 | LNCC | Opened on emergency basis due to tower bent near Ghatampur caused by heavy storm
NR376501 | NR376501 | 306092 | 765KV VARANASI-KANPUR(GIS)-I | 2018-06-13 11:16 | 2018-06-13 22:01 | 0 | 0 | 0 | 0.44792 | N-1128 | LCSD | Emergency S/D taken to facilitate rectification work of broken earth wire at loc no 701-704 of 765KV D/C Varanasi-Kanpur line-2
NR376502 | NR376502 | 305037 | 765KV VARANASI-KANPUR(GIS)-II | 2018-06-01 | 2018-06-03 20:49 | 0 | 0 | 1900-01-01 20:49 | 0 | **** | LNCC | Tripped due to R-N fault due to heavy storm. FD: 22.1kM from KNP and 244.2kM from varanasi. FC: 8.347kA at KNP and 3.053kA at Varanasi. Charging attemp tajken at 0257 hrs dtd 03.05.18 but line didn't hold on SOTF on Y-B fault. 23.7kM from KNP. Fault in KNP jurisdiction.
NR376502 | NR376502 | 306089 | 765KV VARANASI-KANPUR(GIS)-II | 2018-06-13 00:35 | 2018-06-14 12:33 | 0 | 0 | 1899-12-31 11:58 | 0 | **** | LNCC | Tripped due to Y-N fault,M1:F.D.=199.6km from VNS,F.C.=3.63KA, M2:F.D.=206.7km from VNS ,F.C.=2.47KA, M1:F.D.=56.2km from KNP(GIS),F.C.=6.154KA, M2:F.D.=52.7km from KNP(GIS) ,F.C.=6.25KA caused by heavy storm(Kanpur Jurisdiction)
NRNEDCP03 | NRNEDCP03 | 305029B | 800KV HVDC AGRA-APD POLE-III | 2018-06-01 | 2018-06-25 01:42 | 0 | 0 | 1900-01-23 01:42 | 0 | **** | LNCC | Tripped due to heavy storm due to 3 Nos. Tower(4328,4347,4428) damaged.
NRNEDCP03 | NRNEDCP03 | 306157 | 800KV HVDC AGRA-APD POLE-III | 2018-06-26 05:10 | 2018-06-26 06:42 | 0.063889 | 0 | 0 | 0 | **** | OMST | Tripped due to converter T/F Differential Protection Operated at HVDC Agra.
NRNEDCP03 | NRNEDCP03 | 306177 | 800KV HVDC AGRA-APD POLE-III | 2018-06-28 03:12 | 2018-06-30 16:16 | 0 | 0 | 0 | 1900-01-01 13:04 | N-2089 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP04 | NRNEDCP04 | 306109 | 800KV HVDC AGRA-APD POLE-IV | 2018-06-15 16:09 | 2018-06-15 18:14 | 0.086806 | 0 | 0 | 0 | N-1304 | OSFT | S/D availed to attend hot spot in P4.WT.Q11.Q11 B-phase isolator at Agra.
NRNEDCP04 | NRNEDCP04 | 305029A | 800KV HVDC AGRA-APD POLE-IV | 2018-06-01 | 2018-06-07 23:08 | 0 | 0 | 1900-01-05 23:08 | 0 | **** | LNCC | Tripped due to heavy storm due to 3 Nos. Tower(4328,4347,4428) damaged.
NRNEDCP04 | NRNEDCP04 | 306065 | 800KV HVDC AGRA-APD POLE-IV | 2018-06-09 17:54 | 2018-06-10 | 0 | 0 | 0 | 0.25417 | NL-450 | LVRD | Blocked for voltage regulation as per NLDC instruction
NRNEDCP04 | NRNEDCP04 | 306126 | 800KV HVDC AGRA-APD POLE-IV | 2018-06-20 05:49 | 2018-06-25 12:22 | 0 | 0 | 0 | 1900-01-04 06:33 | N-1550 | LCSD | S/D availed for restoration of HVDC line to normal tower at two separate locations.
NRNEDCP04 | NRNEDCP04 | 306163 | 800KV HVDC AGRA-APD POLE-IV | 2018-06-27 04:41 | 2018-06-27 11:48 | 0 | 0 | 0 | 0.29653 | N-2007 | LVRD | Blocked on Voltage regulation as per NRLDC instruction.
NRNEDCP04 | NRNEDCP04 | 306176 | 800KV HVDC AGRA-APD POLE-IV | 2018-06-28 03:09 | 2018-06-28 21:54 | 0 | 0 | 0 | 0.78125 | N-2090 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NRNEDCP04 | NRNEDCP04 | 306185 | 800KV HVDC AGRA-APD POLE-IV | 2018-06-29 | 2018-06-29 00:36 | 0.025 | 0 | 0 | 0 | **** | OMST | Tripped due to Zone-1 Fire in VESDA system (Mal functioning) at Alipuduar.
NRNEDCP01 | NRNEDCP01 | 305029C | 800KV HVDC AGRA-BNC POLE-I | 2018-06-01 | 2018-06-25 01:25 | 0 | 0 | 1900-01-23 01:25 | 0 | **** | LNCC | Tripped due to heavy storm due to 3 Nos. Tower(4328,4347,4428) damaged.
NRNEDCP02 | NRNEDCP02 | 306070 | 800KV HVDC AGRA-BNC POLE-II | 2018-06-10 06:25 | 2018-06-10 15:54 | 0 | 0 | 0 | 0.39514 | N-872 | LVRD | Blocked for voltage regulation as per NLDC instruction
NRNEDCP02 | NRNEDCP02 | 306127 | 800KV HVDC AGRA-BNC POLE-II | 2018-06-20 06:02 | 2018-06-25 11:51 | 0 | 0 | 0 | 1900-01-04 05:49 | N-1552 | LCSD | S/D availed for restoration of HVDC line to normal tower at two separate locations.
NRNEDCP02 | NRNEDCP02 | 306173 | 800KV HVDC AGRA-BNC POLE-II | 2018-06-28 01:53 | 2018-06-29 09:52 | 0 | 0 | 0 | 1899-12-31 07:59 | N-2084 | LVRD | Blocked on Voltage regulation as per NLDC/NRLDC instruction.
NR1BRT03 | NR1BRT03 | 306099 | 80MVAR B/Reactor BAREILLY | 2018-06-13 18:58 | 2018-06-28 03:38 | 0 | 0 | 0 | 1900-01-13 08:40 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=392kV
NR1BRT03 | NR1BRT03 | 306183 | 80MVAR B/Reactor BAREILLY | 2018-06-28 16:49 | 2018-07-01 | 0 | 0 | 0 | 1900-01-01 07:11 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareily=398kV
NR1BRT03 | NR1BRT03 | 305258A | 80MVAR B/Reactor BAREILLY | 2018-06-01 | 2018-06-01 20:16 | 0 | 0 | 0 | 0.84444 | **** | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=393kV
NR1DCB01 | NR1DCB01 | 306160 | VINDH HVDC B/B BLOCK-I | 2018-06-26 15:21 | 2018-06-26 15:55 | 0.023611 | 0 | 0 | 0 | **** | OSFT | Emergency Hand Tripped due to attend sparking in R phase of 400kV filter bank.
NR1DCB01 | NR1DCB01 | 306016 | VINDH HVDC B/B BLOCK-I | 2018-06-02 15:23 | 2018-06-02 17:30 | 0 | 0 | 0.088194 | 0 | **** | SNCC | Tripped due to DC Over current protection operated due to heavy storm at Vindhyachal.
NR1DCB01 | NR1DCB01 | 306074 | VINDH HVDC B/B BLOCK-I | 2018-06-10 15:05 | 2018-06-10 18:04 | 0 | 0.12431 | 0 | 0 | **** | OMSU | Tripped due to DC over current protection due to external disturbance at NTPC, Singrauli due to heavy wind pressure and rain.
NR1DCB01 | NR1DCB01 | 306087 | VINDH HVDC B/B BLOCK-I | 2018-06-12 20:00 | 2018-06-12 22:03 | 0 | 0.085417 | 0 | 0 | **** | OMSU | Tripped due to DC over current protection caused by external disturbance in western system at VSTPP/NTPC
NR1DCB01 | NR1DCB01 | 306152 | VINDH HVDC B/B BLOCK-I | 2018-06-25 16:06 | 2018-06-25 17:44 | 0 | 0.068056 | 0 | 0 | **** | OMSU | Tripped on DC over current protection operated due to external disturbance in north side system at NTPC due to lightning & heavy rain.
NR1DCB02 | NR1DCB02 | 311198 | VINDH HVDC B/B BLOCK-II | 2018-06-01 | 2018-07-01 | 1900-01-29 | 0 | 0 | 0 | **** | OMST | Tripped due to Converter T/F Differential Protection Operated at HVDC VINDHYACHAL.

## Sheet3 (hidden)
400kv LINES |  |  |  | 220kv LINES |  | ICTs,HVDC & SVC. |  | OTHER LINES
400kv LINES NR-I |  | 400kv LINES NR-III |  | 220kv LINES & ICT & Reactor NR-I |  | 220kv LINES & ICT & Reactor NR-III
400KV AGRA-JAIPUR(S)-I | 1 | 400KV AGRA-FATEHABD(UP)-I | 1 | 220KV ANTA-BHIL-I | 1 | 220KV ALLD-JHUSI(UP) | RRVPNL | 220KV BASSI-KUKAS-I
400KV AGRA-JAIPUR(S)-II | 2 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2 | 220KV ANTA-BHIL-II | 2 | 220KV ALLD-REWA RD-I | RRVPNL | 220KV BASSI-KUNDA KI DHANI
400KV AGRA-SIKAR-I | 3 | 400KV AGRA-AGRA(UP)-II | 3 | 220KV ANTA-LALSOT | 3 | 220KV ALLD-REWA RD-II | RRVPNL | 220KV BHIWADI(PG)-BHIWADI
400KV AGRA-SIKAR-II | 4 | 400KV AGRA-AURAIYA-I | 4 | 220KV ANTA-RAPPC | 4 | 220KV AUR-SIKANDARA-I | RRVPNL | 220KV BHIWADI-KHUSHKHERA-I
400KV BASSI-BHIWADI-I | 5 | 400KV AGRA-AURAIYA-II | 5 | 220KV ANTA-S.MDHPR | 5 | 220KV AUR-SIKANDARA-II | RRVPNL | 220KV BHIWADI-KHUSHKHERA-II
400KV BASSI-HIRAPURA-I | 6 | 400KV AGRA-BASSI-I | 6 | 220KV BASSI-BAGRU | 6 | 220KV DGANGA-BLY(UP)-II | RRVPNL | 220KV BHIWADI-NIMRANA(RJ)
400KV BASSI-HIRAPURA-II | 7 | 400KV AGRA-BHIWADI-I | 7 | 220KV BASSI-DAUSA-I | 7 | 220KV DGANGA-PITHORAGRH | RRVPNL | 220KV BHINMAL-BHINMAL-I
400KV BASSI-JAIPUR(S)-I | 8 | 400KV AGRA-BHIWADI-II | 8 | 220KV BASSI-DAUSA-II | 8 | 220KV FATEHPUR-FTHPR(UP)-I | RRVPNL | 220KV BHINMAL-BHINMAL-II
400KV BASSI-JAIPUR(S)-II | 9 | 400KV AGRA-BLBGRH | 9 | 220KV BASSI-IG NAGAR | 9 | 220KV FATEHPUR-FTHPR(UP)-II | RRVPNL | 220KV BHINMAL-SANCHORE
400KV BASSI-KOTPUTLI | 10 | 400KV ALLD-FATEHPUR-I | 10 | 220KV FGPP-PALLA-I | 10 | 220KV FATEHPUR-KNP SOUTH | RRVPNL | 220KV BHINMAL-SIROHI
400KV BASSI-PHAGI-I | 11 | 400KV ALLD-FATEHPUR-II | 11 | 220KV FGPP-PALLA-II | 11 | 220KV FATEHPUR-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-CHAKSU-I |  | LEGENDS
400KV BASSI-PHAGI-II | 12 | 400KV ALLD-FATEHPUR-III | 12 | 220KV FGPP-SPUR-I | 12 | 220KV JHUSI(UP)-PHULPUR(UP) | RRVPNL | 220KV JAIPUR(S)-CHAKSU-II
400KV BHINMAL-ZERDA | 13 | 400KV ALLD-KNP-II | 13 | 220KV FGPP-SPUR-II | 13 | 220KV KNP-MAINPURI | RRVPNL | 220KV JAIPUR(S)-SEZ |  |  | Lines maintained by ER
400KV BHIWADI-GURGAON | 14 | 400KV ALLD-VARANASI | 14 | 220KV HIRAPURA-IG NAGAR | 14 | 220KV KNP-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-DOONI
400KV BHIWADI-HISAR-I | 15 | 400KV BALIA-MAU-I | 15 | 220KV HIRAPURA-SANGANER | 15 | 220 KV KANPUR(PG) - RANIYA( UP)-1 | RRVPNL | 220KV KANKROLI(PG)-BHILWARA
400KV BHIWADI-KOTPUTLI | 16 | 400KV BALIA-MAU-II | 16 | 220KV LALSOT-DAUSA | 16 | 220 KV RANIYA( UP) - PANKI (UP)-1 | RRVPNL | 220KV KANKROLI(PG)-KANK-I
400KV BHIWADI-NIMRANA-I | 17 | 400KV BALIA-SOHAWAL-I | 17 | 220KV MEERUT-MPURAM-I | 17 | 220KV KNP-PANKI-II | RRVPNL | 220KV KANKROLI(PG)-KANK-II
400KV BHIWADI-NIMRANA-II | 18 | 400KV BALIA-SOHAWAL-II | 18 | 220KV MEERUT-MPURAM-II | 18 | 220KV KNP-UNCHR-I | RRVPNL | 220KV KANKROLI-DEBARI |  |  | lines maintained by WR
400KV BLBGRH-GURGAON | 19 | 400KV BAREILLY-BRLY(765)-I | 19 | 220KV MEERUT-NARA | 19 | 220KV KNP-UNCHR-II | RRVPNL | 220KV KOTA-KTPS-1
400KV BLBGRH-MAHRANIBG | 20 | 400KV BAREILLY-BRLY(765)-II | 20 | 220KV MEERUT-SHTBDNGR | 20 | 220KV KNP-UNCHR-III | RRVPNL | 220KV KOTA-KTPS-2 |  |  | LILO portions only of POWERGRID
400KV BLBGRH-NAVADA(HVPN) | 21 | 400KV BAREILLY-BRLY(UP)-I | 21 | 220KV MEERUT-SIMBHOLI | 21 | 220KV KNP-UNCHR-IV | RRVPNL | 220KV KOTA-BHILWARA
400KV DAD-GR.NOIDA | 22 | 400KV BAREILLY-BRLY(UP)-II | 22 | 220KV RAPPB-CHITT-I | 22 | 220KV PITHORAGRH-BRLY(UP) | RRVPNL | 220KV KOTA-DHUNI |  |  | LILO portion maintained by constituents
400KV DAD-MAHRANIBG | 23 | 400KV BAREILLY-LKO(UP) | 23 | 220KV RAPPB-CHITT-II | 23 | 220KV RAIBRLY-CHINHAT | RRVPNL | 220KV KOTPUTLI-KOTPUTLI
400KV DAD-MANDOLA-I | 24 | 400KV BAREILLY-MBAD-I | 24 | 220KV RAPPB-RAPPC | 24 | 220KV RAIBRLY-LKO(UP) | RRVPNL | 220KV KOTPUTLI-MANOHARPUR
400KV DAD-MANDOLA-II | 25 | 400KV BAREILLY-MBAD-II | 25 | 220KV RAPPB-UDAIPUR | 25 | 220KV SITARGANJ-BLY(UP) | RRVPNL | 220KV NIMRANA-NIMRANA
400KV DAD-MURADNGR | 26 | 400KV BAREILLY-ROSA-I | 26 | 220KV S.MDHPR-DAUSA-I | 26 | 220KV TNKPR-BLY(UP) | RRVPNL | 220KV NIMRANA-KHUSHKHERA |  |  | Maintained by NR-1 & NR-II
400KV DAD-PANIPAT-I | 27 | 400KV BAREILLY-SHAHJHNPR-I | 27 | 220KV SIKAR-RATANGARH-I | 27 | 220KV TNKPR-SITARGANJ | HVPNL | 220KV BHIWADI-MAU
400KV DAD-PANIPAT-II | 28 | 400KV BAREILLY-SHAHJHNPR-II | 28 | 220KV SIKAR-RATANGARH-II | 28 | 220KV UNCHR-RAIBRLY-I | HVPNL | 220KV BHIWADI-REWARI-I
400KV GURGAON-MANESAR-I | 29 | 400KV BARLY(765)-KASHIPUR-I | 29 | 220KV SIKAR-SIKAR(RJ)-I | 29 | 220KV UNCHR-RAIBRLY-II | HVPNL | 220KV BHIWADI-REWARI-II
400KV GURGAON-MANESAR-II | 30 | 400KV BARLY(765)-KASHIPUR-II | 30 | 220KV SIKAR-SIKAR(RJ)-II | 30 | 220KV UNCHR-RAIBRLY-III | HVPNL | 220KV BHIWADI-BAWAL
400KV JHATIKALA-BAMNOLI-I | 31 | 400KV BLBGRH-MAINPURI-I | 31 | 220KV HISAR-HISAR I/A-I |  |  | HVPNL | 220KV GURGAON-GURGAON-I
400KV JHATIKALA-BAMNOLI-II | 32 | 400KV BLBGRH-MAINPURI-II | 32 | 220KV HISAR-HISAR I/A-II |  |  | HVPNL | 220KV GURGAON-GURGAON-II
400KV JHATIKALA-MUNDKA-I | 33 | 400KV FATEHPUR-MAINPURI-I |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-III
400KV JHATIKALA-MUNDKA-II | 34 | 400KV FATEHPUR-MAINPURI-II |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-IV
400KV KANKROLI-BHINMAL | 35 | 400KV GORAKH-GORAKH-I |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-I
400KV KANKROLI-JODHPUR | 36 | 400KV GORAKH-GORAKH-II |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-II
400KV KANKROLI-CHITTOR(RJ)-I | 37 | 400KV KNP-AGRA |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-I
400KV KANKROLI-RAPPC-II | 38 | 400KV KNP-AURAIYA-I |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-II
400KV KANKROLI-ZERDA-I | 39 | 400KV KNP-AURAIYA-II |  | 400KV & 220KV ICT NR-I |  |  | HVPNL | 220 KV MANESAR-BADSHAHPUR-I
400KV KOTA-BEAWAR | 40 | 400KV KNP-BLBGARH-I | 1 | 315MVA ICT-I BASSI |  | 400KV & 220KV ICT NR-III | HVPNL | 220 KV MANESAR-BADSHAHPUR-II
400KV KOTA-MERTA-I | 41 | 400KV KNP-BLBGARH-II | 2 | 315MVA ICT-II BASSI | 1 | 315MVA ICT-I AGRA | HVPNL | 220 KV MANESAR-MAU-I
400KV KOTA-RAPPC | 42 | 400KV KNP-BLBGARH-III | 3 | 500MVA ICT-III BASSI | 2 | 315MVA ICT-I ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-II
400KV KOTESHWR-KHEP-I | 43 | 400KV KNP-FATEHPUR-I | 4 | 315MVA ICT-III BAWANA | 3 | 315MVA ICT-II ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-III
400KV KOTESHWR-KHEP-II | 44 | 400KV KNP-FATEHPUR-II | 5 | 315MVA ICT-I BHINMAL | 4 | 315MVA ICT-III ALLAHABAD | HVPNL | 220 KV SONIPAT-MOHANA-I
400KV KOTESHWR-TEHRI-I | 45 | 400KV KNP-PANKI-I | 6 | 315MVA ICT-II BHINMAL | 5 | 315MVA ICT-I FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-I
400KV KOTESHWR-TEHRI-II | 46 | 400KV KNP-PANKI-II | 7 | 315MVA ICT-I BHIWADI | 6 | 315MVA ICT-II FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-II
400KV MBAD-MURADNGR | 47 | 400KV LUCKNOW-GORAKH-III | 8 | 315MVA ICT-II BHIWADI | 7 | 315MVA ICT-I GORAKHPR | HVPNL | 220KV HISAR-SRWL-I
400KV MEERUT-BAGPAT-I | 48 | 400KV LUCKNOW-GORAKH-IV | 9 | 315MVA ICT-III BHIWADI | 8 | 315MVA ICT-II GORAKHPR | HVPNL | 220KV HISAR-SRWL-II
400KV MEERUT-BAREILLY-I | 49 | 400KV LUCKNOW-LKO(765)-I | 10 | 500MVA ICT-I BLBGARH | 9 | 315MVA ICT-I KANPUR | HVPNL | 220KV HISAR-FATEHABAD-I
400KV MEERUT-BAREILLY-II | 50 | 400KV LUCKNOW-LKO(765)-II | 11 | 315MVA ICT-II BLBGARH | 10 | 315MVA ICT-II KANPUR | HVPNL | 220KV HISAR-FATEHABAD-II
400KV MEERUT-KOTESHWR-I | 51 | 400KV LUCKNOW-LKO(UP) | 12 | 315MVA ICT-III BLBGARH | 11 | 315MVA ICT-I LUCKNOW | NTPC | 132KV SING-VINDH-RIH
400KV MEERUT-KOTESHWR-II | 52 | 400KV LUCKNOW-ROSA-I | 13 | 315MVA ICT-IV BLBGARH | 12 | 500MVA ICT-II LUCKNOW | NTPC | 132KV SING-RENUSAGAR-PIPRI
400KV MEERUT-MND-I | 53 | 400KV LUCKNOW-SHAHJHNPR-I | 14 | 315MVA ICT-I GURGAON | 13 | 315MVA ICT-I MAINPURI | DTL | 400KV B'GARH-BAMNOLI-I
400KV MEERUT-MND-II | 54 | 400KV LUCKNOW-SHAHJHNPR-II | 15 | 315MVA ICT-II GURGAON | 14 | 315MVA ICT-II MAINPURI | DTL | 400KV B'GARH-BAMNOLI-II
400KV MEERUT-MND-III | 55 | 400KV LUCKNOW-SOHAWAL-I | 16 | 500MVA ICT-I JAIPUR(S) | 15 | 100MVA ICT-I PITHORAGRH | DTL | 400KV MND-BAWANA-I
400KV MEERUT-MND-IV | 56 | 400KV LUCKNOW-SOHAWAL-II | 17 | 500MVA ICT-II JAIPUR(S) | 16 | 100MVA ICT-II PITHORAGRH | DTL | 400KV MND-BAWANA-II
400KV MEERUT-MUZFRNGR | 57 | 400KV LUCKNOW-SULTANPR | 18 | 315MVA ICT-I KANKROLI | 17 | 100MVA ICT-I RAIBAREILLY | DTL | 220KV MND-S.WZRBD-I
400KV MERTA-BEAWAR | 58 | 400KV LUCKNOW-UNNAO-I | 19 | 315MVA ICT-II KANKROLI | 18 | 100MVA ICT-II RAIBAREILLY | DTL | 220KV MND-S.WZRBD-II
400KV NAVADA(HVPN)-GR.NOIDA | 59 | 400KV LUCKNOW-UNNAO-II | 20 | 315MVA ICT-III KANKROLI | 19 | 100MVA ICT-III RAIBAREILLY | DTL | 220KV MND-S.WZRBD-III
400KV NIMRANA-MANESAR-I | 60 | 400KV MEERUT-BAREILLY-I | 21 | 315MVA ICT-I KOTA | 20 | 500MVA ICT-I SHAHJHNPR | DTL | 220KV MND-S.WZRBD-IV
400KV NIMRANA-MANESAR-II | 61 | 400KV MEERUT-BAREILLY-II | 22 | 315MVA ICT-II KOTA | 21 | 500MVA ICT-II SHAHJHNPR | DTL | 220KV MND-NARELA-I
400KV NIMRANA-SIKAR-I | 62 | 400KV RIHAND-ALLD-I | 23 | 315MVA ICT-I KOTPUTLI | 22 | 100MVA ICT-I SITARGANJ | DTL | 220KV MND-NARELA-II
400KV NIMRANA-SIKAR-II | 63 | 400KV RIHAND-ALLD-II | 24 | 315MVA ICT-II KOTPUTLI | 23 | 100MVA ICT-II SITARGANJ | DTL | 220KV MND-GOPALPUR-I
400KV ROORKI-KASHIPUR-I | 64 | 400KV RIHAND3-VINDH(Pool)-I | 25 | 315MVA ICT-I MAHRANIBAG | 24 | 315MVA ICT-I SOHAWAL | DTL | 220KV MND-GOPALPUR-II
400KV ROORKI-KASHIPUR-II | 65 | 400KV RIHAND3-VINDH(Pool)-II | 26 | 315MVA ICT-II MAHRANIBAG | 25 | 315MVA ICT-II SOHAWAL | DTL | 220KV MBAG-SARITAVIHAR
400KV ROORKI-MUZFRNGR | 66 | 400KV SING-ALLD-I | 27 | 500MVA ICT-III MAHRANIBAG | 26 |  | DTL | 220KV MBAG-LODHIROAD-I
400KV ROORKI-RISHIKESH | 67 | 400KV SING-ALLD-II | 28 | 500MVA ICT-IV MAHRANIBAG | 27 |  | DTL | 220KV MBAG-LODHIROAD-II
400KV SIKAR-RATANGARH-I | 68 | 400KV SING(NTPC)-ANPARA(UP) | 29 | 500MVA ICT-I MANDOLA | 28 |  | DTL | 220KV MBAG-I P EXTN
400KV SIKAR-RATANGARH-II | 69 | 400KV SING-FATEHPUR | 30 | 500MVA ICT-II MANDOLA | 29 |  | UPPCL | 220KV AGRA-SHAMSABD-I
400KV MEERUT-BAGPAT-II | 70 | 400KV SING-LKO(UP)-I | 31 | 500MVA ICT-III MANDOLA | 30 |  | UPPCL | 220KV AGRA-FEROZABAD
400KV ROORKI-SAHARANPUR-I | 71 | 400KV SING-RIHAND-I | 32 | 500MVA ICT-IV MANDOLA |  |  | UPPCL | 220KV BAGHPAT(PG)-BAGHPAT(UP)
400KV ROORKI-SAHARANPUR-II | 72 | 400KV SING-RIHAND-II | 33 | 500MVA ICT-I MANESAR |  |  | UPPCL | 220KV BAGHPAT-MURADNGR
400KV RAPPC-CHITTOR(RJ)-I | 73 | 400KV SING-VINDH-I | 34 | 500MVA ICT-II MANESAR |  |  | UPPCL | 220KV BAGHPAT-SHAMLI
| 74 | 400KV SING-VINDH-II | 35 | 315MVA ICT-I MEERUT |  |  | UPPCL | 220KV GORAKH-BARHUA
| 75 | 400KV KANPUR-KANPUR(GIS)-I | 36 | 315MVA ICT-II MEERUT |  | 765KV ICT NR-III | UPPCL | 220KV GORAKH-BASTI
| 76 | 400KV KANPUR-KANPUR(GIS)-II | 37 | 315MVA ICT-III MEERUT | 1 | 765/400KV ICT-I BALIA | UPPCL | 220KV LKO(PG)-Bakhsi Ka Talab
| 77 | 400KV VARANASI-SASARAM(ER) | 38 | 500MVA ICT-IV MEERUT | 2 | 765/400KV ICT-II BALIA | UPPCL | 220KV LKO(PG)-CHINHAT
400KV BAHADURGRH-BAWANA | 78 | 400KV VARANASI-SARNATH-I | 39 | 315MVA ICT-III MUZFRNGR | 3 | 765/400KV ICT-I LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-I
400KV BAHADURGRH-SONIPAT-I | 79 | 400KV VARANASI-SARNATH-II | 40 | 315MVA ICT-II NIMRANA | 4 | 765/400KV ICT-II LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-II
400KV BAHADURGRH-SONIPAT-II | 80 | 400KV ALLAHABAD-MEJA(NTPC)-I | 41 | 315MVA ICT-I ROORKI | 5 | 765/400KV ICT-I FATEHPUR | UPPCL | 220KV M'PURI-ETAH
400KV BHIWANI-BAWANA | 81 | 400KV BALIA-BIHARSHRF-I | 42 | 315MVA ICT-II ROORKI | 6 | 765/400KV ICT-II FATEHPUR | UPPCL | 220KV M'PURI-SIRSAGANJ-I
400KV BHIWANI-BHIWANI(BBMB) | 82 | 400KV BALIA-BIHARSHRF-II | 43 | 315MVA ICT-I SIKAR | 7 | 765/400KV ICT-I AGRA | UPPCL | 220KV M'PURI-M'PURI(UP)-II
400KV BHIWANI-HISAR-I | 83 | 400KV ALLD-SASARAM | 44 | 315MVA ICT-II SIKAR | 8 | 765/400KV ICT-II AGRA | UPPCL | 220KV M'PURI-FEROZBD
400KV BHIWANI-HISAR-II | 84 | 400KV BALIA-PATNA-I | 45 | 500MVA ICT-I BAGPAT | 9 | 765/400KV ICT-I BAREILLY | UPPCL | 400KV M'PURI-ORAI-I
400KV BHIWANI-HISAR-III | 85 | 400KV BALIA-PATNA-II | 46 | 500MVA ICT-II BAGPAT | 10 | 765/400KV ICT-II BAREILLY | UPPCL | 400KV M'PURI-PARICHA-II
400KV BHIWANI-JIND-I | 86 | 400KV BALIA-PATNA-III | 47 | 315MVA ICT-I SAHARANPUR | 11 | 765/400KV ICT-I VARANASI | UPPCL | 220KV MEERUT-GAJRAULA
400KV BHIWANI-JIND-II | 87 | 400KV BALIA-PATNA-IV | 48 | 315MVA ICT-II SAHARANPUR | 12 | 765/400KV ICT-II VARANASI | UPPCL | 220KV MEERUT-NEHTAUR
400KV FATEHABAD-HISAR | 88 | 400KV LKO(765)-KANPUR(GIS)-I |  |  | 13 | 765/400KV ICT-I KANPUR(GIS) | UPPCL | 220KV ORAI-KANPUR
400KV BHIWADI-HISAR-II | 89 | 400KV LKO(765)-KANPUR(GIS)-II |  |  | 14 | 765/400KV ICT-II KANPUR(GIS) | UPPCL | 400KV PANKI-MURADNGR
400KV BHIWADI-HISAR-III | [6 empty] | UPPCL | 220KV SHAHJHNP-HARDOI
400KV HISAR-BHIWANI(BBMB) | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-I | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-II |  | 400kv LINES of ER-1 in NR-III Availability |  | NR-I Additional ICT from NR-II |  |  | UPPCL | 220KV SOHAWAL(PG) - SOHAWAL(UP)
400KV KABULPR-BAHADURGRH | 1 | 400KV SASARAM-BIHARSHRF-I | 1 | 315MVA ICT-I BAHADURGARH |  | NR-III HVDC SYSTEM / SVC | UPPCL | 220KV UNCHR-RBRLY-I
400KV KABULPR-BHIWANI | 2 | 400KV SASARAM-BIHARSHRF-II | 2 | 500MVA ICT-II BAHADURGARH | 1 | 500KV HVDC R-D POLE-I | UPPCL | 220KV UNCHR-RBRLY-II
|  |  | 3 | 315MVA ICT-I HISAR | 2 | 500KV HVDC R-D POLE-II | PTCUL | 220KV ROORKI-HARDWAR
|  |  | 4 | 315MVA ICT-II HISAR | 3 | 500KV HVDC BALIA-BHWD POLE-I | PTCUL | 220KV ROORKI--RAMNAGAR
|  | 765 KV TRANS LINES NR-III | 5 | 315MVA ICT-III HISAR | 4 | 500KV HVDC BALIA-BHWD POLE-II | PTCUL | 132KV SITARGNJ(PG)-SITARGNJ(PTCUL)
765 KV TRANS LINES NR-I | 1 | 765KV AGRA-FATEHPUR-I | 6 | 315MVA ICT-I SONIPAT | 5 | 800KV HVDC AGRA-BNC POLE-I | PTCUL | 132KV PITHORAGRH-CHANDOK
765KV AGRA-JHATIKALA | 2 | 765KV AGRA-FATEHPUR-II | 7 | 315MVA ICT-II SONIPAT | 6 | 800KV HVDC AGRA-BNC POLE-II | PTCUL | 132KV PITHORAGRH-ALMORA
765KV BHIWANI-PHAGI(JPR)-I | 3 | 765KV AGRA-GR.NOIDA | 8 | 315MVA ICT-I BHIWANI | 7 | VINDH HVDC B/B BLOCK-I | PTCUL | 132KV PTRGRH-PTRGRH(PTCUL)
765KV MEERUT-GR.NOIDA | 4 | 765KV FATEHPUR-SASARAM | 9 | 315MVA ICT-II BHIWANI | 8 | VINDH HVDC B/B BLOCK-II | POWERLINK
765KV MOGA-BHIWANI | 5 | 765KV LUCKNOW-BALIA | 10 | 500MVA ICT-I JIND | 9 | SASARAM HVDC B/B | PLINK | 400KV LUCKNOW-GORAKH-I (PL)
765KV JHATIKALA-BHIWANI | 6 | 765KV LUCKNOW-BAREILLY | 11 | 500MVA ICT-II JIND | 10 | +/-140MVAR SVC-I KANPUR | PLINK | 400KV LUCKNOW-GORAKH-II (PL)
765KV MEERUT-BHIWANI | 7 | 765KV VARANASI-BALIA |  |  | 11 | +/-140MVAR SVC-II KANPUR | PLINK | 400KV GRKHPR-MZFRPR-I (PL)
765KV BHIWANI-PHAGI(JPR)-II | 8 | 765KV VARANASI-FATEHPUR |  |  |  |  | PLINK | 400KV GRKHPR-MZFRPR-II (PL)
| 9 | 765KV VARANASI-GAYA-I |  | 765KV ICT NR-I
| 10 | 765KV VARANASI-KANPUR(GIS)-I | 1 | 765/400KV ICT-I JHATIKALA
BUS REACTORS NR-I | 11 | 765KV VARANASI-KANPUR(GIS)-II | 2 | 765/400KV ICT-II JHATIKALA |  | SWITCABLE LINE REACTORS NR-III | NR-II | 400KV DAD-M'KOTLA
125MVAR B/Reactor-I BAGPAT | 12 | 765KV KANPUR(GIS)-JHATIKRA-I | 3 | 765/400KV ICT-III JHATIKALA | 1 | AGRA 240MVAR S/R FATEHPR line | NR-II | 400KV BAGHPAT-KAITHAL-I
50MVAR B/Reactor-I BASSI |  |  | 4 | 765/400KV ICT-IV JHATIKALA | 2 | AGRA 50MVAR S/R BHIWADI-I LINE | NR-II | 400KV BAGHPAT-KAITHAL-II
50MVAR B/Reactor-II BASSI |  |  | 5 | 765/400KV ICT-I MEERUT | 3 | ALLHBD 50MVAR S/R MNPR-I LINE | NR-II | 765KV MEERUT-MOGA
50MVAR B/Reactor-III BASSI |  | BUS REACTORS NR-III | 6 | 765/400KV ICT-II MEERUT | 4 | ALLHBD 50MVAR S/R MNPR-II LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-I | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
125MVAR B/Reactor-IV BASSI | 1 | 125MVAR B/Reactor-I AGRA | 7 | 765/400KV ICT-I BHIWANI | 5 | BARLLY 50MVAR S/R MND-I LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-II | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
80MVAR B/Reactor BHINMAL | 2 | 125MVAR B/Reactor-II AGRA | 8 | 765/400KV ICT-II BHIWANI | 6 | BARLLY 50MVAR S/R MND-II LINE | NR-II | 400KV HISAR-MOGA-I
80MVAR B/Reactor BHIWADI | 3 | 240MVAR B/Reactor-II AGRA-765 |  |  | 7 | BALIA 240MVAR S/R LUCKNW Ckt-I | NR-II | 400KV HISAR-MOGA-II
80MVAR B/Reactor BLBGARH | 4 | 240MVAR B/Reactor-1 AGRA-765 |  |  | 8 | BALIA 240MVAR S/R GAYA Line | NR-II | 400KV HISAR-MOGA-III
125MVAR B/Reactor-I JAIPUR(S) | 5 | 80MVAR B/Reactor ALLAHABAD |  |  | 9 | FATEHPR 330MVAR S/R AGRA line
125MVAR B/Reactor-II JAIPUR(S) | 6 | 125MVAR B/Reactor-II ALLAHABAD |  |  | 10 | GORAKH 50MVAR S/R LKO-I LINE
240MVAR B/Reactor-I JHATIKALA-765 | 7 | 80MVAR B/Reactor-I BALIA |  |  | 11 | GORAKH 50MVAR S/R LKO-II LINE
240MVAR B/Reactor-II JHATIKALA-765 | 8 | 125MVAR B/Reactor-II BALIA |  |  | 12 | GORAKH 63MVAR S/R LKO-III LINE
50MVAR B/Reactor KANKROLI | 9 | 125MVAR B/Reactor-III BALIA |  | SWITCABLE LINE REACTORS NR-I | 13 | GORAKH 63MVAR S/R LKO-IV LINE | ER-I | 400KV BALIA-SASARAM
125MVAR B/Reactor-II KANKROLI | 10 | 125MVAR B/Reactor-IV BALIA | 1 | BHINML 50MVAR S/R KANKROLI | 14 | GORAKH 80MVAR S/R Barh-I line | ER-I | 765KV BALIA-GAYA
80MVAR B/Reactor-I KOTA | 11 | 240MVAR B/Reactor-I BALIA-765 | 2 | MEERUT 50MVAR S/R Kotesh-I LINE | 15 | GORAKH 80MVAR S/R Barh-II line | ER-I | 400KV BARH- GRKHPR-I
50MVAR B/Reactor-II KOTA | 12 | 240MVAR B/Reactor-II BALIA-765 | 3 | MEERUT 50MVAR S/R Kotesh-II LINE | 16 | LUCKNW 240MVAR S/R BRLY Line | ER-I | 400KV BARH- GRKHPR-II
80MVAR B/Reactor-I KOTPUTLI | 13 | 80MVAR B/Reactor BAREILLY | 4 | JHATIKALA 240MVAR S/R AGRA Line | 17 | LUCKNW 63MVAR S/R GKP-III LINE | ER-I | 765KV VARANASI-GAYA-II
50MVAR B/Reactor MANDOLA | 14 | 2x50MVAR B/Reactor BAREILLY | 5 | MEERUT 240MVAR S/R AGRA line | 18 | LUCKNW 63MVAR S/R GKP-IV LINE | ER-I | 400KV VARANASI-BIHARSHRF-I
240MVAR B/Reactor-I MEERUT-765 | 15 | 240MVAR B/Reactor-I BAREILLY-765 | 6 | SIKAR 50MVAR S/R AGRA Ckt-I | 19 | LUCKNW 240MVAR S/R BALIA Ckt-I | ER-I | 400KV VARANASI-BIHARSHRF-II
125MVAR B/Reactor MANESAR | 16 | 80MVAR B/Reactor BIHARSHRF | 7 | SIKAR 50MVAR S/R AGRA Ckt-II | 20 | VARANASI 240MVAR S/R KNP(GIS) ckt-1
50MVAR B/Reactor MURADNGR | 17 | 125MVAR B/Reactor-I FATEHPUR | 8 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | 21 | VARANASI 240MVAR S/R KNP(GIS) ckt-2
80MVAR B/Reactor NIMRANA | 18 | 125MVAR B/Reactor-II FATEHPUR | 9 | BHIWANI 240MVAR S/R MEERUT line | 22 | KNP(GIS) 330MVAR S/R JHATIKRA ckt-1 | WR | 765KV AGRA-GWALIOR-I
240MVAR B/Reactor-I PHAGI(JPR)-765 | 19 | 330MVAR B/Reactor-III FTHPR-765 | 10 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line |  |  | WR | 765KV AGRA-GWALIOR-II
125MVAR B/Reactor ROORKEE | 20 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | WR | 765KV GWALIOR-PHAGI-I
125MVAR B/Reactor-I RATANGRH(RJ) | 21 | 125MVAR B/Reactor-II LUCKNOW |  | SVC NR-I |  |  | WR | 765KV GWALIOR-PHAGI-II
80MVAR B/Reactor SIKAR | 22 | 125MVAR B/Reactor-III LUCKNOW | 1 | +400/-300MVAR SVC KANKROLI
50MVAR B/Reactor-I SAHARANPUR | 23 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-I
50MVAR B/Reactor-II SAHARANPUR | 24 | 125MVAR B/Reactor-I VINDH |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-II
125MVAR B/Reactor-II SONIPAT | 25 | 125MVAR B/Reactor-II VINDH
| 26 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - I
BUS REACTORS NR-I From NR2 | 27 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - II
240MVAR B/Reactor-I BHIWANI | 28 | 125MVAR B/Reactor-1 Mainpuri
240MVAR B/Reactor-II BHIWANI | 29 | 125MVAR B/Reactor Gorakhpur-I
50MVAR B/Reactor HISAR | 30 | 125MVAR B/Reactor-II Gorakhpur
125MVAR B/Reactor HISAR | 31 | 125MVAR B/Reactor-I SHAHJHNPR
125MVAR Bus/eactor JIND | 32 | 240MVAR B/Reactor-I KANPUR(GIS)
125MVAR B/Reactor SONIPAT | 33 | 240MVAR B/Reactor-II KANPUR(GIS)
| 34 | 125MVAR B/Reactor-III KANPUR(GIS)
| 35 | 125MVAR B/Reactor-I VARANASI
| 36 | 330MVAR B/Reactor-I VARANASI
| 37 | 330MVAR B/Reactor-II VARANASI
| 38 | 125MVAR B/Reactor KANPUR
Note on E50: a: DOC-01.04.12
Note on I83: 220KV M'PURI-M'PURI(UP)-I LILO at SIRSAGANJ
Note on E84: a: DOC-01.04.12
Note on I86: '400KV M'PURI-PARICHA-I LILO at URI
Note on A96: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on A97: Total-45.6km, PG-26.64km, HVPN-19km.
Note on I98: DELL: 220KV ROORKI-SIDKUL
Note on C108: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C109: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on I112: LILO of 400KV MEERUT-KAITHAL-I at Baghpat
Note on I113: LILO of 400KV MEERUT-KAITHAL-II at Baghpat
Note on I128: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet4
SL.NO. | ELEMENT | Element Name |  | ELEMENT ID | Element name | Total LINE length | 765KV AGRA-JHATIKARA | 253.147
| ID | [5 empty] | 765KV AGRA-Gr Noida | 148.034
|  |  |  | NR176502 | 765KV AGRA-FATEHPUR-I | 8025:36 | 765KV BALLIA-VARANASI | 165.98
A |  | 765 KV TRANS LINES |  | NR176501 | 765KV LUCKNOW-BALIA | 7653:43 | 765KV FATEHPUR-SASARAM | 355.008
1 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR140001 | 400KV AGRA-AGRA(UP)-I | 719:34 | 765KV FATEHPUR-AGRA-1 | 334.52
2 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR140002 | 400KV AGRA-AGRA(UP)-II | 719:34 | 765KV FATEHPUR-AGRA-2 | 334.8
3 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR140003 | 400KV AGRA-AURAIYA-I | 3980:02 | 765KV GAYA-VARANASI-I (OLD FTP-GAYA) | 263.94
4 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR140004 | 400KV AGRA-AURAIYA-II | 0:00 | 765KV GWALIOR-AGRA I | 129.435
5 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR140005 | 400KV AGRA-BASSI-I | 5093:31 | 765KV GWALIOR-AGRA II | 127.934
6 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR140008 | 400KV AGRA-BHIWADI-I | 5023:55 | 765KV KANPUR-JHATIKARA | 465.8
7 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR140009 | 400KV AGRA-BHIWADI-II | 5023:55 | 765KV KANPUR-VARANASI-I | 326.172
8 | NR176513 | 765KV VARANASI-FATEHPUR | 224.963 | NR140010 | 400KV AGRA-BLBGRH | 4347:22 | 765KV KANPUR-VARANASI-II
9 | NR176514 | 765KV VARANASI-GAYA-I | 80.925 | NR140122 | 400KV ALLD-FATEHPUR-I | 3353:31 | 765KV LUCKNOW-BALIA | 318.919
10 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR140123 | 400KV ALLD-FATEHPUR-II | 3353:31 | 765KV LUCKNOW-BAREILLY | 251.613
11 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR140104 | 400KV ALLD-FATEHPUR-III | 3574:19 | 765KV VARANASI-FATEHPUR | 224.963
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR140012 | 400KV ALLD-KNP-II | 5260:24 | 765KV GAYA-VARANASI-II | 80.925
13 | NR376504 | 765KV ALIGARH-JHATIKARA |  | NR140016 | 400KV ALLD-SASARAM | 4548:43 | 765KV GAYA-BALIA | 238
14 | NR376505 | 765KV KANPUR(GIS)-ALIGARH |  | NR140017 | 400KV BALIA-BIHARSHRF-I | 5802:43 | Total 17 765KV Lines | 4019.19
15 | NR376506 | 765KV AGRA-ALIGARH |  | NR140018 | 400KV BALIA-BIHARSHRF-II | 5802:43 | AGRA-FATEHABAD(UP)-I | 43.013
16 | NR376507 | 765KV ALIGARH-GR.NOIDA |  | NR140019 | 400KV BALIA-MAU-I | 221:10 | FATEHABAD(UP)-AGRA(UP)-I | 57.159
17 | NR376508 | 765KV ORAI-ALIGARH-II |  | NR140020 | 400KV BALIA-MAU-II | 221:10 | AGRA-AGRA-(UP)-II | 29.969
18 | NR376509 | 765KV ORAI-ALIGARH-I |  | NR140021 | 400KV BALIA-PATNA-I | 4685:34 | AURAIYA-AGRA-I | 167.2
|  |  |  | NR140022 | 400KV BALIA-PATNA-II | 4685:34 | AURAIYA-AGRA-II
|  |  |  | NR140136 | 400KV BALIA-PATNA-III | 4440:00 | AGRA-BASSI | 211.433
B |  | 400 KV TRANS LINES |  | NR140137 | 400KV BALIA-PATNA-IV | 4440:00 | AGRA-BHIWADI-I | 208.98
1 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR140140 | 400KV BALIA-SOHAWAL-I | 5499:55 | AGRA-BHIWADI-II | 209.51
2 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR140120 | 400KV BALIA-SOHAWAL-II | 5499:55 | AGRA-BLB | 181.137
3 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 |  | 400KV BLBGRH-MAINPURI-I | 5662:51 | AGRA-JAIPUR(S)-I | 254.41
4 | NR140005 | 400KV AGRA-BASSI-I | 212.23 |  | 400KV BLBGRH-MAINPURI-II | 5662:51 | AGRA-JAIPUR(S)-II
5 | NR140008 | 400KV AGRA-BHIWADI-I | 209.33 | NR140025 | 400KV BAREILLY-LKO(UP) | 6691:12 | AGRA-SIKAR-I | 393.9
6 | NR140009 | 400KV AGRA-BHIWADI-II | 209.33 | NR140026 | 400KV BAREILLY-MBAD-I | 2226:43 | AGRA-SIKAR-II
7 | NR140010 | 400KV AGRA-BLBGRH | 181.14 | NR140027 | 400KV BAREILLY-MBAD-II | 2210:54 | ALLD-FATEHPUR-I | 139.73
8 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 |  | 400KV BAREILLY-MEERUT-I | 5899:12 | ALLD-FATEHPUR-II
9 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 |  | 400KV BAREILLY-MEERUT-II | 5899:12 | ALLD-FATEHPUR-III | 148.934
10 | NR140104 | 400KV ALLD-FATEHPUR-III | 148.93 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 6241:13 | ALLD-KNP-II | 0
11 | NR140012 | 400KV ALLD-KNP-II | 219.183 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 6241:13 | BALIA-MAU-I | 13
12 | NR140163 | 400KV ALLD-VARANASI | 98.791 | NR140046 | 400KV GORKH-GORAKH-I | 1102:35 | BALIA-MAU-II
13 | NR140016 | 400KV ALLD-SASARAM | 189.53 | NR140047 | 400KV GORKH-GORAKH-II | 1102:35 | BALIA-SOHAWAL-I | 229.163
14 | NR140017 | 400KV BALIA-BIHARSHRF-I | 241.78 | NR140052 | 400KV KNP-AGRA | 5760:00 | BALIA-SOHAWAL-II
15 | NR140018 | 400KV BALIA-BIHARSHRF-II | 241.78 | NR140053 | 400KV KNP-AURAIYA-I | 1754:55 | BAREILLY(400)-BAREILLY(765)-I | 1.559
16 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR140054 | 400KV KNP-AURAIYA-II | 1754:55 | BAREILLY(400)-BAREILLY(765)-II
17 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR140055 | 400KV KNP-BLBGARH-I | 9256:48 | BAREILLY-BLY(UP)-I | 14.3
18 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR140056 | 400KV KNP-BLBGARH-II | 8898:32 | BAREILLY-BLY(UP)-II | 14.3
19 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR140057 | 400KV KNP-BLBGARH-III | 8898:32 | BAREILLY-MEERUT-I | 249.52
20 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 14.3 | NR140110 | 400KV KNP-FATEHPUR-I | 2569:54 | BAREILLY-MEERUT-II | 249.52
21 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 14.3 | NR140105 | 400KV KNP-FATEHPUR-II | 2570:24 | LKO(UP)-BAREILLY | 278.76
22 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.8 | NR140058 | 400KV KNP-PANKI-I | 141:36 | BAREILLY-MORADABAD-I | 92.68
23 | NR140026 | 400KV BAREILLY-MBAD-I | 92.78 | NR140059 | 400KV KNP-PANKI-II | 141:36 | BAREILLY-MORADABAD-II | 92.121
24 | NR140027 | 400KV BAREILLY-MBAD-II | 92.121 | NR140070 | 400KV LUCKNOW-GORAKH-III | 6294:14 | SHAHJAHANPUR-BAREILLY-I | 116.917
25 | NR340010 | 400KV BAREILLY-SHAHJHNPR-I | 116.917 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 6294:14 | SHAHJAHANPUR-BAREILLY-II | 116.917
26 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.917 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 68:41 | B'GARH-M'PURI-I | 235.952
27 | NR140158 | 400KV BARLY(765)-KASHIPUR-I | 100.659 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 68:41 | B'GARH-M'PURI-II
28 | NR140159 | 400KV BARLY(765)-KASHIPUR-II | 100.659 | NR140072 | 400KV LUCKNOW-LKO(UP) | 1518:29 | FATEHPUR-MAINPURI-I | 260.051
29 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR140114 | 400KV LUCKNOW-ROSA-I | 4248:00 | FATEHPUR-MAINPURI-II
30 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 2359:09 | GORAKH-GORAKH-I | 45.941
31 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 2359:09 | GORAKH-GORAKH-II
32 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR140073 | 400KV LUCKNOW-SULTANPR | 3926:24 |  | 240
33 | NR140046 | 400KV GORAKH-GORAKH-I | 45.941 | NR140074 | 400KV LUCKNOW-UNNAO-I | 1771:49 | KANPUR-AURAIYA-I | 0
34 | NR140047 | 400KV GORAKH-GORAKH-II | 45.941 | NR140075 | 400KV LUCKNOW-UNNAO-II | 1771:49 | KANPUR-AURAIYA-II
35 | NR140052 | 400KV KNP-AGRA | 240 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 747:48 | KNP-B'GARH-I | 385.69
36 | NR140053 | 400KV KNP-AURAIYA-I | 73.1212 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 747:48 | KNP-B'GARH-II | 370.772
37 | NR140054 | 400KV KNP-AURAIYA-II | 73.1212 | NR140084 | 400KV RIHAND-ALLD-I | 6685:47 | KNP-B'GARH-III
38 | NR140055 | 400KV KNP-BLBGARH-I | 385.7 | NR140085 | 400KV RIHAND-ALLD-II | 6685:47 | KNP-FATEHPUR-II | 107.1
39 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR140088 | 400KV VARANASI-BIHARSHRF-I | 3420:00 | KNP-FATEHPUR-I | 107.079
40 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR140089 | 400KV VARANASI-BIHARSHRF-II | 3420:00 | KNP-PANKI-I | 5.924
41 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR140090 | 400KV SASARAM-VARANASI | 1140:29 | KNP-PANKI-II | 5.863
42 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR140091 | 400KV SING-ALLD-I | 5422:28 | KASHIPUR-BAREILLY-I | 100.659
43 | NR140058 | 400KV KNP-PANKI-I | 5.9 | NR140092 | 400KV SING-ALLD-II | 4829:02 | KASHIPUR-BAREILLY-II
44 | NR140059 | 400KV KNP-PANKI-II | 5.9 | NR140093 | 400KV SING-ANPARA | 724:38 | KANPUR(400)-KANPUR(765)-I | 21.32
45 | NR140070 | 400KV LUCKNOW-GORAKH-III | 262.26 | NR140111 | 400KV SING-FATEHPUR | 7942:52 | KANPUR(400)-KANPUR(765)-II
46 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 262.26 | NR140095 | 400KV SING-LKO(UP) | 7920:00 | LUCKNOW-GORAKHPUR-III | 263.933
47 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.862 | NR140096 | 400KV SING-RIHAND-I | 1008:00 | LUCKNOW-GORAKHPUR-IV
48 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.862 | NR140097 | 400KV SING-RIHAND-II | 1008:00 | LUCKNOW(765)-LUCKNOW(400)-I | 2.862
49 | NR140072 | 400KV LUCKNOW-LKO(UP) | 63.27 | N-W40001 | 400KV SING-VINDH-I | 80:11 | LUCKNOW(765)-LUCKNOW(400)-II
50 | NR140114 | 400KV LUCKNOW-ROSA-I | 177 | N-W40002 | 400KV SING-VINDH-II | 40:05 | LUCKNOW-LUCKNOW (UP) | 63.27
51 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR140164 | 400KV VARANASI-SARNATH-I | 1289:31 | LUCKNOW-SULTANPUR | 163.6
52 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.298 | NR140165 | 400KV VARANASI-SARNATH-II | 1289:31 | LUCKNOW-SHAHJHNPR-I | 169.729
53 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.298 |  |  |  | LUCKNOW-SHAHJHNPR-II
54 | NR140073 | 400KV LUCKNOW-SULTANPR | 163.6 |  | 220 KV TRANS LINES |  | LUCKNOW-SOHAWAL-I | 98.281
55 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | LUCKNOW-SOHAWAL-II
56 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 405:27 | LUCKNOW-UNNAO-I | 73.826
57 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 31.158 | BILUP2202 | 220KV ALLD-REWA RD-I | 71:02 | LUCKNOW-UNNAO-II
58 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.158 | BILUP2203 | 220KV ALLD-REWA RD-II | 71:02 | RIHAND-ALLD-I | 279.245
59 | NR140084 | 400KV RIHAND-ALLD-I | 278.574 | NR122006 | 220KV AUR-SIKANDARA-I | 4380:46 | RIHAND-ALLD-II
60 | NR140085 | 400KV RIHAND-ALLD-II | 278.574 | NR122007 | 220KV AUR-SIKANDARA-II | 4380:46 | RIHAND-VINDHYACHAL Pooling-I | 31.158
61 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 142.5 | NR122012 | 220KV DGANGA-BLY(UP)-II | 5630:10 | RIHAND-VINDHYACHAL Pooling-II
62 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 142.5 | NR122013 | 220KV DGANGA-PITHORAGRH | 1416:14 | SING-ALLD-I | 224
63 | NR140091 | 400KV SING-ALLD-I | 225.936 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 148:05 | SING-ALLD-II | 202
64 | NR140092 | 400KV SING-ALLD-II | 201.21 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 148:05 | SING-ANPARA | 25.057
65 | NR140093 | 400KV SING-ANPARA | 30.193 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 126:52 | SING-FATEHPUR | 330.953
66 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR122041 | 220KV FATEHPUR-NAUBASTA | 126:52 | SING-LUCKNOW(UP) | 408.6
67 | NR140095 | 400KV SING-LKO(UP)-I | 330 | NR122016 | 220KV KNP-MAINPURI | 3624:00 | SING-RIHAND-I | 42.026
68 | NR140096 | 400KV SING-RIHAND-I | 42 | NR122017 | 220KV KNP-NAUBASTA | 463:41 | SING-RIHAND-II
69 | NR140097 | 400KV SING-RIHAND-II | 42 | NR122018 | 220KV KNP-PANKI-I | 374:24 | SING-VINDH-I | 3.341
70 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR122019 | 220KV KNP-PANKI-II | 572:38 | SING-VINDH-II
71 | N-W40002 | 400KV SING-VINDH-II | 1.67 | NR122020 | 220KV KNP-UNCHR-I | 3445:16 | HVDC Feeder I | 1.25
72 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.32 | NR122021 | 220KV KNP-UNCHR-II | 3445:16 | HVDC Feeder I
73 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.32 | NR122022 | 220KV KNP-UNCHR-III | 3471:07 | HVDC Feeder II | 1.25
74 | NR340003 | 400KV VARANASI-SASARAM(ER) | 139.482 | NR122023 | 220KV KNP-UNCHR-IV | 3471:07 | HVDC Feeder II
75 | NR340004 | 400KV VARANASI-SARNATH-I | 106.7 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | VINDHYACHAL POOLING-SASAN | 6.02
76 | NR340005 | 400KV VARANASI-SARNATH-II | 106.7 | NR122025 | 220KV RAIBRLY-CHINHAT |  | BIHARSHARIF-VARANASI-I | 285
77 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 43.013 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1026:03 | BIHARSHARIF-VARANASI-II
78 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 43.013 | NR122032 | 220KV SITARGANJ-BLY(UP) | 2534:47 | VARANASI-SARNATH-I | 106.7
79 | NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR122033 | 220KV TNKPR-BLY(UP) | 2544:00 | VARANASI-SARNATH-II | 106.7
80 | NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR122034 | 220KV TNKPR-SITARGANJ | 1026:03 | SASARAM-ALLAHABAD | 213.729
81 | NR140142 | 400KV MEERUT-BAREILLY-I | 249.52 | NR122035 | 220KV UNCHR-RAIBRLY-I | 1025:02 | SASARAM-VARANASI | 139.482
82 | NR140130 | 400KV MEERUT-BAREILLY-II | 249.52 | NR122036 | 220KV UNCHR-RAIBRLY-II | 1025:02 | VARANASI-ALLAHABAD | 98.791
83 | NR340011 | 400KV LUCKNOW-SHAHJHNPR-I | 159.7 | NR122037 | 220KV UNCHR-RAIBRLY-III | 1048:48 | BARH-GORAKHPUR-I | 353
84 | NR340012 | 400KV Lucknow(765)-Kanpur(GIS)-I | 159.7 |  | 220 KV KNP(400KV)-RANIA(UP) | 18.372 | BARH-GORAKHPUR-II
85 | NR340013 | 400KV Lucknow(765)-Kanpur(GIS)-II |  |  | 220 KV RANIA(UP)-PANKI(UP) | 30.39 | BIHARSHARIF-BALIA-I | 242
86 | NR340014 | 400KV Kanpur(GIS)-Allahabad-I |  |  | 132 KV TRANS LINES |  | BIHARSHARIF-BALIA-I
87 | NR340015 | 400KV Kanpur(GIS)-Allahabad-II |  | BILUP13201 | 132KV MAU-BALIA | 57.825 | ALLAHABAD-MEJA-I | 28.19
88 | NR340016 | 400KV ORAI-ORAI(UP)-I |  |  | 132 KV Tankpur - Mahendranagar | 3.06 | ALLAHABAD-MEJA-II
89 | NR340017 | 400KV ORAI-ORAI(UP)-II |  |  |  |  | UCHAHAR-FATEHPUR-I | 53.7
90 | NR140019 | 400KV BALIA-MAU-I | 9.215 |  | 220KV ALLD-JHUSI(UP) | 21.879 | UCHAHAR-FATEHPUR-II
91 | NR140020 | 400KV BALIA-MAU-II | 9.215 |  | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | PATNA-BALIA-I | 195
92 | NR140021 | 400KV BALIA-PATNA-I | 195.232 |  | 220KV ALLD-REWA RD-I&II | 2.96 | PATNA-BALIA-II
93 | NR140022 | 400KV BALIA-PATNA-II | 195.232 |  | 220KV ALLD-REWA RD-II |  | PATNA-BALIA-III | 185
94 | NR140136 | 400KV BALIA-PATNA-III | 185 |  | 220KV AURAIYA-SIKANDARA-I | 182.532 | PATNA-BALIA-IV
95 | NR140137 | 400KV BALIA-PATNA-IV | 185 |  | 220KV AURAIYA-SIKANDARA-II |  | LUCKNOW-KANPUR-I | 159.7
[5 empty] | 220KV D'GANGA-BRLY(UP)-II | 234.59 | LUCKNOW-KANPUR-II
[5 empty] | 220KV D'GANGA-PITHORAGRH | 59.01 | ALLAHABAD-KANPUR(GIS)-I | 240.39
[5 empty] | 220KV PITHORAGRH-BRLY(UP)-I | 177.88 | ALLAHABAD-KANPUR(GIS)-II
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-I | 6.169 | Total 105 400KV Lines | 10198.266
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-II | 6.169 | HVDC R-D POLE-I | 815
[5 empty] | 220KV FATEHPUR-KNP SOUTH | 5.286 | HVDC R-D POLE-II
[5 empty] | 220KV FATEHPUR-NAUBASTA | 5.286 | HVDC B-B POLE-I | 789.786
[5 empty] | 220KV KNP-MAINPURI | 151 | HVDC B-B POLE-II
[5 empty] | 220KV KNP-RANIA(UP) | 18.372 | BNC-AGRA POLE-I | 1734
[5 empty] | 220KV RANIA(UP)-PANKI(UP) | 30.39 | BNC-AGRA POLE-II
[5 empty] | 220KV KNP-NAUBASTA | 19.32 | CHAMPA-KURUKSHETRA-I | 1305
[5 empty] | 220KV KNP-PANKI-II | 23.86 | CHAMPA-KURUKSHETRA-II
[5 empty] | 220KV KNP-UNCHAHAR-I | 143.553
220KV KNP-UNCHAHAR-II
[5 empty] | 220KV KNP-UNCHAHAR-III | 144.63
220KV KNP-UNCHAHAR-IV
C |  | 220 KV TRANS LINES |  |  | 220KV SITARGANJ-BLY(UP) | 105.72
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 |  | 220KV TNKPR-BLY(UP) | 106
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 |  | 220KV TNKPR-SITARGANJ | 42.55
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 2.96 |  | 220KV RBRLY-CHINHAT | 93.61
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 2.96 |  | 220KV UNCHR-RBRLY-I | 42.71
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.532 |  | 220KV RBRLY-LKO(UP) | 1.19
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.532 |  | 220KV UNCHR-RBRLY-II | 42.71
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 |  | 220KV UNCHR-RBRLY-III | 43.7
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 |  | TOTAL 30 Lines
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 6.17 |  | 132KV LINES
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 6.17 |  | 132KV MAU-BALIA | 57.825
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 5.286 |  | 132KV TNKPR-MHNDRNGR | 3.06
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 5.286
13 | NR122016 | 220KV KNP-MAINPURI | 151
14 | NR122017 | 220KV KNP-NAUBASTA | 19.32
15 | NR122019 | 220KV KNP-PANKI-II | 23.86
16 | NR122020 | 220KV KNP-UNCHR-I | 143.553
17 | NR122021 | 220KV KNP-UNCHR-II | 143.553
18 | NR122022 | 220KV KNP-UNCHR-III | 144.63
19 | NR122023 | 220KV KNP-UNCHR-IV | 144.63
20 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88
21 | NR122025 | 220KV RAIBRLY-CHINHAT | 93.61
22 | NR122026 | 220KV RAIBRLY-LKO(UP) | 42.752
23 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.616
24 | NR122033 | 220KV TNKPR-BLY(UP) | 106
25 | NR122034 | 220KV TNKPR-SITARGANJ | 42.752
26 | NR122035 | 220KV UNCHR-RAIBRLY-I | 42.71
27 | NR122036 | 220KV UNCHR-RAIBRLY-II | 42.71
28 | NR122037 | 220KV UNCHR-RAIBRLY-III | 43.7
29 | NR320001 | 220 KV KANPUR(PG) - RANIYA( UP) | 18.372
30 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP) | 30.39
31 | NR320003 | 220KV RAIBRLY-CG CITY(UP)
32 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP)
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA | 57.825
| Lines | TOTAL FOR T/LS
142 |  | OVERALL SYSTEM AVAILABILITY=
E |  | 765/400 KV ICT'S
1 | NR1ICT707 | 765/400KV ICT-I AGRA
2 | NR1ICT708 | 765/400KV ICT-II AGRA
3 | NR1ICT701 | 765/400KV ICT-I BALIA
4 | NR1ICT702 | 765/400KV ICT-II BALIA
5 | NR1ICT715 | 765/400KV ICT-I BAREILLY
6 | NR1ICT716 | 765/400KV ICT-II BAREILLY
7 | NR1ICT705 | 765/400KV ICT-I FATEHPUR
8 | NR1ICT706 | 765/400KV ICT-II FATEHPUR
9 | NR1ICT703 | 765/400KV ICT-I LUCKNOW
10 | NR1ICT704 | 765/400KV ICT-II LUCKNOW
11 | NR1ICT717 | 765/400KV ICT-I VARANASI
12 | NR1ICT718 | 765/400KV ICT-II VARANASI
13 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS)
14 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS)
| NR3ICT703 | 1000MVA ICT-I ORAI(GIS)
| NR3ICT704 | 1000MVA ICT-II ORAI(GIS)
815
F |  | 400/220 KV ICT'S
1 | NR1ICT70 | 315MVA ICT-I AGRA
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 815
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 789.786
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 789.786
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 1734
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 1734
10 | NR1ICT20 | 315MVA ICT-II KANPUR
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW
13 | NR1ICT26 | 315MVA ICT-I MAINPURI
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 0
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 0
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL
| NR3ICT01 | 315MVA ICT-2 at Agra
| NR3ICT02 | 500MVA ICT-3 at Mainpuri
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 100MVA ICT-I PITHORAGRH
2 | NR1ICT44 | 100MVA ICT-II PITHORAGRH
3 | NR1ICT47 | 100MVA ICT-I RAIBAREILLY
4 | NR1ICT38 | 100MVA ICT-II RAIBAREILLY
5 | NR1ICT39 | 200MVA ICT-III RAIBAREILLY
6 | NR1ICT40 | 100MVA ICT-I SITARGANJ
7 | NR1ICT41 | 100MVA ICT-II SITARGANJ
| NR3ICT03 | 200MVA ICT-3 at Raibareilly
| NR3ICT04 | 200MVA ICT-2 at Raibareilly
TOTAL FOR ICTs
39 |  | HVDC RIHAND-DADRI
H | NR1DCP01 | 500KV HVDC R-D POLE-I
1 | NR1DCP02 | 500KV HVDC R-D POLE-II
2 | NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I
3 | NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II
4 |  | TOTAL FOR HVDC line
HVDC AGRA-BNC
J | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I
1 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II
| NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III
| NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV
2 |  | TOTAL of HVDC POLE-I
HVDC BTB VINDHYACHAL
K | NR1DCB01 | VINDH HVDC B/B BLOCK-I
1 | NR1DCB02 | VINDH HVDC B/B BLOCK-II
2 |  | TOTAL FOR HVDC VINDHYACHAL
HVDC BTB SASARAM
L | NEDCB01 | +/-500MW HVDC B/B SASARAM
1 |  | TOTAL FOR HVDC SASARAM
SVC, KANPUR
M | NR1SVC01 | +/-140MVAR SVC-I KANPUR
1 | NR1SVC02 | +/-140MVAR SVC-II KANPUR
2 |  | TOTAL FOR SVC
N |  | Bus & Switch Line Reactor
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA
3 | NR1BRT36 | 240MVAR B/Reactor-I AGRA-765
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD
6 | NR1BRT33 | 125MVAR B/Reactor-II ALLAHABAD
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY
14 | NR1BRT44 | 2x50MVAR B/Reactor BAREILLY
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR
20 | NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI
28 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR
29 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W
30 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N
31 | NR1BRT42 | 125MVAR B/Reactor-I VINDH
32 | NR1BRT43 | 125MVAR B/Reactor-II VINDH
33 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI
34 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI
35 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I
36 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line
37 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I
38 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II
39 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line
40 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 393.9
41 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 393.9
42 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 213.729
43 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 285
44 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 285
45 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 238
46 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 263.94
47 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 139.482
48 | NR1SRT24 | GORAKH 80MVAR S/R Barh-I line
49 | NR1SRT25 | GORAKH 80MVAR S/R Barh-II line
50 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE
51 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE
52 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I
53 | NR1SRT26 | LUCKNW 240MVAR S/R Bareilly Line
54 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS)
55 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS)
56 | NR3SRT01 | VARANASI 240MVAR S/R KNP(GIS)-1
57 | NR3SRT02 | VARANASI 240MVAR S/R KNP(GIS)-2
58 | NR3SRT03 | KNP(GIS) 330MVAR S/R JHATIKRA-1
59 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS)
60 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI
61 | NR3BRT05 | 125MVAR B/Reactor-I KANPUR
62 | NR3BRT06 | 330MVAR B/Reactor-III VARANASI-765
63 | NR3BRT08 | 330MVAR Bus Reactor-II AT ALIGARH GIS |  |  | 400KV AGRA-SIKAR-I
64 | NR3SLRT06 | ALIGARH 330MVAR Switachable Line Reactor KANPUR LINE |  |  | 400KV AGRA-SIKAR-II
65 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH |  |  | 400KV ALLAHABAD-SASARAM
66 | NR3LRT07 | ORAI 240MVAR Non Switchable Line Reactor ALIGARH-II LINE |  |  | 400KV VARANASI-BIHARSHRF-I
67 | NR3LRT08 | ALIGARH 240MVAR Non Switchable Line Reactor ORAI-II LINE |  |  | 400KV VARANASI-BIHARSHRF-II
68 | NR3BRT10 | 330MVAR Bus Reactor-I ORAI |  |  | 765KV BALIA-GAYA
69 | NR3LRT09 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-I LINE |  |  | 765KV VARANASI-GAYA
70 | NR3LRT10 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-II LINE |  |  | 400KV SASARAM-VARANASI
71 | NR3BRT11 | 330MVAR Bus Reactor-II ORAI |  |  | 400KV MOTIHARI-GRKHPR-I
72 | NR3LRT11 | ORAI 240MVAR Non-Switchable Line Reactor SATNA LINE |  |  | 400KV MOTIHARI-GRKHPR-II
73 | NR3LRT12 | ORAI 240MVAR Non-Switchable Line Reactor ALIGARH-I LINE
74 | NR3LRT13 | ALIGARH 240MVAR Non-Switchable Line Reactor ORAI-I LINE
75 | NR3BRT07 | 63MVAR B/Reactor-I SOHAWAL
Note on C7: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C12: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C13: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C17: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C18: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C19: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C20: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C37: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16
Note on C76: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on F76: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on F77: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C102: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C103: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C279: DOC-26/05/2014
Note on F325: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet5
220KV ALLD-JHUSI(UP)
220KV JHUSI(UP)-PHULPUR(UP)
220KV ALLD-REWA RD-I
220KV ALLD-REWA RD-II
220KV AUR-SIKANDARA-I
220KV AUR-SIKANDARA-II
220KV DGANGA-BLY(UP)-II
220KV DGANGA-PITHORAGRH
220KV FATEHPUR-FTHPR(UP)-I
220KV FATEHPUR-FTHPR(UP)-II
220KV FATEHPUR-KNP SOUTH
220KV FATEHPUR-NAUBASTA
220KV KNP-MAINPURI
220KV KNP-NAUBASTA
220KV KNP-PANKI-I
220KV KNP-PANKI-II
220KV KNP-UNCHR-I
220KV KNP-UNCHR-II
220KV KNP-UNCHR-III
220KV KNP-UNCHR-IV
220KV PITHORAGRH-BRLY(UP)
220KV RAIBRLY-CHINHAT
220KV RAIBRLY-LKO(UP)
220KV SITARGANJ-BLY(UP)
220KV TNKPR-BLY(UP)
220KV TNKPR-SITARGANJ
220KV UNCHR-RAIBRLY-I
220KV UNCHR-RAIBRLY-II
220KV UNCHR-RAIBRLY-III
220KV KNP-RANIA
132 KV TRANS LINES
Note on A31: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Sheet2 (hidden)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
125MVAR B/Reactor-1 Mainpuri | 2017-05-27 22:42 | 2017-05-28 06:46 | 0 | 0 | 0 | 0.33611 | N-2790 | SVRD | H-T for voltage regulation as per NRLDC instruction. Mainpuri=386KV
125MVAR B/Reactor-I GORAKHPUR | 2017-05-22 21:55 | 2017-06-01 | 0 | 0 | 0 | 1900-01-08 02:05 | N-2235 | SVRD | H-T for voltage regulation as per NRLDC instruction. Gorakhpur=393KV
125MVAR B/Reactor-III KANPUR(GIS) | 2017-05-25 23:46 | 2017-05-26 06:58 | 0 | 0 | 0 | 0.3 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. Kanpur=395KV
240MVAR B/Reactor-I BALIA-765 | 2017-05-13 21:25 | 2017-05-27 01:23 | 0 | 0 | 0 | 1900-01-12 03:58 | N-1003 | SVRD | H-T for voltage regulation as per NRLDC instruction. Ballia=744KV
240MVAR B/Reactor-I BAREILLY-765 | 2017-05-25 09:56 | 2017-05-28 05:20 | 0 | 0 | 0 | 1900-01-01 19:24 | N-2455 | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-13 21:24 | 2017-05-14 06:52 | 0 | 0 | 0 | 0.39444 | N-1002 | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-16 20:01 | 2017-05-17 07:40 | 0 | 0 | 0 | 0.48542 | N-1534 | SVRD | H-T for voltage regulation as per NRLDC instruction. Lucknow=749KV
330MVAR B/Reactor-II VARANASI | 2017-05-19 15:05 | 2017-05-19 22:00 | 0 | 0 | 0 | 0.28819 | N-1850 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=751KV
330MVAR B/Reactor-II VARANASI | 2017-05-22 21:34 | 2017-05-24 06:25 | 0 | 0 | 0 | 1899-12-31 08:51 | N-2234 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=761KV
80MVAR B/Reactor BAREILLY | 2017-05-25 23:41 | 2017-05-26 07:02 | 0 | 0 | 0 | 0.30625 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=395KV
80MVAR B/Reactor LUCKNOW | 2017-05-25 23:35 | 2017-05-26 06:53 | 0 | 0 | 0 | 0.30417 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=396KV
Note on A9: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1
Note on A10: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1