## Sheet3 (hidden)
400kv LINES |  |  |  | 220kv LINES |  | ICTs,HVDC & SVC. |  | OTHER LINES
400kv LINES NR-I |  | 400kv LINES NR-III |  | 220kv LINES & ICT & Reactor NR-I |  | 220kv LINES & ICT & Reactor NR-III
400KV AGRA-JAIPUR(S)-I | 1 | 400KV AGRA-FATEHABD(UP)-I | 1 | 220KV ANTA-BHIL-I | 1 | 220KV ALLD-JHUSI(UP) | RRVPNL | 220KV BASSI-KUKAS-I
400KV AGRA-JAIPUR(S)-II | 2 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2 | 220KV ANTA-BHIL-II | 2 | 220KV ALLD-REWA RD-I | RRVPNL | 220KV BASSI-KUNDA KI DHANI
400KV AGRA-SIKAR-I | 3 | 400KV AGRA-AGRA(UP)-II | 3 | 220KV ANTA-LALSOT | 3 | 220KV ALLD-REWA RD-II | RRVPNL | 220KV BHIWADI(PG)-BHIWADI
400KV AGRA-SIKAR-II | 4 | 400KV AGRA-AURAIYA-I | 4 | 220KV ANTA-RAPPC | 4 | 220KV AUR-SIKANDARA-I | RRVPNL | 220KV BHIWADI-KHUSHKHERA-I
400KV BASSI-BHIWADI-I | 5 | 400KV AGRA-AURAIYA-II | 5 | 220KV ANTA-S.MDHPR | 5 | 220KV AUR-SIKANDARA-II | RRVPNL | 220KV BHIWADI-KHUSHKHERA-II
400KV BASSI-HIRAPURA-I | 6 | 400KV AGRA-BASSI-I | 6 | 220KV BASSI-BAGRU | 6 | 220KV DGANGA-BLY(UP)-II | RRVPNL | 220KV BHIWADI-NIMRANA(RJ)
400KV BASSI-HIRAPURA-II | 7 | 400KV AGRA-BHIWADI-I | 7 | 220KV BASSI-DAUSA-I | 7 | 220KV DGANGA-PITHORAGRH | RRVPNL | 220KV BHINMAL-BHINMAL-I
400KV BASSI-JAIPUR(S)-I | 8 | 400KV AGRA-BHIWADI-II | 8 | 220KV BASSI-DAUSA-II | 8 | 220KV FATEHPUR-FTHPR(UP)-I | RRVPNL | 220KV BHINMAL-BHINMAL-II
400KV BASSI-JAIPUR(S)-II | 9 | 400KV AGRA-BLBGRH | 9 | 220KV BASSI-IG NAGAR | 9 | 220KV FATEHPUR-FTHPR(UP)-II | RRVPNL | 220KV BHINMAL-SANCHORE
400KV BASSI-KOTPUTLI | 10 | 400KV ALLD-FATEHPUR-I | 10 | 220KV FGPP-PALLA-I | 10 | 220KV FATEHPUR-KNP SOUTH | RRVPNL | 220KV BHINMAL-SIROHI
400KV BASSI-PHAGI-I | 11 | 400KV ALLD-FATEHPUR-II | 11 | 220KV FGPP-PALLA-II | 11 | 220KV FATEHPUR-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-CHAKSU-I |  | LEGENDS
400KV BASSI-PHAGI-II | 12 | 400KV ALLD-FATEHPUR-III | 12 | 220KV FGPP-SPUR-I | 12 | 220KV JHUSI(UP)-PHULPUR(UP) | RRVPNL | 220KV JAIPUR(S)-CHAKSU-II
400KV BHINMAL-ZERDA | 13 | 400KV ALLD-KNP-II | 13 | 220KV FGPP-SPUR-II | 13 | 220KV KNP-MAINPURI | RRVPNL | 220KV JAIPUR(S)-SEZ |  |  | Lines maintained by ER
400KV BHIWADI-GURGAON | 14 | 400KV ALLD-VARANASI | 14 | 220KV HIRAPURA-IG NAGAR | 14 | 220KV KNP-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-DOONI
400KV BHIWADI-HISAR-I | 15 | 400KV BALIA-MAU-I | 15 | 220KV HIRAPURA-SANGANER | 15 | 220 KV KANPUR(PG) - RANIYA( UP)-1 | RRVPNL | 220KV KANKROLI(PG)-BHILWARA
400KV BHIWADI-KOTPUTLI | 16 | 400KV BALIA-MAU-II | 16 | 220KV LALSOT-DAUSA | 16 | 220 KV RANIYA( UP) - PANKI (UP)-1 | RRVPNL | 220KV KANKROLI(PG)-KANK-I
400KV BHIWADI-NIMRANA-I | 17 | 400KV BALIA-SOHAWAL-I | 17 | 220KV MEERUT-MPURAM-I | 17 | 220KV KNP-PANKI-II | RRVPNL | 220KV KANKROLI(PG)-KANK-II
400KV BHIWADI-NIMRANA-II | 18 | 400KV BALIA-SOHAWAL-II | 18 | 220KV MEERUT-MPURAM-II | 18 | 220KV KNP-UNCHR-I | RRVPNL | 220KV KANKROLI-DEBARI |  |  | lines maintained by WR
400KV BLBGRH-GURGAON | 19 | 400KV BAREILLY-BRLY(765)-I | 19 | 220KV MEERUT-NARA | 19 | 220KV KNP-UNCHR-II | RRVPNL | 220KV KOTA-KTPS-1
400KV BLBGRH-MAHRANIBG | 20 | 400KV BAREILLY-BRLY(765)-II | 20 | 220KV MEERUT-SHTBDNGR | 20 | 220KV KNP-UNCHR-III | RRVPNL | 220KV KOTA-KTPS-2 |  |  | LILO portions only of POWERGRID
400KV BLBGRH-NAVADA(HVPN) | 21 | 400KV BAREILLY-BRLY(UP)-I | 21 | 220KV MEERUT-SIMBHOLI | 21 | 220KV KNP-UNCHR-IV | RRVPNL | 220KV KOTA-BHILWARA
400KV DAD-GR.NOIDA | 22 | 400KV BAREILLY-BRLY(UP)-II | 22 | 220KV RAPPB-CHITT-I | 22 | 220KV PITHORAGRH-BRLY(UP) | RRVPNL | 220KV KOTA-DHUNI |  |  | LILO portion maintained by constituents
400KV DAD-MAHRANIBG | 23 | 400KV BAREILLY-LKO(UP) | 23 | 220KV RAPPB-CHITT-II | 23 | 220KV RAIBRLY-CHINHAT | RRVPNL | 220KV KOTPUTLI-KOTPUTLI
400KV DAD-MANDOLA-I | 24 | 400KV BAREILLY-MBAD-I | 24 | 220KV RAPPB-RAPPC | 24 | 220KV RAIBRLY-LKO(UP) | RRVPNL | 220KV KOTPUTLI-MANOHARPUR
400KV DAD-MANDOLA-II | 25 | 400KV BAREILLY-MBAD-II | 25 | 220KV RAPPB-UDAIPUR | 25 | 220KV SITARGANJ-BLY(UP) | RRVPNL | 220KV NIMRANA-NIMRANA
400KV DAD-MURADNGR | 26 | 400KV BAREILLY-ROSA-I | 26 | 220KV S.MDHPR-DAUSA-I | 26 | 220KV TNKPR-BLY(UP) | RRVPNL | 220KV NIMRANA-KHUSHKHERA |  |  | Maintained by NR-1 & NR-II
400KV DAD-PANIPAT-I | 27 | 400KV BAREILLY-SHAHJHNPR-I | 27 | 220KV SIKAR-RATANGARH-I | 27 | 220KV TNKPR-SITARGANJ | HVPNL | 220KV BHIWADI-MAU
400KV DAD-PANIPAT-II | 28 | 400KV BAREILLY-SHAHJHNPR-II | 28 | 220KV SIKAR-RATANGARH-II | 28 | 220KV UNCHR-RAIBRLY-I | HVPNL | 220KV BHIWADI-REWARI-I
400KV GURGAON-MANESAR-I | 29 | 400KV BARLY(765)-KASHIPUR-I | 29 | 220KV SIKAR-SIKAR(RJ)-I | 29 | 220KV UNCHR-RAIBRLY-II | HVPNL | 220KV BHIWADI-REWARI-II
400KV GURGAON-MANESAR-II | 30 | 400KV BARLY(765)-KASHIPUR-II | 30 | 220KV SIKAR-SIKAR(RJ)-II | 30 | 220KV UNCHR-RAIBRLY-III | HVPNL | 220KV BHIWADI-BAWAL
400KV JHATIKALA-BAMNOLI-I | 31 | 400KV BLBGRH-MAINPURI-I | 31 | 220KV HISAR-HISAR I/A-I |  |  | HVPNL | 220KV GURGAON-GURGAON-I
400KV JHATIKALA-BAMNOLI-II | 32 | 400KV BLBGRH-MAINPURI-II | 32 | 220KV HISAR-HISAR I/A-II |  |  | HVPNL | 220KV GURGAON-GURGAON-II
400KV JHATIKALA-MUNDKA-I | 33 | 400KV FATEHPUR-MAINPURI-I |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-III
400KV JHATIKALA-MUNDKA-II | 34 | 400KV FATEHPUR-MAINPURI-II |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-IV
400KV KANKROLI-BHINMAL | 35 | 400KV GORAKH-GORAKH-I |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-I
400KV KANKROLI-JODHPUR | 36 | 400KV GORAKH-GORAKH-II |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-II
400KV KANKROLI-CHITTOR(RJ)-I | 37 | 400KV KNP-AGRA |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-I
400KV KANKROLI-RAPPC-II | 38 | 400KV KNP-AURAIYA-I |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-II
400KV KANKROLI-ZERDA-I | 39 | 400KV KNP-AURAIYA-II |  | 400KV & 220KV ICT NR-I |  |  | HVPNL | 220 KV MANESAR-BADSHAHPUR-I
400KV KOTA-BEAWAR | 40 | 400KV KNP-BLBGARH-I | 1 | 315MVA ICT-I BASSI |  | 400KV & 220KV ICT NR-III | HVPNL | 220 KV MANESAR-BADSHAHPUR-II
400KV KOTA-MERTA-I | 41 | 400KV KNP-BLBGARH-II | 2 | 315MVA ICT-II BASSI | 1 | 315MVA ICT-I AGRA | HVPNL | 220 KV MANESAR-MAU-I
400KV KOTA-RAPPC | 42 | 400KV KNP-BLBGARH-III | 3 | 500MVA ICT-III BASSI | 2 | 315MVA ICT-I ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-II
400KV KOTESHWR-KHEP-I | 43 | 400KV KNP-FATEHPUR-I | 4 | 315MVA ICT-III BAWANA | 3 | 315MVA ICT-II ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-III
400KV KOTESHWR-KHEP-II | 44 | 400KV KNP-FATEHPUR-II | 5 | 315MVA ICT-I BHINMAL | 4 | 315MVA ICT-III ALLAHABAD | HVPNL | 220 KV SONIPAT-MOHANA-I
400KV KOTESHWR-TEHRI-I | 45 | 400KV KNP-PANKI-I | 6 | 315MVA ICT-II BHINMAL | 5 | 315MVA ICT-I FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-I
400KV KOTESHWR-TEHRI-II | 46 | 400KV KNP-PANKI-II | 7 | 315MVA ICT-I BHIWADI | 6 | 315MVA ICT-II FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-II
400KV MBAD-MURADNGR | 47 | 400KV LUCKNOW-GORAKH-III | 8 | 315MVA ICT-II BHIWADI | 7 | 315MVA ICT-I GORAKHPR | HVPNL | 220KV HISAR-SRWL-I
400KV MEERUT-BAGPAT-I | 48 | 400KV LUCKNOW-GORAKH-IV | 9 | 315MVA ICT-III BHIWADI | 8 | 315MVA ICT-II GORAKHPR | HVPNL | 220KV HISAR-SRWL-II
400KV MEERUT-BAREILLY-I | 49 | 400KV LUCKNOW-LKO(765)-I | 10 | 500MVA ICT-I BLBGARH | 9 | 315MVA ICT-I KANPUR | HVPNL | 220KV HISAR-FATEHABAD-I
400KV MEERUT-BAREILLY-II | 50 | 400KV LUCKNOW-LKO(765)-II | 11 | 315MVA ICT-II BLBGARH | 10 | 315MVA ICT-II KANPUR | HVPNL | 220KV HISAR-FATEHABAD-II
400KV MEERUT-KOTESHWR-I | 51 | 400KV LUCKNOW-LKO(UP) | 12 | 315MVA ICT-III BLBGARH | 11 | 315MVA ICT-I LUCKNOW | NTPC | 132KV SING-VINDH-RIH
400KV MEERUT-KOTESHWR-II | 52 | 400KV LUCKNOW-ROSA-I | 13 | 315MVA ICT-IV BLBGARH | 12 | 500MVA ICT-II LUCKNOW | NTPC | 132KV SING-RENUSAGAR-PIPRI
400KV MEERUT-MND-I | 53 | 400KV LUCKNOW-SHAHJHNPR-I | 14 | 315MVA ICT-I GURGAON | 13 | 315MVA ICT-I MAINPURI | DTL | 400KV B'GARH-BAMNOLI-I
400KV MEERUT-MND-II | 54 | 400KV LUCKNOW-SHAHJHNPR-II | 15 | 315MVA ICT-II GURGAON | 14 | 315MVA ICT-II MAINPURI | DTL | 400KV B'GARH-BAMNOLI-II
400KV MEERUT-MND-III | 55 | 400KV LUCKNOW-SOHAWAL-I | 16 | 500MVA ICT-I JAIPUR(S) | 15 | 100MVA ICT-I PITHORAGRH | DTL | 400KV MND-BAWANA-I
400KV MEERUT-MND-IV | 56 | 400KV LUCKNOW-SOHAWAL-II | 17 | 500MVA ICT-II JAIPUR(S) | 16 | 100MVA ICT-II PITHORAGRH | DTL | 400KV MND-BAWANA-II
400KV MEERUT-MUZFRNGR | 57 | 400KV LUCKNOW-SULTANPR | 18 | 315MVA ICT-I KANKROLI | 17 | 100MVA ICT-I RAIBAREILLY | DTL | 220KV MND-S.WZRBD-I
400KV MERTA-BEAWAR | 58 | 400KV LUCKNOW-UNNAO-I | 19 | 315MVA ICT-II KANKROLI | 18 | 100MVA ICT-II RAIBAREILLY | DTL | 220KV MND-S.WZRBD-II
400KV NAVADA(HVPN)-GR.NOIDA | 59 | 400KV LUCKNOW-UNNAO-II | 20 | 315MVA ICT-III KANKROLI | 19 | 100MVA ICT-III RAIBAREILLY | DTL | 220KV MND-S.WZRBD-III
400KV NIMRANA-MANESAR-I | 60 | 400KV MEERUT-BAREILLY-I | 21 | 315MVA ICT-I KOTA | 20 | 500MVA ICT-I SHAHJHNPR | DTL | 220KV MND-S.WZRBD-IV
400KV NIMRANA-MANESAR-II | 61 | 400KV MEERUT-BAREILLY-II | 22 | 315MVA ICT-II KOTA | 21 | 500MVA ICT-II SHAHJHNPR | DTL | 220KV MND-NARELA-I
400KV NIMRANA-SIKAR-I | 62 | 400KV RIHAND-ALLD-I | 23 | 315MVA ICT-I KOTPUTLI | 22 | 100MVA ICT-I SITARGANJ | DTL | 220KV MND-NARELA-II
400KV NIMRANA-SIKAR-II | 63 | 400KV RIHAND-ALLD-II | 24 | 315MVA ICT-II KOTPUTLI | 23 | 100MVA ICT-II SITARGANJ | DTL | 220KV MND-GOPALPUR-I
400KV ROORKI-KASHIPUR-I | 64 | 400KV RIHAND3-VINDH(Pool)-I | 25 | 315MVA ICT-I MAHRANIBAG | 24 | 315MVA ICT-I SOHAWAL | DTL | 220KV MND-GOPALPUR-II
400KV ROORKI-KASHIPUR-II | 65 | 400KV RIHAND3-VINDH(Pool)-II | 26 | 315MVA ICT-II MAHRANIBAG | 25 | 315MVA ICT-II SOHAWAL | DTL | 220KV MBAG-SARITAVIHAR
400KV ROORKI-MUZFRNGR | 66 | 400KV SING-ALLD-I | 27 | 500MVA ICT-III MAHRANIBAG | 26 |  | DTL | 220KV MBAG-LODHIROAD-I
400KV ROORKI-RISHIKESH | 67 | 400KV SING-ALLD-II | 28 | 500MVA ICT-IV MAHRANIBAG | 27 |  | DTL | 220KV MBAG-LODHIROAD-II
400KV SIKAR-RATANGARH-I | 68 | 400KV SING(NTPC)-ANPARA(UP) | 29 | 500MVA ICT-I MANDOLA | 28 |  | DTL | 220KV MBAG-I P EXTN
400KV SIKAR-RATANGARH-II | 69 | 400KV SING-FATEHPUR | 30 | 500MVA ICT-II MANDOLA | 29 |  | UPPCL | 220KV AGRA-SHAMSABD-I
400KV MEERUT-BAGPAT-II | 70 | 400KV SING-LKO(UP)-I | 31 | 500MVA ICT-III MANDOLA | 30 |  | UPPCL | 220KV AGRA-FEROZABAD
400KV ROORKI-SAHARANPUR-I | 71 | 400KV SING-RIHAND-I | 32 | 500MVA ICT-IV MANDOLA |  |  | UPPCL | 220KV BAGHPAT(PG)-BAGHPAT(UP)
400KV ROORKI-SAHARANPUR-II | 72 | 400KV SING-RIHAND-II | 33 | 500MVA ICT-I MANESAR |  |  | UPPCL | 220KV BAGHPAT-MURADNGR
400KV RAPPC-CHITTOR(RJ)-I | 73 | 400KV SING-VINDH-I | 34 | 500MVA ICT-II MANESAR |  |  | UPPCL | 220KV BAGHPAT-SHAMLI
| 74 | 400KV SING-VINDH-II | 35 | 315MVA ICT-I MEERUT |  |  | UPPCL | 220KV GORAKH-BARHUA
| 75 | 400KV KANPUR-KANPUR(GIS)-I | 36 | 315MVA ICT-II MEERUT |  | 765KV ICT NR-III | UPPCL | 220KV GORAKH-BASTI
| 76 | 400KV KANPUR-KANPUR(GIS)-II | 37 | 315MVA ICT-III MEERUT | 1 | 765/400KV ICT-I BALIA | UPPCL | 220KV LKO(PG)-Bakhsi Ka Talab
| 77 | 400KV VARANASI-SASARAM(ER) | 38 | 500MVA ICT-IV MEERUT | 2 | 765/400KV ICT-II BALIA | UPPCL | 220KV LKO(PG)-CHINHAT
400KV BAHADURGRH-BAWANA | 78 | 400KV VARANASI-SARNATH-I | 39 | 315MVA ICT-III MUZFRNGR | 3 | 765/400KV ICT-I LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-I
400KV BAHADURGRH-SONIPAT-I | 79 | 400KV VARANASI-SARNATH-II | 40 | 315MVA ICT-II NIMRANA | 4 | 765/400KV ICT-II LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-II
400KV BAHADURGRH-SONIPAT-II | 80 | 400KV ALLAHABAD-MEJA(NTPC)-I | 41 | 315MVA ICT-I ROORKI | 5 | 765/400KV ICT-I FATEHPUR | UPPCL | 220KV M'PURI-ETAH
400KV BHIWANI-BAWANA | 81 | 400KV BALIA-BIHARSHRF-I | 42 | 315MVA ICT-II ROORKI | 6 | 765/400KV ICT-II FATEHPUR | UPPCL | 220KV M'PURI-SIRSAGANJ-I
400KV BHIWANI-BHIWANI(BBMB) | 82 | 400KV BALIA-BIHARSHRF-II | 43 | 315MVA ICT-I SIKAR | 7 | 765/400KV ICT-I AGRA | UPPCL | 220KV M'PURI-M'PURI(UP)-II
400KV BHIWANI-HISAR-I | 83 | 400KV ALLD-SASARAM | 44 | 315MVA ICT-II SIKAR | 8 | 765/400KV ICT-II AGRA | UPPCL | 220KV M'PURI-FEROZBD
400KV BHIWANI-HISAR-II | 84 | 400KV BALIA-PATNA-I | 45 | 500MVA ICT-I BAGPAT | 9 | 765/400KV ICT-I BAREILLY | UPPCL | 400KV M'PURI-ORAI-I
400KV BHIWANI-HISAR-III | 85 | 400KV BALIA-PATNA-II | 46 | 500MVA ICT-II BAGPAT | 10 | 765/400KV ICT-II BAREILLY | UPPCL | 400KV M'PURI-PARICHA-II
400KV BHIWANI-JIND-I | 86 | 400KV BALIA-PATNA-III | 47 | 315MVA ICT-I SAHARANPUR | 11 | 765/400KV ICT-I VARANASI | UPPCL | 220KV MEERUT-GAJRAULA
400KV BHIWANI-JIND-II | 87 | 400KV BALIA-PATNA-IV | 48 | 315MVA ICT-II SAHARANPUR | 12 | 765/400KV ICT-II VARANASI | UPPCL | 220KV MEERUT-NEHTAUR
400KV FATEHABAD-HISAR | 88 | 400KV LKO(765)-KANPUR(GIS)-I |  |  | 13 | 765/400KV ICT-I KANPUR(GIS) | UPPCL | 220KV ORAI-KANPUR
400KV BHIWADI-HISAR-II | 89 | 400KV LKO(765)-KANPUR(GIS)-II |  |  | 14 | 765/400KV ICT-II KANPUR(GIS) | UPPCL | 400KV PANKI-MURADNGR
400KV BHIWADI-HISAR-III | [6 empty] | UPPCL | 220KV SHAHJHNP-HARDOI
400KV HISAR-BHIWANI(BBMB) | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-I | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-II |  | 400kv LINES of ER-1 in NR-III Availability |  | NR-I Additional ICT from NR-II |  |  | UPPCL | 220KV SOHAWAL(PG) - SOHAWAL(UP)
400KV KABULPR-BAHADURGRH | 1 | 400KV SASARAM-BIHARSHRF-I | 1 | 315MVA ICT-I BAHADURGARH |  | NR-III HVDC SYSTEM / SVC | UPPCL | 220KV UNCHR-RBRLY-I
400KV KABULPR-BHIWANI | 2 | 400KV SASARAM-BIHARSHRF-II | 2 | 500MVA ICT-II BAHADURGARH | 1 | 500KV HVDC R-D POLE-I | UPPCL | 220KV UNCHR-RBRLY-II
|  |  | 3 | 315MVA ICT-I HISAR | 2 | 500KV HVDC R-D POLE-II | PTCUL | 220KV ROORKI-HARDWAR
|  |  | 4 | 315MVA ICT-II HISAR | 3 | 500KV HVDC BALIA-BHWD POLE-I | PTCUL | 220KV ROORKI--RAMNAGAR
|  | 765 KV TRANS LINES NR-III | 5 | 315MVA ICT-III HISAR | 4 | 500KV HVDC BALIA-BHWD POLE-II | PTCUL | 132KV SITARGNJ(PG)-SITARGNJ(PTCUL)
765 KV TRANS LINES NR-I | 1 | 765KV AGRA-FATEHPUR-I | 6 | 315MVA ICT-I SONIPAT | 5 | 800KV HVDC AGRA-BNC POLE-I | PTCUL | 132KV PITHORAGRH-CHANDOK
765KV AGRA-JHATIKALA | 2 | 765KV AGRA-FATEHPUR-II | 7 | 315MVA ICT-II SONIPAT | 6 | 800KV HVDC AGRA-BNC POLE-II | PTCUL | 132KV PITHORAGRH-ALMORA
765KV BHIWANI-PHAGI(JPR)-I | 3 | 765KV AGRA-GR.NOIDA | 8 | 315MVA ICT-I BHIWANI | 7 | VINDH HVDC B/B BLOCK-I | PTCUL | 132KV PTRGRH-PTRGRH(PTCUL)
765KV MEERUT-GR.NOIDA | 4 | 765KV FATEHPUR-SASARAM | 9 | 315MVA ICT-II BHIWANI | 8 | VINDH HVDC B/B BLOCK-II | POWERLINK
765KV MOGA-BHIWANI | 5 | 765KV LUCKNOW-BALIA | 10 | 500MVA ICT-I JIND | 9 | SASARAM HVDC B/B | PLINK | 400KV LUCKNOW-GORAKH-I (PL)
765KV JHATIKALA-BHIWANI | 6 | 765KV LUCKNOW-BAREILLY | 11 | 500MVA ICT-II JIND | 10 | +/-140MVAR SVC-I KANPUR | PLINK | 400KV LUCKNOW-GORAKH-II (PL)
765KV MEERUT-BHIWANI | 7 | 765KV VARANASI-BALIA |  |  | 11 | +/-140MVAR SVC-II KANPUR | PLINK | 400KV GRKHPR-MZFRPR-I (PL)
765KV BHIWANI-PHAGI(JPR)-II | 8 | 765KV VARANASI-FATEHPUR |  |  |  |  | PLINK | 400KV GRKHPR-MZFRPR-II (PL)
| 9 | 765KV VARANASI-GAYA-I |  | 765KV ICT NR-I
| 10 | 765KV VARANASI-KANPUR(GIS)-I | 1 | 765/400KV ICT-I JHATIKALA
BUS REACTORS NR-I | 11 | 765KV VARANASI-KANPUR(GIS)-II | 2 | 765/400KV ICT-II JHATIKALA |  | SWITCABLE LINE REACTORS NR-III | NR-II | 400KV DAD-M'KOTLA
125MVAR B/Reactor-I BAGPAT | 12 | 765KV KANPUR(GIS)-JHATIKRA-I | 3 | 765/400KV ICT-III JHATIKALA | 1 | AGRA 240MVAR S/R FATEHPR line | NR-II | 400KV BAGHPAT-KAITHAL-I
50MVAR B/Reactor-I BASSI |  |  | 4 | 765/400KV ICT-IV JHATIKALA | 2 | AGRA 50MVAR S/R BHIWADI-I LINE | NR-II | 400KV BAGHPAT-KAITHAL-II
50MVAR B/Reactor-II BASSI |  |  | 5 | 765/400KV ICT-I MEERUT | 3 | ALLHBD 50MVAR S/R MNPR-I LINE | NR-II | 765KV MEERUT-MOGA
50MVAR B/Reactor-III BASSI |  | BUS REACTORS NR-III | 6 | 765/400KV ICT-II MEERUT | 4 | ALLHBD 50MVAR S/R MNPR-II LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-I | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
125MVAR B/Reactor-IV BASSI | 1 | 125MVAR B/Reactor-I AGRA | 7 | 765/400KV ICT-I BHIWANI | 5 | BARLLY 50MVAR S/R MND-I LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-II | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
80MVAR B/Reactor BHINMAL | 2 | 125MVAR B/Reactor-II AGRA | 8 | 765/400KV ICT-II BHIWANI | 6 | BARLLY 50MVAR S/R MND-II LINE | NR-II | 400KV HISAR-MOGA-I
80MVAR B/Reactor BHIWADI | 3 | 240MVAR B/Reactor-II AGRA-765 |  |  | 7 | BALIA 240MVAR S/R LUCKNW Ckt-I | NR-II | 400KV HISAR-MOGA-II
80MVAR B/Reactor BLBGARH | 4 | 240MVAR B/Reactor-1 AGRA-765 |  |  | 8 | BALIA 240MVAR S/R GAYA Line | NR-II | 400KV HISAR-MOGA-III
125MVAR B/Reactor-I JAIPUR(S) | 5 | 80MVAR B/Reactor ALLAHABAD |  |  | 9 | FATEHPR 330MVAR S/R AGRA line
125MVAR B/Reactor-II JAIPUR(S) | 6 | 125MVAR B/Reactor-II ALLAHABAD |  |  | 10 | GORAKH 50MVAR S/R LKO-I LINE
240MVAR B/Reactor-I JHATIKALA-765 | 7 | 80MVAR B/Reactor-I BALIA |  |  | 11 | GORAKH 50MVAR S/R LKO-II LINE
240MVAR B/Reactor-II JHATIKALA-765 | 8 | 125MVAR B/Reactor-II BALIA |  |  | 12 | GORAKH 63MVAR S/R LKO-III LINE
50MVAR B/Reactor KANKROLI | 9 | 125MVAR B/Reactor-III BALIA |  | SWITCABLE LINE REACTORS NR-I | 13 | GORAKH 63MVAR S/R LKO-IV LINE | ER-I | 400KV BALIA-SASARAM
125MVAR B/Reactor-II KANKROLI | 10 | 125MVAR B/Reactor-IV BALIA | 1 | BHINML 50MVAR S/R KANKROLI | 14 | GORAKH 80MVAR S/R Barh-I line | ER-I | 765KV BALIA-GAYA
80MVAR B/Reactor-I KOTA | 11 | 240MVAR B/Reactor-I BALIA-765 | 2 | MEERUT 50MVAR S/R Kotesh-I LINE | 15 | GORAKH 80MVAR S/R Barh-II line | ER-I | 400KV BARH- GRKHPR-I
50MVAR B/Reactor-II KOTA | 12 | 240MVAR B/Reactor-II BALIA-765 | 3 | MEERUT 50MVAR S/R Kotesh-II LINE | 16 | LUCKNW 240MVAR S/R BRLY Line | ER-I | 400KV BARH- GRKHPR-II
80MVAR B/Reactor-I KOTPUTLI | 13 | 80MVAR B/Reactor BAREILLY | 4 | JHATIKALA 240MVAR S/R AGRA Line | 17 | LUCKNW 63MVAR S/R GKP-III LINE | ER-I | 765KV VARANASI-GAYA-II
50MVAR B/Reactor MANDOLA | 14 | 2x50MVAR B/Reactor BAREILLY | 5 | MEERUT 240MVAR S/R AGRA line | 18 | LUCKNW 63MVAR S/R GKP-IV LINE | ER-I | 400KV VARANASI-BIHARSHRF-I
240MVAR B/Reactor-I MEERUT-765 | 15 | 240MVAR B/Reactor-I BAREILLY-765 | 6 | SIKAR 50MVAR S/R AGRA Ckt-I | 19 | LUCKNW 240MVAR S/R BALIA Ckt-I | ER-I | 400KV VARANASI-BIHARSHRF-II
125MVAR B/Reactor MANESAR | 16 | 80MVAR B/Reactor BIHARSHRF | 7 | SIKAR 50MVAR S/R AGRA Ckt-II | 20 | VARANASI 240MVAR S/R KNP(GIS) ckt-1
50MVAR B/Reactor MURADNGR | 17 | 125MVAR B/Reactor-I FATEHPUR | 8 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | 21 | VARANASI 240MVAR S/R KNP(GIS) ckt-2
80MVAR B/Reactor NIMRANA | 18 | 125MVAR B/Reactor-II FATEHPUR | 9 | BHIWANI 240MVAR S/R MEERUT line | 22 | KNP(GIS) 330MVAR S/R JHATIKRA ckt-1 | WR | 765KV AGRA-GWALIOR-I
240MVAR B/Reactor-I PHAGI(JPR)-765 | 19 | 330MVAR B/Reactor-III FTHPR-765 | 10 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line |  |  | WR | 765KV AGRA-GWALIOR-II
125MVAR B/Reactor ROORKEE | 20 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | WR | 765KV GWALIOR-PHAGI-I
125MVAR B/Reactor-I RATANGRH(RJ) | 21 | 125MVAR B/Reactor-II LUCKNOW |  | SVC NR-I |  |  | WR | 765KV GWALIOR-PHAGI-II
80MVAR B/Reactor SIKAR | 22 | 125MVAR B/Reactor-III LUCKNOW | 1 | +400/-300MVAR SVC KANKROLI
50MVAR B/Reactor-I SAHARANPUR | 23 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-I
50MVAR B/Reactor-II SAHARANPUR | 24 | 125MVAR B/Reactor-I VINDH |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-II
125MVAR B/Reactor-II SONIPAT | 25 | 125MVAR B/Reactor-II VINDH
| 26 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - I
BUS REACTORS NR-I From NR2 | 27 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - II
240MVAR B/Reactor-I BHIWANI | 28 | 125MVAR B/Reactor-1 Mainpuri
240MVAR B/Reactor-II BHIWANI | 29 | 125MVAR B/Reactor Gorakhpur-I
50MVAR B/Reactor HISAR | 30 | 125MVAR B/Reactor-II Gorakhpur
125MVAR B/Reactor HISAR | 31 | 125MVAR B/Reactor-I SHAHJHNPR
125MVAR Bus/eactor JIND | 32 | 240MVAR B/Reactor-I KANPUR(GIS)
125MVAR B/Reactor SONIPAT | 33 | 240MVAR B/Reactor-II KANPUR(GIS)
| 34 | 125MVAR B/Reactor-III KANPUR(GIS)
| 35 | 125MVAR B/Reactor-I VARANASI
| 36 | 330MVAR B/Reactor-I VARANASI
| 37 | 330MVAR B/Reactor-II VARANASI
| 38 | 125MVAR B/Reactor KANPUR
Note on E50: a: DOC-01.04.12
Note on I83: 220KV M'PURI-M'PURI(UP)-I LILO at SIRSAGANJ
Note on E84: a: DOC-01.04.12
Note on I86: '400KV M'PURI-PARICHA-I LILO at URI
Note on A96: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on A97: Total-45.6km, PG-26.64km, HVPN-19km.
Note on I98: DELL: 220KV ROORKI-SIDKUL
Note on C108: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C109: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on I112: LILO of 400KV MEERUT-KAITHAL-I at Baghpat
Note on I113: LILO of 400KV MEERUT-KAITHAL-II at Baghpat
Note on I128: LILO of 765KV FATEHPUR-GAYA at VARANASI

## SOP DATA NR3
Standard of Performance data for the month of July-2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD. NORTHERN REGION - III
NAME OF REGION : NR-III
ANNEXURE-A
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency |  | Number of Sub-Conductor
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
765 KV TRANS LINES
1 | NR376507 | 765KV ALIGARH-GR.NOIDA | 51 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100 | 744
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1327 | 51 | 67677 | 67677 |  |  | 4
2 | NR376506 | 765KV AGRA-ALIGARH | 122.5 | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1327 | 122.5 | 162557.5 | 162557.5 |  |  | 4
3 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2019-07-02 06:43 | 2019-07-02 15:37 |  |  |  | 0 | 0 | 0 | 0.37083 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-801kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-07 06:26 | 2019-07-07 20:49 |  |  |  | 0 | 0 | 0 | 0.59931 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=797kV
[6 empty] | 2019-07-09 02:06 | 2019-07-10 06:26 |  |  |  | 0 | 0 | 0 | 1899-12-31 04:20 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
[6 empty] | 2019-07-10 08:07 | 2019-07-10 09:54 |  |  |  | 0 | 0 | 0 | 0.074306 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
[6 empty] | 2019-07-13 08:04 | 2019-07-13 22:54 |  |  |  | 0 | 0 | 0 | 0.61806 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
[6 empty] | 2019-07-15 07:11 | 2019-07-19 10:45 |  |  |  | 0 | 0 | 0 | 1900-01-03 03:34 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
[6 empty] | 2019-07-23 06:48 | 2019-07-23 10:33 |  |  |  | 0 | 0 | 0 | 0.15625 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-06 03:33 | [6 empty] | 744 | 1216 | 334.52 | 406776.32 | 406776.32 |  |  | 4
4 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2019-07-01 | 2019-07-01 14:24 |  |  |  | 0 | 0 | 0 | 0.6 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-801kV | NRPC | [5 empty] | 99.9754
[6 empty] | 2019-07-06 03:37 | 2019-07-06 21:42 |  |  |  | 0 | 0 | 0 | 0.75347 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
[6 empty] | 2019-07-08 04:08 | 2019-07-08 21:07 |  |  |  | 0 | 0 | 0 | 0.70764 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV
[6 empty] | 2019-07-10 03:22 | 2019-07-12 19:38 |  |  |  | 0 | 0 | 0 | 1900-01-01 16:16 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
[6 empty] | 2019-07-14 07:45 | 2019-07-14 21:30 |  |  |  | 0 | 0 | 0 | 0.57292 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
[6 empty] | 2019-07-20 06:51 | 2019-07-21 22:32 |  |  |  | 0 | 0 | 0 | 1899-12-31 15:41 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=427kV
[6 empty] | 2019-07-24 16:09 | 2019-07-24 16:20 |  |  |  | 0.0076389 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped end due to R-N fault. Fatehpur Details: M1-F/D- 201.7km,F/C- 3.01KA, M2-F/D-- n/a, F/C- 2.7KA. Agra Details: M1- F/D--108.5km,F/C-6.17KA, M2-F/D-109.1km, F/C-6.12KA.
[6 empty] | 2019-07-24 16:20 | 2019-07-28 20:11 |  |  |  | 0 | 0 | 0 | 1900-01-03 03:51 |  |  |  | LVRD | Line kept open on voltage regulation s per NRLDC instruction. In this regards mail sent at 1733hrs dtd 24.07.19 (Mail copy enclosed)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.0076389 | 0 | 0 | 1900-01-10 03:01 | [6 empty] | 744 | 1210 | 334.8 | 405108 | 405008.175
5 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1374 | 318.919 | 438194.706 | 438194.706 |  |  | 4
6 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1019 | 251.613 | 256393.647 | 256393.647 |  |  | 4
7 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1419 | 165.98 | 235525.62 | 235525.62 |  |  | 4
8 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1393 | 223 | 310639 | 310639 |  |  | 4
9 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 471970.884 |  |  | 6
10 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1447 | 326.172 | 471970.884 | 471970.884 |  |  | 6
11 | NR376504 | 765KV ALIGARH-JHATIKARA | 158 | NR3 | -- | 2019-07-27 04:01 | 2019-07-27 10:12 |  |  |  | 0 | 0 | 0 | 0.25764 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=801kV | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.25764 | [6 empty] | 744 | 1440 | 158 | 227520 | 227520 |  |  | 4
12 | NR376505 | 765KV KANPUR(GIS)-ALIGARH | 327 | NR3 | -- | 2019-07-04 17:22 | 2019-07-06 14:02 |  |  |  | 0 | 0 | 0 | 1899-12-31 20:40 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh-799kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-09 04:51 | 2019-07-09 20:25 |  |  |  | 0 | 0 | 0 | 0.64861 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=800kV
[6 empty] | 2019-07-10 04:09 | 2019-07-10 15:38 |  |  |  | 0 | 0 | 0 | 0.47847 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=800kV
[6 empty] | 2019-07-14 09:58 | 2019-07-14 19:47 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Knp=798kV
[6 empty] | 2019-07-15 16:02 | 2019-07-16 19:48 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:46 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=804kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 13:18 | [6 empty] | 744 | 1440 | 327 | 470880 | 470880 |  |  | 4
13 | NR376508 | 765KV ORAI-ALIGARH-II | 331.958 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1440 | 331.958 | 478019.52 | 478019.52 |  |  | 6
14 | NR376509 | 765KV ORAI-ALIGARH-I | 331.958 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1440 | 331.958 | 478019.52 | 478019.52 |  |  | 6
|  | 400 KV TRANS LINES |  |  | -- | [14 empty] | NRPC
1 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 43.013 | NR3 | -- | 2019-07-29 07:53 | 2019-07-29 20:13 | -- | -- |  | 0 | 0 | 0 | 0.51389 |  |  |  | OSPD | S/D taken by UPPCL for maintenance work | NRPC | [5 empty] | 100
[6 empty] | 2019-07-30 08:14 | 2019-07-30 19:32 |  |  |  | 0 | 0 | 0 | 0.47083 |  |  |  | OSPD | S/D taken by UPPCL for maintenance work
[6 empty] | 2019-07-31 08:34 | 2019-07-31 18:50 |  |  |  | 0 | 0 | 0 | 0.42778 |  |  |  | OSPD | S/D taken by UPPCL for maintenance work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1899-12-31 09:54 | [6 empty] | 744 | 515 | 43.013 | 22151.695 | 22151.695 |  |  | 2
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- | 2019-07-02 16:53 | 2019-07-02 19:44 | -- | -- |  | 0 | 0 | 0 | 0.11875 |  |  |  | OSFD | Emergency S/D taken by UPPCL for R-ph dropper tightening at Agra (UP) end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.11875 | [6 empty] | 744 | 515 | 29.982 | 15440.73 | 15440.73 |  |  | 2
3 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 57.159 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 57.159 | 29436.885 | 29436.885 |  |  | 2
4 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2019-07-02 06:15 | 2019-07-02 21:28 | -- | -- | -- | 0 | 0 | 0 | 0.63403 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-432kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-03 08:17 | 2019-07-07 19:55 |  |  |  | 0 | 0 | 0 | 1900-01-03 11:38 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-431kV
[6 empty] | 2019-07-08 07:56 | 2019-07-08 21:11 |  |  |  | 0 | 0 | 0 | 0.55208 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV
[6 empty] | 2019-07-09 01:55 | 2019-07-10 09:23 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:28 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-431kV
[6 empty] | 2019-07-14 06:08 | 2019-07-14 19:59 |  |  |  | 0 | 0 | 0 | 0.57708 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
[6 empty] | 2019-07-20 18:46 | 2019-07-22 21:10 |  |  |  | 0 | 0 | 0 | 1900-01-01 02:24 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
[6 empty] | 2019-07-24 16:45 | 2019-07-28 19:54 |  |  |  | 0 | 0 | 0 | 1900-01-03 03:09 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-12 18:58 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 |  |  | 2
5 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2019-07-10 04:06 | 2019-07-13 22:45 |  |  |  | 0 | 0 | 0 | 1900-01-02 18:39 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-435kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-15 15:54 | 2019-07-20 10:22 |  |  |  | 0 | 0 | 0 | 1900-01-03 18:28 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2019-07-23 05:41 | 2019-07-23 14:40 |  |  |  | 0 | 0 | 0 | 0.37431 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 22:06 | [6 empty] | 744 | 367 | 167.2 | 61362.4 | 61362.4 |  |  | 2
6 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 245 | 211.433 | 51801.085 | 51801.085 |  |  | 2
7 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2019-07-18 03:35 | 2019-07-19 14:41 | -- | -- | -- | 0 | 0 | 0 | 1899-12-31 11:06 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-21 06:06 | 2019-07-22 09:43 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:37 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432 kV
[6 empty] | 2019-07-26 02:07 | 2019-07-29 15:48 |  |  |  | 0 | 0 | 0 | 1900-01-02 13:41 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-05 04:24 | [6 empty] | 744 | 402 | 208.98 | 84009.96 | 84009.96 |  |  | 2
8 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2019-07-04 17:16 | 2019-07-06 20:26 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 03:10 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-07 10:04 | 2019-07-07 19:43 |  |  |  | 0 | 0 | 0 | 0.40208 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV
[6 empty] | 2019-07-10 08:03 | 2019-07-11 08:39 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:36 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-434kV
[6 empty] | 2019-07-14 09:12 | 2019-07-14 19:54 |  |  |  | 0 | 0 | 0 | 0.44583 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
[6 empty] | 2019-07-15 15:57 | 2019-07-16 15:08 |  |  |  | 0 | 0 | 0 | 0.96597 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
[6 empty] | 2019-07-25 04:08 | 2019-07-25 20:09 |  |  |  | 0 | 0 | 0 | 0.66736 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-04 15:19 | [6 empty] | 744 | 515 | 209.51 | 107897.65 | 107897.65 |  |  | 2
9 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | 2019-07-08 14:18 | 2019-07-08 22:15 |  |  |  | 0 | 0 | 0 | 0.33125 |  |  |  | LCSD | S/D taken for replacement of disc insulator with Polymer Insulator. | NRPC | [5 empty] | 99.2966
[5 empty] | -- | 2019-07-11 08:54 | 2019-07-11 14:08 |  |  |  | 0.21806 | 0 | 0 | 0 |  |  |  | OSFT | S/D taken to attend hot spot at Ballabhgarh
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.21806 | 0 | 0 | 0.33125 | [6 empty] | 744 | 382 | 181.137 | 69194.334 | 68707.6176 |  |  | 2
10 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | 2019-07-01 | 2019-07-04 21:27 |  |  |  | 0 | 0 | 0 | 1900-01-02 21:27 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=428kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-11 04:14 | 2019-07-17 22:50 |  |  |  | 0 | 0 | 0 | 1900-01-05 18:36 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=429kV
[6 empty] | 2019-07-24 18:17 | 2019-07-25 20:35 |  |  |  | 0 | 0 | 0 | 1899-12-31 02:18 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=427kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 18:21 | [6 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 |  |  | 2
11 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | 2019-07-05 08:39 | 2019-07-11 15:55 |  |  |  | 0 | 0 | 0 | 1900-01-05 07:16 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=424kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-18 03:50 | 2019-07-20 10:25 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:35 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=429kV
[6 empty] | 2019-07-26 03:07 | 2019-07-31 01:00 |  |  |  | 0 | 0 | 0 | 1900-01-03 21:53 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=426kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-12 11:44 | [6 empty] | 744 | 332 | 139.73 | 46390.36 | 46390.36 |  |  | 2
12 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 155.932 | 80304.98 | 80304.98 |  |  | 2
13 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | 2019-07-09 08:10 | 2019-07-11 22:53 |  |  |  | 0 | 0 | 0 | 1900-01-01 14:43 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=431 kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-25 07:19 | 2019-07-30 22:14 |  |  |  | 0 | 0 | 0 | 1900-01-04 14:55 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. ALD=428kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-07 05:38 | [6 empty] | 744 | 515 | 224 | 115360 | 115360 |  |  | 2
14 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 98.792 | 50877.88 | 50877.88 |  |  | 2
15 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- | 2019-07-10 09:48 | 2019-07-10 12:18 | -- | -- |  | 0 | 0.10417 | 0 | 0 |  |  |  | OMSU | Tripped only from Mau (UP) end due to multiple trippings at Mau end (400kV Azamgarh - Mau line). Fault in UPPCL Jurisdiction | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.10417 | 0 | 0 | [6 empty] | 744 | 515 | 13 | 6695 | 6695 |  |  | 2
16 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- | 2019-07-10 09:48 | 2019-07-10 12:19 | -- | -- | -- | 0 | 0.10486 | 0 | 0 |  |  |  | OMSU | Tripped only from Mau (UP) end due to multiple trippings at Mau end (400kV Azamgarh - Mau line). Fault in UPPCL Jurisdiction | NRPC | [5 empty] | 100
[6 empty] | 2019-07-17 07:38 | 2019-07-17 08:31 |  |  |  | 0 | 0.036806 | 0 | 0 |  |  |  | OMSU | Tripped only from Mau (UP) end due to failure of R-ph trip circuit of Circuit Breaker at Mau (UP) end. Fault in UPPCL Jurisdiction
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.14167 | 0 | 0 | [6 empty] | 744 | 515 | 13 | 6695 | 6695 |  |  | 2
17 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 227 | 229.163 | 52020.001 | 52020.001 |  |  | 2
18 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 227 | 229.163 | 52020.001 | 52020.001 |  |  | 2
19 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 1.559 | 1071.033 | 1071.033 |  |  | 2
20 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 687 | 1.559 | 1071.033 | 1071.033 | 100 |  | 2
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
21 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 9.2 | 4738 | 4738 |  |  | 2
22 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 9.2 | 4738 | 4738 |  |  | 2
23 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- | 2019-07-16 11:21 | 2019-07-16 13:54 | -- | -- | -- | 0.10625 | 0 | 0 | 0 |  |  |  | OSPT | Emergency S/D taken for attending buchholz alarm in NGR. | NRPC | [5 empty] | 99.6371
[6 empty] | 2019-07-23 10:20 | 2019-07-23 10:24 |  |  |  | 0.0027778 | 0 | 0 | 0 |  |  |  | OSPT | SD taken to take out LKO (UP) line reactor (nonswitchable) from service for AMP and Reactor FDS measurement at Bareilly.
[6 empty] | 2019-07-23 18:24 | 2019-07-23 18:29 |  |  |  | 0.0034722 | 0 | 0 | 0 |  |  |  | OSPT | SD taken to take line reactor(nonswitchable) in service after AMP and Reactor FDS measurement at Bareilly.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.1125 | 0 | 0 | 0 | [6 empty] | 744 | 331 | 278.76 | 92269.56 | 91934.7108 |  |  | 2
25 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 |  |  | 2
26 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 92.68 | 47730.2 | 47730.2 |  |  | 2
27 | NR340010 | 400KV BAREILLY-SHAHJHNPR-I | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 |  |  | 2
28 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 116.03 | 59755.45 | 59755.45 |  |  | 2
29 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 |  | 2019-07-30 12:06 | 2019-07-30 13:08 |  |  |  | 0 | 0.043056 | 0 | 0 |  |  |  | OMSU | Tripped on R-N fault at Kashipur, LBB of 400kV Bus-II operated due to which main breaker of Bareilly -2 opened at Kashipur end & also Moradabad Tie CB opened, 315MVA ICT-I & II Main CB tripped and DT received at Bareilly end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.043056 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 |  |  | 4
30 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 101.841 | 69964.767 | 69964.767 |  |  | 4
31 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2019-07-10 08:50 | 2019-07-10 19:46 | -- | -- | -- | 0 | 0 | 0 | 0.45556 |  |  |  | LCSD | S/D taken for replacement of disc insulator with Polymer Insulator. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.45556 | [6 empty] | 744 | 515 | 235.952 | 121515.28 | 121515.28 |  |  | 2
32 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- | 2019-07-11 09:26 | 2019-07-11 19:51 | -- | -- |  | 0 | 0 | 0 | 0.43403 |  |  |  | LCSD | S/D taken for OPGW installation work | NRPC | [5 empty] | 100
[6 empty] | 2019-07-13 08:12 | 2019-07-13 13:31 |  |  |  | 0 | 0 | 0 | 0.22153 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri= 422kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.65556 | [6 empty] | 744 | 515 | 235.952 | 121515.28 | 121515.28 |  |  | 2
33 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2019-07-13 08:05 | 2019-07-13 20:08 | -- | -- | -- | 0 | 0 | 0 | 0.50208 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur= 428kV | NRPC | [5 empty] | 99.9216
[6 empty] | 2019-07-14 06:09 | 2019-07-17 20:47 |  |  |  | 0 | 0 | 0 | 1900-01-02 14:38 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur= 427kV
[6 empty] | 2019-07-19 23:33 | 2019-07-20 00:08 |  |  |  | 0.024306 | 0 | 0 | 0 |  |  |  | OSFT | Emergency hand tripped due to heavy sparking in B Ph of line isolator at Mainpuri end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.024306 | 0 | 0 | 1900-01-03 02:41 | [6 empty] | 744 | 469 | 260.051 | 121963.919 | 121868.2932 |  |  | 2
34 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- | 2019-07-06 08:22 | 2019-07-07 00:30 | -- | -- | -- | 0 | 0 | 0 | 0.67222 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Mainpuri = 419kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-18 03:56 | 2019-07-20 10:15 |  |  |  | 0 | 0 | 0 | 1900-01-01 06:19 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur= 427kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 22:27 | [6 empty] | 744 | 469 | 260.051 | 121963.919 | 121963.919 |  |  | 2
35 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 |  |  | 2
36 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | 2019-07-11 12:30 | 2019-07-11 18:02 |  |  |  | 0 | 0.23056 | 0 | 0 |  |  |  | OMSU | Tripped only from UP end due to problem at Gorakhpur(UP) end | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.23056 | 0 | 0 | [6 empty] | 744 | 515 | 45.94 | 23659.1 | 23659.1 |  |  | 2
37 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 291 | 240 | 69840 | 69840 |  |  | 2
38 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | 2019-07-04 17:08 | 2019-07-07 19:59 |  |  |  | 0 | 0 | 0 | 1900-01-02 02:51 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-424kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-09 07:11 | 2019-07-13 23:03 |  |  |  | 0 | 0 | 0 | 1900-01-03 15:52 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=420 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-06 18:43 | [6 empty] | 744 | 515 | 72.6 | 37389 | 37389 |  |  | 2
39 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 73.2 | 37698 | 37698 |  |  | 2
40 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- | 2019-07-30 09:12 | 2019-07-30 23:25 | -- | -- |  | 0 | 0 | 0 | 0.59236 |  |  |  | LCSD | S/D taken for replacement of disk insulator with polymer insulator. | NRPC | [5 empty] | 100
[6 empty] | 2019-07-31 13:16 | 2019-07-31 16:43 |  |  |  | 0 | 0 | 0 | 0.14375 |  |  |  | LCSD | S/D taken for replacement of disk insulator with polymer insulator.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.73611 | [6 empty] | 744 | 342 | 385.69 | 131905.98 | 131905.98 |  |  | 2
41 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- | 2019-07-14 09:54 | 2019-07-14 20:53 | -- | -- |  | 0 | 0 | 0 | 0.45764 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Knp=428kV | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.45764 | [6 empty] | 744 | 361 | 370.772 | 133848.692 | 133848.692 |  |  | 2
42 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 361 | 370.772 | 133848.692 | 133848.692 |  |  | 2
43 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 107.079 | 55145.685 | 55145.685 |  |  | 2
44 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 107.1 | 55156.5 | 55156.5 |  |  | 2
45 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 5.922 | 3049.83 | 3049.83 |  |  | 2
46 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 5.86 | 3017.9 | 3017.9 |  |  | 2
47 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 289 | 263.933 | 76276.637 | 76276.637 |  |  | 2
48 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- | 2019-07-14 10:11 | 2019-07-14 21:03 | -- | -- | -- | 0 | 0 | 0 | 0.45278 |  |  |  | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lko=428kV | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.45278 | [6 empty] | 744 | 289 | 263.933 | 76276.637 | 76276.637 |  |  | 2
49 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 |  |  | 4
50 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 2.86 | 1964.82 | 1964.82 |  |  | 4
51 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | 2019-07-11 03:35 | 2019-07-11 04:12 |  |  |  | 0 | 0.025694 | 0 | 0 |  |  |  | OMSU | Tripped only from Lucknow (PG) end due to DT received from Lucknow (UP) end. Fault in UPPCL Jurisdiction | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.025694 | 0 | 0 | [6 empty] | 744 | 515 | 41.743 | 21497.645 | 21497.645 |  |  | 2
52 | NR140114 | 400KV LUCKNOW-SHAHJHNPR-I | 169.785 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 371 | 169.785 | 62990.235 | 62990.235 |  |  | 2
53 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 |  | 2019-07-07 18:14 | 2019-07-07 18:35 |  |  |  | 0.014583 | 0 | 0 | 0 |  |  |  | LEFT | Line tripped on due to B-N fault. FD: 12.7 km from Shahjhnpr and 146 km from Lucknow. FC: 10.5kA at Shahjhnpr and 2.67kA at Lucknow. | NRPC | [5 empty] | 99.953
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.014583 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 169.729 | 87410.435 | 87369.3145 |  |  | 2
54 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- | 2019-07-29 07:32 | 2019-08-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 16:28 |  |  |  | LCSD | SD taken for Tower Erection & stringing work ( 842 to 843 & 849 to 850) ,due to construction of outer ring road by NHAI. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 16:28 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 |  |  | 2
55 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  | 2019-07-29 07:34 | 2019-08-01 | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 16:26 |  |  |  | LCSD | SD taken for Tower Erection & stringing work ( 842 to 843 & 849 to 850) ,due to construction of outer ring road by NHAI. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 16:26 | [6 empty] | 744 | 515 | 98.281 | 50614.715 | 50614.715 |  |  | 2
56 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- | 2019-07-29 13:00 | 2019-07-29 18:27 | -- | -- | -- | 0 | 0 | 0 | 0.22708 |  |  |  | OSFD | E/S/D availed by UPPCL for installation of new energy meter by replacing existing meter. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.22708 | [6 empty] | 744 | 515 | 41.743 | 21497.645 | 21497.645 |  |  | 2
57 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 73.826 | 38020.39 | 38020.39 |  |  | 2
58 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- | 2019-07-18 08:27 | 2019-07-18 20:03 | -- | -- | -- | 0 | 0 | 0 | 0.48333 |  |  |  | OSPD | S/D taken by UPPCL for maintenance work at their end | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.48333 | [6 empty] | 734.52 | 515 | 73.826 | 38020.39 | 38020.39 |  |  | 2
59 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 691 | 30.703 | 21215.773 | 21215.773 |  |  | 4
60 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 691 | 31.159 | 21530.869 | 21530.869 |  |  | 4
61 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 433 | 279.245 | 120913.085 | 120913.085 |  |  | 2
62 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 433 | 279.245 | 120913.085 | 120913.085 |  |  | 2
63 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 332 | 224 | 74368 | 74368 |  |  | 2
64 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 306 | 202 | 61812 | 61812 |  |  | 2
65 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 25.057 | 12904.355 | 12904.355 |  |  | 2
66 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 236 | 330.953 | 78104.908 | 78104.908 |  |  | 2
67 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 337 | 408.6 | 137698.2 | 137698.2 |  |  | 2
68 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 42.026 | 21643.39 | 21643.39 |  |  | 2
69 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 43.952 | 22635.28 | 22635.28 |  |  | 2
70 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 3.341 | 1720.615 | 1720.615 |  |  | 2
71 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 3.317 | 1708.255 | 1708.255 |  |  | 2
72 | NR340004 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 69.677 | 35883.655 | 35883.655 |  |  | 4
73 | NR340005 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 69.677 | 35883.655 | 35883.655 |  |  | 4
74 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 |  |  | 4
75 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 21.233 | 14587.071 | 14587.071 |  |  | 4
76 | NR340010 | 400KV LKO(765)-KANPUR(GIS)-I | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 159.7 | 82245.5 | 82245.5 |  |  | 2
77 | NR340013 | 400KV LKO(765)-KANPUR(GIS)-II | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 159.7 | 82245.5 | 82245.5 |  |  | 2
78 | NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 28.19 | 14517.85 | 14517.85 |  |  | 2
79 | NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 28.19 | 14517.85 | 14517.85 |  |  | 2
80 |  | 400KV Kanpur(GIS)-Allahabad-1 | 240.39 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 240.39 | 123800.85 | 123800.85 |  |  | 2
81 | NR340015 | 400KV Kanpur(GIS)-Allahabad-2 | 240.391 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 515 | 240.391 | 123801.365 | 123801.365 |  |  | 2
82 | NR340016 | 400KV ORAI-ORAI(UP)-I | 41.832 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 41.832 | 28738.584 | 28738.584 |  |  | 4
83 | NR340017 | 400KV ORAI-ORAI(UP)-II | 41.832 | NR3 | -- | 2019-07-10 09:38 | 2019-07-10 20:13 |  |  |  | 0.44097 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for AMP work of line side equipment. | NRPC | [5 empty] | 98.5775
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.44097 | 0 | 0 | 0 | [6 empty] | 744 | 687 | 41.832 | 28738.584 | 28329.7802 |  |  | 4
|  | 220kV Trans.Line | [17 empty] | NRPC | [5 empty] | 100
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 21.879 | 2888.028 | 2888.028 |  |  | 1
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 16.894 | 2230.008 | 2230.008 |  |  | 1
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- | 2019-07-26 22:41 | 2019-07-27 20:24 | -- | -- |  | 0 | 0 | 0 | 0.90486 |  |  |  | LPRD | Hand tripped on Power regulation as per NRLDC instruction due to avoid ICTs overloading at Allahabad | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.90486 | [6 empty] | 744 | 132 | 3 | 396 | 396 |  |  | 1
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | 2019-07-11 09:55 | 2019-07-11 11:40 |  |  |  | 0 | 0.072917 | 0 | 0 |  |  |  | OMSU | Tripped only from Rewa Road due to problem at Rewa Road(UP) end | NRPC | [5 empty] | 100
[6 empty] | 2019-07-28 16:10 | 2019-07-28 17:00 |  |  |  | 0 | 0.034722 | 0 | 0 |  |  |  | OMSU | Tripped only from Rewa road(UPPCL) end due to some problem at their end
[6 empty] | 2019-07-29 13:11 | 2019-07-29 16:39 |  |  |  | 0 | 0.14444 | 0 | 0 |  |  |  | OMSU | S/D taken by UPPCL for maintenance work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.25208 | 0 | 0 | [6 empty] | 744 | 132 | 3 | 396 | 396 |  |  | 1
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | 2019-07-26 07:30 | 2019-07-26 20:40 |  |  |  | 0.54861 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken for restringing of bottom conductor in line 1 due to low clearance at loc no 411 | NRPC | [5 empty] | 98.2303
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.54861 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 23621.6649 |  |  | 1
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | 2019-07-23 11:28 | 2019-07-23 16:00 |  |  |  | 0.18889 | 0 | 0 | 0 |  |  |  | OSFT | Taken Emergency SD for attending Hot Spot at Loc. No.-411 in Y-Ph jumper. | NRPC | [5 empty] | 98.0242
[6 empty] | 2019-07-26 10:31 | 2019-07-26 20:41 |  |  |  | 0.42361 | 0 | 0 | 0 |  |  |  | OSFT | Emergency s/d taken for restringing of bottom conductor in line 2 due to low clearance at loc no 411
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.6125 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 182.176 | 24047.232 | 23572.1052 |  |  | 1
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- | 2019-07-02 13:19 | 2019-07-02 14:29 | -- | -- |  | 0 | 0.048611 | 0 | 0 |  |  |  | OMSU | Tripped due to Y-B fault. Zone-4 (Reverse zone) protection operated at Bareilly (UP) end and Zone-2 operated at Dhauliganga end. Fault is in UPPCL switchyard. | NRPC | [5 empty] | 100
[6 empty] | 2019-07-24 16:23 | 2019-07-24 17:32 |  |  |  | 0 | 0 | 0.047917 | 0 |  |  |  | LNCC | E/S/D taken for removal of Tarpoline hanging on line which stuck on line due to heavy rain and thunderstorm.
[6 empty] | 2019-07-30 12:20 | 2019-07-30 16:28 |  |  |  | 0 | 0 | 0 | 0.17222 |  |  |  | OSPD | E/S/D taken by Dhauliganga (NHPC) to check gas pressure in 220kV GIS chamber.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.048611 | 0.047917 | 0.17222 | [6 empty] | 742.85 | 109 | 234.59 | 25570.31 | 25570.31 |  |  | 2
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- | 2019-07-30 12:06 | 2019-07-30 15:57 | -- | -- | -- | 0 | 0 | 0 | 0.16042 |  |  |  | OSPD | E/S/D taken by Dhauliganga (NHPC) to check gas pressure in 220kV GIS chamber. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.16042 | [6 empty] | 744 | 156 | 59.01 | 9205.56 | 9205.56 |  |  | 2
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- | 2019-07-11 00:25 | 2019-07-11 00:48 | -- | -- |  | 0 | 0.015972 | 0 | 0 |  |  |  | OMSU | Tripped on R-N fault. Fault details from Fatehpur (PG): Zone-2. M-1: F/D=12.2 km, F/C=3.18 kA. M-2: F/D=12.2 km, F/C=3.187 kA. Fault in UPPCL Jurisdiction | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.015972 | 0 | 0 | [6 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 |  |  | 1
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 5.284 | 692.204 | 692.204 |  |  | 1
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | 2019-07-12 14:26 | 2019-07-12 14:50 |  |  |  | 0 | 0.016667 | 0 | 0 |  |  |  | OMSU | Tripped due to R-N fault. DT received at Fatehpur.FD: Fatehpur- 65km, FC: Fatehpur- 2.4KA. Fault is under UPPCL jurisdiction | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.016667 | 0 | 0 | [6 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 |  |  | 1
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 6.17 | 808.27 | 808.27 |  |  | 1
13 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- | 2019-07-06 12:05 | 2019-07-06 12:53 |  |  | -- | 0 | 0.033333 | 0 | 0 |  |  |  | SBBU | Bus Bar protection operated at Mainpuri(UPPCL) end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.033333 | 0 | 0 | [6 empty] | 744 | 131 | 10.4 | 1362.4 | 1362.4 |  |  | 1
14 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 |  |  | 1
15 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)-1 | 13.701 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 13.701 | 1794.831 | 1794.831 |  |  | 1
16 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 14.86 | 1946.66 | 1946.66 |  |  | 1
17 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 143.553 | 18805.443 | 18805.443 |  |  | 1
18 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 143.553 | 18805.443 | 18805.443 |  |  | 1
19 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 144.63 | 18946.53 | 18946.53 |  |  | 1
20 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | 2019-07-17 04:21 | 2019-07-17 21:49 |  |  |  | 0 | 0 | 0 | 0.72778 |  |  |  | OSFD | Emergency s/d availed by Unchahar, NTPC for attending DC earth fault at their end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0.72778 | [6 empty] | 744 | 131 | 144.63 | 18946.53 | 18946.53 |  |  | 1
21 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | 2019-07-02 13:19 | 2019-07-02 14:19 |  |  |  | 0 | 0.041667 | 0 | 0 |  |  |  | OMSU | Tripped only from Bareilly (UP) end. Zone-4 (Reverse zone) protection operated at Bareilly (UP) end. Fault is in UPPCL switchyard. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.041667 | 0 | 0 | [6 empty] | 744 | 156 | 177.88 | 27749.28 | 27749.28 |  |  | 2
22 | NR320003 | 220KV RAIBRLY-CG CITY(UP) | 2 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 1.19 | 157.08 | 157.08 |  |  | 1
23 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP) | 2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 1.19 | 157.08 | 157.08
24 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 105.72 | 13955.04 | 13955.04 |  |  | 1
25 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | 2019-07-06 09:18 | 2019-07-06 10:14 |  |  |  | 0 | 0 | 0.038889 | 0 |  |  |  | GOVC | Tripped due to Over voltage at Tanapur end, Email received from Tanakpur end at 1039hrs. (Mail copy enclosed) | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.038889 | 0 | [6 empty] | 743.0667 | 132 | 106 | 13992 | 13992 |  |  | 1
26 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | 2019-07-06 09:18 | 2019-07-06 09:57 |  |  |  | 0 | 0 | 0.027083 | 0 |  |  |  | GOVC | Tripped due to Over voltage at Tanapur end, Email received from Tanakpur end at 0941hrs. (mail copy enclosed) | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0.027083 | 0 | [6 empty] | 743.35 | 132 | 42.55 | 5616.6 | 5616.6 |  |  | 1
27 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 0.92 | 121.44 | 121.44
28 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- | 2019-07-02 12:35 | 2019-07-02 19:20 | -- | -- |  | 0 | 0.28125 | 0 | 0 |  |  |  | OMSU | Tripped on Y-B fault. Details from Raibareily: F/D=30.36 KM, F/C: Iy=2.99 kA, Ib=3.41 kA. Details from unchahar: F/D=7.7 KM. Fault is in UPPCL Jurisdiction | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0.28125 | 0 | 0 | [6 empty] | 744 | 132 | 0.92 | 121.44 | 121.44 |  |  | 1
29 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 132 | 42.5 | 5610 | 5610 |  |  | 1
30 | NR320001 | 220KV KANPUR(PG) - RANIYA( UP)-1 | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 131 | 18.372 | 2406.732 | 2406.732 |  |  | 1
31 | NR320003 | 220kV AGRA(PG)-SIKANDARA(UP) | 55.858 | NR3 | -- | 2019-07-19 10:35 | 2019-07-19 19:15 | -- | -- |  | 0 | 0 | 0 | 0.36111 |  |  |  | OSPD | Line taken under S/D by Rajasthan (RRVUNL) for line maintenance | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.36111 | [6 empty] | 744 | 132 | 55.858 | 7373.256 | 7373.256 |  |  | 1
31 | NR320004 | 220kV AGRA(PG)-BHARATPUR(RRVPNL) | 55.858 | NR3 | -- | 2019-07-27 13:18 | 2019-07-27 15:46 | -- | -- |  | 0 | 0 | 0 | 0.10278 |  |  |  | OSFD | Emergency S/D availed by Rajasthan (RRVUNL) for line maintenance | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0.10278 | [6 empty] | 744 | 132 | 55.858 | 7373.256 | 7373.256 |  |  | 1
|  | 132 KV TRANS LINES |  |  | -- | [14 empty] | NRPC
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 | 58 | 2900 | 2900 | 100 |  | 1
129 | Lines | TOTAL FOR T/LS | [8 empty] | 1899-12-31 23:30 | 1899-12-31 05:38 | 0.11389 | 1900-04-28 01:32 | [5 empty] | NRPC |  |  | 16215.198 | 9580362.112 | 9577994.4774 | 99.9753 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 99.9716 | % (HVDC) | 99.5827 | [5 empty] | NRPC
|  | 765/400 KV ICT'S |  |  | -- | [14 empty] | NRPC |  | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | 2019-07-27 12:18 | 2019-07-27 14:26 |  |  |  | 0.088889 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed to attend hot spot in Y Ph CT pad | NRPC | [5 empty] | 99.7133
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.088889 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1495.6989
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
17 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
18 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
19 | NR3ICT701 | 765/400KV ICT-I Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
20 | NR3ICT702 | 765/400KV ICT-II Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1500
21 | NR3ICT05 | 1000MVA ICT-1 ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1000 |  | 1000 | 1000
22 | NR3ICT06 | 1000MVA ICT-II ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1000 |  | 1000 | 1000
|  | 400/220 KV ICT'S |  | NR3 | -- | [14 empty] | NRPC
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 |  | 2019-07-07 07:51 | 2019-08-01 |  |  | 24.6667 | 0 | 0 | 0 | 0 | 120 | N | -95.3333 | SEFT | ICT-III failed. Initiation of fault is y Phase Winding. | NRPC | 744 | 315 |  | 315 | 315 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | 2019-07-11 10:19 | 2019-07-11 19:52 |  |  |  | 0.39792 | 0 | 0 | 0 |  |  |  | OSPT | S/D availed for attending Tertiary Insulation work and Oil leakage in ICT. | NRPC | 744 | 315 |  | 315 | 310.9567 | 98.7164
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0.39792 | 0 | 0 | 0 | [6 empty] | 744 | 1500 |  | 1500 | 1480.746
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 500 |  | 500 | 500
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 315 |  | 315 | 315
15 | NR3ICT02 | 500MVA ICT-III MAINPURI | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
16 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
17 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 500 |  | 500 | 500 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
18 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
19 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 315 |  | 315 | 315 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
|  | 220/132 KV ICT'S |  | NR3 | -- | [14 empty] | NRPC
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 100 |  | 100 | 100 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100
4 | NR3ICT04 | 220/132KV ICT-II RAIBAREILLY | 200 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 200 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100
46 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 0.48681 | 0 | 0 | 0 | [5 empty] | NRPC |  | 31425 |  | 31425 | 31397.4015 | 99.9122 | %
|  | HVDC RIHAND-DADRI |  |  | -- | [14 empty] | NRPC |  | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2019-07-07 07:27 | 2019-07-07 14:55 |  |  |  | 0.31111 | 0 | 0 | 0 |  |  |  | OSPT | S/D taken For replacement of faulty insulator strings. | NRPC | [5 empty] | 98.9964
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.31111 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 605115.5914
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | 2019-07-31 10:35 | 2019-07-31 12:46 |  |  |  | 0.090972 | 0 | 0 | 0 |  |  |  | OSFT | E/S/D taken for replacement of WTI of Pole 2 Y phase Converter Transformer. | NRPC | [5 empty] | 99.7065
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.090972 | 0 | 0 | 0 | [6 empty] | 744 | 750 | 815 | 611250 | 609456.2332
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1250 | 789.786 | 987232.5 | 987232.5
5 | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2019-07-01 17:14 | 2019-07-01 18:16 |  |  |  | 0.043056 | 0 | 0 | 0 |  |  |  | LEFT | Tripped only at BNC end due to line fault between APD and BNC section | NRPC | [5 empty] | 99.2787
[6 empty] | 2019-07-19 12:19 | 2019-07-19 13:44 |  |  |  | 0.059028 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to tripping of line-1 on earth fault. FD: Agra- 227.06km, APD-1108km.
[6 empty] | 2019-07-19 15:19 | 2019-07-19 18:14 |  |  |  | 0.12153 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for rectification of broken jumper at loc no 3805
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.22361 | 0 | 0 | 0 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2573303.2258
6 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2592000
7 | NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III | 789.786 | NR3 | -- | 2019-07-09 12:17 | 2019-07-09 14:13 |  |  |  | 0.080556 | 0 | 0 | 0 |  |  |  | SRET | Tripped only from Alipurduar (APD) end due to OLTC-2 Gas relay operated at APD end. | NRPC | [5 empty] | 99.1891
[6 empty] | 2019-07-19 12:19 | 2019-07-19 13:46 |  |  |  | 0.060417 | 0 | 0 | 0 |  |  |  | LEFT | Tripped due to tripping of line-1 on earth fault. FD: Agra- 227.06km, APD-1108km.
[6 empty] | 2019-07-19 15:22 | 2019-07-19 18:01 |  |  |  | 0.11042 | 0 | 0 | 0 |  |  |  | OSFT | Emergency S/D availed for rectification of broken jumper at loc no 3805
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.25139 | 0 | 0 | 0 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2570980.6452
8 | NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV | 789.786 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 1500 | 1728 | 2592000 | 2592000
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0.87708 | 0 | 0 | 0 | [5 empty] | NRPC |  |  | 10121.572 | 13564965 | 13517320.6956 | 99.6488 | %
|  | HVDC BTB VINDH |  |  | -- | [14 empty] | NRPC |  | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2019-07-16 08:44 | 2019-07-16 20:19 |  |  |  | 0.48264 | 0 | 0 | 0 |  |  |  | OSPT | Emergency S/D taken by Vindhaychal for replacement of faulty thyristor and other snubber circuit components. | NRPC | [5 empty] | 98.2191
[6 empty] | 2019-07-21 12:43 | 2019-07-21 15:26 |  |  |  | 0 | 0.11319 | 0 | 0 |  |  |  | OMSU | Tripped due to DC over current protection operated due to disturbance in western grid.
[6 empty] | 2019-07-24 15:03 | 2019-07-24 16:43 |  |  |  | 0.069444 | 0 | 0 | 0 |  |  |  | OMST | Tripping due to DC over current protection operated.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0.55208 | 0.11319 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 245.5477
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | 2019-07-21 12:43 | 2019-07-21 14:36 |  |  |  | 0 | 0.078472 | 0 | 0 |  |  |  | OMSU | Tripped due to tripping of 400KV VSTPS HVDC FEEDER#2 from VSTPS end | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0.078472 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 0.55208 | 0.19167 | 0 | 0 | [5 empty] | NRPC |  |  |  | 500 | 495.5477 | 99.1095 | %
3 | NEDCB01 | Sasaram HVDC B/B BLOCK-I | 250 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250
|  | HVDC BTB TOTAL |  |  | -- | [5 empty] | 0.55208 | 0.19167 | 0 | 0 | [5 empty] | NRPC |  | RC
|  | SVC, KANPUR |  |  | -- | [14 empty] | NRPC |  | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 250 |  | 250 | 250
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 280 |  | 280 | 280
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC |  |  |  | 530 | 530 | 100 | %
|  | Bus & Switch Line Reactor |  |  | -- | [14 empty] | NRPC |  | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- | 2019-07-01 | 2019-07-04 15:29 | -- | -- | -- | 0 | 0 | 0 | 1900-01-02 15:29 |  |  |  | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 755 /760kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-11 21:06 | 2019-07-12 07:48 |  |  |  | 0 | 0 | 0 | 0.44583 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=754kV
[6 empty] | 2019-07-17 19:38 | 2019-07-24 18:26 |  |  |  | 0 | 0 | 0 | 1900-01-05 22:48 |  |  |  | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Ballia = 751/763kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-10 00:59 | [6 empty] | 744 | 240 |  | 240 | 240
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- | 2019-07-03 21:09 | 2019-07-07 09:43 | -- | -- |  | 0 | 0 | 0 | 1900-01-02 12:34 |  |  |  | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 758 /765kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-30 20:58 | 2019-08-01 |  |  |  | 0 | 0 | 0 | 1899-12-31 03:02 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=738kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-03 15:36 | [6 empty] | 744 | 240 |  | 240 | 240
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80
14 | NR1BRT44 | 2X50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 100 |  | 100 | 100
15 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 50 |  | 50 | 50
16 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
17 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
18 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330
19 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
20 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
21 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 80 |  | 80 | 80
22 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
23 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
24 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | 2019-07-03 20:58 | 2019-07-04 15:26 |  |  |  | 0 | 0 | 0 | 0.76944 |  |  |  | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 754 /763kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-17 19:32 | 2019-07-24 07:50 |  |  |  | 0 | 0 | 0 | 1900-01-05 12:18 |  |  |  | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. LKO 765 = 783/784kV
[6 empty] | 2019-07-30 22:25 | 2019-07-31 06:53 |  |  |  | 0 | 0 | 0 | 0.35278 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV
[6 empty] | 2019-07-31 21:49 | 2019-08-01 |  |  |  | 0 | 0 | 0 | 0.090972 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=746/763kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 1900-01-06 17:25 | [6 empty] | 744 | 240 |  | 240 | 240
25 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
26 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
27 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
28 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
29 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
30 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
31 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
32 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
33 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
34 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
35 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 330 |  | 330 | 330 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
36 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
37 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
38 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
39 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
40 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
41 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
42 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
43 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 744 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125
44 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | 2019-07-01 | 2019-07-03 08:17 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:17 |  |  |  | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 750/765kV | NRPC | [5 empty] | 100
[6 empty] | 2019-07-30 22:17 | 2019-07-31 06:51 |  |  |  | 0 | 0 | 0 | 0.35694 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=745kV
[6 empty] | 2019-07-31 21:49 | 2019-08-01 |  |  |  | 0 | 0 | 0 | 0.090972 |  |  |  | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=745/764kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 1900-01-01 19:02 | [6 empty] | 744 | 240 |  | 240 | 240
45 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330
46 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330
47 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 |  | %
48 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS) | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 125 |  | 125 | 125 |  | %
49 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS) | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 240 |  | 240 | 240 |  | %
50 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 |  | %
51 | NR3BRT08 | 330MVAR B/Reactor-II ALIGARH | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 |  | %
52 | NR3BRT07 | 63MVAR B/Reactor-II SOHAWAL | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 744 | 330 |  | 330 | 330 |  | %
53 | NR1BRT06 | 80MVAR B/Reactor BIHARSHARIF | 80 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
54 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I | 50 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
55 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
56 | NR1SRT04 | 50MVAR S/R BARLLY - MND Ckt-I | 50 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
57 | NR1SRT05 | 50MVAR S/R BARLLY - MND Ckt-II | 50 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
58 | NR1SRT24 | 80MVAR S/R GORAKH- Barh line-I | 80 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
59 | NR1SRT25 | 80MVAR S/R GORAKH- Barh line-II | 80 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
60 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS) | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
61 | NR3SRT01 | 240MVAR S/R VARANASI - KNP(GIS) ckt-I | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
62 | NR3SRT02 | 240MVAR S/R VARANASI - KNP(GIS) ckt-II | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
63 | NR3SRT03 | 330MVAR S/R KNP(GIS) -JHATIKRA ckt-1 | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
64 | NR3BRT05 | 125MVAR B/Reactor-I KANPUR | 125 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
65 | NR3BRT06 | 330MVAR B/Reactor-III VARANASI-765 | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
66 | NR3SLRT06 | ALIGARH 330MVAR Switachable L/R KANPUR | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
67 | NR3LRT07 | ORAI 240MVAR Non Switchable L/R ALIGARH-II | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
68 | NR3LRT08 | ALIGARH 240MVAR Non Switchable L/R ORAI-II | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
69 | NR3BRT10 | 330MVAR B/R-I ORAI | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
70 | NR3LRT09 | ORAI 330MVAR Non-Switchable L/R JABALPUR-I | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
71 | NR3LRT10 | ORAI 330MVAR Non-Switchable L/R JABALPUR-II | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
72 | NR3BRT11 | 330MVAR Bus Reactor-II ORAI | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
73 | NR3LRT11 | ORAI 240MVAR Non-Switchable L/R SATNA | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
74 | NR3LRT12 | ORAI 240MVAR Non-Switchable L/R ALIGARH-I | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
75 | NR3LRT13 | ALIGARH 240MVAR Non-Switchable L/R ORAI-I | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
|  | TOTAL FOR Reactor |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [7 empty] | 10683.4 |  | 10683.4 | 10683.4 | 100
Formulas:
ISTS Licensee = IF(RIGHT([Classification/ Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
ISTS Licensee = SUM([ISTS Licensee, row above]:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Classification/ Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM([OTHERS, row above]:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Classification/ Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM([Hrs:Min, row above]:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Classification/ Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM([Deemed Available, row above]:[Deemed Available, row above])
Note on C11: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C13: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C38: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C40: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C42: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C44: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C46: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C133: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C135: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C229: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C231: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C317: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C319: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Master (hidden)
POWER GRID CORPORATION OF INDIA LTD.
DOC No: NR-III-CPCC- Total
MONTH –August LINE- ICT OUTAGE DETAILS |  | JULY'19 Total
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | NRLDC CODE | Classification- Category Code | REASON OF OUTAGE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint- Natural calamity- Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  | Code
|  | ELEMENT NAME Total |  |  | 1900-01-27 16:34 | 1899-12-31 10:14 | 0.11389 | 1900-05-24 06:34
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 11 | 12
|  | 3 Total |  |  | 6 | 7 | 8 | 9
NR1DCB01 | 307091 | VINDH HVDC B/B BLOCK-I | 2019-07-16 08:44 | 2019-07-16 20:19 | 0.48264 | 0 | 0 | 0 | N-1097 | OSPT | Emergency S/D taken by Vindhaychal for replacement of faulty thyristor and other snubber circuit components.
NR1DCB01 | 307116 | VINDH HVDC B/B BLOCK-I | 2019-07-21 12:43 | 2019-07-21 15:26 | 0 | 0.11319 | 0 | 0 | **** | OMSU | Tripped due to DC over current protection operated due to disturbance in western grid.
NR1DCB01 | 307128 | VINDH HVDC B/B BLOCK-I | 2019-07-24 15:03 | 2019-07-24 16:43 | 0.069444 | 0 | 0 | 0 | **** | OMST | Tripping due to DC over current protection operated.
NR1DCB02 | 307117 | VINDH HVDC B/B BLOCK-II | 2019-07-21 12:43 | 2019-07-21 14:36 | 0 | 0.078472 | 0 | 0 | **** | OMSU | Tripped due to tripping of 400KV VSTPS HVDC FEEDER#2 from VSTPS end
NRNEDCP03 | 307050 | 800KV HVDC AGRA-APD POLE-III | 2019-07-09 12:17 | 2019-07-09 14:13 | 0.080556 | 0 | 0 | 0 | **** | SRET | Tripped only from Alipurduar (APD) end due to OLTC-2 Gas relay operated at APD end.
NRNEDCP03 | 307107 | 800KV HVDC AGRA-APD POLE-III | 2019-07-19 12:19 | 2019-07-19 13:46 | 0.060417 | 0 | 0 | 0 | **** | LEFT | Tripped due to tripping of line-1 on earth fault. FD: Agra- 227.06km, APD-1108km.
NRNEDCP03 | 307109 | 800KV HVDC AGRA-APD POLE-III | 2019-07-19 15:22 | 2019-07-19 18:01 | 0.11042 | 0 | 0 | 0 | N-1371 | OSFT | Emergency S/D availed for rectification of broken jumper at loc no 3805
NRNEDCP01 | 307001 | 800KV HVDC AGRA-BNC POLE-I | 2019-07-01 17:14 | 2019-07-01 18:16 | 0.043056 | 0 | 0 | 0 | **** | LEFT | Tripped only at BNC end due to line fault between APD and BNC section
NRNEDCP01 | 307106 | 800KV HVDC AGRA-BNC POLE-I | 2019-07-19 12:19 | 2019-07-19 13:44 | 0.059028 | 0 | 0 | 0 | **** | LEFT | Tripped due to tripping of line-1 on earth fault. FD: Agra- 227.06km, APD-1108km.
NRNEDCP01 | 307108 | 800KV HVDC AGRA-BNC POLE-I | 2019-07-19 15:19 | 2019-07-19 18:14 | 0.12153 | 0 | 0 | 0 | N-1370 | OSFT | Emergency S/D availed for rectification of broken jumper at loc no 3805
NR1DCP01 | 307035 | 500KV HVDC R-D POLE-I | 2019-07-07 07:27 | 2019-07-07 14:55 | 0.31111 | 0 | 0 | 0 | N-442 | OSPT | S/D taken For replacement of faulty insulator strings.
NR1DCP02 | 307165 | 500KV HVDC R-D POLE-II | 2019-07-31 10:35 | 2019-07-31 12:46 | 0.090972 | 0 | 0 | 0 | N-2184 | OSFT | E/S/D taken for replacement of WTI of Pole 2 Y phase Converter Transformer.
NR176502 | 307007 | 765KV AGRA-FATEHPUR-I | 2019-07-02 06:43 | 2019-07-02 15:37 | 0 | 0 | 0 | 0.37083 | N-87 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-801kV
NR176502 | 307034 | 765KV AGRA-FATEHPUR-I | 2019-07-07 06:26 | 2019-07-07 20:49 | 0 | 0 | 0 | 0.59931 | N-438 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=797kV
NR176502 | 307044 | 765KV AGRA-FATEHPUR-I | 2019-07-09 02:06 | 2019-07-10 06:26 | 0 | 0 | 0 | 1899-12-31 04:20 | N-564 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=799kV
NR176502 | 307057 | 765KV AGRA-FATEHPUR-I | 2019-07-10 08:07 | 2019-07-10 09:54 | 0 | 0 | 0 | 0.074306 | N-651 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
NR176502 | 307075 | 765KV AGRA-FATEHPUR-I | 2019-07-13 08:04 | 2019-07-13 22:54 | 0 | 0 | 0 | 0.61806 | N-879 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=795kV
NR176502 | 307087 | 765KV AGRA-FATEHPUR-I | 2019-07-15 07:11 | 2019-07-19 10:45 | 0 | 0 | 0 | 1900-01-03 03:34 | N-1013 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
NR176502 | 307119 | 765KV AGRA-FATEHPUR-I | 2019-07-23 06:48 | 2019-07-23 10:33 | 0 | 0 | 0 | 0.15625 | N-1582 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR176507 | 306167 | 765KV AGRA-FATEHPUR-II | 2019-07-01 | 2019-07-01 14:24 | 0 | 0 | 0 | 0.6 | N-2142 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-801kV
NR176507 | 307025 | 765KV AGRA-FATEHPUR-II | 2019-07-06 03:37 | 2019-07-06 21:42 | 0 | 0 | 0 | 0.75347 | N-375 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792kV
NR176507 | 307040 | 765KV AGRA-FATEHPUR-II | 2019-07-08 04:08 | 2019-07-08 21:07 | 0 | 0 | 0 | 0.70764 | N-500 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV
NR176507 | 307053 | 765KV AGRA-FATEHPUR-II | 2019-07-10 03:22 | 2019-07-12 19:38 | 0 | 0 | 0 | 1900-01-01 16:16 | N-635 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
NR176507 | 307080 | 765KV AGRA-FATEHPUR-II | 2019-07-14 07:45 | 2019-07-14 21:30 | 0 | 0 | 0 | 0.57292 | N-954 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
NR176507 | 307112 | 765KV AGRA-FATEHPUR-II | 2019-07-20 06:51 | 2019-07-21 22:32 | 0 | 0 | 0 | 1899-12-31 15:41 | N-1397 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=427kV
NR176507 | 307129 | 765KV AGRA-FATEHPUR-II | 2019-07-24 16:09 | 2019-07-24 16:20 | 0.0076389 | 0 | 0 | 0 | **** | LEFT | Line tripped end due to R-N fault. Fatehpur Details: M1-F/D- 201.7km,F/C- 3.01KA, M2-F/D-- n/a, F/C- 2.7KA. Agra Details: M1- F/D--108.5km,F/C-6.17KA, M2-F/D-109.1km, F/C-6.12KA.
NR176507 | 307124 | 765KV AGRA-FATEHPUR-II | 2019-07-24 16:20 | 2019-07-28 20:11 | 0 | 0 | 0 | 1900-01-03 03:51 | **** | LVRD | Line kept open on voltage regulation s per NRLDC instruction. In this regards mail sent at 1733hrs dtd 24.07.19 (Mail copy enclosed)
NR376504 | 307143 | 765KV ALIGARH-JHATIKARA | 2019-07-27 04:01 | 2019-07-27 10:12 | 0 | 0 | 0 | 0.25764 | N-1878 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=801kV
NR376505 | 307018 | 765KV KANPUR(GIS)-ALIGARH | 2019-07-04 17:22 | 2019-07-06 14:02 | 0 | 0 | 0 | 1899-12-31 20:40 | N-286 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh-799kV
NR376505 | 307045 | 765KV KANPUR(GIS)-ALIGARH | 2019-07-09 04:51 | 2019-07-09 20:25 | 0 | 0 | 0 | 0.64861 | N-571 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=800kV
NR376505 | 307055 | 765KV KANPUR(GIS)-ALIGARH | 2019-07-10 04:09 | 2019-07-10 15:38 | 0 | 0 | 0 | 0.47847 | N-640 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=800kV
NR376505 | 307083 | 765KV KANPUR(GIS)-ALIGARH | 2019-07-14 09:58 | 2019-07-14 19:47 | 0 | 0 | 0 | 0.40903 | N-966 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Knp=798kV
NR376505 | 307090 | 765KV KANPUR(GIS)-ALIGARH | 2019-07-15 16:02 | 2019-07-16 19:48 | 0 | 0 | 0 | 1899-12-31 03:46 | N-1047 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=804kV
NR140002 | 307011 | 400KV AGRA-AGRA(UP)-II | 2019-07-02 16:53 | 2019-07-02 19:44 | 0 | 0 | 0 | 0.11875 | N-126 | OSFD | Emergency S/D taken by UPPCL for R-ph dropper tightening at Agra (UP) end.
NR140003 | 307005 | 400KV AGRA-AURAIYA-I | 2019-07-02 06:15 | 2019-07-02 21:28 | 0 | 0 | 0 | 0.63403 | N-84 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-432kV
NR140003 | 307012 | 400KV AGRA-AURAIYA-I | 2019-07-03 08:17 | 2019-07-07 19:55 | 0 | 0 | 0 | 1900-01-03 11:38 | N-167 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-431kV
NR140003 | 307041 | 400KV AGRA-AURAIYA-I | 2019-07-08 07:56 | 2019-07-08 21:11 | 0 | 0 | 0 | 0.55208 | N-506 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV
NR140003 | 307043 | 400KV AGRA-AURAIYA-I | 2019-07-09 01:55 | 2019-07-10 09:23 | 0 | 0 | 0 | 1899-12-31 07:28 | N-562 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-431kV
NR140003 | 307078 | 400KV AGRA-AURAIYA-I | 2019-07-14 06:08 | 2019-07-14 19:59 | 0 | 0 | 0 | 0.57708 | N-946 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140003 | 307113 | 400KV AGRA-AURAIYA-I | 2019-07-20 18:46 | 2019-07-22 21:10 | 0 | 0 | 0 | 1900-01-01 02:24 | N-1432 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
NR140003 | 307126 | 400KV AGRA-AURAIYA-I | 2019-07-24 16:45 | 2019-07-28 19:54 | 0 | 0 | 0 | 1900-01-03 03:09 | N-1684 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
NR140004 | 307054 | 400KV AGRA-AURAIYA-II | 2019-07-10 04:06 | 2019-07-13 22:45 | 0 | 0 | 0 | 1900-01-02 18:39 | N-639 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-435kV
NR140004 | 307088 | 400KV AGRA-AURAIYA-II | 2019-07-15 15:54 | 2019-07-20 10:22 | 0 | 0 | 0 | 1900-01-03 18:28 | N-1044 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140004 | 307118 | 400KV AGRA-AURAIYA-II | 2019-07-23 05:41 | 2019-07-23 14:40 | 0 | 0 | 0 | 0.37431 | N-1579 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
NR140008 | 307100 | 400KV AGRA-BHIWADI-I | 2019-07-18 03:35 | 2019-07-19 14:41 | 0 | 0 | 0 | 1899-12-31 11:06 | N-1236 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140008 | 307114 | 400KV AGRA-BHIWADI-I | 2019-07-21 06:06 | 2019-07-22 09:43 | 0 | 0 | 0 | 1899-12-31 03:37 | N-1448 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=432 kV
NR140008 | 307136 | 400KV AGRA-BHIWADI-I | 2019-07-26 02:07 | 2019-07-29 15:48 | 0 | 0 | 0 | 1900-01-02 13:41 | N-1789 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140009 | 307017 | 400KV AGRA-BHIWADI-II | 2019-07-04 17:16 | 2019-07-06 20:26 | 0 | 0 | 0 | 1900-01-01 03:10 | N-284 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV
NR140009 | 307036 | 400KV AGRA-BHIWADI-II | 2019-07-07 10:04 | 2019-07-07 19:43 | 0 | 0 | 0 | 0.40208 | N-456 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-430kV
NR140009 | 307056 | 400KV AGRA-BHIWADI-II | 2019-07-10 08:03 | 2019-07-11 08:39 | 0 | 0 | 0 | 1899-12-31 00:36 | N-650 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-434kV
NR140009 | 307081 | 400KV AGRA-BHIWADI-II | 2019-07-14 09:12 | 2019-07-14 19:54 | 0 | 0 | 0 | 0.44583 | N-960 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=800kV
NR140009 | 307089 | 400KV AGRA-BHIWADI-II | 2019-07-15 15:57 | 2019-07-16 15:08 | 0 | 0 | 0 | 0.96597 | N-1044 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140009 | 307132 | 400KV AGRA-BHIWADI-II | 2019-07-25 04:08 | 2019-07-25 20:09 | 0 | 0 | 0 | 0.66736 | N-1718 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=428kV
NR140010 | 307042 | 400KV AGRA-BLBGRH | 2019-07-08 14:18 | 2019-07-08 22:15 | 0 | 0 | 0 | 0.33125 | N-528 | LCSD | S/D taken for replacement of disc insulator with Polymer Insulator.
NR140010 | 307065 | 400KV AGRA-BLBGRH | 2019-07-11 08:54 | 2019-07-11 14:08 | 0.21806 | 0 | 0 | 0 | N-728 | OSFT | S/D taken to attend hot spot at Ballabhgarh
NR340006 | 307152 | 400KV AGRA-FATEHABD(UP)-I | 2019-07-29 07:53 | 2019-07-29 20:13 | 0 | 0 | 0 | 0.51389 | N-2028 | OSPD | S/D taken by UPPCL for maintenance work
NR340006 | 307155 | 400KV AGRA-FATEHABD(UP)-I | 2019-07-30 08:14 | 2019-07-30 19:32 | 0 | 0 | 0 | 0.47083 | N-2101 | OSPD | S/D taken by UPPCL for maintenance work
NR340006 | 307164 | 400KV AGRA-FATEHABD(UP)-I | 2019-07-31 08:34 | 2019-07-31 18:50 | 0 | 0 | 0 | 0.42778 | N-2172 | OSPD | S/D taken by UPPCL for maintenance work
NR140122 | 306120 | 400KV ALLD-FATEHPUR-I | 2019-07-01 | 2019-07-04 21:27 | 0 | 0 | 0 | 1900-01-02 21:27 | N-1607 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=428kV
NR140122 | 307064 | 400KV ALLD-FATEHPUR-I | 2019-07-11 04:14 | 2019-07-17 22:50 | 0 | 0 | 0 | 1900-01-05 18:36 | N-713 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=429kV
NR140122 | 307127 | 400KV ALLD-FATEHPUR-I | 2019-07-24 18:17 | 2019-07-25 20:35 | 0 | 0 | 0 | 1899-12-31 02:18 | N-1696 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur=427kV
NR140123 | 307019 | 400KV ALLD-FATEHPUR-II | 2019-07-05 08:39 | 2019-07-11 15:55 | 0 | 0 | 0 | 1900-01-05 07:16 | N-323 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=424kV
NR140123 | 307101 | 400KV ALLD-FATEHPUR-II | 2019-07-18 03:50 | 2019-07-20 10:25 | 0 | 0 | 0 | 1900-01-01 06:35 | N-1237 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=429kV
NR140123 | 307137 | 400KV ALLD-FATEHPUR-II | 2019-07-26 03:07 | 2019-07-31 01:00 | 0 | 0 | 0 | 1900-01-03 21:53 | N-1791 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=426kV
NR140012 | 307049 | 400KV ALLD-KNP-II | 2019-07-09 08:10 | 2019-07-11 22:53 | 0 | 0 | 0 | 1900-01-01 14:43 | N-584 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=431 kV
NR140012 | 307135 | 400KV ALLD-KNP-II | 2019-07-25 07:19 | 2019-07-30 22:14 | 0 | 0 | 0 | 1900-01-04 14:55 | N-1725 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. ALD=428kV
NR140019 | 307060 | 400KV BALIA-MAU-I | 2019-07-10 09:48 | 2019-07-10 12:18 | 0 | 0.10417 | 0 | 0 | **** | OMSU | Tripped only from Mau (UP) end due to multiple trippings at Mau end (400kV Azamgarh - Mau line). Fault in UPPCL Jurisdiction
NR140020 | 307061 | 400KV BALIA-MAU-II | 2019-07-10 09:48 | 2019-07-10 12:19 | 0 | 0.10486 | 0 | 0 | **** | OMSU | Tripped only from Mau (UP) end due to multiple trippings at Mau end (400kV Azamgarh - Mau line). Fault in UPPCL Jurisdiction
NR140020 | 307095 | 400KV BALIA-MAU-II | 2019-07-17 07:38 | 2019-07-17 08:31 | 0 | 0.036806 | 0 | 0 | **** | OMSU | Tripped only from Mau (UP) end due to failure of R-ph trip circuit of Circuit Breaker at Mau (UP) end. Fault in UPPCL Jurisdiction
NR140025 | 307092 | 400KV BAREILLY-LKO(UP) | 2019-07-16 11:21 | 2019-07-16 13:54 | 0.10625 | 0 | 0 | 0 | N-1109 | OSPT | Emergency S/D taken for attending buchholz alarm in NGR.
NR140025 | 307120 | 400KV BAREILLY-LKO(UP) | 2019-07-23 10:20 | 2019-07-23 10:24 | 0.0027778 | 0 | 0 | 0 | N-1598 | OSPT | SD taken to take out LKO (UP) line reactor (nonswitchable) from service for AMP and Reactor FDS measurement at Bareilly.
NR140025 | 307121 | 400KV BAREILLY-LKO(UP) | 2019-07-23 18:24 | 2019-07-23 18:29 | 0.0034722 | 0 | 0 | 0 | N-1617 | OSPT | SD taken to take line reactor(nonswitchable) in service after AMP and Reactor FDS measurement at Bareilly.
NR140158 | 307157 | 400KV BARLY(765)-KASHIPUR-I | 2019-07-30 12:06 | 2019-07-30 13:08 | 0 | 0.043056 | 0 | 0 | **** | OMSU | Tripped on R-N fault at Kashipur, LBB of 400kV Bus-II operated due to which main breaker of Bareilly -2 opened at Kashipur end & also Moradabad Tie CB opened, 315MVA ICT-I & II Main CB tripped and DT received at Bareilly end.
NR140037 | 307058 | 400KV BLBGRH-MAINPURI-I | 2019-07-10 08:50 | 2019-07-10 19:46 | 0 | 0 | 0 | 0.45556 | N-652 | LCSD | S/D taken for replacement of disc insulator with Polymer Insulator.
NR140038 | 307066 | 400KV BLBGRH-MAINPURI-II | 2019-07-11 09:26 | 2019-07-11 19:51 | 0 | 0 | 0 | 0.43403 | N-732 | LCSD | S/D taken for OPGW installation work
NR140038 | 307077 | 400KV BLBGRH-MAINPURI-II | 2019-07-13 08:12 | 2019-07-13 13:31 | 0 | 0 | 0 | 0.22153 | N-881 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Mainpuri= 422kV
NR140124 | 307076 | 400KV FATEHPUR-MAINPURI-I | 2019-07-13 08:05 | 2019-07-13 20:08 | 0 | 0 | 0 | 0.50208 | N-881 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur= 428kV
NR140124 | 307079 | 400KV FATEHPUR-MAINPURI-I | 2019-07-14 06:09 | 2019-07-17 20:47 | 0 | 0 | 0 | 1900-01-02 14:38 | N-946 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur= 427kV
NR140124 | 307110 | 400KV FATEHPUR-MAINPURI-I | 2019-07-19 23:33 | 2019-07-20 00:08 | 0.024306 | 0 | 0 | 0 | **** | OSFT | Emergency hand tripped due to heavy sparking in B Ph of line isolator at Mainpuri end
NR140125 | 307027 | 400KV FATEHPUR-MAINPURI-II | 2019-07-06 08:22 | 2019-07-07 00:30 | 0 | 0 | 0 | 0.67222 | N-389 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction.Mainpuri = 419kV
NR140125 | 307102 | 400KV FATEHPUR-MAINPURI-II | 2019-07-18 03:56 | 2019-07-20 10:15 | 0 | 0 | 0 | 1900-01-01 06:19 | N-1237 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Fatehpur= 427kV
NR140047 | 307069 | 400KV GORAKH-GORAKH-II | 2019-07-11 12:30 | 2019-07-11 18:02 | 0 | 0.23056 | 0 | 0 | **** | OMSU | Tripped only from UP end due to problem at Gorakhpur(UP) end
NR140053 | 307016 | 400KV KNP-AURAIYA-I | 2019-07-04 17:08 | 2019-07-07 19:59 | 0 | 0 | 0 | 1900-01-02 02:51 | N-281 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. KNP-424kV
NR140053 | 307048 | 400KV KNP-AURAIYA-I | 2019-07-09 07:11 | 2019-07-13 23:03 | 0 | 0 | 0 | 1900-01-03 15:52 | N-578 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Kanpur=420 kV
NR140055 | 307156 | 400KV KNP-BLBGARH-I | 2019-07-30 09:12 | 2019-07-30 23:25 | 0 | 0 | 0 | 0.59236 | N-2104 | LCSD | S/D taken for replacement of disk insulator with polymer insulator.
NR140055 | 307166 | 400KV KNP-BLBGARH-I | 2019-07-31 13:16 | 2019-07-31 16:43 | 0 | 0 | 0 | 0.14375 | N-2191 | LCSD | S/D taken for replacement of disk insulator with polymer insulator.
NR140056 | 307082 | 400KV KNP-BLBGARH-II | 2019-07-14 09:54 | 2019-07-14 20:53 | 0 | 0 | 0 | 0.45764 | N-965 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Knp=428kV
NR140071 | 307084 | 400KV LUCKNOW-GORAKH-IV | 2019-07-14 10:11 | 2019-07-14 21:03 | 0 | 0 | 0 | 0.45278 | N-970 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lko=428kV
NR140072 | 307063 | 400KV LUCKNOW-LKO(UP) | 2019-07-11 03:35 | 2019-07-11 04:12 | 0 | 0.025694 | 0 | 0 | **** | OMSU | Tripped only from Lucknow (PG) end due to DT received from Lucknow (UP) end. Fault in UPPCL Jurisdiction
NR140153 | 307039 | 400KV LUCKNOW-SHAHJHNPR-II | 2019-07-07 18:14 | 2019-07-07 18:35 | 0.014583 | 0 | 0 | 0 | **** | LEFT | Line tripped on due to B-N fault. FD: 12.7 km from Shahjhnpr and 146 km from Lucknow. FC: 10.5kA at Shahjhnpr and 2.67kA at Lucknow.
NR140141 | 307150 | 400KV LUCKNOW-SOHAWAL-I | 2019-07-29 07:32 | 2019-08-01 | 0 | 0 | 0 | 1900-01-01 16:28 | N-2024 | LCSD | SD taken for Tower Erection & stringing work ( 842 to 843 & 849 to 850) ,due to construction of outer ring road by NHAI.
NR140121 | 307151 | 400KV LUCKNOW-SOHAWAL-II | 2019-07-29 07:34 | 2019-08-01 | 0 | 0 | 0 | 1900-01-01 16:26 | N-2025 | LCSD | SD taken for Tower Erection & stringing work ( 842 to 843 & 849 to 850) ,due to construction of outer ring road by NHAI.
NR140073 | 307153 | 400KV LUCKNOW-SULTANPR | 2019-07-29 13:00 | 2019-07-29 18:27 | 0 | 0 | 0 | 0.22708 | N-2049 | OSFD | E/S/D availed by UPPCL for installation of new energy meter by replacing existing meter.
NR140075 | 307103 | 400KV LUCKNOW-UNNAO-II | 2019-07-18 08:27 | 2019-07-18 20:03 | 0 | 0 | 0 | 0.48333 | N-1251 | OSPD | S/D taken by UPPCL for maintenance work at their end
NR140142 | 307072A | 400KV MEERUT-BAREILLY-I | 2019-07-12 17:19 | 2019-07-12 20:15 | 0.12222 | 0 | 0 | 0 | N-846 | OSFT | Emergency S/D taken to attend opened jumper at loc no 70
NR340017 | 307059 | 400KV ORAI-ORAI(UP)-II | 2019-07-10 09:38 | 2019-07-10 20:13 | 0.44097 | 0 | 0 | 0 | N-657 | OSPT | S/D taken for AMP work of line side equipment.
NR320004 | 307145 | 220kv Agra(PG)-Bharatpur(Raj.) | 2019-07-27 13:18 | 2019-07-27 15:46 | 0 | 0 | 0 | 0.10278 | N-1917 | OSFD | Emergency S/D availed by Rajasthan (RRVUNL) for line maintenance
NR320003 | 307105 | 220kv Agra(PG)-Sikandara(UP) | 2019-07-19 10:35 | 2019-07-19 19:15 | 0 | 0 | 0 | 0.36111 | N-1332 | OSPD | Line taken under S/D by Rajasthan (RRVUNL) for line maintenance
BILUP2202 | 307140 | 220KV ALLD-REWA RD-I | 2019-07-26 22:41 | 2019-07-27 20:24 | 0 | 0 | 0 | 0.90486 | N-1873 | LPRD | Hand tripped on Power regulation as per NRLDC instruction due to avoid ICTs overloading at Allahabad
BILUP2203 | 307067 | 220KV ALLD-REWA RD-II | 2019-07-11 09:55 | 2019-07-11 11:40 | 0 | 0.072917 | 0 | 0 | **** | OMSU | Tripped only from Rewa Road due to problem at Rewa Road(UP) end
BILUP2203 | 307148 | 220KV ALLD-REWA RD-II | 2019-07-28 16:10 | 2019-07-28 17:00 | 0 | 0.034722 | 0 | 0 | **** | OMSU | Tripped only from Rewa road(UPPCL) end due to some problem at their end
BILUP2203 | 307154 | 220KV ALLD-REWA RD-II | 2019-07-29 13:11 | 2019-07-29 16:39 | 0 | 0.14444 | 0 | 0 | N-2051 | OMSU | S/D taken by UPPCL for maintenance work
NR122006 | 307138 | 220KV AUR-SIKANDARA-I | 2019-07-26 07:30 | 2019-07-26 20:40 | 0.54861 | 0 | 0 | 0 | N-1798 | OSPT | S/D taken for restringing of bottom conductor in line 1 due to low clearance at loc no 411
NR122007 | 307122 | 220KV AUR-SIKANDARA-II | 2019-07-23 11:28 | 2019-07-23 16:00 | 0.18889 | 0 | 0 | 0 | N-1603 | OSFT | Taken Emergency SD for attending Hot Spot at Loc. No.-411 in Y-Ph jumper.
NR122007 | 307139 | 220KV AUR-SIKANDARA-II | 2019-07-26 10:31 | 2019-07-26 20:41 | 0.42361 | 0 | 0 | 0 | N-1819 | OSFT | Emergency s/d taken for restringing of bottom conductor in line 2 due to low clearance at loc no 411
NR122012 | 307010 | 220KV DGANGA-BLY(UP)-II | 2019-07-02 13:19 | 2019-07-02 14:29 | 0 | 0.048611 | 0 | 0 | **** | OMSU | Tripped due to Y-B fault. Zone-4 (Reverse zone) protection operated at Bareilly (UP) end and Zone-2 operated at Dhauliganga end. Fault is in UPPCL switchyard.
NR122012 | 307125 | 220KV DGANGA-BLY(UP)-II | 2019-07-24 16:23 | 2019-07-24 17:32 | 0 | 0 | 0.047917 | 0 | N-1617 | LNCC | E/S/D taken for removal of Tarpoline hanging on line which stuck on line due to heavy rain and thunderstorm.
NR122012 | 307159 | 220KV DGANGA-BLY(UP)-II | 2019-07-30 12:20 | 2019-07-30 16:28 | 0 | 0 | 0 | 0.17222 | N-2115 | OSPD | E/S/D taken by Dhauliganga (NHPC) to check gas pressure in 220kV GIS chamber.
NR122013 | 307158 | 220KV DGANGA-PITHORAGRH | 2019-07-30 12:06 | 2019-07-30 15:57 | 0 | 0 | 0 | 0.16042 | N-2116 | OSPD | E/S/D taken by Dhauliganga (NHPC) to check gas pressure in 220kV GIS chamber.
NR122038 | 307062 | 220KV FATEHPUR-FTHPR(UP)-I | 2019-07-11 00:25 | 2019-07-11 00:48 | 0 | 0.015972 | 0 | 0 | **** | OMSU | Tripped on R-N fault. Fault details from Fatehpur (PG): Zone-2. M-1: F/D=12.2 km, F/C=3.18 kA. M-2: F/D=12.2 km, F/C=3.187 kA. Fault in UPPCL Jurisdiction
NR122040 | 307072 | 220KV FATEHPUR-KNP SOUTH | 2019-07-12 14:26 | 2019-07-12 14:50 | 0 | 0.016667 | 0 | 0 | **** | OMSU | Tripped due to R-N fault. DT received at Fatehpur.FD: Fatehpur- 65km, FC: Fatehpur- 2.4KA. Fault is under UPPCL jurisdiction
NR122016 | 307030 | 220KV KNP-MAINPURI | 2019-07-06 12:05 | 2019-07-06 12:53 | 0 | 0.033333 | 0 | 0 | **** | SBBU | Bus Bar protection operated at Mainpuri(UPPCL) end.
NR122023 | 307094 | 220KV KNP-UNCHR-IV | 2019-07-17 04:21 | 2019-07-17 21:49 | 0 | 0 | 0 | 0.72778 | N-1149 | OSFD | Emergency s/d availed by Unchahar, NTPC for attending DC earth fault at their end.
NR122024 | 307009 | 220KV PITHORAGRH-BRLY(UP) | 2019-07-02 13:19 | 2019-07-02 14:19 | 0 | 0.041667 | 0 | 0 | **** | OMSU | Tripped only from Bareilly (UP) end. Zone-4 (Reverse zone) protection operated at Bareilly (UP) end. Fault is in UPPCL switchyard.
NR122033 | 307029 | 220KV TNKPR-BLY(UP) | 2019-07-06 09:18 | 2019-07-06 10:14 | 0 | 0 | 0.038889 | 0 | **** | GOVC | Tripped due to Over voltage at Tanapur end, Email received from Tanakpur end at 1039hrs. (Mail copy enclosed)
NR122034 | 307028 | 220KV TNKPR-SITARGANJ | 2019-07-06 09:18 | 2019-07-06 09:57 | 0 | 0 | 0.027083 | 0 | **** | GOVC | Tripped due to Over voltage at Tanapur end, Email received from Tanakpur end at 0941hrs. (mail copy enclosed)
NR122036 | 307008 | 220KV UNCHR-RAIBRLY-II | 2019-07-02 12:35 | 2019-07-02 19:20 | 0 | 0.28125 | 0 | 0 | **** | OMSU | Tripped on Y-B fault. Details from Raibareily: F/D=30.36 KM, F/C: Iy=2.99 kA, Ib=3.41 kA. Details from unchahar: F/D=7.7 KM. Fault is in UPPCL Jurisdiction
NR1ICT70 | 307144 | 315MVA ICT-I AGRA | 2019-07-27 12:18 | 2019-07-27 14:26 | 0.088889 | 0 | 0 | 0 | N-1711 | OSFT | Emergency S/D availed to attend hot spot in Y Ph CT pad
NR1ICT14 | 307068 | 315MVA ICT-I GORAKHPR | 2019-07-11 10:19 | 2019-07-11 19:52 | 0.39792 | 0 | 0 | 0 | N-738 | OSPT | S/D availed for attending Tertiary Insulation work and Oil leakage in ICT.
NR1ICT67 | 307037 | 315MVA ICT-III ALLAHABAD | 2019-07-07 07:51 | 2019-08-01 | 1900-01-23 16:09 | 0 | 0 | 0 | **** | SEFT | ICT-III failed. Initiation of fault is y Phase Winding.
NR1BRT32 | 306087 | 240MVAR B/Reactor-I BALIA-765 | 2019-07-01 | 2019-07-04 15:29 | 0 | 0 | 0 | 1900-01-02 15:29 | N-1082 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 755 /760kV
NR1BRT32 | 307070 | 240MVAR B/Reactor-I BALIA-765 | 2019-07-11 21:06 | 2019-07-12 07:48 | 0 | 0 | 0 | 0.44583 | N-786 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Ballia=754kV
NR1BRT32 | 307097 | 240MVAR B/Reactor-I BALIA-765 | 2019-07-17 19:38 | 2019-07-24 18:26 | 0 | 0 | 0 | 1900-01-05 22:48 | N-1222 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Ballia = 751/763kV
NR1BRT50 | 306172 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-07-01 | 2019-07-03 08:17 | 0 | 0 | 0 | 1900-01-01 08:17 | N-2194 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 750/765kV
NR1BRT50 | 307161 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-07-30 22:17 | 2019-07-31 06:51 | 0 | 0 | 0 | 0.35694 | N-2150 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=745kV
NR1BRT50 | 307167 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-07-31 21:49 | 2019-08-01 | 0 | 0 | 0 | 0.090972 | N-2223 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Bareilly=745/764kV
NR1BRT22 | 307014 | 240MVAR B/Reactor-II BALIA-765 | 2019-07-03 21:09 | 2019-07-07 09:43 | 0 | 0 | 0 | 1900-01-02 12:34 | N-222 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 758 /765kV
NR1BRT22 | 307160 | 240MVAR B/Reactor-II BALIA-765 | 2019-07-30 20:58 | 2019-08-01 | 0 | 0 | 0 | 1899-12-31 03:02 | N-2146 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Balia=738kV
NR1BRT28 | 307013 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-07-03 20:58 | 2019-07-04 15:26 | 0 | 0 | 0 | 0.76944 | N-220 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 754 /763kV
NR1BRT28 | 307096 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-07-17 19:32 | 2019-07-24 07:50 | 0 | 0 | 0 | 1900-01-05 12:18 | N-1221 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. LKO 765 = 783/784kV
NR1BRT28 | 307163 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-07-30 22:25 | 2019-07-31 06:53 | 0 | 0 | 0 | 0.35278 | N-2151 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=750kV
NR1BRT28 | 307168 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-07-31 21:49 | 2019-08-01 | 0 | 0 | 0 | 0.090972 | N-2222 | SVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Lucknow=746/763kV
|  | Grand Total |  |  | 1900-03-03 09:08 | 1900-01-08 20:28 | 1900-01-07 05:28 | 1900-10-25 13:08
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="T",(+[RESTORATION]-[OUTAGE]),0))
DURATION OF OUTAGE ATTRIBUTABLE TO = SUBTOTAL(9,F2:[DURATION OF OUTAGE ATTRIBUTABLE TO, row above])
OTHERS = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="U",(+[RESTORATION]-[OUTAGE]),0))
OTHERS = SUBTOTAL(9,G2:[OTHERS, row above])
Hrs:Min = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="C",(+[RESTORATION]-[OUTAGE]),0))
Hrs:Min = SUBTOTAL(9,H2:[Hrs:Min, row above])
Deemed Available = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="D",(+[RESTORATION]-[OUTAGE]),0))
Deemed Available = SUBTOTAL(9,I2:[Deemed Available, row above])
Note on C38: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C39: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C42: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C43: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C66: Author: LILO of Agra(PG)-Agra(UP)#1 at Fatehabad(UP)
Note on C67: Author: LILO of Agra(PG)-Agra(UP)#1 at Fatehabad(UP)
Note on C68: Author: LILO of Agra(PG)-Agra(UP)#1 at Fatehabad(UP)
Note on C107: Author: LILO of 220kV Sikandara(UP)-Bharatpur(RRVPNL) at Agra(PG)
Note on C108: Author: LILO of 220kV Sikandara(UP)-Bharatpur(RRVPNL)

## Sheet4 (hidden)
SL.NO. | ELEMENT | Element Name |  | ELEMENT ID | Element name | Total LINE length | 765KV AGRA-JHATIKARA | 253.147
| ID | [5 empty] | 765KV AGRA-Gr Noida | 148.034
|  |  |  | NR176502 | 765KV AGRA-FATEHPUR-I | 8025:36 | 765KV BALLIA-VARANASI | 165.98
A |  | 765 KV TRANS LINES |  | NR176501 | 765KV LUCKNOW-BALIA | 7653:43 | 765KV FATEHPUR-SASARAM | 355.008
1 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR140001 | 400KV AGRA-AGRA(UP)-I | 719:34 | 765KV FATEHPUR-AGRA-1 | 334.52
2 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR140002 | 400KV AGRA-AGRA(UP)-II | 719:34 | 765KV FATEHPUR-AGRA-2 | 334.8
3 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR140003 | 400KV AGRA-AURAIYA-I | 3980:02 | 765KV GAYA-VARANASI-I (OLD FTP-GAYA) | 263.94
4 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR140004 | 400KV AGRA-AURAIYA-II | 0:00 | 765KV GWALIOR-AGRA I | 129.435
5 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR140005 | 400KV AGRA-BASSI-I | 5093:31 | 765KV GWALIOR-AGRA II | 127.934
6 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR140008 | 400KV AGRA-BHIWADI-I | 5023:55 | 765KV KANPUR-JHATIKARA | 465.8
7 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR140009 | 400KV AGRA-BHIWADI-II | 5023:55 | 765KV KANPUR-VARANASI-I | 326.172
8 | NR176513 | 765KV VARANASI-FATEHPUR | 224.963 | NR140010 | 400KV AGRA-BLBGRH | 4347:22 | 765KV KANPUR-VARANASI-II
9 | NR176514 | 765KV VARANASI-GAYA-I | 80.925 | NR140122 | 400KV ALLD-FATEHPUR-I | 3353:31 | 765KV LUCKNOW-BALIA | 318.919
10 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR140123 | 400KV ALLD-FATEHPUR-II | 3353:31 | 765KV LUCKNOW-BAREILLY | 251.613
11 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR140104 | 400KV ALLD-FATEHPUR-III | 3574:19 | 765KV VARANASI-FATEHPUR | 224.963
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR140012 | 400KV ALLD-KNP-II | 5260:24 | 765KV GAYA-VARANASI-II | 80.925
13 | NR376504 | 765KV ALIGARH-JHATIKARA |  | NR140016 | 400KV ALLD-SASARAM | 4548:43 | 765KV GAYA-BALIA | 238
14 | NR376505 | 765KV KANPUR(GIS)-ALIGARH |  | NR140017 | 400KV BALIA-BIHARSHRF-I | 5802:43 | Total 17 765KV Lines | 4019.19
15 | NR376506 | 765KV AGRA-ALIGARH |  | NR140018 | 400KV BALIA-BIHARSHRF-II | 5802:43 | AGRA-FATEHABAD(UP)-I | 43.013
16 | NR376507 | 765KV ALIGARH-GR.NOIDA |  | NR140019 | 400KV BALIA-MAU-I | 221:10 | FATEHABAD(UP)-AGRA(UP)-I | 57.159
17 | NR376508 | 765KV ORAI-ALIGARH-II |  | NR140020 | 400KV BALIA-MAU-II | 221:10 | AGRA-AGRA-(UP)-II | 29.969
18 | NR376509 | 765KV ORAI-ALIGARH-I |  | NR140021 | 400KV BALIA-PATNA-I | 4685:34 | AURAIYA-AGRA-I | 167.2
|  |  |  | NR140022 | 400KV BALIA-PATNA-II | 4685:34 | AURAIYA-AGRA-II
|  |  |  | NR140136 | 400KV BALIA-PATNA-III | 4440:00 | AGRA-BASSI | 211.433
B |  | 400 KV TRANS LINES |  | NR140137 | 400KV BALIA-PATNA-IV | 4440:00 | AGRA-BHIWADI-I | 208.98
1 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR140140 | 400KV BALIA-SOHAWAL-I | 5499:55 | AGRA-BHIWADI-II | 209.51
2 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR140120 | 400KV BALIA-SOHAWAL-II | 5499:55 | AGRA-BLB | 181.137
3 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 |  | 400KV BLBGRH-MAINPURI-I | 5662:51 | AGRA-JAIPUR(S)-I | 254.41
4 | NR140005 | 400KV AGRA-BASSI-I | 212.23 |  | 400KV BLBGRH-MAINPURI-II | 5662:51 | AGRA-JAIPUR(S)-II
5 | NR140008 | 400KV AGRA-BHIWADI-I | 209.33 | NR140025 | 400KV BAREILLY-LKO(UP) | 6691:12 | AGRA-SIKAR-I | 393.9
6 | NR140009 | 400KV AGRA-BHIWADI-II | 209.33 | NR140026 | 400KV BAREILLY-MBAD-I | 2226:43 | AGRA-SIKAR-II
7 | NR140010 | 400KV AGRA-BLBGRH | 181.14 | NR140027 | 400KV BAREILLY-MBAD-II | 2210:54 | ALLD-FATEHPUR-I | 139.73
8 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 |  | 400KV BAREILLY-MEERUT-I | 5899:12 | ALLD-FATEHPUR-II
9 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 |  | 400KV BAREILLY-MEERUT-II | 5899:12 | ALLD-FATEHPUR-III | 148.934
10 | NR140104 | 400KV ALLD-FATEHPUR-III | 148.93 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 6241:13 | ALLD-KNP-II | 0
11 | NR140012 | 400KV ALLD-KNP-II | 219.183 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 6241:13 | BALIA-MAU-I | 13
12 | NR140163 | 400KV ALLD-VARANASI | 98.791 | NR140046 | 400KV GORKH-GORAKH-I | 1102:35 | BALIA-MAU-II
13 | NR140016 | 400KV ALLD-SASARAM | 189.53 | NR140047 | 400KV GORKH-GORAKH-II | 1102:35 | BALIA-SOHAWAL-I | 229.163
14 | NR140017 | 400KV BALIA-BIHARSHRF-I | 241.78 | NR140052 | 400KV KNP-AGRA | 5760:00 | BALIA-SOHAWAL-II
15 | NR140018 | 400KV BALIA-BIHARSHRF-II | 241.78 | NR140053 | 400KV KNP-AURAIYA-I | 1754:55 | BAREILLY(400)-BAREILLY(765)-I | 1.559
16 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR140054 | 400KV KNP-AURAIYA-II | 1754:55 | BAREILLY(400)-BAREILLY(765)-II
17 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR140055 | 400KV KNP-BLBGARH-I | 9256:48 | BAREILLY-BLY(UP)-I | 14.3
18 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR140056 | 400KV KNP-BLBGARH-II | 8898:32 | BAREILLY-BLY(UP)-II | 14.3
19 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR140057 | 400KV KNP-BLBGARH-III | 8898:32 | BAREILLY-MEERUT-I | 249.52
20 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 14.3 | NR140110 | 400KV KNP-FATEHPUR-I | 2569:54 | BAREILLY-MEERUT-II | 249.52
21 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 14.3 | NR140105 | 400KV KNP-FATEHPUR-II | 2570:24 | LKO(UP)-BAREILLY | 278.76
22 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.8 | NR140058 | 400KV KNP-PANKI-I | 141:36 | BAREILLY-MORADABAD-I | 92.68
23 | NR140026 | 400KV BAREILLY-MBAD-I | 92.78 | NR140059 | 400KV KNP-PANKI-II | 141:36 | BAREILLY-MORADABAD-II | 92.121
24 | NR140027 | 400KV BAREILLY-MBAD-II | 92.121 | NR140070 | 400KV LUCKNOW-GORAKH-III | 6294:14 | SHAHJAHANPUR-BAREILLY-I | 116.917
25 | NR340010 | 400KV BAREILLY-SHAHJHNPR-I | 116.917 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 6294:14 | SHAHJAHANPUR-BAREILLY-II | 116.917
26 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.917 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 68:41 | B'GARH-M'PURI-I | 235.952
27 | NR140158 | 400KV BARLY(765)-KASHIPUR-I | 100.659 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 68:41 | B'GARH-M'PURI-II
28 | NR140159 | 400KV BARLY(765)-KASHIPUR-II | 100.659 | NR140072 | 400KV LUCKNOW-LKO(UP) | 1518:29 | FATEHPUR-MAINPURI-I | 260.051
29 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR140114 | 400KV LUCKNOW-ROSA-I | 4248:00 | FATEHPUR-MAINPURI-II
30 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 2359:09 | GORAKH-GORAKH-I | 45.941
31 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 2359:09 | GORAKH-GORAKH-II
32 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR140073 | 400KV LUCKNOW-SULTANPR | 3926:24 |  | 240
33 | NR140046 | 400KV GORAKH-GORAKH-I | 45.941 | NR140074 | 400KV LUCKNOW-UNNAO-I | 1771:49 | KANPUR-AURAIYA-I | 0
34 | NR140047 | 400KV GORAKH-GORAKH-II | 45.941 | NR140075 | 400KV LUCKNOW-UNNAO-II | 1771:49 | KANPUR-AURAIYA-II
35 | NR140052 | 400KV KNP-AGRA | 240 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 747:48 | KNP-B'GARH-I | 385.69
36 | NR140053 | 400KV KNP-AURAIYA-I | 73.1212 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 747:48 | KNP-B'GARH-II | 370.772
37 | NR140054 | 400KV KNP-AURAIYA-II | 73.1212 | NR140084 | 400KV RIHAND-ALLD-I | 6685:47 | KNP-B'GARH-III
38 | NR140055 | 400KV KNP-BLBGARH-I | 385.7 | NR140085 | 400KV RIHAND-ALLD-II | 6685:47 | KNP-FATEHPUR-II | 107.1
39 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR140088 | 400KV VARANASI-BIHARSHRF-I | 3420:00 | KNP-FATEHPUR-I | 107.079
40 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR140089 | 400KV VARANASI-BIHARSHRF-II | 3420:00 | KNP-PANKI-I | 5.924
41 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR140090 | 400KV SASARAM-VARANASI | 1140:29 | KNP-PANKI-II | 5.863
42 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR140091 | 400KV SING-ALLD-I | 5422:28 | KASHIPUR-BAREILLY-I | 100.659
43 | NR140058 | 400KV KNP-PANKI-I | 5.9 | NR140092 | 400KV SING-ALLD-II | 4829:02 | KASHIPUR-BAREILLY-II
44 | NR140059 | 400KV KNP-PANKI-II | 5.9 | NR140093 | 400KV SING-ANPARA | 724:38 | KANPUR(400)-KANPUR(765)-I | 21.32
45 | NR140070 | 400KV LUCKNOW-GORAKH-III | 262.26 | NR140111 | 400KV SING-FATEHPUR | 7942:52 | KANPUR(400)-KANPUR(765)-II
46 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 262.26 | NR140095 | 400KV SING-LKO(UP) | 7920:00 | LUCKNOW-GORAKHPUR-III | 263.933
47 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.862 | NR140096 | 400KV SING-RIHAND-I | 1008:00 | LUCKNOW-GORAKHPUR-IV
48 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.862 | NR140097 | 400KV SING-RIHAND-II | 1008:00 | LUCKNOW(765)-LUCKNOW(400)-I | 2.862
49 | NR140072 | 400KV LUCKNOW-LKO(UP) | 63.27 | N-W40001 | 400KV SING-VINDH-I | 80:11 | LUCKNOW(765)-LUCKNOW(400)-II
50 | NR140114 | 400KV LUCKNOW-ROSA-I | 177 | N-W40002 | 400KV SING-VINDH-II | 40:05 | LUCKNOW-LUCKNOW (UP) | 63.27
51 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR140164 | 400KV VARANASI-SARNATH-I | 1289:31 | LUCKNOW-SULTANPUR | 163.6
52 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.298 | NR140165 | 400KV VARANASI-SARNATH-II | 1289:31 | LUCKNOW-SHAHJHNPR-I | 169.729
53 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.298 |  |  |  | LUCKNOW-SHAHJHNPR-II
54 | NR140073 | 400KV LUCKNOW-SULTANPR | 163.6 |  | 220 KV TRANS LINES |  | LUCKNOW-SOHAWAL-I | 98.281
55 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | LUCKNOW-SOHAWAL-II
56 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 405:27 | LUCKNOW-UNNAO-I | 73.826
57 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 31.158 | BILUP2202 | 220KV ALLD-REWA RD-I | 71:02 | LUCKNOW-UNNAO-II
58 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.158 | BILUP2203 | 220KV ALLD-REWA RD-II | 71:02 | RIHAND-ALLD-I | 279.245
59 | NR140084 | 400KV RIHAND-ALLD-I | 278.574 | NR122006 | 220KV AUR-SIKANDARA-I | 4380:46 | RIHAND-ALLD-II
60 | NR140085 | 400KV RIHAND-ALLD-II | 278.574 | NR122007 | 220KV AUR-SIKANDARA-II | 4380:46 | RIHAND-VINDHYACHAL Pooling-I | 31.158
61 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 142.5 | NR122012 | 220KV DGANGA-BLY(UP)-II | 5630:10 | RIHAND-VINDHYACHAL Pooling-II
62 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 142.5 | NR122013 | 220KV DGANGA-PITHORAGRH | 1416:14 | SING-ALLD-I | 224
63 | NR140091 | 400KV SING-ALLD-I | 225.936 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 148:05 | SING-ALLD-II | 202
64 | NR140092 | 400KV SING-ALLD-II | 201.21 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 148:05 | SING-ANPARA | 25.057
65 | NR140093 | 400KV SING-ANPARA | 30.193 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 126:52 | SING-FATEHPUR | 330.953
66 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR122041 | 220KV FATEHPUR-NAUBASTA | 126:52 | SING-LUCKNOW(UP) | 408.6
67 | NR140095 | 400KV SING-LKO(UP)-I | 330 | NR122016 | 220KV KNP-MAINPURI | 3624:00 | SING-RIHAND-I | 42.026
68 | NR140096 | 400KV SING-RIHAND-I | 42 | NR122017 | 220KV KNP-NAUBASTA | 463:41 | SING-RIHAND-II
69 | NR140097 | 400KV SING-RIHAND-II | 42 | NR122018 | 220KV KNP-PANKI-I | 374:24 | SING-VINDH-I | 3.341
70 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR122019 | 220KV KNP-PANKI-II | 572:38 | SING-VINDH-II
71 | N-W40002 | 400KV SING-VINDH-II | 1.67 | NR122020 | 220KV KNP-UNCHR-I | 3445:16 | HVDC Feeder I | 1.25
72 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.32 | NR122021 | 220KV KNP-UNCHR-II | 3445:16 | HVDC Feeder I
73 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.32 | NR122022 | 220KV KNP-UNCHR-III | 3471:07 | HVDC Feeder II | 1.25
74 | NR340003 | 400KV VARANASI-SASARAM(ER) | 139.482 | NR122023 | 220KV KNP-UNCHR-IV | 3471:07 | HVDC Feeder II
75 | NR340004 | 400KV VARANASI-SARNATH-I | 106.7 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | VINDHYACHAL POOLING-SASAN | 6.02
76 | NR340005 | 400KV VARANASI-SARNATH-II | 106.7 | NR122025 | 220KV RAIBRLY-CHINHAT |  | BIHARSHARIF-VARANASI-I | 285
77 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 43.013 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1026:03 | BIHARSHARIF-VARANASI-II
78 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 43.013 | NR122032 | 220KV SITARGANJ-BLY(UP) | 2534:47 | VARANASI-SARNATH-I | 106.7
79 | NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR122033 | 220KV TNKPR-BLY(UP) | 2544:00 | VARANASI-SARNATH-II | 106.7
80 | NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR122034 | 220KV TNKPR-SITARGANJ | 1026:03 | SASARAM-ALLAHABAD | 213.729
81 | NR140142 | 400KV MEERUT-BAREILLY-I | 249.52 | NR122035 | 220KV UNCHR-RAIBRLY-I | 1025:02 | SASARAM-VARANASI | 139.482
82 | NR140130 | 400KV MEERUT-BAREILLY-II | 249.52 | NR122036 | 220KV UNCHR-RAIBRLY-II | 1025:02 | VARANASI-ALLAHABAD | 98.791
83 | NR340011 | 400KV LUCKNOW-SHAHJHNPR-I | 159.7 | NR122037 | 220KV UNCHR-RAIBRLY-III | 1048:48 | BARH-GORAKHPUR-I | 353
84 | NR340012 | 400KV Lucknow(765)-Kanpur(GIS)-I | 159.7 |  | 220 KV KNP(400KV)-RANIA(UP) | 18.372 | BARH-GORAKHPUR-II
85 | NR340013 | 400KV Lucknow(765)-Kanpur(GIS)-II |  |  | 220 KV RANIA(UP)-PANKI(UP) | 30.39 | BIHARSHARIF-BALIA-I | 242
86 | NR340014 | 400KV Kanpur(GIS)-Allahabad-I |  |  | 132 KV TRANS LINES |  | BIHARSHARIF-BALIA-I
87 | NR340015 | 400KV Kanpur(GIS)-Allahabad-II |  | BILUP13201 | 132KV MAU-BALIA | 57.825 | ALLAHABAD-MEJA-I | 28.19
88 | NR340016 | 400KV ORAI-ORAI(UP)-I |  |  | 132 KV Tankpur - Mahendranagar | 3.06 | ALLAHABAD-MEJA-II
89 | NR340017 | 400KV ORAI-ORAI(UP)-II |  |  |  |  | UCHAHAR-FATEHPUR-I | 53.7
90 | NR140019 | 400KV BALIA-MAU-I | 9.215 |  | 220KV ALLD-JHUSI(UP) | 21.879 | UCHAHAR-FATEHPUR-II
91 | NR140020 | 400KV BALIA-MAU-II | 9.215 |  | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | PATNA-BALIA-I | 195
92 | NR140021 | 400KV BALIA-PATNA-I | 195.232 |  | 220KV ALLD-REWA RD-I&II | 2.96 | PATNA-BALIA-II
93 | NR140022 | 400KV BALIA-PATNA-II | 195.232 |  | 220KV ALLD-REWA RD-II |  | PATNA-BALIA-III | 185
94 | NR140136 | 400KV BALIA-PATNA-III | 185 |  | 220KV AURAIYA-SIKANDARA-I | 182.532 | PATNA-BALIA-IV
95 | NR140137 | 400KV BALIA-PATNA-IV | 185 |  | 220KV AURAIYA-SIKANDARA-II |  | LUCKNOW-KANPUR-I | 159.7
[5 empty] | 220KV D'GANGA-BRLY(UP)-II | 234.59 | LUCKNOW-KANPUR-II
[5 empty] | 220KV D'GANGA-PITHORAGRH | 59.01 | ALLAHABAD-KANPUR(GIS)-I | 240.39
[5 empty] | 220KV PITHORAGRH-BRLY(UP)-I | 177.88 | ALLAHABAD-KANPUR(GIS)-II
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-I | 6.169 | Total 105 400KV Lines | 10198.266
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-II | 6.169 | HVDC R-D POLE-I | 815
[5 empty] | 220KV FATEHPUR-KNP SOUTH | 5.286 | HVDC R-D POLE-II
[5 empty] | 220KV FATEHPUR-NAUBASTA | 5.286 | HVDC B-B POLE-I | 789.786
[5 empty] | 220KV KNP-MAINPURI | 151 | HVDC B-B POLE-II
[5 empty] | 220KV KNP-RANIA(UP) | 18.372 | BNC-AGRA POLE-I | 1734
[5 empty] | 220KV RANIA(UP)-PANKI(UP) | 30.39 | BNC-AGRA POLE-II
[5 empty] | 220KV KNP-NAUBASTA | 19.32 | CHAMPA-KURUKSHETRA-I | 1305
[5 empty] | 220KV KNP-PANKI-II | 23.86 | CHAMPA-KURUKSHETRA-II
[5 empty] | 220KV KNP-UNCHAHAR-I | 143.553
220KV KNP-UNCHAHAR-II
[5 empty] | 220KV KNP-UNCHAHAR-III | 144.63
220KV KNP-UNCHAHAR-IV
C |  | 220 KV TRANS LINES |  |  | 220KV SITARGANJ-BLY(UP) | 105.72
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 |  | 220KV TNKPR-BLY(UP) | 106
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 |  | 220KV TNKPR-SITARGANJ | 42.55
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 2.96 |  | 220KV RBRLY-CHINHAT | 93.61
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 2.96 |  | 220KV UNCHR-RBRLY-I | 42.71
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.532 |  | 220KV RBRLY-LKO(UP) | 1.19
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.532 |  | 220KV UNCHR-RBRLY-II | 42.71
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 |  | 220KV UNCHR-RBRLY-III | 43.7
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 |  | TOTAL 30 Lines
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 6.17 |  | 132KV LINES
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 6.17 |  | 132KV MAU-BALIA | 57.825
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 5.286 |  | 132KV TNKPR-MHNDRNGR | 3.06
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 5.286
13 | NR122016 | 220KV KNP-MAINPURI | 151
14 | NR122017 | 220KV KNP-NAUBASTA | 19.32
15 | NR122019 | 220KV KNP-PANKI-II | 23.86
16 | NR122020 | 220KV KNP-UNCHR-I | 143.553
17 | NR122021 | 220KV KNP-UNCHR-II | 143.553
18 | NR122022 | 220KV KNP-UNCHR-III | 144.63
19 | NR122023 | 220KV KNP-UNCHR-IV | 144.63
20 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88
21 | NR122025 | 220KV RAIBRLY-CHINHAT | 93.61
22 | NR122026 | 220KV RAIBRLY-LKO(UP) | 42.752
23 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.616
24 | NR122033 | 220KV TNKPR-BLY(UP) | 106
25 | NR122034 | 220KV TNKPR-SITARGANJ | 42.752
26 | NR122035 | 220KV UNCHR-RAIBRLY-I | 42.71
27 | NR122036 | 220KV UNCHR-RAIBRLY-II | 42.71
28 | NR122037 | 220KV UNCHR-RAIBRLY-III | 43.7
29 | NR320001 | 220 KV KANPUR(PG) - RANIYA( UP) | 18.372
30 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP) | 30.39
31 | NR320003 | 220KV RAIBRLY-CG CITY(UP)
32 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP)
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA | 57.825
| Lines | TOTAL FOR T/LS
142 |  | OVERALL SYSTEM AVAILABILITY=
E |  | 765/400 KV ICT'S
1 | NR1ICT707 | 765/400KV ICT-I AGRA
2 | NR1ICT708 | 765/400KV ICT-II AGRA
3 | NR1ICT701 | 765/400KV ICT-I BALIA
4 | NR1ICT702 | 765/400KV ICT-II BALIA
5 | NR1ICT715 | 765/400KV ICT-I BAREILLY
6 | NR1ICT716 | 765/400KV ICT-II BAREILLY
7 | NR1ICT705 | 765/400KV ICT-I FATEHPUR
8 | NR1ICT706 | 765/400KV ICT-II FATEHPUR
9 | NR1ICT703 | 765/400KV ICT-I LUCKNOW
10 | NR1ICT704 | 765/400KV ICT-II LUCKNOW
11 | NR1ICT717 | 765/400KV ICT-I VARANASI
12 | NR1ICT718 | 765/400KV ICT-II VARANASI
13 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS)
14 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS)
| NR3ICT703 | 1000MVA ICT-I ORAI(GIS)
| NR3ICT704 | 1000MVA ICT-II ORAI(GIS)
815
F |  | 400/220 KV ICT'S
1 | NR1ICT70 | 315MVA ICT-I AGRA
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 815
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 789.786
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 789.786
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 1734
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 1734
10 | NR1ICT20 | 315MVA ICT-II KANPUR
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW
13 | NR1ICT26 | 315MVA ICT-I MAINPURI
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 0
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 0
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL
| NR3ICT01 | 315MVA ICT-2 at Agra
| NR3ICT02 | 500MVA ICT-3 at Mainpuri
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 100MVA ICT-I PITHORAGRH
2 | NR1ICT44 | 100MVA ICT-II PITHORAGRH
3 | NR1ICT47 | 100MVA ICT-I RAIBAREILLY
4 | NR1ICT38 | 100MVA ICT-II RAIBAREILLY
5 | NR1ICT39 | 200MVA ICT-III RAIBAREILLY
6 | NR1ICT40 | 100MVA ICT-I SITARGANJ
7 | NR1ICT41 | 100MVA ICT-II SITARGANJ
| NR3ICT03 | 200MVA ICT-3 at Raibareilly
| NR3ICT04 | 200MVA ICT-2 at Raibareilly
TOTAL FOR ICTs
39 |  | HVDC RIHAND-DADRI
H | NR1DCP01 | 500KV HVDC R-D POLE-I
1 | NR1DCP02 | 500KV HVDC R-D POLE-II
2 | NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I
3 | NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II
4 |  | TOTAL FOR HVDC line
HVDC AGRA-BNC
J | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I
1 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II
| NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III
| NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV
2 |  | TOTAL of HVDC POLE-I
HVDC BTB VINDHYACHAL
K | NR1DCB01 | VINDH HVDC B/B BLOCK-I
1 | NR1DCB02 | VINDH HVDC B/B BLOCK-II
2 |  | TOTAL FOR HVDC VINDHYACHAL
HVDC BTB SASARAM
L | NEDCB01 | +/-500MW HVDC B/B SASARAM
1 |  | TOTAL FOR HVDC SASARAM
SVC, KANPUR
M | NR1SVC01 | +/-140MVAR SVC-I KANPUR
1 | NR1SVC02 | +/-140MVAR SVC-II KANPUR
2 |  | TOTAL FOR SVC
N |  | Bus & Switch Line Reactor
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA
3 | NR1BRT36 | 240MVAR B/Reactor-I AGRA-765
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD
6 | NR1BRT33 | 125MVAR B/Reactor-II ALLAHABAD
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY
14 | NR1BRT44 | 2x50MVAR B/Reactor BAREILLY
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR
20 | NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI
28 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR
29 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W
30 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N
31 | NR1BRT42 | 125MVAR B/Reactor-I VINDH
32 | NR1BRT43 | 125MVAR B/Reactor-II VINDH
33 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI
34 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI
35 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I
36 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line
37 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I
38 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II
39 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line
40 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 393.9
41 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 393.9
42 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 213.729
43 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 285
44 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 285
45 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 238
46 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 263.94
47 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 139.482
48 | NR1SRT24 | GORAKH 80MVAR S/R Barh-I line
49 | NR1SRT25 | GORAKH 80MVAR S/R Barh-II line
50 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE
51 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE
52 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I
53 | NR1SRT26 | LUCKNW 240MVAR S/R Bareilly Line
54 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS)
55 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS)
56 | NR3SRT01 | VARANASI 240MVAR S/R KNP(GIS)-1
57 | NR3SRT02 | VARANASI 240MVAR S/R KNP(GIS)-2
58 | NR3SRT03 | KNP(GIS) 330MVAR S/R JHATIKRA-1
59 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS)
60 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI
61 | NR3BRT05 | 125MVAR B/Reactor-I KANPUR
62 | NR3BRT06 | 330MVAR B/Reactor-III VARANASI-765
63 | NR3BRT08 | 330MVAR Bus Reactor-II AT ALIGARH GIS |  |  | 400KV AGRA-SIKAR-I
64 | NR3SLRT06 | ALIGARH 330MVAR Switachable Line Reactor KANPUR LINE |  |  | 400KV AGRA-SIKAR-II
65 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH |  |  | 400KV ALLAHABAD-SASARAM
66 | NR3LRT07 | ORAI 240MVAR Non Switchable Line Reactor ALIGARH-II LINE |  |  | 400KV VARANASI-BIHARSHRF-I
67 | NR3LRT08 | ALIGARH 240MVAR Non Switchable Line Reactor ORAI-II LINE |  |  | 400KV VARANASI-BIHARSHRF-II
68 | NR3BRT10 | 330MVAR Bus Reactor-I ORAI |  |  | 765KV BALIA-GAYA
69 | NR3LRT09 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-I LINE |  |  | 765KV VARANASI-GAYA
70 | NR3LRT10 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-II LINE |  |  | 400KV SASARAM-VARANASI
71 | NR3BRT11 | 330MVAR Bus Reactor-II ORAI |  |  | 400KV MOTIHARI-GRKHPR-I
72 | NR3LRT11 | ORAI 240MVAR Non-Switchable Line Reactor SATNA LINE |  |  | 400KV MOTIHARI-GRKHPR-II
73 | NR3LRT12 | ORAI 240MVAR Non-Switchable Line Reactor ALIGARH-I LINE
74 | NR3LRT13 | ALIGARH 240MVAR Non-Switchable Line Reactor ORAI-I LINE
75 | NR3BRT07 | 63MVAR B/Reactor-I SOHAWAL
Note on C7: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C12: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C13: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C17: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C18: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C19: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C20: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C37: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16
Note on C76: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on F76: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on F77: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C102: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C103: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C279: DOC-26/05/2014
Note on F325: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet2 (hidden)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
125MVAR B/Reactor-1 Mainpuri | 2017-05-27 22:42 | 2017-05-28 06:46 | 0 | 0 | 0 | 0.33611 | N-2790 | SVRD | H-T for voltage regulation as per NRLDC instruction. Mainpuri=386KV
125MVAR B/Reactor-I GORAKHPUR | 2017-05-22 21:55 | 2017-06-01 | 0 | 0 | 0 | 1900-01-08 02:05 | N-2235 | SVRD | H-T for voltage regulation as per NRLDC instruction. Gorakhpur=393KV
125MVAR B/Reactor-III KANPUR(GIS) | 2017-05-25 23:46 | 2017-05-26 06:58 | 0 | 0 | 0 | 0.3 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. Kanpur=395KV
240MVAR B/Reactor-I BALIA-765 | 2017-05-13 21:25 | 2017-05-27 01:23 | 0 | 0 | 0 | 1900-01-12 03:58 | N-1003 | SVRD | H-T for voltage regulation as per NRLDC instruction. Ballia=744KV
240MVAR B/Reactor-I BAREILLY-765 | 2017-05-25 09:56 | 2017-05-28 05:20 | 0 | 0 | 0 | 1900-01-01 19:24 | N-2455 | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-13 21:24 | 2017-05-14 06:52 | 0 | 0 | 0 | 0.39444 | N-1002 | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-16 20:01 | 2017-05-17 07:40 | 0 | 0 | 0 | 0.48542 | N-1534 | SVRD | H-T for voltage regulation as per NRLDC instruction. Lucknow=749KV
330MVAR B/Reactor-II VARANASI | 2017-05-19 15:05 | 2017-05-19 22:00 | 0 | 0 | 0 | 0.28819 | N-1850 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=751KV
330MVAR B/Reactor-II VARANASI | 2017-05-22 21:34 | 2017-05-24 06:25 | 0 | 0 | 0 | 1899-12-31 08:51 | N-2234 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=761KV
80MVAR B/Reactor BAREILLY | 2017-05-25 23:41 | 2017-05-26 07:02 | 0 | 0 | 0 | 0.30625 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=395KV
80MVAR B/Reactor LUCKNOW | 2017-05-25 23:35 | 2017-05-26 06:53 | 0 | 0 | 0 | 0.30417 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=396KV
Note on A9: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1
Note on A10: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1