## Sheet3 (hidden)
400kv LINES |  |  |  | 220kv LINES |  | ICTs,HVDC & SVC. |  | OTHER LINES
400kv LINES NR-I |  | 400kv LINES NR-III |  | 220kv LINES & ICT & Reactor NR-I |  | 220kv LINES & ICT & Reactor NR-III
400KV AGRA-JAIPUR(S)-I | 1 | 400KV AGRA-FATEHABD(UP)-I | 1 | 220KV ANTA-BHIL-I | 1 | 220KV ALLD-JHUSI(UP) | RRVPNL | 220KV BASSI-KUKAS-I
400KV AGRA-JAIPUR(S)-II | 2 | 400KV AGRA(UP)-FATEHABD(UP)-II | 2 | 220KV ANTA-BHIL-II | 2 | 220KV ALLD-REWA RD-I | RRVPNL | 220KV BASSI-KUNDA KI DHANI
400KV AGRA-SIKAR-I | 3 | 400KV AGRA-AGRA(UP)-II | 3 | 220KV ANTA-LALSOT | 3 | 220KV ALLD-REWA RD-II | RRVPNL | 220KV BHIWADI(PG)-BHIWADI
400KV AGRA-SIKAR-II | 4 | 400KV AGRA-AURAIYA-I | 4 | 220KV ANTA-RAPPC | 4 | 220KV AUR-SIKANDARA-I | RRVPNL | 220KV BHIWADI-KHUSHKHERA-I
400KV BASSI-BHIWADI-I | 5 | 400KV AGRA-AURAIYA-II | 5 | 220KV ANTA-S.MDHPR | 5 | 220KV AUR-SIKANDARA-II | RRVPNL | 220KV BHIWADI-KHUSHKHERA-II
400KV BASSI-HIRAPURA-I | 6 | 400KV AGRA-BASSI-I | 6 | 220KV BASSI-BAGRU | 6 | 220KV DGANGA-BLY(UP)-II | RRVPNL | 220KV BHIWADI-NIMRANA(RJ)
400KV BASSI-HIRAPURA-II | 7 | 400KV AGRA-BHIWADI-I | 7 | 220KV BASSI-DAUSA-I | 7 | 220KV DGANGA-PITHORAGRH | RRVPNL | 220KV BHINMAL-BHINMAL-I
400KV BASSI-JAIPUR(S)-I | 8 | 400KV AGRA-BHIWADI-II | 8 | 220KV BASSI-DAUSA-II | 8 | 220KV FATEHPUR-FTHPR(UP)-I | RRVPNL | 220KV BHINMAL-BHINMAL-II
400KV BASSI-JAIPUR(S)-II | 9 | 400KV AGRA-BLBGRH | 9 | 220KV BASSI-IG NAGAR | 9 | 220KV FATEHPUR-FTHPR(UP)-II | RRVPNL | 220KV BHINMAL-SANCHORE
400KV BASSI-KOTPUTLI | 10 | 400KV ALLD-FATEHPUR-I | 10 | 220KV FGPP-PALLA-I | 10 | 220KV FATEHPUR-KNP SOUTH | RRVPNL | 220KV BHINMAL-SIROHI
400KV BASSI-PHAGI-I | 11 | 400KV ALLD-FATEHPUR-II | 11 | 220KV FGPP-PALLA-II | 11 | 220KV FATEHPUR-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-CHAKSU-I |  | LEGENDS
400KV BASSI-PHAGI-II | 12 | 400KV ALLD-FATEHPUR-III | 12 | 220KV FGPP-SPUR-I | 12 | 220KV JHUSI(UP)-PHULPUR(UP) | RRVPNL | 220KV JAIPUR(S)-CHAKSU-II
400KV BHINMAL-ZERDA | 13 | 400KV ALLD-KNP-II | 13 | 220KV FGPP-SPUR-II | 13 | 220KV KNP-MAINPURI | RRVPNL | 220KV JAIPUR(S)-SEZ |  |  | Lines maintained by ER
400KV BHIWADI-GURGAON | 14 | 400KV ALLD-VARANASI | 14 | 220KV HIRAPURA-IG NAGAR | 14 | 220KV KNP-NAUBASTA | RRVPNL | 220KV JAIPUR(S)-DOONI
400KV BHIWADI-HISAR-I | 15 | 400KV BALIA-MAU-I | 15 | 220KV HIRAPURA-SANGANER | 15 | 220 KV KANPUR(PG) - RANIYA( UP)-1 | RRVPNL | 220KV KANKROLI(PG)-BHILWARA
400KV BHIWADI-KOTPUTLI | 16 | 400KV BALIA-MAU-II | 16 | 220KV LALSOT-DAUSA | 16 | 220 KV RANIYA( UP) - PANKI (UP)-1 | RRVPNL | 220KV KANKROLI(PG)-KANK-I
400KV BHIWADI-NIMRANA-I | 17 | 400KV BALIA-SOHAWAL-I | 17 | 220KV MEERUT-MPURAM-I | 17 | 220KV KNP-PANKI-II | RRVPNL | 220KV KANKROLI(PG)-KANK-II
400KV BHIWADI-NIMRANA-II | 18 | 400KV BALIA-SOHAWAL-II | 18 | 220KV MEERUT-MPURAM-II | 18 | 220KV KNP-UNCHR-I | RRVPNL | 220KV KANKROLI-DEBARI |  |  | lines maintained by WR
400KV BLBGRH-GURGAON | 19 | 400KV BAREILLY-BRLY(765)-I | 19 | 220KV MEERUT-NARA | 19 | 220KV KNP-UNCHR-II | RRVPNL | 220KV KOTA-KTPS-1
400KV BLBGRH-MAHRANIBG | 20 | 400KV BAREILLY-BRLY(765)-II | 20 | 220KV MEERUT-SHTBDNGR | 20 | 220KV KNP-UNCHR-III | RRVPNL | 220KV KOTA-KTPS-2 |  |  | LILO portions only of POWERGRID
400KV BLBGRH-NAVADA(HVPN) | 21 | 400KV BAREILLY-BRLY(UP)-I | 21 | 220KV MEERUT-SIMBHOLI | 21 | 220KV KNP-UNCHR-IV | RRVPNL | 220KV KOTA-BHILWARA
400KV DAD-GR.NOIDA | 22 | 400KV BAREILLY-BRLY(UP)-II | 22 | 220KV RAPPB-CHITT-I | 22 | 220KV PITHORAGRH-BRLY(UP) | RRVPNL | 220KV KOTA-DHUNI |  |  | LILO portion maintained by constituents
400KV DAD-MAHRANIBG | 23 | 400KV BAREILLY-LKO(UP) | 23 | 220KV RAPPB-CHITT-II | 23 | 220KV RAIBRLY-CHINHAT | RRVPNL | 220KV KOTPUTLI-KOTPUTLI
400KV DAD-MANDOLA-I | 24 | 400KV BAREILLY-MBAD-I | 24 | 220KV RAPPB-RAPPC | 24 | 220KV RAIBRLY-LKO(UP) | RRVPNL | 220KV KOTPUTLI-MANOHARPUR
400KV DAD-MANDOLA-II | 25 | 400KV BAREILLY-MBAD-II | 25 | 220KV RAPPB-UDAIPUR | 25 | 220KV SITARGANJ-BLY(UP) | RRVPNL | 220KV NIMRANA-NIMRANA
400KV DAD-MURADNGR | 26 | 400KV BAREILLY-ROSA-I | 26 | 220KV S.MDHPR-DAUSA-I | 26 | 220KV TNKPR-BLY(UP) | RRVPNL | 220KV NIMRANA-KHUSHKHERA |  |  | Maintained by NR-1 & NR-II
400KV DAD-PANIPAT-I | 27 | 400KV BAREILLY-SHAHJHNPR-I | 27 | 220KV SIKAR-RATANGARH-I | 27 | 220KV TNKPR-SITARGANJ | HVPNL | 220KV BHIWADI-MAU
400KV DAD-PANIPAT-II | 28 | 400KV BAREILLY-SHAHJHNPR-II | 28 | 220KV SIKAR-RATANGARH-II | 28 | 220KV UNCHR-RAIBRLY-I | HVPNL | 220KV BHIWADI-REWARI-I
400KV GURGAON-MANESAR-I | 29 | 400KV BARLY(765)-KASHIPUR-I | 29 | 220KV SIKAR-SIKAR(RJ)-I | 29 | 220KV UNCHR-RAIBRLY-II | HVPNL | 220KV BHIWADI-REWARI-II
400KV GURGAON-MANESAR-II | 30 | 400KV BARLY(765)-KASHIPUR-II | 30 | 220KV SIKAR-SIKAR(RJ)-II | 30 | 220KV UNCHR-RAIBRLY-III | HVPNL | 220KV BHIWADI-BAWAL
400KV JHATIKALA-BAMNOLI-I | 31 | 400KV BLBGRH-MAINPURI-I | 31 | 220KV HISAR-HISAR I/A-I |  |  | HVPNL | 220KV GURGAON-GURGAON-I
400KV JHATIKALA-BAMNOLI-II | 32 | 400KV BLBGRH-MAINPURI-II | 32 | 220KV HISAR-HISAR I/A-II |  |  | HVPNL | 220KV GURGAON-GURGAON-II
400KV JHATIKALA-MUNDKA-I | 33 | 400KV FATEHPUR-MAINPURI-I |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-III
400KV JHATIKALA-MUNDKA-II | 34 | 400KV FATEHPUR-MAINPURI-II |  |  |  |  | HVPNL | 220KV GURGAON-GURGAON-IV
400KV KANKROLI-BHINMAL | 35 | 400KV GORAKH-GORAKH-I |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-I
400KV KANKROLI-JODHPUR | 36 | 400KV GORAKH-GORAKH-II |  |  |  |  | HVPNL | 400KV GURGAON-DAULTABAD-II
400KV KANKROLI-CHITTOR(RJ)-I | 37 | 400KV KNP-AGRA |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-I
400KV KANKROLI-RAPPC-II | 38 | 400KV KNP-AURAIYA-I |  |  |  |  | HVPNL | 220 KV GURGAON-BADSHAHPUR-II
400KV KANKROLI-ZERDA-I | 39 | 400KV KNP-AURAIYA-II |  | 400KV & 220KV ICT NR-I |  |  | HVPNL | 220 KV MANESAR-BADSHAHPUR-I
400KV KOTA-BEAWAR | 40 | 400KV KNP-BLBGARH-I | 1 | 315MVA ICT-I BASSI |  | 400KV & 220KV ICT NR-III | HVPNL | 220 KV MANESAR-BADSHAHPUR-II
400KV KOTA-MERTA-I | 41 | 400KV KNP-BLBGARH-II | 2 | 315MVA ICT-II BASSI | 1 | 315MVA ICT-I AGRA | HVPNL | 220 KV MANESAR-MAU-I
400KV KOTA-RAPPC | 42 | 400KV KNP-BLBGARH-III | 3 | 500MVA ICT-III BASSI | 2 | 315MVA ICT-I ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-II
400KV KOTESHWR-KHEP-I | 43 | 400KV KNP-FATEHPUR-I | 4 | 315MVA ICT-III BAWANA | 3 | 315MVA ICT-II ALLAHABAD | HVPNL | 220 KV MANESAR-MAU-III
400KV KOTESHWR-KHEP-II | 44 | 400KV KNP-FATEHPUR-II | 5 | 315MVA ICT-I BHINMAL | 4 | 315MVA ICT-III ALLAHABAD | HVPNL | 220 KV SONIPAT-MOHANA-I
400KV KOTESHWR-TEHRI-I | 45 | 400KV KNP-PANKI-I | 6 | 315MVA ICT-II BHINMAL | 5 | 315MVA ICT-I FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-I
400KV KOTESHWR-TEHRI-II | 46 | 400KV KNP-PANKI-II | 7 | 315MVA ICT-I BHIWADI | 6 | 315MVA ICT-II FATEHPUR | HVPNL | 220KV BAHADURGRH-NUNMAJRA-II
400KV MBAD-MURADNGR | 47 | 400KV LUCKNOW-GORAKH-III | 8 | 315MVA ICT-II BHIWADI | 7 | 315MVA ICT-I GORAKHPR | HVPNL | 220KV HISAR-SRWL-I
400KV MEERUT-BAGPAT-I | 48 | 400KV LUCKNOW-GORAKH-IV | 9 | 315MVA ICT-III BHIWADI | 8 | 315MVA ICT-II GORAKHPR | HVPNL | 220KV HISAR-SRWL-II
400KV MEERUT-BAREILLY-I | 49 | 400KV LUCKNOW-LKO(765)-I | 10 | 500MVA ICT-I BLBGARH | 9 | 315MVA ICT-I KANPUR | HVPNL | 220KV HISAR-FATEHABAD-I
400KV MEERUT-BAREILLY-II | 50 | 400KV LUCKNOW-LKO(765)-II | 11 | 315MVA ICT-II BLBGARH | 10 | 315MVA ICT-II KANPUR | HVPNL | 220KV HISAR-FATEHABAD-II
400KV MEERUT-KOTESHWR-I | 51 | 400KV LUCKNOW-LKO(UP) | 12 | 315MVA ICT-III BLBGARH | 11 | 315MVA ICT-I LUCKNOW | NTPC | 132KV SING-VINDH-RIH
400KV MEERUT-KOTESHWR-II | 52 | 400KV LUCKNOW-ROSA-I | 13 | 315MVA ICT-IV BLBGARH | 12 | 500MVA ICT-II LUCKNOW | NTPC | 132KV SING-RENUSAGAR-PIPRI
400KV MEERUT-MND-I | 53 | 400KV LUCKNOW-SHAHJHNPR-I | 14 | 315MVA ICT-I GURGAON | 13 | 315MVA ICT-I MAINPURI | DTL | 400KV B'GARH-BAMNOLI-I
400KV MEERUT-MND-II | 54 | 400KV LUCKNOW-SHAHJHNPR-II | 15 | 315MVA ICT-II GURGAON | 14 | 315MVA ICT-II MAINPURI | DTL | 400KV B'GARH-BAMNOLI-II
400KV MEERUT-MND-III | 55 | 400KV LUCKNOW-SOHAWAL-I | 16 | 500MVA ICT-I JAIPUR(S) | 15 | 100MVA ICT-I PITHORAGRH | DTL | 400KV MND-BAWANA-I
400KV MEERUT-MND-IV | 56 | 400KV LUCKNOW-SOHAWAL-II | 17 | 500MVA ICT-II JAIPUR(S) | 16 | 100MVA ICT-II PITHORAGRH | DTL | 400KV MND-BAWANA-II
400KV MEERUT-MUZFRNGR | 57 | 400KV LUCKNOW-SULTANPR | 18 | 315MVA ICT-I KANKROLI | 17 | 100MVA ICT-I RAIBAREILLY | DTL | 220KV MND-S.WZRBD-I
400KV MERTA-BEAWAR | 58 | 400KV LUCKNOW-UNNAO-I | 19 | 315MVA ICT-II KANKROLI | 18 | 100MVA ICT-II RAIBAREILLY | DTL | 220KV MND-S.WZRBD-II
400KV NAVADA(HVPN)-GR.NOIDA | 59 | 400KV LUCKNOW-UNNAO-II | 20 | 315MVA ICT-III KANKROLI | 19 | 100MVA ICT-III RAIBAREILLY | DTL | 220KV MND-S.WZRBD-III
400KV NIMRANA-MANESAR-I | 60 | 400KV MEERUT-BAREILLY-I | 21 | 315MVA ICT-I KOTA | 20 | 500MVA ICT-I SHAHJHNPR | DTL | 220KV MND-S.WZRBD-IV
400KV NIMRANA-MANESAR-II | 61 | 400KV MEERUT-BAREILLY-II | 22 | 315MVA ICT-II KOTA | 21 | 500MVA ICT-II SHAHJHNPR | DTL | 220KV MND-NARELA-I
400KV NIMRANA-SIKAR-I | 62 | 400KV RIHAND-ALLD-I | 23 | 315MVA ICT-I KOTPUTLI | 22 | 100MVA ICT-I SITARGANJ | DTL | 220KV MND-NARELA-II
400KV NIMRANA-SIKAR-II | 63 | 400KV RIHAND-ALLD-II | 24 | 315MVA ICT-II KOTPUTLI | 23 | 100MVA ICT-II SITARGANJ | DTL | 220KV MND-GOPALPUR-I
400KV ROORKI-KASHIPUR-I | 64 | 400KV RIHAND3-VINDH(Pool)-I | 25 | 315MVA ICT-I MAHRANIBAG | 24 | 315MVA ICT-I SOHAWAL | DTL | 220KV MND-GOPALPUR-II
400KV ROORKI-KASHIPUR-II | 65 | 400KV RIHAND3-VINDH(Pool)-II | 26 | 315MVA ICT-II MAHRANIBAG | 25 | 315MVA ICT-II SOHAWAL | DTL | 220KV MBAG-SARITAVIHAR
400KV ROORKI-MUZFRNGR | 66 | 400KV SING-ALLD-I | 27 | 500MVA ICT-III MAHRANIBAG | 26 |  | DTL | 220KV MBAG-LODHIROAD-I
400KV ROORKI-RISHIKESH | 67 | 400KV SING-ALLD-II | 28 | 500MVA ICT-IV MAHRANIBAG | 27 |  | DTL | 220KV MBAG-LODHIROAD-II
400KV SIKAR-RATANGARH-I | 68 | 400KV SING(NTPC)-ANPARA(UP) | 29 | 500MVA ICT-I MANDOLA | 28 |  | DTL | 220KV MBAG-I P EXTN
400KV SIKAR-RATANGARH-II | 69 | 400KV SING-FATEHPUR | 30 | 500MVA ICT-II MANDOLA | 29 |  | UPPCL | 220KV AGRA-SHAMSABD-I
400KV MEERUT-BAGPAT-II | 70 | 400KV SING-LKO(UP)-I | 31 | 500MVA ICT-III MANDOLA | 30 |  | UPPCL | 220KV AGRA-FEROZABAD
400KV ROORKI-SAHARANPUR-I | 71 | 400KV SING-RIHAND-I | 32 | 500MVA ICT-IV MANDOLA |  |  | UPPCL | 220KV BAGHPAT(PG)-BAGHPAT(UP)
400KV ROORKI-SAHARANPUR-II | 72 | 400KV SING-RIHAND-II | 33 | 500MVA ICT-I MANESAR |  |  | UPPCL | 220KV BAGHPAT-MURADNGR
400KV RAPPC-CHITTOR(RJ)-I | 73 | 400KV SING-VINDH-I | 34 | 500MVA ICT-II MANESAR |  |  | UPPCL | 220KV BAGHPAT-SHAMLI
| 74 | 400KV SING-VINDH-II | 35 | 315MVA ICT-I MEERUT |  |  | UPPCL | 220KV GORAKH-BARHUA
| 75 | 400KV KANPUR-KANPUR(GIS)-I | 36 | 315MVA ICT-II MEERUT |  | 765KV ICT NR-III | UPPCL | 220KV GORAKH-BASTI
| 76 | 400KV KANPUR-KANPUR(GIS)-II | 37 | 315MVA ICT-III MEERUT | 1 | 765/400KV ICT-I BALIA | UPPCL | 220KV LKO(PG)-Bakhsi Ka Talab
| 77 | 400KV VARANASI-SASARAM(ER) | 38 | 500MVA ICT-IV MEERUT | 2 | 765/400KV ICT-II BALIA | UPPCL | 220KV LKO(PG)-CHINHAT
400KV BAHADURGRH-BAWANA | 78 | 400KV VARANASI-SARNATH-I | 39 | 315MVA ICT-III MUZFRNGR | 3 | 765/400KV ICT-I LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-I
400KV BAHADURGRH-SONIPAT-I | 79 | 400KV VARANASI-SARNATH-II | 40 | 315MVA ICT-II NIMRANA | 4 | 765/400KV ICT-II LUCKNOW | UPPCL | 220 KV LKO(Pg)-LKO(Paigamau-UP)-II
400KV BAHADURGRH-SONIPAT-II | 80 | 400KV ALLAHABAD-MEJA(NTPC)-I | 41 | 315MVA ICT-I ROORKI | 5 | 765/400KV ICT-I FATEHPUR | UPPCL | 220KV M'PURI-ETAH
400KV BHIWANI-BAWANA | 81 | 400KV BALIA-BIHARSHRF-I | 42 | 315MVA ICT-II ROORKI | 6 | 765/400KV ICT-II FATEHPUR | UPPCL | 220KV M'PURI-SIRSAGANJ-I
400KV BHIWANI-BHIWANI(BBMB) | 82 | 400KV BALIA-BIHARSHRF-II | 43 | 315MVA ICT-I SIKAR | 7 | 765/400KV ICT-I AGRA | UPPCL | 220KV M'PURI-M'PURI(UP)-II
400KV BHIWANI-HISAR-I | 83 | 400KV ALLD-SASARAM | 44 | 315MVA ICT-II SIKAR | 8 | 765/400KV ICT-II AGRA | UPPCL | 220KV M'PURI-FEROZBD
400KV BHIWANI-HISAR-II | 84 | 400KV BALIA-PATNA-I | 45 | 500MVA ICT-I BAGPAT | 9 | 765/400KV ICT-I BAREILLY | UPPCL | 400KV M'PURI-ORAI-I
400KV BHIWANI-HISAR-III | 85 | 400KV BALIA-PATNA-II | 46 | 500MVA ICT-II BAGPAT | 10 | 765/400KV ICT-II BAREILLY | UPPCL | 400KV M'PURI-PARICHA-II
400KV BHIWANI-JIND-I | 86 | 400KV BALIA-PATNA-III | 47 | 315MVA ICT-I SAHARANPUR | 11 | 765/400KV ICT-I VARANASI | UPPCL | 220KV MEERUT-GAJRAULA
400KV BHIWANI-JIND-II | 87 | 400KV BALIA-PATNA-IV | 48 | 315MVA ICT-II SAHARANPUR | 12 | 765/400KV ICT-II VARANASI | UPPCL | 220KV MEERUT-NEHTAUR
400KV FATEHABAD-HISAR | 88 | 400KV LKO(765)-KANPUR(GIS)-I |  |  | 13 | 765/400KV ICT-I KANPUR(GIS) | UPPCL | 220KV ORAI-KANPUR
400KV BHIWADI-HISAR-II | 89 | 400KV LKO(765)-KANPUR(GIS)-II |  |  | 14 | 765/400KV ICT-II KANPUR(GIS) | UPPCL | 400KV PANKI-MURADNGR
400KV BHIWADI-HISAR-III | [6 empty] | UPPCL | 220KV SHAHJHNP-HARDOI
400KV HISAR-BHIWANI(BBMB) | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-I | [6 empty] | UPPCL | 220KV SAHARNPR- SAHARNPR(UP)
400KV HISAR-KAITHAL-II |  | 400kv LINES of ER-1 in NR-III Availability |  | NR-I Additional ICT from NR-II |  |  | UPPCL | 220KV SOHAWAL(PG) - SOHAWAL(UP)
400KV KABULPR-BAHADURGRH | 1 | 400KV SASARAM-BIHARSHRF-I | 1 | 315MVA ICT-I BAHADURGARH |  | NR-III HVDC SYSTEM / SVC | UPPCL | 220KV UNCHR-RBRLY-I
400KV KABULPR-BHIWANI | 2 | 400KV SASARAM-BIHARSHRF-II | 2 | 500MVA ICT-II BAHADURGARH | 1 | 500KV HVDC R-D POLE-I | UPPCL | 220KV UNCHR-RBRLY-II
|  |  | 3 | 315MVA ICT-I HISAR | 2 | 500KV HVDC R-D POLE-II | PTCUL | 220KV ROORKI-HARDWAR
|  |  | 4 | 315MVA ICT-II HISAR | 3 | 500KV HVDC BALIA-BHWD POLE-I | PTCUL | 220KV ROORKI--RAMNAGAR
|  | 765 KV TRANS LINES NR-III | 5 | 315MVA ICT-III HISAR | 4 | 500KV HVDC BALIA-BHWD POLE-II | PTCUL | 132KV SITARGNJ(PG)-SITARGNJ(PTCUL)
765 KV TRANS LINES NR-I | 1 | 765KV AGRA-FATEHPUR-I | 6 | 315MVA ICT-I SONIPAT | 5 | 800KV HVDC AGRA-BNC POLE-I | PTCUL | 132KV PITHORAGRH-CHANDOK
765KV AGRA-JHATIKALA | 2 | 765KV AGRA-FATEHPUR-II | 7 | 315MVA ICT-II SONIPAT | 6 | 800KV HVDC AGRA-BNC POLE-II | PTCUL | 132KV PITHORAGRH-ALMORA
765KV BHIWANI-PHAGI(JPR)-I | 3 | 765KV AGRA-GR.NOIDA | 8 | 315MVA ICT-I BHIWANI | 7 | VINDH HVDC B/B BLOCK-I | PTCUL | 132KV PTRGRH-PTRGRH(PTCUL)
765KV MEERUT-GR.NOIDA | 4 | 765KV FATEHPUR-SASARAM | 9 | 315MVA ICT-II BHIWANI | 8 | VINDH HVDC B/B BLOCK-II | POWERLINK
765KV MOGA-BHIWANI | 5 | 765KV LUCKNOW-BALIA | 10 | 500MVA ICT-I JIND | 9 | SASARAM HVDC B/B | PLINK | 400KV LUCKNOW-GORAKH-I (PL)
765KV JHATIKALA-BHIWANI | 6 | 765KV LUCKNOW-BAREILLY | 11 | 500MVA ICT-II JIND | 10 | +/-140MVAR SVC-I KANPUR | PLINK | 400KV LUCKNOW-GORAKH-II (PL)
765KV MEERUT-BHIWANI | 7 | 765KV VARANASI-BALIA |  |  | 11 | +/-140MVAR SVC-II KANPUR | PLINK | 400KV GRKHPR-MZFRPR-I (PL)
765KV BHIWANI-PHAGI(JPR)-II | 8 | 765KV VARANASI-FATEHPUR |  |  |  |  | PLINK | 400KV GRKHPR-MZFRPR-II (PL)
| 9 | 765KV VARANASI-GAYA-I |  | 765KV ICT NR-I
| 10 | 765KV VARANASI-KANPUR(GIS)-I | 1 | 765/400KV ICT-I JHATIKALA
BUS REACTORS NR-I | 11 | 765KV VARANASI-KANPUR(GIS)-II | 2 | 765/400KV ICT-II JHATIKALA |  | SWITCABLE LINE REACTORS NR-III | NR-II | 400KV DAD-M'KOTLA
125MVAR B/Reactor-I BAGPAT | 12 | 765KV KANPUR(GIS)-JHATIKRA-I | 3 | 765/400KV ICT-III JHATIKALA | 1 | AGRA 240MVAR S/R FATEHPR line | NR-II | 400KV BAGHPAT-KAITHAL-I
50MVAR B/Reactor-I BASSI |  |  | 4 | 765/400KV ICT-IV JHATIKALA | 2 | AGRA 50MVAR S/R BHIWADI-I LINE | NR-II | 400KV BAGHPAT-KAITHAL-II
50MVAR B/Reactor-II BASSI |  |  | 5 | 765/400KV ICT-I MEERUT | 3 | ALLHBD 50MVAR S/R MNPR-I LINE | NR-II | 765KV MEERUT-MOGA
50MVAR B/Reactor-III BASSI |  | BUS REACTORS NR-III | 6 | 765/400KV ICT-II MEERUT | 4 | ALLHBD 50MVAR S/R MNPR-II LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-I | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
125MVAR B/Reactor-IV BASSI | 1 | 125MVAR B/Reactor-I AGRA | 7 | 765/400KV ICT-I BHIWANI | 5 | BARLLY 50MVAR S/R MND-I LINE | NR-II | 400KV SONIPAT-KURUKSHETRA-II | LILO of 400KV MEERUT-KAITHAL-II at Baghpat
80MVAR B/Reactor BHINMAL | 2 | 125MVAR B/Reactor-II AGRA | 8 | 765/400KV ICT-II BHIWANI | 6 | BARLLY 50MVAR S/R MND-II LINE | NR-II | 400KV HISAR-MOGA-I
80MVAR B/Reactor BHIWADI | 3 | 240MVAR B/Reactor-II AGRA-765 |  |  | 7 | BALIA 240MVAR S/R LUCKNW Ckt-I | NR-II | 400KV HISAR-MOGA-II
80MVAR B/Reactor BLBGARH | 4 | 240MVAR B/Reactor-1 AGRA-765 |  |  | 8 | BALIA 240MVAR S/R GAYA Line | NR-II | 400KV HISAR-MOGA-III
125MVAR B/Reactor-I JAIPUR(S) | 5 | 80MVAR B/Reactor ALLAHABAD |  |  | 9 | FATEHPR 330MVAR S/R AGRA line
125MVAR B/Reactor-II JAIPUR(S) | 6 | 125MVAR B/Reactor-II ALLAHABAD |  |  | 10 | GORAKH 50MVAR S/R LKO-I LINE
240MVAR B/Reactor-I JHATIKALA-765 | 7 | 80MVAR B/Reactor-I BALIA |  |  | 11 | GORAKH 50MVAR S/R LKO-II LINE
240MVAR B/Reactor-II JHATIKALA-765 | 8 | 125MVAR B/Reactor-II BALIA |  |  | 12 | GORAKH 63MVAR S/R LKO-III LINE
50MVAR B/Reactor KANKROLI | 9 | 125MVAR B/Reactor-III BALIA |  | SWITCABLE LINE REACTORS NR-I | 13 | GORAKH 63MVAR S/R LKO-IV LINE | ER-I | 400KV BALIA-SASARAM
125MVAR B/Reactor-II KANKROLI | 10 | 125MVAR B/Reactor-IV BALIA | 1 | BHINML 50MVAR S/R KANKROLI | 14 | GORAKH 80MVAR S/R Barh-I line | ER-I | 765KV BALIA-GAYA
80MVAR B/Reactor-I KOTA | 11 | 240MVAR B/Reactor-I BALIA-765 | 2 | MEERUT 50MVAR S/R Kotesh-I LINE | 15 | GORAKH 80MVAR S/R Barh-II line | ER-I | 400KV BARH- GRKHPR-I
50MVAR B/Reactor-II KOTA | 12 | 240MVAR B/Reactor-II BALIA-765 | 3 | MEERUT 50MVAR S/R Kotesh-II LINE | 16 | LUCKNW 240MVAR S/R BRLY Line | ER-I | 400KV BARH- GRKHPR-II
80MVAR B/Reactor-I KOTPUTLI | 13 | 80MVAR B/Reactor BAREILLY | 4 | JHATIKALA 240MVAR S/R AGRA Line | 17 | LUCKNW 63MVAR S/R GKP-III LINE | ER-I | 765KV VARANASI-GAYA-II
50MVAR B/Reactor MANDOLA | 14 | 2x50MVAR B/Reactor BAREILLY | 5 | MEERUT 240MVAR S/R AGRA line | 18 | LUCKNW 63MVAR S/R GKP-IV LINE | ER-I | 400KV VARANASI-BIHARSHRF-I
240MVAR B/Reactor-I MEERUT-765 | 15 | 240MVAR B/Reactor-I BAREILLY-765 | 6 | SIKAR 50MVAR S/R AGRA Ckt-I | 19 | LUCKNW 240MVAR S/R BALIA Ckt-I | ER-I | 400KV VARANASI-BIHARSHRF-II
125MVAR B/Reactor MANESAR | 16 | 80MVAR B/Reactor BIHARSHRF | 7 | SIKAR 50MVAR S/R AGRA Ckt-II | 20 | VARANASI 240MVAR S/R KNP(GIS) ckt-1
50MVAR B/Reactor MURADNGR | 17 | 125MVAR B/Reactor-I FATEHPUR | 8 | PHAGI(JPR) 240MVAR S/R BHIWANI-I Line | 21 | VARANASI 240MVAR S/R KNP(GIS) ckt-2
80MVAR B/Reactor NIMRANA | 18 | 125MVAR B/Reactor-II FATEHPUR | 9 | BHIWANI 240MVAR S/R MEERUT line | 22 | KNP(GIS) 330MVAR S/R JHATIKRA ckt-1 | WR | 765KV AGRA-GWALIOR-I
240MVAR B/Reactor-I PHAGI(JPR)-765 | 19 | 330MVAR B/Reactor-III FTHPR-765 | 10 | PHAGI(JPR) 240MVAR S/R BHIWANI-II Line |  |  | WR | 765KV AGRA-GWALIOR-II
125MVAR B/Reactor ROORKEE | 20 | 80MVAR B/Reactor LUCKNOW |  |  |  |  | WR | 765KV GWALIOR-PHAGI-I
125MVAR B/Reactor-I RATANGRH(RJ) | 21 | 125MVAR B/Reactor-II LUCKNOW |  | SVC NR-I |  |  | WR | 765KV GWALIOR-PHAGI-II
80MVAR B/Reactor SIKAR | 22 | 125MVAR B/Reactor-III LUCKNOW | 1 | +400/-300MVAR SVC KANKROLI
50MVAR B/Reactor-I SAHARANPUR | 23 | 240MVAR B/Reactor-IV LUCKNOW-765 |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-I
50MVAR B/Reactor-II SAHARANPUR | 24 | 125MVAR B/Reactor-I VINDH |  |  |  |  | ADANI | 400 KV BHIWANI-MHNDRGRH-II
125MVAR B/Reactor-II SONIPAT | 25 | 125MVAR B/Reactor-II VINDH
| 26 | 93MVAR B/Reactor VINDH AR1-W |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - I
BUS REACTORS NR-I From NR2 | 27 | 93MVAR B/Reactor VINDH AR2-N |  |  |  |  | PTUL | 400KV FATEHPUR- UNCHAHAR(NTPC) - II
240MVAR B/Reactor-I BHIWANI | 28 | 125MVAR B/Reactor-1 Mainpuri
240MVAR B/Reactor-II BHIWANI | 29 | 125MVAR B/Reactor Gorakhpur-I
50MVAR B/Reactor HISAR | 30 | 125MVAR B/Reactor-II Gorakhpur
125MVAR B/Reactor HISAR | 31 | 125MVAR B/Reactor-I SHAHJHNPR
125MVAR Bus/eactor JIND | 32 | 240MVAR B/Reactor-I KANPUR(GIS)
125MVAR B/Reactor SONIPAT | 33 | 240MVAR B/Reactor-II KANPUR(GIS)
| 34 | 125MVAR B/Reactor-III KANPUR(GIS)
| 35 | 125MVAR B/Reactor-I VARANASI
| 36 | 330MVAR B/Reactor-I VARANASI
| 37 | 330MVAR B/Reactor-II VARANASI
| 38 | 125MVAR B/Reactor KANPUR
Note on E50: a: DOC-01.04.12
Note on I83: 220KV M'PURI-M'PURI(UP)-I LILO at SIRSAGANJ
Note on E84: a: DOC-01.04.12
Note on I86: '400KV M'PURI-PARICHA-I LILO at URI
Note on A96: Total-44.8km, PG-38.58km, HVPN-6.22km.
Note on A97: Total-45.6km, PG-26.64km, HVPN-19km.
Note on I98: DELL: 220KV ROORKI-SIDKUL
Note on C108: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C109: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on I112: LILO of 400KV MEERUT-KAITHAL-I at Baghpat
Note on I113: LILO of 400KV MEERUT-KAITHAL-II at Baghpat
Note on I128: LILO of 765KV FATEHPUR-GAYA at VARANASI

## SOP DATA NR3
Standard of Performance data for the month of June-2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD. NORTHERN REGION - III
NAME OF REGION : NR-III
ANNEXURE-A
Sr.No. | Unique ID of transmission Element | ELEMENT NAME | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Classification/ Category Code | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | Total Duration Available for Consideration | SIL | Ckt. Kms. | Weightage Factor | H=(G*(Z-@))/Z | % Availability as certified by certifying agency |  | Number of Sub-Conductor
[6 empty] | DATE TIME | DATE TIME | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[11 empty] | @ (T) | # (U) | & ( C ) | * (D) | [6 empty] | Z | ( E) | ( F) | G=E x F
[11 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  |  |  | Code |  |  | Hrs | E | F | G | H
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 19 | 20 | [5 empty] | 21
765 KV TRANS LINES
1 | NR376507 | 765KV ALIGARH-GR.NOIDA | 51 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100 | 720
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1327 | 51 | 67677 | 67677 |  |  | 4
2 | NR376506 | 765KV AGRA-ALIGARH | 122.5 | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1327 | 122.5 | 162557.5 | 162557.5 |  |  | 4
3 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR3 | -- | 2019-06-02 07:35 | 2019-06-03 15:23 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-04 07:47 | 2019-06-04 15:33 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
[6 empty] | 2019-06-12 08:12 | 2019-06-13 11:28 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=799 kV
[6 empty] | 2019-06-16 07:38 | 2019-06-18 19:46 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=790 kV
[6 empty] | 2019-06-23 08:09 | 2019-06-23 20:50 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
[6 empty] | 2019-06-24 17:10 | 2019-06-25 16:25 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1216 | 334.52 | 406776.32 | 406776.32 |  |  | 4
4 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR3 | -- | 2019-06-07 02:03 | 2019-06-07 15:06 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-27 07:18 | 2019-06-27 14:55 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792 kV
[6 empty] | 2019-06-30 07:55 | 2019-07-01 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-801kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1210 | 334.8 | 405108 | 405108
5 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR3 | -- | 2019-06-23 03:33 | 2019-06-23 14:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to B-N fault due to heavy rains and stormy winds. FD: 173.2kM from Balia and 125.6kM from Lucknow. FC: 3.54 kA at Balia and 3.8 kA from Lucknow. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1374 | 318.919 | 438194.706 | 438194.706 |  |  | 4
6 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1019 | 251.613 | 256393.647 | 256393.647 |  |  | 4
7 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1419 | 165.98 | 235525.62 | 235525.62 |  |  | 4
8 | NR176513 | 765KV VARANASI-FATEHPUR | 223 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1393 | 223 | 310639 | 310639 |  |  | 4
9 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1447 | 326.172 | 471970.884 | 471970.884 |  |  | 6
10 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1447 | 326.172 | 471970.884 | 471970.884 |  |  | 6
11 | NR376504 | 765KV ALIGARH-JHATIKARA | 158 | NR3 | -- | 2019-06-04 17:20 | 2019-06-04 21:53 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand Tripped from Jhatikara end to attend sparking in R-ph ICT-4 isolator. However as Main Bay at Jhatikara end was already out, so hand tripping of ICT caused tripping of line also. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-05 16:07 | 2019-06-05 16:48 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency Hand tripped due to gas pressure low alarm in one of the GD ( Gase Density monitor) of Aligarh-Jhatikara line at Aligarh end.
[6 empty] | 2019-06-26 07:48 | 2019-06-26 11:18 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency S/D availed for Y Ph jumper rectification work at loc no 965.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1440 | 158 | 227520 | 227520 |  |  | 4
12 | NR376505 | 765KV KANPUR(GIS)-ALIGARH | 327 | NR3 | -- | 2019-06-02 07:57 | 2019-06-03 08:02 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=798kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-12 08:11 | 2019-06-12 15:32 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=803 kV
[6 empty] | 2019-06-16 09:36 | 2019-06-16 18:33 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=802 kV
[6 empty] | 2019-06-18 03:36 | 2019-06-19 10:12 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=801 kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1440 | 327 | 470880 | 470880 |  |  | 4
13 | NR376508 | 765KV ORAI-ALIGARH-II | 331.958 | NR3 | -- | 2019-06-24 17:09 | 2019-06-24 17:32 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on B-N fault due to heavy rain and thunderstorm,F.D.=73.5km from Orai,F.C.=6.86KA, F.D.=236.4km from Aligarh,F.C.=3.2KA. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1440 | 331.958 | 478019.52 | 478019.52 |  |  | 6
14 | NR376509 | 765KV ORAI-ALIGARH-I | 331.958 | NR3 | -- | 2019-06-18 04:12 | 2019-06-18 13:04 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Orai=802 kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-26 17:45 | 2019-06-26 18:14 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on R-N fault. FD: Orai(PG)- 70.2km, Aligarh- 214km, FC: Orai- 6.3KA, Aligarh- 3.8KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1440 | 331.958 | 478019.52 | 478019.52 |  |  | 6
|  | 400 KV TRANS LINES |  |  | -- | [14 empty] | NRPC
1 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 43.013 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 43.013 | 22151.695 | 22151.695 |  |  | 2
2 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 29.982 | 15440.73 | 15440.73 |  |  | 2
3 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 57.159 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 57.159 | 29436.885 | 29436.885 |  |  | 2
4 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR3 | -- | 2019-06-01 07:47 | 2019-06-01 21:19 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-16 07:34 | 2019-06-16 16:57 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=428 kV
[6 empty] | 2019-06-24 16:56 | 2019-06-29 12:14 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 61362.4 |  |  | 2
5 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 | NR3 | -- | 2019-06-02 06:35 | 2019-06-03 14:36 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-09 12:16 | 2019-06-09 12:59 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to B-N fault. FD: 143.1km from Agra, FC:3.56kA.
[6 empty] | 2019-06-23 07:15 | 2019-06-23 20:18 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 367 | 167.2 | 61362.4 | 61362.4 |  |  | 2
6 | NR140005 | 400KV AGRA-BASSI-I | 211.433 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 245 | 211.433 | 51801.085 | 51801.085 |  |  | 2
7 | NR140008 | 400KV AGRA-BHIWADI-I | 208.98 | NR3 | -- | 2019-06-01 | 2019-06-01 18:11 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to Flashover in R-ph Line reactor at Agra end | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 402 | 208.98 | 84009.96 | 84009.96 |  |  | 2
8 | NR140009 | 400KV AGRA-BHIWADI-II | 209.51 | NR3 | -- | 2019-06-16 10:03 | 2019-06-16 16:51 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=429 kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-18 01:34 | 2019-06-19 13:46 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=430 kV
[6 empty] | 2019-06-23 07:43 | 2019-06-23 20:09 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=427kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 209.51 | 107897.65 | 107897.65 |  |  | 2
9 | NR140010 | 400KV AGRA-BLBGRH | 181.137 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 382 | 181.137 | 69194.334 | 69194.334 |  |  | 2
10 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 | NR3 | -- | 2019-06-23 07:35 | 2019-07-01 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=428kV | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 332 | 139.73 | 46390.36 | 46390.36 |  |  | 2
11 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 332 | 139.73 | 46390.36 | 46390.36 |  |  | 2
12 | NR140104 | 400KV ALLD-FATEHPUR-III | 155.932 | NR3 | -- | 2019-06-07 02:06 | 2019-06-07 20:31 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=427kV | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 155.932 | 80304.98 | 80304.98 |  |  | 2
13 | NR140012 | 400KV ALLD-KNP-II | 224 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 224 | 115360 | 115360 |  |  | 2
14 | NR140163 | 400KV ALLD-VARANASI | 98.792 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.792 | 50877.88 | 50877.88 |  |  | 2
15 | NR140019 | 400KV BALIA-MAU-I | 13 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 13 | 6695 | 6695 |  |  | 2
16 | NR140020 | 400KV BALIA-MAU-II | 13 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 13 | 6695 | 6695 |  |  | 2
17 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR3 | -- | 2019-06-25 15:43 | 2019-06-25 16:02 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on R-N fault. FD: Ballia- 115km, Sohawal- 105.5km, FC: Ballia- 3.81KA, Sohawal- 4.8KA. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 227 | 229.163 | 52020.001 | 52020.001 |  |  | 2
18 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 227 | 229.163 | 52020.001 | 52020.001 |  |  | 2
19 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 1.559 | 1071.033 | 1071.033 |  |  | 2
20 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 687 | 1.559 | 1071.033 | 1071.033 | 100 |  | 2
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
21 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 9.2 | 4738 | 4738 |  |  | 2
22 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 9.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 9.2 | 4738 | 4738 |  |  | 2
23 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.76 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 331 | 278.76 | 92269.56 | 92269.56 |  |  | 2
25 | NR140026 | 400KV BAREILLY-MBAD-I | 92.68 | NR3 | -- | 2019-06-12 05:36 | 2019-06-12 10:21 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on Y-B fault due to heavy stormy winds. Details at Bareilly: F/D=43.2 KM and F/C= Iy-9.02kA Ib-9.05kA. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 92.68 | 47730.2 | 47730.2 |  |  | 2
26 | NR140027 | 400KV BAREILLY-MBAD-II | 92.68 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 92.68 | 47730.2 | 47730.2 |  |  | 2
27 | NR340010 | 400KV BAREILLY-SHAHJHNPR-I | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 116.03 | 59755.45 | 59755.45 |  |  | 2
28 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.03 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 116.03 | 59755.45 | 59755.45 |  |  | 2
29 | NR140158 | 400KV BRLY(765)-KASHIPUR-I | 101.841 | NR3 |  | 2019-06-06 20:54 | 2019-06-06 22:36 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency hand tripped by Kashipur(PTCUL) due to heavy sparking in R Ph line isolator at Kashipur end | NRPC | [5 empty] | 100
[6 empty] | 2019-06-15 14:22 | 2019-06-15 14:48 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on Y-B fault. Detail at Bareilly- FC: Ir-1.3 kA, Ib-1.3kA.
[6 empty] | 2019-06-18 12:27 | 2019-06-18 13:15 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency S/D taken by Kashipur(PTCUL) to attend hot spot at their end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 101.841 | 69964.767 | 69964.767 |  |  | 4
30 | NR140159 | 400KV BRLY(765)-KASHIPUR-II | 101.841 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 101.841 | 69964.767 | 69964.767 |  |  | 4
31 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR3 | -- | 2019-06-10 11:59 | 2019-06-10 12:18 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to R-N fault. FD: 196.4km (M1) & 149.9km (M2) from Mainpuri and 46km from Ballabgarh. FC: 2.37 KA(M1) & 2.43kA (M2) at Mainpuri & 4 kA at Ballabgarh. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 235.952 | 121515.28 | 121515.28 |  |  | 2
32 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 235.952 | 121515.28 | 121515.28 |  |  | 2
33 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR3 | -- | 2019-06-17 17:09 | 2019-06-17 18:47 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to R-N fault. FD: Fatehpur- 9km, Mainpuri- 310km, FC: Fatehpur- 18.93KA, Mainpuri- 1.4KA. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-17 18:47 | 2019-06-17 19:08 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | After tripping, charging attempt taken but line got tripped on over voltage protection.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 469 | 260.051 | 121963.919 | 121963.919 |  |  | 2
34 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 469 | 260.051 | 121963.919 | 121963.919 |  |  | 2
35 | NR140046 | 400KV GORAKH-GORAKH-I | 45.94 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 45.94 | 23659.1 | 23659.1 |  |  | 2
36 | NR140047 | 400KV GORKH-GORAKH-II | 45.94 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 45.94 | 23659.1 | 23659.1 |  |  | 2
37 | NR140052 | 400KV KNP-AGRA | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 291 | 240 | 69840 | 69840 |  |  | 2
38 | NR140053 | 400KV KNP-AURAIYA-I | 72.6 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 72.6 | 37389 | 37389 |  |  | 2
39 | NR140054 | 400KV KNP-AURAIYA-II | 73.2 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 73.2 | 37698 | 37698 |  |  | 2
40 | NR140055 | 400KV KNP-BLBGARH-I | 385.69 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 342 | 385.69 | 131905.98 | 131905.98 |  |  | 2
41 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR3 | -- | 2019-06-04 10:43 | 2019-06-04 11:35 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | Hand Tripped from Ballabhgarh end due to chattering observed in PLCC Panel at Ballabhgarh end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 361 | 370.772 | 133848.692 | 133848.692 |  |  | 2
42 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 361 | 370.772 | 133848.692 | 133848.692 |  |  | 2
43 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 107.079 | 55145.685 | 55145.685 |  |  | 2
44 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 107.1 | 55156.5 | 55156.5 |  |  | 2
45 | NR140058 | 400KV KNP-PANKI-I | 5.922 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 5.922 | 3049.83 | 3049.83 |  |  | 2
46 | NR140059 | 400KV KNP-PANKI-II | 5.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 5.86 | 3017.9 | 3017.9 |  |  | 2
47 | NR140070 | 400KV LUCKNOW-GORAKH-III | 263.933 | NR3 | -- | 2019-06-29 10:05 | 2019-06-29 19:51 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by UPPTCL for overhead line crossing work | NRPC | [5 empty] | 100
[6 empty] | 2019-06-30 10:30 | 2019-06-30 19:18 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by UPPTCL for overhead line crossing work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 289 | 263.933 | 76276.637 | 76276.637 |  |  | 2
48 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 263.933 | NR3 | -- | 2019-06-29 10:05 | 2019-06-29 20:23 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by UPPTCL for overhead line crossing work | NRPC | [5 empty] | 100
[6 empty] | 2019-06-30 10:33 | 2019-06-30 19:27 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by UPPTCL for overhead line crossing work
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 289 | 263.933 | 76276.637 | 76276.637 |  |  | 2
49 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 |  |  | 4
50 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.86 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 2.86 | 1964.82 | 1964.82 |  |  | 4
51 | NR140072 | 400KV LUCKNOW-LKO(UP) | 41.743 | NR3 | -- | 2019-06-15 08:04 | 2019-06-22 13:57 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken for tapping of 400kV D/C Lucknow-Sulatanpur TL with new diverted 400kV D/C Lucknow-Sultanpur TL due to infringement on account of construction of Outer Ring Road by NHAI. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-22 13:57 | 2019-06-22 16:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D availed by UPPTCL for rectification work at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 41.743 | 21497.645 | 21497.645 |  |  | 2
52 | NR140114 | 400KV LUCKNOW-SHAHJHNPR-I | 169.785 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 371 | 169.785 | 62990.235 | 62990.235 |  |  | 2
53 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR3 |  | 2019-06-06 21:14 | 2019-06-06 21:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to B-N fault due to heavy rains and thunderstorm. FD: Shahjahanpur- 12.8km, LKO- 146km, FC: Shahjahapur- 12.89KA, LKO- 2.634KA. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 169.729 | 87410.435 | 87410.435 |  |  | 2
54 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.281 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.281 | 50614.715 | 50614.715 |  |  | 2
55 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.281 | NR3 |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 98.281 | 50614.715 | 50614.715 |  |  | 2
56 | NR140073 | 400KV LUCKNOW-SULTANPR | 41.743 | NR3 | -- | 2019-06-09 22:55 | 2019-06-09 23:44 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on DT Received at Lucknow end due to B-ph CT blast of 400kV Sultanpur-Tanda line at UPPTCL Sultanpur end resulting in complete black-out at UPPTCL Sultanpur S/S. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-15 08:11 | 2019-06-22 15:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken for tapping of 400kV D/C Lucknow-Sulatanpur TL with new diverted 400kV D/C Lucknow-Sultanpur TL due to infringement on account of construction of Outer Ring Road by NHAI.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 41.743 | 21497.645 | 21497.645 |  |  | 2
57 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | NR3 | -- | 2019-06-14 08:29 | 2019-06-14 17:54 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D Taken by UPPTCL for General Maintenance of Bay & Routine Protection Testing at 400kV Substation Unnao. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 73.826 | 38020.39 | 38020.39 |  |  | 2
58 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 734.52 | 515 | 73.826 | 38020.39 | 38020.39 |  |  | 2
59 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 30.703 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 691 | 30.703 | 21215.773 | 21215.773 |  |  | 4
60 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.159 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 691 | 31.159 | 21530.869 | 21530.869 |  |  | 4
61 | NR140084 | 400KV RIHAND-ALLD-I | 279.245 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 433 | 279.245 | 120913.085 | 120913.085 |  |  | 2
62 | NR140085 | 400KV RIHAND-ALLD-II | 279.245 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 433 | 279.245 | 120913.085 | 120913.085 |  |  | 2
63 | NR140091 | 400KV SING-ALLD-I | 224 | NR3 | -- | 2019-06-02 19:25 | 2019-06-02 20:15 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on R-N fault due to heavy rains and thunderstorm. FD: Singrauli-10.8km, ALLD- 225km, FC: Singrauli- 18.58KA, ALLD- 1.835KA. Charging code issued at 2015 hrs but line could not be charged due to isolator problem at NTPC-Singrauli (E-mail sent to NRLDC in this regard and copy enclosed) | NRPC | [5 empty] | 100
[6 empty] | 2019-06-02 20:15 | 2019-06-02 20:55 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | After tripping, charging code issued at 2015 hrs but could not be charged due to isolator problem at NTPC-Singrauli (E-mail sent to NRLDC in this regard and copy enclosed)
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 332 | 224 | 74368 | 74368 |  |  | 2
64 | NR140092 | 400KV SING-ALLD-II | 202 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 306 | 202 | 61812 | 61812 |  |  | 2
65 | NR140093 | 400KV SING-ANPARA | 25.057 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 25.057 | 12904.355 | 12904.355 |  |  | 2
66 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR3 | -- | 2019-06-02 17:28 | 2019-06-02 18:26 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on R-N fault due to heavy rains and thunderstorm. FD: FTP- 183.334km(AFAS), 209.2km(S/S), FC: FTP- 1.96KA. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 236 | 330.953 | 78104.908 | 78104.908 |  |  | 2
67 | NR140095 | 400KV SING-LKO(UP) | 408.6 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 337 | 408.6 | 137698.2 | 137698.2 |  |  | 2
68 | NR140096 | 400KV SING-RIHAND-I | 42.026 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 42.026 | 21643.39 | 21643.39 |  |  | 2
69 | NR140097 | 400KV SING-RIHAND-II | 43.952 | NR3 | -- | 2019-06-22 11:58 | 2019-06-24 19:55 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to failure(blast) of CVT and LA of R phase at NTPC-Singrauli end | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 43.952 | 22635.28 | 22635.28 |  |  | 2
70 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 3.341 | 1720.615 | 1720.615 |  |  | 2
71 | N-W40002 | 400KV SING-VINDH-II | 3.317 | NR3 | -- | 2019-06-22 11:58 | 2019-06-22 12:37 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped from NTPC Vindhyachal end due to failure(blast) of CVT and LA of R phase of 400kV Singrauli-Rihand-II Line at NTPC-Singrauli end. Tripping detail at Singrauli end: R-N fault, 24.05kM, Z3. Fault at NTPC Singrauli end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 3.317 | 1708.255 | 1708.255 |  |  | 2
72 | NR340004 | 400KV VARANASI-SARNATH-I | 69.677 | NR3 | -- | 2019-06-12 11:05 | 2019-06-12 14:04 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D availed by UPPTCL for testing of CVT at their end. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-15 16:03 | 2019-06-15 19:36 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency shutdown taken to attend Hot spot in Y-ph CVT Connector.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 69.677 | 35883.655 | 35883.655 |  |  | 4
73 | NR340005 | 400KV VARANASI-SARNATH-II | 69.677 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 69.677 | 35883.655 | 35883.655 |  |  | 4
74 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 21.233 | 14587.071 | 14587.071 |  |  | 4
75 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.233 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 21.233 | 14587.071 | 14587.071 |  |  | 4
76 | NR340010 | 400KV LKO(765)-KANPUR(GIS)-I | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 159.7 | 82245.5 | 82245.5 |  |  | 2
77 | NR340013 | 400KV LKO(765)-KANPUR(GIS)-II | 159.7 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 159.7 | 82245.5 | 82245.5 |  |  | 2
78 | NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR3 | -- | 2019-06-28 10:33 | 2019-06-28 20:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by Meja Urja Nigam Limited (MUNL) for maintenance works at their end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 28.19 | 14517.85 | 14517.85 |  |  | 2
79 | NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR3 | -- | 2019-06-29 09:54 | 2019-06-29 19:03 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by Meja Urja Nigam Limited (MUNL) for maintenance works | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 28.19 | 14517.85 | 14517.85 |  |  | 2
80 |  | 400KV Kanpur(GIS)-Allahabad-1 | 240.39 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 240.39 | 123800.85 | 123800.85 |  |  | 2
81 | NR340015 | 400KV Kanpur(GIS)-Allahabad-2 | 240.391 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 515 | 240.391 | 123801.365 | 123801.365 |  |  | 2
82 | NR340016 | 400KV ORAI-ORAI(UP)-I | 41.832 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 41.832 | 28738.584 | 28738.584 |  |  | 4
83 | NR340017 | 400KV ORAI-ORAI(UP)-II | 41.832 | NR3 | -- | 2019-06-16 15:13 | 2019-06-16 17:06 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on R-N fault. Detail at Orai(PG)-F.D.- 31.2kM,FC: Ir-4.5kA. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-26 16:33 | 2019-06-26 17:53 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on R-N fault. FD: Orai(PG)-34.2km, Orai(UP)- 0.76km, FC: Orai(PG)- 6.4KA, Orai(UP)- 18.6KA. Fault under UPPTCL jurisdiction
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 687 | 41.832 | 28738.584 | 28738.584 |  |  | 4
|  | 220kV Trans.Line | [17 empty] | NRPC
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 21.879 | 2888.028 | 2888.028 |  |  | 1
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 16.894 | 2230.008 | 2230.008 |  |  | 1
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 3 | NR3 | -- | 2019-06-23 11:38 | 2019-06-23 13:43 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D availed by UPPTCL for attending hot spot at their end | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 3 | 396 | 396 |  |  | 1
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 3 | NR3 | -- | 2019-06-07 10:30 | 2019-06-07 11:36 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to R-N Fault FD-21.2 Km from Allahabad. Zone II FC-5.7KA Fault in UPPTCL Jurisdiction. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-20 14:58 | 2019-06-20 17:23 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency S/D taken by UPPTCL for attending hot spot in Y-phase isolator at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 3 | 396 | 396 |  |  | 1
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.176 | NR3 | -- | 2019-06-26 14:07 | 2019-06-26 18:12 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to Bus Bar protection operated at Sikandra(UPPTCL) end and also resulting blackout at Sikandra(UPPTCL) Substation. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 182.176 | 24047.232 | 24047.232 |  |  | 1
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.176 | NR3 | -- | 2019-06-26 14:07 | 2019-06-26 18:13 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to Bus Bar protection operated at Sikandra(UPPTCL) end and also resulting blackout at Sikandra(UPPTCL) Substation. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 182.176 | 24047.232 | 24047.232 |  |  | 1
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 | NR3 | -- | 2019-06-24 10:35 | 2019-06-24 13:31 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped from UPPTCL CBGanj(Bareilly) end due to both Bus bar earth fault operated at CBGanj(Bareilly) end. Also all generating units were also tripped at NHPC/Dhauliganga, | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 109 | 234.59 | 25570.31 | 25570.31 |  |  | 2
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 | NR3 | -- | 2019-06-24 11:04 | 2019-06-24 11:39 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Due to Over-Voltage, Line was Hand Tripped at NHPC Dhauliganga end and D/T received at Pithoragarh end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 156 | 59.01 | 9205.56 | 9205.56 |  |  | 2
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 5.284 | 692.204 | 692.204 |  |  | 1
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 5.284 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 5.284 | 692.204 | 692.204 |  |  | 1
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 6.17 | 808.27 | 808.27 |  |  | 1
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 6.17 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 6.17 | 808.27 | 808.27 |  |  | 1
13 | NR122016 | 220KV KNP-MAINPURI | 10.4 | NR3 | -- | 2019-06-03 17:57 | 2019-06-03 20:28 |  |  | -- | 0 | 0 | 0 | 0 |  |  |  |  | E/S/D taken by UPPTCL to attend Hot spot at their end. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-20 08:50 | 2019-06-20 09:41 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to tripping of 220kV Mainpuri(UP)-Sikanadara(UP) and Mainpuri(UP) - Barh (UP) lines and Bus dead at Mainpuri(UPPTCL) end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 10.4 | 1362.4 | 1362.4 |  |  | 1
14 | NR122017 | 220KV KNP-NAUBASTA | 14.86 | NR3 | -- | 2019-06-16 12:10 | 2019-06-16 17:24 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | E/S/D taken to attend broken jumper of B-Phase(bottom) at Loc no. 75. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-20 17:05 | 2019-06-20 19:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency S/D taken by UPPTCL to rectify R-phase CT clamp of line at their end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 14.86 | 1946.66 | 1946.66 |  |  | 1
15 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP)-1 | 13.701 | NR3 | -- | 2019-06-01 | 2019-06-04 19:20 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | S/D availed by UPPTCL for de-stringing of 220KV Chhibramau-Panki line by UPPTCL | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 13.701 | 1794.831 | 1794.831 |  |  | 1
16 | NR122019 | 220KV KNP-PANKI-II | 14.86 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 14.86 | 1946.66 | 1946.66 |  |  | 1
17 | NR122020 | 220KV KNP-UNCHR-I | 143.553 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 143.553 | 18805.443 | 18805.443 |  |  | 1
18 | NR122021 | 220KV KNP-UNCHR-II | 143.553 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 143.553 | 18805.443 | 18805.443 |  |  | 1
19 | NR122022 | 220KV KNP-UNCHR-III | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 144.63 | 18946.53 | 18946.53 |  |  | 1
20 | NR122023 | 220KV KNP-UNCHR-IV | 144.63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 144.63 | 18946.53 | 18946.53 |  |  | 1
21 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | NR3 | -- | 2019-06-24 10:35 | 2019-06-24 11:04 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped from UPPTCL CBGanj(Bareilly) end due to both Bus bar earth fault operated at CBGanj(Bareilly) end. Also all generating units were also tripped at NHPC/Dhauliganga, | NRPC | [5 empty] | 100
[6 empty] | 2019-06-27 07:42 | 2019-06-27 15:03 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken for AMP works
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 156 | 177.88 | 27749.28 | 27749.28 |  |  | 2
22 | NR320003 | 220KV RAIBRLY-CG CITY(UP) | 2 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 1.19 | 157.08 | 157.08 |  |  | 1
23 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP) | 2 | NR3 | -- | 2019-06-24 10:42 | 2019-06-24 19:29 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | E/S/D taken by UPPTCL for attending hot spot at their end | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 1.19 | 157.08 | 157.08
24 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.72 | NR3 | -- | 2019-06-07 15:20 | 2019-06-07 16:11 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to multiple line trippings occurred at UPPTCL CBGANJ(Bareilly) S/S .Fault in UPPTCL Jurisdiction. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-25 11:13 | 2019-06-25 11:44 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency hand tripped to attend isolator Alignment problem at Sitarganj end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 105.72 | 13955.04 | 13955.04 |  |  | 1
25 | NR122033 | 220KV TNKPR-BLY(UP) | 106 | NR3 | -- | 2019-06-12 11:43 | 2019-06-12 12:49 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on R-Y-N fault phase fault. F.D.= 5.20KM from Bareilly (UP) due to tree cutting by local villagers below loc no 295-296 in line Corridor. Matter is sub-judiced in Allahabad High Court | NRPC | [5 empty] | 100
[6 empty] | 2019-06-24 10:35 | 2019-06-24 14:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped from UPPTCL CBGanj(Bareilly) end due to both Bus bar earth fault operated at CBGanj(Bareilly) end. Also all generating units were also tripped at NHPC/Dhauliganga,
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 106 | 13992 | 13992 |  |  | 1
26 | NR122034 | 220KV TNKPR-SITARGANJ | 42.55 | NR3 | -- | 2019-06-07 15:20 | 2019-06-07 16:07 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped only from Tanakpur (NHPC) end due to some protection problem at their end | NRPC | [5 empty] | 100
[6 empty] | 2019-06-12 05:46 | 2019-06-12 06:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Line tripped on R-G fault due to heavy stormy wind. Details at Sitargaj: F/D=0.4 KM and F/C= Ir-2.81kA.
[5 empty] | -- | 2019-06-25 11:13 | 2019-06-25 11:41 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency hand tripped to attend isolator Alignment problem at Sitarganj end
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 42.55 | 5616.6 | 5616.6 |  |  | 1
27 | NR122035 | 220KV UNCHR-RAIBRLY-I | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 0.92 | 121.44 | 121.44
28 | NR122036 | 220KV UNCHR-RAIBRLY-II | 0.92 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 0.92 | 121.44 | 121.44 |  |  | 1
29 | NR122037 | 220KV UNCHR-RAIBRLY-III | 42.5 | NR3 | -- | 2019-06-28 19:37 | 2019-06-28 20:49 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on Y-B fault. FD: 14.75km from Raebarelly, FC.=> Ib=6.25KA, Iy=5.8KA. Line charged from Raebarelly end at 2049hrs but could not synchronised from NTPC-Unchahar end due to B-ph CVT fuse failure at their end. | NRPC | [5 empty] | 100
[5 empty] | -- | 2019-06-28 20:49 | 2019-06-29 11:20 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by NTPC Unchahar to attend B-ph CVT fuse fail at Unchahar end.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 42.5 | 5610 | 5610 |  |  | 1
30 | NR320001 | 220KV KANPUR(PG) - RANIYA( UP)-1 | 1.683 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 131 | 18.372 | 2406.732 | 2406.732 |  |  | 1
31 |  | 220kV AGRA(PG)-SIKANDARA(UP) | 55.858 | NR3 | -- | 2019-06-01 14:19 | 2019-06-01 19:40 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to Y-B Ph fault. FD: Agra- 36.04km, Sikandra- 47km, FC: Agra- Iy- 4.95KA, Ib- 4.58KA. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-26 14:07 | 2019-06-26 18:01 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to Bus Bar protection operated at Sikandra(UPPTCL) end and also resulting blackout at Sikandra(UPPTCL) Substation.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 55.858 | 7373.256 | 7373.256 |  |  | 1
31 | NR320004 | 220kV AGRA(PG)-BHARATPUR(RRVPNL) | 55.858 | NR3 | -- | 2019-06-08 11:07 | 2019-06-08 16:56 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | E/S/D taken for repairing of damaged Multi strands of conductor at loc 64 and 113. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-20 10:41 | 2019-06-20 18:32 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken by RRVPNL for Maintenance of line & bay at their end.
[6 empty] | 2019-06-30 19:12 | 2019-06-30 20:23 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on B-N fault. FD: Agra- 14.9km, FC: Agra- 8.3KA.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 132 | 55.858 | 7373.256 | 7373.256 |  |  | 1
|  | 132 KV TRANS LINES |  |  | -- | [14 empty] | NRPC
1 | BILUP13201 | 132KV MAU-BALIA | 58 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 50 | 58 | 2900 | 2900 | 100 |  | 1
129 | Lines | TOTAL FOR T/LS | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC |  |  | 16215.198 | 9580362.112 | 9580362.112 | 100 | Lines availability
|  | OVERALL SYSTEM AVAILABILITY= | [9 empty] | 100 | % (HVDC) | 100 | [5 empty] | NRPC
|  | 765/400 KV ICT'S |  |  | -- | [14 empty] | NRPC |  | MVA |  | Weitage Factor
1 | NR1ICT707 | 765/400KV ICT-I AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
2 | NR1ICT708 | 400/765KV ICT-II AGRA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
3 | NR1ICT701 | 765/400kv ICT-I BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
4 | NR1ICT702 | 765/400kv ICT-II BALIA | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 1500 |  | 1500 | 1500 | 100
5 | NR1ICT705 | 765/400kv ICT-I FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
6 | NR1ICT706 | 765/400kv ICT-II FATEHPUR | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
11 | NR1ICT703 | 765/400kv ICT-I LUCKNOW | 1500 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
12 | NR1ICT704 | 765/400kv ICT-II LUCKNOW | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
15 | NR1ICT715 | 765/400kv ICT-I BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
16 | NR1ICT716 | 765/400kv ICT-II BAREILLY | 1500 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
17 | NR1ICT717 | 765/400KV ICT-I VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
18 | NR1ICT717 | 765/400KV ICT-II VARANASI | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
19 | NR3ICT701 | 765/400KV ICT-I Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
20 | NR3ICT702 | 765/400KV ICT-II Kanpur(GIS) | 1500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
21 | NR3ICT05 | 1000MVA ICT-1 ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1000 |  | 1000 | 1000
22 | NR3ICT06 | 1000MVA ICT-II ORAI(GIS) | 1000 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1000 |  | 1000 | 1000
|  | 400/220 KV ICT'S |  | NR3 | -- | [14 empty] | NRPC
1 | NR1ICT03 | 315MVA ICT-I AGRA | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 315 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 |  | 1500 | 1500
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315
10 | NR1ICT20 | 315MVA ICT-II KANPUR | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW | 500 | NR3 | -- | 2019-06-16 08:05 | 2019-06-16 17:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken for relay replacement. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 500 |  | 500 | 500
13 | NR1ICT26 | 315MVA ICT-I MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 315 |  | 315 | 315
15 | NR3ICT02 | 500MVA ICT-III MAINPURI | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
16 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 500 |  | 500 | 500 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
17 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR | 500 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 500 |  | 500 | 500 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
18 | NR1ICT59 | 315MVA ICT-I SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
19 | NR1ICT60 | 315MVA ICT-II SOHAWAL | 315 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 315 |  | 315 | 315 | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
|  | 220/132 KV ICT'S |  | NR3 | -- | [14 empty] | NRPC
1 | NR1ICT43 | 220/132KV ICT-I PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100
2 | NR1ICT44 | 220/132KV ICT-II PITHORAGRH | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 100 |  | 100 | 100 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0
3 | NR1ICT47 | 220/132KV ICT-I RAIBAREILLY | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100
4 | NR3ICT04 | 220/132KV ICT-II RAIBAREILLY | 200 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100
5 | NR1ICT39 | 220/132KV ICT-III RAIBAREILLY | 200 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100
6 | NR1ICT40 | 220/132KV ICT-I SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100
7 | NR1ICT41 | 220/132KV ICT-II SITARGANJ | 100 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100
46 |  | TOTAL FOR ICTs |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC |  | 31425 |  | 31425 | 31425 | 100 | %
|  | HVDC RIHAND-DADRI |  |  | -- | [14 empty] | NRPC |  | RC | Length
1 | NR1DCP01 | 500KV HVDC R-D POLE-I | 815 | NR3 | -- | 2019-06-15 09:28 | 2019-06-15 20:03 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Shutdown taken for replacement of Flashover Insulator String at four location in line | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 611250
2 | NR1DCP02 | 500KV HVDC R-D POLE-II | 815 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 750 | 815 | 611250 | 611250
3 | NR1DCP03 | HVDC BALIA-BHWD POLE-I | 789.786 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 987232.5
4 | NR1DCP04 | HVDC BALIA-BHWD POLE-II | 789.786 | NR3 | -- | 2019-06-06 11:31 | 2019-06-06 14:51 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency S/D taken for maintaining water level of valve cooling system at Bhiwadi end. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1250 | 789.786 | 987232.5 | 987232.5
5 | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I | 789.786 | NR3 | -- | 2019-06-28 12:03 | 2019-06-28 14:44 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency S/D taken for jumper rectification work at Loc. No. 3853. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000
6 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II | 789.786 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000
7 | NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III | 789.786 | NR3 | -- | 2019-06-28 12:03 | 2019-06-28 15:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Emergency S/D taken for jumper rectification work at Loc. No. 3853. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000
8 | NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV | 789.786 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 1500 | 1728 | 2592000 | 2592000
|  | TOTAL FOR HVDC line |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC |  |  | 10121.572 | 13564965 | 13564965 | 100 | %
|  | HVDC BTB VINDH |  |  | -- | [14 empty] | NRPC |  | RC
1 | NR1DCB01 | VINDH HVDC B/B BLOCK-I | 250 | NR3 | -- | 2019-06-02 19:38 | 2019-06-02 21:29 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to DC over current protection operated due to disturbance in western grid. | NRPC | [5 empty] | 100
[6 empty] | 2019-06-07 16:34 | 2019-06-07 17:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped due to operation of DC overcurrent protection caused by some external disturbance in NTPC Vindhyachal and also disturbance in western grid.
[6 empty] | 2019-06-13 16:16 | 2019-06-13 17:40 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on DC overcurent operated due to external disturbance in western system at VSTPP/NTPC.
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250
2 | NR1DCB02 | VINDH HVDC B/B BLOCK-II | 250 | NR3 | -- | 2019-06-19 11:13 | 2019-06-19 12:36 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Tripped on fine water high temperature (Valve cooling system) | NRPC | [5 empty] | 100
[6 empty] | 2019-06-27 10:17 | 2019-06-27 17:23 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | S/D taken for replacement of AirCell in converter transformer-2
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250
|  | TOTAL FOR HVDC VINDHYACHAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC |  |  |  | 500 | 500 | 100 | %
3 | NEDCB01 | Sasaram HVDC B/B BLOCK-I | 250 | NR3 | -- | 2019-06-21 23:03 | 2019-06-22 00:50 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | TRIPPED DUE TO TRIPPING OF 400 KV BSF-SASARAM-II ON O/V AT BIHARSHARIF END AS PER SCHEME. | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250
|  | HVDC BTB TOTAL |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC |  | RC
|  | SVC, KANPUR |  |  | -- | [14 empty] | NRPC |  | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1SVC01 | +/-140MVAR SVC-I |  | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 250 |  | 250 | 250
2 | NR1ICT46 | +/-140MVAR SVC-II | 280 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 280 |  | 280 | 280
|  | TOTAL FOR SVC |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC |  |  |  | 530 | 530 | 100 | %
|  | Bus & Switch Line Reactor |  |  | -- | [14 empty] | NRPC |  | MVAR |  | OHxMVARxMF | THMxMVARxMF
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
3 | NR1BRT36 | 240MVAR B/Reactor-1 AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765 | 240 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 80 |  | 80 | 80 | 100
6 | NR1BRT33 | 125MVAR B/Reactor ALLAHABAD | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 125 |  | 125 | 125 | 100
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA | 125 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765 | 240 | NR3 | -- | 2019-06-01 | 2019-06-03 02:47 | -- | -- | -- | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia=755/760kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-03 22:38 | 2019-06-11 08:17 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia=745/752kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765 | 240 | NR3 | -- | 2019-06-01 | 2019-06-03 03:53 | -- | -- |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia=738kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-10 23:25 | 2019-06-16 09:39 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 745 /752kV
[6 empty] | 2019-06-16 21:38 | 2019-07-01 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 755 /760kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY | 80 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80
14 | NR1BRT44 | 2X50MVAR B/Reactor-I BAREILLY | 50 | NR3 | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 100 |  | 100 | 100
15 | NR1BRT04 | 50MVAR B/Reactor- I BASSI | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 50 |  | 50 | 50
16 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
17 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
18 | NR1BRT23 | 330MVAR B/Reactor-III FATEHPUR-765 | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330
19 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
20 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
21 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW | 80 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 80 |  | 80 | 80
22 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
23 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 125 |  | 125 | 125 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
24 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765 | 240 | NR3 | -- | 2019-06-01 | 2019-06-01 11:12 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow=755/760kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-01 21:13 | 2019-06-02 07:03 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow=750kV
[6 empty] | 2019-06-03 22:45 | 2019-06-07 07:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow=747/756kV
[6 empty] | 2019-06-08 21:04 | 2019-06-10 08:30 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 759/769 kV
[6 empty] | 2019-06-10 23:29 | 2019-06-11 08:21 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 759/769 kV
[6 empty] | 2019-06-11 23:17 | 2019-06-12 06:09 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 755/764 kV
[6 empty] | 2019-06-13 23:18 | 2019-06-16 10:05 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 755/762kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240
25 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- |  | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
26 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
27 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
28 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N | 93.2 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 93.2 |  | 93.2 | 93.2 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
29 | NR1BRT42 | 125MVAR B/Reactor-I VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
30 | NR1BRT43 | 125MVAR B/Reactor-II VINDH | 125 | NR3 | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
31 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
32 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
33 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
34 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
35 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 330 |  | 330 | 330 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
36 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
37 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 50 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 50 |  | 50 | 50 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
38 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
39 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
40 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
41 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 63 |  | 63 | 63 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
42 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
43 | NR1SRT26 | LUCKNW 240MVAR S/R BAREILLY Ckt-I | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | 720 | 240 |  | 240 | 240 | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125
44 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765 | 240 | NR3 | -- | 2019-06-01 21:14 | 2019-06-02 06:46 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly=750kV | NRPC | [5 empty] | 100
[6 empty] | 2019-06-10 23:26 | 2019-06-11 08:17 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 759/769 kV
[6 empty] | 2019-06-11 23:12 | 2019-06-12 06:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 750/761 kV
[6 empty] | 2019-06-14 22:37 | 2019-06-15 06:43 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction.Bareilly = 754/765kV
[6 empty] | 2019-06-30 23:49 | 2019-07-01 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 750/765kV
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240
45 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330
46 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330
47 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 |  | %
48 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS) | 125 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 125 |  | 125 | 125 |  | %
49 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS) | 240 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 240 |  | 240 | 240 |  | %
50 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 |  | %
51 | NR3BRT08 | 330MVAR B/Reactor-II ALIGARH | 330 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 |  | %
52 | NR3BRT07 | 63MVAR B/Reactor-II SOHAWAL | 63 | NR3 | -- | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL |  |  | -- |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [6 empty] | 720 | 330 |  | 330 | 330 |  | %
53 | NR1BRT06 | 80MVAR B/Reactor BIHARSHARIF | 80 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
54 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I | 50 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
55 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
56 | NR1SRT04 | 50MVAR S/R BARLLY - MND Ckt-I | 50 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
57 | NR1SRT05 | 50MVAR S/R BARLLY - MND Ckt-II | 50 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
58 | NR1SRT24 | 80MVAR S/R GORAKH- Barh line-I | 80 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
59 | NR1SRT25 | 80MVAR S/R GORAKH- Barh line-II | 80 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
60 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS) | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
61 | NR3SRT01 | 240MVAR S/R VARANASI - KNP(GIS) ckt-I | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
62 | NR3SRT02 | 240MVAR S/R VARANASI - KNP(GIS) ckt-II | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
63 | NR3SRT03 | 330MVAR S/R KNP(GIS) -JHATIKRA ckt-1 | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
64 | NR3BRT05 | 125MVAR B/Reactor-I KANPUR | 125 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
65 | NR3BRT06 | 330MVAR B/Reactor-III VARANASI-765 | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
66 | NR3SLRT06 | ALIGARH 330MVAR Switachable L/R KANPUR | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
67 | NR3LRT07 | ORAI 240MVAR Non Switchable L/R ALIGARH-II | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
68 | NR3LRT08 | ALIGARH 240MVAR Non Switchable L/R ORAI-II | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
69 | NR3BRT10 | 330MVAR B/R-I ORAI | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
70 | NR3LRT09 | ORAI 330MVAR Non-Switchable L/R JABALPUR-I | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
71 | NR3LRT10 | ORAI 330MVAR Non-Switchable L/R JABALPUR-II | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC
72 | NR3BRT11 | 330MVAR Bus Reactor-II ORAI | 330 | NR3 | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | NRPC | [5 empty] | 100
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
73 | NR3LRT11 | ORAI 240MVAR Non-Switchable L/R SATNA | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
74 | NR3LRT12 | ORAI 240MVAR Non-Switchable L/R ALIGARH-I | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
75 | NR3LRT13 | ALIGARH 240MVAR Non-Switchable L/R ORAI-I | 240 | NR3 | [6 empty] | 0 | 0 | 0 | 0
|  | SUB TOTAL | [8 empty] | 0 | 0 | 0 | 0
|  | TOTAL FOR Reactor |  |  | -- | [5 empty] | 0 | 0 | 0 | 0 | [7 empty] | 10683.4 |  | 10683.4 | 10683.4 | 100
Formulas:
ISTS Licensee = IF(RIGHT([Classification/ Category Code])="T",(+[RESTORATION]-[OUTAGE]),0)
ISTS Licensee = SUM([ISTS Licensee, row above]:[ISTS Licensee, row above])
OTHERS = IF(RIGHT([Classification/ Category Code])="U",(+[RESTORATION]-[OUTAGE]),0)
OTHERS = SUM([OTHERS, row above]:[OTHERS, row above])
Hrs:Min = IF(RIGHT([Classification/ Category Code])="C",(+[RESTORATION]-[OUTAGE]),0)
Hrs:Min = SUM([Hrs:Min, row above]:[Hrs:Min, row above])
Deemed Available = IF(RIGHT([Classification/ Category Code])="D",(+[RESTORATION]-[OUTAGE]),0)
Deemed Available = SUM([Deemed Available, row above]:[Deemed Available, row above])
Note on C11: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C13: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C32: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C34: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C36: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C38: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C42: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C109: Divya Kushwaha {Divya Kushwaha}: LILO of Bareilly rosa 1
Note on C111: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on C207: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C210: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C301: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I
Note on C303: Divya Kushwaha {Divya Kushwaha}: LILO of 220KV KNP-PANKI-I

## Master (hidden)
POWER GRID CORPORATION OF INDIA LTD.
DOC No: NR-III-CPCC- |  | DOC No: NR-III-CPCC-
MONTH –August LINE- ICT OUTAGE DETAILS |  | June"19
CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | NRLDC CODE | Classification- Category Code | REASON OF OUTAGE
|  |  | DATE TIME | DATE TIME | POWER GRID | OTHERS | System constraint- Natural calamity- Militancy | Deemed Available
[5 empty] | @ (T) | # (U) | & ( C ) | * (D)
[5 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min |  | Code
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 11 | 12
NR1DCB01 | 306016 | VINDH HVDC B/B BLOCK-I | 2019-06-02 19:38 | 2019-06-02 21:29 | 0 | 0.077083 | 0 | 0 | **** | OMSU | Tripped due to DC over current protection operated due to disturbance in western grid.
NR1DCB01 | 306043 | VINDH HVDC B/B BLOCK-I | 2019-06-07 16:34 | 2019-06-07 17:58 | 0 | 0.058333 | 0 | 0 | **** | OMSU | Tripped due to operation of DC overcurrent protection caused by some external disturbance in NTPC Vindhyachal and also disturbance in western grid.
NR1DCB01 | 306071 | VINDH HVDC B/B BLOCK-I | 2019-06-13 16:16 | 2019-06-13 17:40 | 0 | 0 | 0.058333 | 0 | **** | GGDC | Tripped on DC overcurent operated due to external disturbance in western system at VSTPP/NTPC.
NR1DCB02 | 306106 | VINDH HVDC B/B BLOCK-II | 2019-06-19 11:13 | 2019-06-19 12:36 | 0.057639 | 0 | 0 | 0 | **** | OMST | Tripped on fine water high temperature (Valve cooling system)
NR1DCB02 | 306154 | VINDH HVDC B/B BLOCK-II | 2019-06-27 10:17 | 2019-06-27 17:23 | 0.29583 | 0 | 0 | 0 | N-1873 | OSPT | S/D taken for replacement of AirCell in converter transformer-2
NEDCB01 | 306110A | +/-500MW HVDC B/B SASARAM | 2019-06-21 23:03 | 2019-06-22 00:50 | 0 | 0.074306 | 0 | 0 | **** | OMSU | TRIPPED DUE TO TRIPPING OF 400 KV BSF-SASARAM-II ON O/V AT BIHARSHARIF END AS PER SCHEME.
NRNEDCP03 | 306158 | 800KV HVDC AGRA-APD POLE-III | 2019-06-28 12:03 | 2019-06-28 15:00 | 0.12292 | 0 | 0 | 0 | N-1983 | OSPT | Emergency S/D taken for jumper rectification work at Loc. No. 3853.
NRNEDCP01 | 306159 | 800KV HVDC AGRA-BNC POLE-I | 2019-06-28 12:03 | 2019-06-28 14:44 | 0.11181 | 0 | 0 | 0 | N-1984 | OSPT | Emergency S/D taken for jumper rectification work at Loc. No. 3853.
NR1DCP04 | 306033 | 500KV HVDC BALIA-BHWD POLE-II | 2019-06-06 11:31 | 2019-06-06 14:51 | 0.13889 | 0 | 0 | 0 | N-338 | OSPT | Emergency S/D taken for maintaining water level of valve cooling system at Bhiwadi end.
NR1DCP01 | 306077 | 500KV HVDC R-D POLE-I | 2019-06-15 09:28 | 2019-06-15 20:03 | 0.44097 | 0 | 0 | 0 | N-964 | OSPT | Shutdown taken for replacement of Flashover Insulator String at four location in line
NR176502 | 306011 | 765KV AGRA-FATEHPUR-I | 2019-06-02 07:35 | 2019-06-03 15:23 | 0 | 0 | 0 | 1899-12-31 07:48 | N-87 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
NR176502 | 306021 | 765KV AGRA-FATEHPUR-I | 2019-06-04 07:47 | 2019-06-04 15:33 | 0 | 0 | 0 | 0.32361 | N-221 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=796kV
NR176502 | 306067 | 765KV AGRA-FATEHPUR-I | 2019-06-12 08:12 | 2019-06-13 11:28 | 0 | 0 | 0 | 1899-12-31 03:16 | N-704 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=799 kV
NR176502 | 306081 | 765KV AGRA-FATEHPUR-I | 2019-06-16 07:38 | 2019-06-18 19:46 | 0 | 0 | 0 | 1900-01-01 12:08 | N-1026 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=790 kV
NR176502 | 306122 | 765KV AGRA-FATEHPUR-I | 2019-06-23 08:09 | 2019-06-23 20:50 | 0 | 0 | 0 | 0.52847 | N-1610 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176502 | 306131 | 765KV AGRA-FATEHPUR-I | 2019-06-24 17:10 | 2019-06-25 16:25 | 0 | 0 | 0 | 0.96875 | N-1686 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=790kV
NR176507 | 306038 | 765KV AGRA-FATEHPUR-II | 2019-06-07 02:03 | 2019-06-07 15:06 | 0 | 0 | 0 | 0.54375 | N-390 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=791kV
NR176507 | 306152 | 765KV AGRA-FATEHPUR-II | 2019-06-27 07:18 | 2019-06-27 14:55 | 0 | 0 | 0 | 0.31736 | N-1849 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=792 kV
NR176507 | 306167 | 765KV AGRA-FATEHPUR-II | 2019-06-30 07:55 | 2019-07-01 | 0 | 0 | 0 | 0.67014 | N-2142 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra-801kV
NR376504 | 306023 | 765KV ALIGARH-JHATIKARA | 2019-06-04 17:20 | 2019-06-04 21:53 | 0.18958 | 0 | 0 | 0 | **** | OSFT | Hand Tripped from Jhatikara end to attend sparking in R-ph ICT-4 isolator. However as Main Bay at Jhatikara end was already out, so hand tripping of ICT caused tripping of line also.
NR376504 | 306028 | 765KV ALIGARH-JHATIKARA | 2019-06-05 16:07 | 2019-06-05 16:48 | 0.028472 | 0 | 0 | 0 | **** | OSFT | Emergency Hand tripped due to gas pressure low alarm in one of the GD ( Gase Density monitor) of Aligarh-Jhatikara line at Aligarh end.
NR376504 | 306145 | 765KV ALIGARH-JHATIKARA | 2019-06-26 07:48 | 2019-06-26 11:18 | 0.14583 | 0 | 0 | 0 | N-1786 | OSPT | Emergency S/D availed for Y Ph jumper rectification work at loc no 965.
NR376505 | 306012 | 765KV KANPUR(GIS)-ALIGARH | 2019-06-02 07:57 | 2019-06-03 08:02 | 0 | 0 | 0 | 1899-12-31 00:05 | N-88 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=798kV
NR376505 | 306066 | 765KV KANPUR(GIS)-ALIGARH | 2019-06-12 08:11 | 2019-06-12 15:32 | 0 | 0 | 0 | 0.30625 | N-705 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=803 kV
NR376505 | 306083 | 765KV KANPUR(GIS)-ALIGARH | 2019-06-16 09:36 | 2019-06-16 18:33 | 0 | 0 | 0 | 0.37292 | N-1036 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=802 kV
NR376505 | 306100 | 765KV KANPUR(GIS)-ALIGARH | 2019-06-18 03:36 | 2019-06-19 10:12 | 0 | 0 | 0 | 1899-12-31 06:36 | N-1174 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=801 kV
NR176501 | 306118 | 765KV LUCKNOW-BALIA | 2019-06-23 03:33 | 2019-06-23 14:16 | 0 | 0 | 0.44653 | 0 | **** | LNCC | Tripped due to B-N fault due to heavy rains and stormy winds. FD: 173.2kM from Balia and 125.6kM from Lucknow. FC: 3.54 kA at Balia and 3.8 kA from Lucknow.
NR376509 | 306101 | 765KV ORAI-ALIGARH-I | 2019-06-18 04:12 | 2019-06-18 13:04 | 0 | 0 | 0 | 0.36944 | N-1177 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Orai=802 kV
NR376509 | 306151 | 765KV ORAI-ALIGARH-I | 2019-06-26 17:45 | 2019-06-26 18:14 | 0.020139 | 0 | 0 | 0 | **** | LEFT | Tripped on R-N fault. FD: Orai(PG)- 70.2km, Aligarh- 214km, FC: Orai- 6.3KA, Aligarh- 3.8KA.
NR376508 | 306134 | 765KV ORAI-ALIGARH-II | 2019-06-24 17:09 | 2019-06-24 17:32 | 0 | 0 | 0.015972 | 0 | **** | LNCC | Tripped on B-N fault due to heavy rain and thunderstorm,F.D.=73.5km from Orai,F.C.=6.86KA, F.D.=236.4km from Aligarh,F.C.=3.2KA.
NR140003 | 306001 | 400KV AGRA-AURAIYA-I | 2019-06-01 07:47 | 2019-06-01 21:19 | 0 | 0 | 0 | 0.56389 | N-05 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=434kV
NR140003 | 306080 | 400KV AGRA-AURAIYA-I | 2019-06-16 07:34 | 2019-06-16 16:57 | 0 | 0 | 0 | 0.39097 | N-1027 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=428 kV
NR140003 | 306130 | 400KV AGRA-AURAIYA-I | 2019-06-24 16:56 | 2019-06-29 12:14 | 0 | 0 | 0 | 1900-01-03 19:18 | N-1685 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=431kV
NR140004 | 306010 | 400KV AGRA-AURAIYA-II | 2019-06-02 06:35 | 2019-06-03 14:36 | 0 | 0 | 0 | 1899-12-31 08:01 | N-82 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=430kV
NR140004 | 306051 | 400KV AGRA-AURAIYA-II | 2019-06-09 12:16 | 2019-06-09 12:59 | 0.029861 | 0 | 0 | 0 | **** | LEFT | Tripped due to B-N fault. FD: 143.1km from Agra, FC:3.56kA.
NR140004 | 306119 | 400KV AGRA-AURAIYA-II | 2019-06-23 07:15 | 2019-06-23 20:18 | 0 | 0 | 0 | 0.54375 | N-1605 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=429kV
NR140008 | 305167 | 400KV AGRA-BHIWADI-I | 2019-06-01 | 2019-06-01 18:11 | 0.75764 | 0 | 0 | 0 | **** | OMST | Tripped due to Flashover in R-ph Line reactor at Agra end
NR140009 | 306084 | 400KV AGRA-BHIWADI-II | 2019-06-16 10:03 | 2019-06-16 16:51 | 0 | 0 | 0 | 0.28333 | N-1040 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Aligarh=429 kV
NR140009 | 306099 | 400KV AGRA-BHIWADI-II | 2019-06-18 01:34 | 2019-06-19 13:46 | 0 | 0 | 0 | 1899-12-31 12:12 | N-1166 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. AGRA=430 kV
NR140009 | 306121 | 400KV AGRA-BHIWADI-II | 2019-06-23 07:43 | 2019-06-23 20:09 | 0 | 0 | 0 | 0.51806 | N-1608 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Agra=427kV
NR340008 | 306157 | 400KV ALLAHABAD-MEJA(NTPC)-I | 2019-06-28 10:33 | 2019-06-28 20:16 | 0 | 0 | 0 | 0.40486 | N-1978 | OSPD | S/D taken by Meja Urja Nigam Limited (MUNL) for maintenance works at their end.
NR340009 | 306166 | 400KV ALLAHABAD-MEJA(NTPC)-II | 2019-06-29 09:54 | 2019-06-29 19:03 | 0 | 0 | 0 | 0.38125 | N-2073 | OSPD | S/D taken by Meja Urja Nigam Limited (MUNL) for maintenance works
NR140122 | 306120 | 400KV ALLD-FATEHPUR-I | 2019-06-23 07:35 | 2019-07-01 | 0 | 0 | 0 | 1900-01-06 16:25 | N-1607 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. FTP=428kV
NR140104 | 306039 | 400KV ALLD-FATEHPUR-III | 2019-06-07 02:06 | 2019-06-07 20:31 | 0 | 0 | 0 | 0.76736 | N-391 | LVRD | Hand tripped on Voltage regulation as per NRLDC instruction. Allahabad=427kV
NR140140 | 306142 | 400KV BALIA-SOHAWAL-I | 2019-06-25 15:43 | 2019-06-25 16:02 | 0.013194 | 0 | 0 | 0 | **** | LEFT | Tripped on R-N fault. FD: Ballia- 115km, Sohawal- 105.5km, FC: Ballia- 3.81KA, Sohawal- 4.8KA.
NR140026 | 306064 | 400KV BAREILLY-MBAD-I | 2019-06-12 05:36 | 2019-06-12 10:21 | 0 | 0 | 0.19792 | 0 | **** | LNCC | Tripped on Y-B fault due to heavy stormy winds. Details at Bareilly: F/D=43.2 KM and F/C= Iy-9.02kA Ib-9.05kA.
NR140158 | 306034 | 400KV BARLY(765)-KASHIPUR-I | 2019-06-06 20:54 | 2019-06-06 22:36 | 0 | 0 | 0 | 0.070833 | **** | OSFD | Emergency hand tripped by Kashipur(PTCUL) due to heavy sparking in R Ph line isolator at Kashipur end
NR140158 | 306078 | 400KV BARLY(765)-KASHIPUR-I | 2019-06-15 14:22 | 2019-06-15 14:48 | 0.018056 | 0 | 0 | 0 | **** | LPPT | Tripped on Y-B fault. Detail at Bareilly- FC: Ir-1.3 kA, Ib-1.3kA.
NR140158 | 306103 | 400KV BARLY(765)-KASHIPUR-I | 2019-06-18 12:27 | 2019-06-18 13:15 | 0 | 0 | 0 | 0.033333 | N-1204 | OSFD | Emergency S/D taken by Kashipur(PTCUL) to attend hot spot at their end
NR140037 | 306058 | 400KV BLBGRH-MAINPURI-I | 2019-06-10 11:59 | 2019-06-10 12:18 | 0.013194 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault. FD: 196.4km (M1) & 149.9km (M2) from Mainpuri and 46km from Ballabgarh. FC: 2.37 KA(M1) & 2.43kA (M2) at Mainpuri & 4 kA at Ballabgarh.
NR140124 | 306096 | 400KV FATEHPUR-MAINPURI-I | 2019-06-17 17:09 | 2019-06-17 18:47 | 0.068056 | 0 | 0 | 0 | **** | LEFT | Tripped due to R-N fault. FD: Fatehpur- 9km, Mainpuri- 310km, FC: Fatehpur- 18.93KA, Mainpuri- 1.4KA.
NR140124 | 306097 | 400KV FATEHPUR-MAINPURI-I | 2019-06-17 18:47 | 2019-06-17 19:08 | 0 | 0 | 0.014583 | 0 | **** | GOVC | After tripping, charging attempt taken but line got tripped on over voltage protection.
NR140056 | 306022 | 400KV KNP-BLBGARH-II | 2019-06-04 10:43 | 2019-06-04 11:35 | 0.036111 | 0 | 0 | 0 | **** | OSFT | Hand Tripped from Ballabhgarh end due to chattering observed in PLCC Panel at Ballabhgarh end.
NR140070 | 306164 | 400KV LUCKNOW-GORAKH-III | 2019-06-29 10:05 | 2019-06-29 19:51 | 0 | 0 | 0 | 0.40694 | N-2068 | OSPD | S/D taken by UPPTCL for overhead line crossing work
NR140070 | 306168 | 400KV LUCKNOW-GORAKH-III | 2019-06-30 10:30 | 2019-06-30 19:18 | 0 | 0 | 0 | 0.36667 | N-2152 | OSPD | S/D taken by UPPTCL for overhead line crossing work
NR140071 | 306165 | 400KV LUCKNOW-GORAKH-IV | 2019-06-29 10:05 | 2019-06-29 20:23 | 0 | 0 | 0 | 0.42917 | N-2068 | OSPD | S/D taken by UPPTCL for overhead line crossing work
NR140071 | 306169 | 400KV LUCKNOW-GORAKH-IV | 2019-06-30 10:33 | 2019-06-30 19:27 | 0 | 0 | 0 | 0.37083 | N-2152 | OSPD | S/D taken by UPPTCL for overhead line crossing work
NR140072 | 306075 | 400KV LUCKNOW-LKO(UP) | 2019-06-15 08:04 | 2019-06-22 13:57 | 0 | 0 | 0 | 1900-01-06 05:53 | N-955 | LCSD | S/D taken for tapping of 400kV D/C Lucknow-Sulatanpur TL with new diverted 400kV D/C Lucknow-Sultanpur TL due to infringement on account of construction of Outer Ring Road by NHAI.
NR140072 | 306115 | 400KV LUCKNOW-LKO(UP) | 2019-06-22 13:57 | 2019-06-22 16:07 | 0 | 0 | 0 | 0.090278 | N-1560 | OSFD | S/D availed by UPPTCL for rectification work at their end.
NR140153 | 306037 | 400KV LUCKNOW-SHAHJHNPR-II | 2019-06-06 21:14 | 2019-06-06 21:43 | 0 | 0 | 0.020139 | 0 | **** | LNCC | Tripped due to B-N fault due to heavy rains and thunderstorm. FD: Shahjahanpur- 12.8km, LKO- 146km, FC: Shahjahapur- 12.89KA, LKO- 2.634KA.
NR140073 | 306056 | 400KV LUCKNOW-SULTANPR | 2019-06-09 22:55 | 2019-06-09 23:44 | 0 | 0.034028 | 0 | 0 | **** | OMSU | Tripped on DT Received at Lucknow end due to B-ph CT blast of 400kV Sultanpur-Tanda line at UPPTCL Sultanpur end resulting in complete black-out at UPPTCL Sultanpur S/S.
NR140073 | 306076 | 400KV LUCKNOW-SULTANPR | 2019-06-15 08:11 | 2019-06-22 15:00 | 0 | 0 | 0 | 1900-01-06 06:49 | N-956 | LCSD | S/D taken for tapping of 400kV D/C Lucknow-Sulatanpur TL with new diverted 400kV D/C Lucknow-Sultanpur TL due to infringement on account of construction of Outer Ring Road by NHAI.
NR140074 | 306073 | 400KV LUCKNOW-UNNAO-I | 2019-06-14 08:29 | 2019-06-14 17:54 | 0 | 0 | 0 | 0.39236 | N-877 | OSPD | S/D Taken by UPPTCL for General Maintenance of Bay & Routine Protection Testing at 400kV Substation Unnao.
NR140130 | 306036 | 400KV MEERUT-BAREILLY-II | 2019-06-06 17:59 | 2019-06-06 19:11 | 0 | 0.05 | 0 | 0 | **** | OMSU | Tripped on Y-N fault. FD: Bareilly- 129.5km, FC: Bareilly- 2.919KA. Fault in Powerlink jurisdiction
NR340017 | 306086 | 400KV ORAI-ORAI(UP)-II | 2019-06-16 15:13 | 2019-06-16 17:06 | 0.078472 | 0 | 0 | 0 | **** | LEFT | Tripped on R-N fault. Detail at Orai(PG)-F.D.- 31.2kM,FC: Ir-4.5kA.
NR340017 | 306150 | 400KV ORAI-ORAI(UP)-II | 2019-06-26 16:33 | 2019-06-26 17:53 | 0 | 0.055556 | 0 | 0 | **** | OMSU | Tripped on R-N fault. FD: Orai(PG)-34.2km, Orai(UP)- 0.76km, FC: Orai(PG)- 6.4KA, Orai(UP)- 18.6KA. Fault under UPPTCL jurisdiction
NR140091 | 306014 | 400KV SING-ALLD-I | 2019-06-02 19:25 | 2019-06-02 20:15 | 0 | 0 | 0.034722 | 0 | **** | LNCC | Tripped on R-N fault due to heavy rains and thunderstorm. FD: Singrauli-10.8km, ALLD- 225km, FC: Singrauli- 18.58KA, ALLD- 1.835KA. Charging code issued at 2015 hrs but line could not be charged due to isolator problem at NTPC-Singrauli (E-mail sent to NRLDC in this regard and copy enclosed)
NR140091 | 306015 | 400KV SING-ALLD-I | 2019-06-02 20:15 | 2019-06-02 20:55 | 0 | 0.027778 | 0 | 0 |  | OMSU | After tripping, charging code issued at 2015 hrs but could not be charged due to isolator problem at NTPC-Singrauli (E-mail sent to NRLDC in this regard and copy enclosed)
NR140111 | 306013 | 400KV SING-FATEHPUR | 2019-06-02 17:28 | 2019-06-02 18:26 | 0 | 0 | 0.040278 | 0 | **** | LNCC | Tripped on R-N fault due to heavy rains and thunderstorm. FD: FTP- 183.334km(AFAS), 209.2km(S/S), FC: FTP- 1.96KA.
NR140097 | 306114 | 400KV SING-RIHAND-II | 2019-06-22 11:58 | 2019-06-24 19:55 | 0 | 1900-01-01 07:57 | 0 | 0 | **** | SEFU | Tripped due to failure(blast) of CVT and LA of R phase at NTPC-Singrauli end
N-W40002 | 306113 | 400KV SING-VINDH-II | 2019-06-22 11:58 | 2019-06-22 12:37 | 0 | 0.027083 | 0 | 0 | **** | OMSU | Tripped from NTPC Vindhyachal end due to failure(blast) of CVT and LA of R phase of 400kV Singrauli-Rihand-II Line at NTPC-Singrauli end. Tripping detail at Singrauli end: R-N fault, 24.05kM, Z3. Fault at NTPC Singrauli end.
NR340004 | 306068 | 400KV VARANASI-SARNATH-I | 2019-06-12 11:05 | 2019-06-12 14:04 | 0 | 0 | 0 | 0.12431 | N-727 | OSPD | S/D availed by UPPTCL for testing of CVT at their end.
NR340004 | 306079 | 400KV VARANASI-SARNATH-I | 2019-06-15 16:03 | 2019-06-15 19:36 | 0.14792 | 0 | 0 | 0 | N-998 | 'OSPT | Emergency shutdown taken to attend Hot spot in Y-ph CVT Connector.
NR322002 | 305143 | 220 KV RANIYA( UP) - PANKI (UP) | 2019-06-01 | 2019-06-04 19:20 | 0 | 0 | 0 | 1900-01-02 19:20 | N-1926 | OSPD | S/D availed by UPPTCL for de-stringing of 220KV Chhibramau-Panki line by UPPTCL
NR320004 | 306047 | 220kv Agra(PG)-Bharatpur(Raj.) | 2019-06-08 11:07 | 2019-06-08 16:56 | 0.24236 | 0 | 0 | 0 | N-475 | 'OSPT | E/S/D taken for repairing of damaged Multi strands of conductor at loc 64 and 113.
NR320004 | 306108 | 220kv Agra(PG)-Bharatpur(Raj.) | 2019-06-20 10:41 | 2019-06-20 18:32 | 0 | 0 | 0 | 0.32708 | N- 1354 | OSPD | S/D taken by RRVPNL for Maintenance of line & bay at their end.
NR320004 | 306171 | 220kv Agra(PG)-Bharatpur(Raj.) | 2019-06-30 19:12 | 2019-06-30 20:23 | 0.049306 | 0 | 0 | 0 | **** | LEFT | Tripped on B-N fault. FD: Agra- 14.9km, FC: Agra- 8.3KA.
NR320003 | 306003 | 220kv Agra(PG)-Sikandara(UP) | 2019-06-01 14:19 | 2019-06-01 19:40 | 0.22292 | 0 | 0 | 0 | **** | LPPT | Tripped due to Y-B Ph fault. FD: Agra- 36.04km, Sikandra- 47km, FC: Agra- Iy- 4.95KA, Ib- 4.58KA.
NR320003 | 306146 | 220kv Agra(PG)-Sikandara(UP) | 2019-06-26 14:07 | 2019-06-26 18:01 | 0 | 0.1625 | 0 | 0 | **** | SBBU | Tripped due to Bus Bar protection operated at Sikandra(UPPTCL) end and also resulting blackout at Sikandra(UPPTCL) Substation.
BILUP2202 | 306123 | 220KV ALLD-REWA RD-I | 2019-06-23 11:38 | 2019-06-23 13:43 | 0 | 0 | 0 | 0.086806 | N-1618 | OSPD | S/D availed by UPPTCL for attending hot spot at their end
BILUP2203 | 306040 | 220KV ALLD-REWA RD-II | 2019-06-07 10:30 | 2019-06-07 11:36 | 0 | 0.045833 | 0 | 0 | **** | OMSU | Tripped due to R-N Fault FD-21.2 Km from Allahabad. Zone II FC-5.7KA Fault in UPPTCL Jurisdiction.
BILUP2203 | 306109 | 220KV ALLD-REWA RD-II | 2019-06-20 14:58 | 2019-06-20 17:23 | 0 | 0 | 0 | 0.10069 | N- 1374 | OSFD | Emergency S/D taken by UPPTCL for attending hot spot in Y-phase isolator at their end.
NR122006 | 306147 | 220KV AUR-SIKANDARA-I | 2019-06-26 14:07 | 2019-06-26 18:12 | 0 | 0.17014 | 0 | 0 | **** | SBBU | Tripped due to Bus Bar protection operated at Sikandra(UPPTCL) end and also resulting blackout at Sikandra(UPPTCL) Substation.
NR122007 | 306148 | 220KV AUR-SIKANDARA-II | 2019-06-26 14:07 | 2019-06-26 18:13 | 0 | 0.17083 | 0 | 0 | **** | SBBU | Tripped due to Bus Bar protection operated at Sikandra(UPPTCL) end and also resulting blackout at Sikandra(UPPTCL) Substation.
NR122012 | 306127 | 220KV DGANGA-BLY(UP)-II | 2019-06-24 10:35 | 2019-06-24 13:31 | 0 | 0.12222 | 0 | 0 | **** | OMSU | Tripped from UPPTCL CBGanj(Bareilly) end due to both Bus bar earth fault operated at CBGanj(Bareilly) end. Also all generating units were also tripped at NHPC/Dhauliganga,
NR122013 | 306129 | 220KV DGANGA-PITHORAGRH | 2019-06-24 11:04 | 2019-06-24 11:39 | 0 | 0.024306 | 0 | 0 | **** | OMSU | Due to Over-Voltage, Line was Hand Tripped at NHPC Dhauliganga end and D/T received at Pithoragarh end.
NR122016 | 306018 | 220KV KNP-MAINPURI | 2019-06-03 17:57 | 2019-06-03 20:28 | 0 | 0 | 0 | 0.10486 | N-188 | OSFD | E/S/D taken by UPPTCL to attend Hot spot at their end.
NR122016 | 306107 | 220KV KNP-MAINPURI | 2019-06-20 08:50 | 2019-06-20 09:41 | 0 | 0.035417 | 0 | 0 | **** | OMSU | Tripped due to tripping of 220kV Mainpuri(UP)-Sikanadara(UP) and Mainpuri(UP) - Barh (UP) lines and Bus dead at Mainpuri(UPPTCL) end.
NR122017 | 306085 | 220KV KNP-NAUBASTA | 2019-06-16 12:10 | 2019-06-16 17:24 | 0.21806 | 0 | 0 | 0 | N-1061 | 'OSPT | E/S/D taken to attend broken jumper of B-Phase(bottom) at Loc no. 75.
NR122017 | 306110 | 220KV KNP-NAUBASTA | 2019-06-20 17:05 | 2019-06-20 19:42 | 0 | 0 | 0 | 0.10903 | N-1384 | OSFD | Emergency S/D taken by UPPTCL to rectify R-phase CT clamp of line at their end.
NR122024 | 306128 | 220KV PITHORAGRH-BRLY(UP) | 2019-06-24 10:35 | 2019-06-24 11:04 | 0 | 0.020139 | 0 | 0 | **** | OMSU | Tripped from UPPTCL CBGanj(Bareilly) end due to both Bus bar earth fault operated at CBGanj(Bareilly) end. Also all generating units were also tripped at NHPC/Dhauliganga,
NR122024 | 306153 | 220KV PITHORAGRH-BRLY(UP) | 2019-06-27 07:42 | 2019-06-27 15:03 | 0.30625 | 0 | 0 | 0 | N-1856 | OSPT | S/D taken for AMP works
NR320004 | 306126 | 220KV RAIBRLY-BACHHRAWAN(UP) | 2019-06-24 10:42 | 2019-06-24 19:29 | 0 | 0 | 0 | 0.36597 | N-1655 | OSFD | E/S/D taken by UPPTCL for attending hot spot at their end
NR122032 | 306042 | 220KV SITARGANJ-BLY(UP) | 2019-06-07 15:20 | 2019-06-07 16:11 | 0 | 0.035417 | 0 | 0 | **** | OMSU | Tripped due to multiple line trippings occurred at UPPTCL CBGANJ(Bareilly) S/S .Fault in UPPTCL Jurisdiction.
NR122032 | 306140 | 220KV SITARGANJ-BLY(UP) | 2019-06-25 11:13 | 2019-06-25 11:44 | 0.021528 | 0 | 0 | 0 | **** | OSFT | Emergency hand tripped to attend isolator Alignment problem at Sitarganj end
NR122033 | 306069 | 220KV TNKPR-BLY(UP) | 2019-06-12 11:43 | 2019-06-12 12:49 | 0 | 0 | 0.045833 | 0 | **** | LMAC | Tripped on R-Y-N fault phase fault. F.D.= 5.20KM from Bareilly (UP) due to tree cutting by local villagers below loc no 295-296 in line Corridor. Matter is sub-judiced in Allahabad High Court
NR122033 | 306132 | 220KV TNKPR-BLY(UP) | 2019-06-24 10:35 | 2019-06-24 14:00 | 0 | 0.14236 | 0 | 0 | **** | OMSU | Tripped from UPPTCL CBGanj(Bareilly) end due to both Bus bar earth fault operated at CBGanj(Bareilly) end. Also all generating units were also tripped at NHPC/Dhauliganga,
NR122034 | 306041 | 220KV TNKPR-SITARGANJ | 2019-06-07 15:20 | 2019-06-07 16:07 | 0 | 0.032639 | 0 | 0 | **** | OMSU | Tripped only from Tanakpur (NHPC) end due to some protection problem at their end
NR122034 | 306065 | 220KV TNKPR-SITARGANJ | 2019-06-12 05:46 | 2019-06-12 06:43 | 0 | 0 | 0.039583 | 0 | **** | LNCC | Line tripped on R-G fault due to heavy stormy wind. Details at Sitargaj: F/D=0.4 KM and F/C= Ir-2.81kA.
NR122034 | 306141 | 220KV TNKPR-SITARGANJ | 2019-06-25 11:13 | 2019-06-25 11:41 | 0.019444 | 0 | 0 | 0 | **** | OSFT | Emergency hand tripped to attend isolator Alignment problem at Sitarganj end
NR122037 | 306160 | 220KV UNCHR-RAIBRLY-III | 2019-06-28 19:37 | 2019-06-28 20:49 | 0.05 | 0 | 0 | 0 | **** | LPPT | Tripped on Y-B fault. FD: 14.75km from Raebarelly, FC.=> Ib=6.25KA, Iy=5.8KA. Line charged from Raebarelly end at 2049hrs but could not synchronised from NTPC-Unchahar end due to B-ph CVT fuse failure at their end.
NR122037 | 306161 | 220KV UNCHR-RAIBRLY-III | 2019-06-28 20:49 | 2019-06-29 11:20 | 0 | 0 | 0 | 0.60486 | N-2047 | OSPD | S/D taken by NTPC Unchahar to attend B-ph CVT fuse fail at Unchahar end.
NR1ICT53 | 306082 | 500MVA ICT-II LUCKNOW | 2019-06-16 08:05 | 2019-06-16 17:43 | 0.40139 | 0 | 0 | 0 | N-1030 | OSPT | S/D taken for relay replacement.
NR1BRT32 | 305161 | 240MVAR B/Reactor-I BALIA-765 | 2019-06-01 | 2019-06-03 02:47 | 0 | 0 | 0 | 1900-01-01 02:47 | N-2166 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia=755/760kV
NR1BRT32 | 306019 | 240MVAR B/Reactor-I BALIA-765 | 2019-06-03 22:38 | 2019-06-11 08:17 | 0 | 0 | 0 | 1900-01-06 09:39 | N-203 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia=745/752kV
NR1BRT50 | 306006 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-06-01 21:14 | 2019-06-02 06:46 | 0 | 0 | 0 | 0.39722 | N-68 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly=750kV
NR1BRT50 | 306061 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-06-10 23:26 | 2019-06-11 08:17 | 0 | 0 | 0 | 0.36875 | N-625 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 759/769 kV
NR1BRT50 | 306062 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-06-11 23:12 | 2019-06-12 06:00 | 0 | 0 | 0 | 0.28333 | N-688 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 750/761 kV
NR1BRT50 | 306074 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-06-14 22:37 | 2019-06-15 06:43 | 0 | 0 | 0 | 0.3375 | N-945 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction.Bareilly = 754/765kV
NR1BRT50 | 306172 | 240MVAR B/Reactor-I BAREILLY-765 | 2019-06-30 23:49 | 2019-07-01 | 0 | 0 | 0 | 0.0076389 | N-2194 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Bareilly = 750/765kV
NR1BRT22 | 305058 | 240MVAR B/Reactor-II BALIA-765 | 2019-06-01 | 2019-06-03 03:53 | 0 | 0 | 0 | 1900-01-01 03:53 | N-503 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia=738kV
NR1BRT22 | 306059 | 240MVAR B/Reactor-II BALIA-765 | 2019-06-10 23:25 | 2019-06-16 09:39 | 0 | 0 | 0 | 1900-01-04 10:14 | N-624 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 745 /752kV
NR1BRT22 | 306087 | 240MVAR B/Reactor-II BALIA-765 | 2019-06-16 21:38 | 2019-07-01 | 0 | 0 | 0 | 1900-01-13 02:22 | N-1082 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Balia = 755 /760kV
NR1BRT28 | 305162 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-06-01 | 2019-06-01 11:12 | 0 | 0 | 0 | 0.46667 | N-2168 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow=755/760kV
NR1BRT28 | 306005 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-06-01 21:13 | 2019-06-02 07:03 | 0 | 0 | 0 | 0.40972 | N-67 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow=750kV
NR1BRT28 | 306020 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-06-03 22:45 | 2019-06-07 07:58 | 0 | 0 | 0 | 1900-01-02 09:13 | N-202 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow=747/756kV
NR1BRT28 | 306050 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-06-08 21:04 | 2019-06-10 08:30 | 0 | 0 | 0 | 1899-12-31 11:26 | N-507 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 759/769 kV
NR1BRT28 | 306060 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-06-10 23:29 | 2019-06-11 08:21 | 0 | 0 | 0 | 0.36944 | N-623 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 759/769 kV
NR1BRT28 | 306063 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-06-11 23:17 | 2019-06-12 06:09 | 0 | 0 | 0 | 0.28611 | N-689 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 755/764 kV
NR1BRT28 | 306072 | 240MVAR B/Reactor-IV LUCKNOW-765 | 2019-06-13 23:18 | 2019-06-16 10:05 | 0 | 0 | 0 | 1900-01-01 10:47 | N-867 | SVRD | Bus Reactor hand tripped for Voltage regulation on RLDC instruction. Lucknow = 755/762kV
Formulas:
DURATION OF OUTAGE ATTRIBUTABLE TO = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="T",(+[RESTORATION]-[OUTAGE]),0))
OTHERS = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="U",(+[RESTORATION]-[OUTAGE]),0))
Hrs:Min = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="C",(+[RESTORATION]-[OUTAGE]),0))
Deemed Available = IF(OR([RESTORATION]="***",[RESTORATION]=""),0,IF(RIGHT([Classification- Category Code])="D",(+[RESTORATION]-[OUTAGE]),0))
Note on C28: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C29: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C30: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C31: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C32: Author: 765KV KANPUR(GIS)-JHATIKARA LILO AT ALIGARH
Note on C33: Author: 765KV KANPUR(GIS)-JHATIKARA LILO AT ALIGARH
Note on C34: Author: 765KV KANPUR(GIS)-JHATIKARA LILO AT ALIGARH
Note on C83: 60020025: LILO of 220kV Sikandara(UP)-Bharatpur(RRVPNL) at Agra(PG)
Note on C86: 60020025: LILO of 220kV Sikandara(UP)-Bharatpur(RRVPNL)
Note on C87: 60020025: LILO of 220kV Sikandara(UP)-Bharatpur(RRVPNL)
Note on C101: LILO OF 220KV RAIBRLY(PG)-CG CITY(UP) at BACHHRAWAN (UP)

## Sheet4 (hidden)
SL.NO. | ELEMENT | Element Name |  | ELEMENT ID | Element name | Total LINE length | 765KV AGRA-JHATIKARA | 253.147
| ID | [5 empty] | 765KV AGRA-Gr Noida | 148.034
|  |  |  | NR176502 | 765KV AGRA-FATEHPUR-I | 8025:36 | 765KV BALLIA-VARANASI | 165.98
A |  | 765 KV TRANS LINES |  | NR176501 | 765KV LUCKNOW-BALIA | 7653:43 | 765KV FATEHPUR-SASARAM | 355.008
1 | NR176502 | 765KV AGRA-FATEHPUR-I | 334.52 | NR140001 | 400KV AGRA-AGRA(UP)-I | 719:34 | 765KV FATEHPUR-AGRA-1 | 334.52
2 | NR176507 | 765KV AGRA-FATEHPUR-II | 334.8 | NR140002 | 400KV AGRA-AGRA(UP)-II | 719:34 | 765KV FATEHPUR-AGRA-2 | 334.8
3 | NR176510 | 765KV AGRA-GR.NOIDA | 148.034 | NR140003 | 400KV AGRA-AURAIYA-I | 3980:02 | 765KV GAYA-VARANASI-I (OLD FTP-GAYA) | 263.94
4 | NR176506 | 765KV FATEHPUR-SASARAM | 355.008 | NR140004 | 400KV AGRA-AURAIYA-II | 0:00 | 765KV GWALIOR-AGRA I | 129.435
5 | NR176501 | 765KV LUCKNOW-BALIA | 318.919 | NR140005 | 400KV AGRA-BASSI-I | 5093:31 | 765KV GWALIOR-AGRA II | 127.934
6 | NR176508 | 765KV LUCKNOW-BAREILLY | 251.613 | NR140008 | 400KV AGRA-BHIWADI-I | 5023:55 | 765KV KANPUR-JHATIKARA | 465.8
7 | NR176512 | 765KV VARANASI-BALIA | 165.98 | NR140009 | 400KV AGRA-BHIWADI-II | 5023:55 | 765KV KANPUR-VARANASI-I | 326.172
8 | NR176513 | 765KV VARANASI-FATEHPUR | 224.963 | NR140010 | 400KV AGRA-BLBGRH | 4347:22 | 765KV KANPUR-VARANASI-II
9 | NR176514 | 765KV VARANASI-GAYA-I | 80.925 | NR140122 | 400KV ALLD-FATEHPUR-I | 3353:31 | 765KV LUCKNOW-BALIA | 318.919
10 | NR376501 | 765KV VARANASI-KANPUR(GIS)-I | 326.172 | NR140123 | 400KV ALLD-FATEHPUR-II | 3353:31 | 765KV LUCKNOW-BAREILLY | 251.613
11 | NR376502 | 765KV VARANASI-KANPUR(GIS)-II | 326.172 | NR140104 | 400KV ALLD-FATEHPUR-III | 3574:19 | 765KV VARANASI-FATEHPUR | 224.963
12 | NR376503 | 765KV KANPUR(GIS)-JHATIKRA-I | 465.8 | NR140012 | 400KV ALLD-KNP-II | 5260:24 | 765KV GAYA-VARANASI-II | 80.925
13 | NR376504 | 765KV ALIGARH-JHATIKARA |  | NR140016 | 400KV ALLD-SASARAM | 4548:43 | 765KV GAYA-BALIA | 238
14 | NR376505 | 765KV KANPUR(GIS)-ALIGARH |  | NR140017 | 400KV BALIA-BIHARSHRF-I | 5802:43 | Total 17 765KV Lines | 4019.19
15 | NR376506 | 765KV AGRA-ALIGARH |  | NR140018 | 400KV BALIA-BIHARSHRF-II | 5802:43 | AGRA-FATEHABAD(UP)-I | 43.013
16 | NR376507 | 765KV ALIGARH-GR.NOIDA |  | NR140019 | 400KV BALIA-MAU-I | 221:10 | FATEHABAD(UP)-AGRA(UP)-I | 57.159
17 | NR376508 | 765KV ORAI-ALIGARH-II |  | NR140020 | 400KV BALIA-MAU-II | 221:10 | AGRA-AGRA-(UP)-II | 29.969
18 | NR376509 | 765KV ORAI-ALIGARH-I |  | NR140021 | 400KV BALIA-PATNA-I | 4685:34 | AURAIYA-AGRA-I | 167.2
|  |  |  | NR140022 | 400KV BALIA-PATNA-II | 4685:34 | AURAIYA-AGRA-II
|  |  |  | NR140136 | 400KV BALIA-PATNA-III | 4440:00 | AGRA-BASSI | 211.433
B |  | 400 KV TRANS LINES |  | NR140137 | 400KV BALIA-PATNA-IV | 4440:00 | AGRA-BHIWADI-I | 208.98
1 | NR140002 | 400KV AGRA-AGRA(UP)-II | 29.982 | NR140140 | 400KV BALIA-SOHAWAL-I | 5499:55 | AGRA-BHIWADI-II | 209.51
2 | NR140003 | 400KV AGRA-AURAIYA-I | 167.2 | NR140120 | 400KV BALIA-SOHAWAL-II | 5499:55 | AGRA-BLB | 181.137
3 | NR140004 | 400KV AGRA-AURAIYA-II | 167.2 |  | 400KV BLBGRH-MAINPURI-I | 5662:51 | AGRA-JAIPUR(S)-I | 254.41
4 | NR140005 | 400KV AGRA-BASSI-I | 212.23 |  | 400KV BLBGRH-MAINPURI-II | 5662:51 | AGRA-JAIPUR(S)-II
5 | NR140008 | 400KV AGRA-BHIWADI-I | 209.33 | NR140025 | 400KV BAREILLY-LKO(UP) | 6691:12 | AGRA-SIKAR-I | 393.9
6 | NR140009 | 400KV AGRA-BHIWADI-II | 209.33 | NR140026 | 400KV BAREILLY-MBAD-I | 2226:43 | AGRA-SIKAR-II
7 | NR140010 | 400KV AGRA-BLBGRH | 181.14 | NR140027 | 400KV BAREILLY-MBAD-II | 2210:54 | ALLD-FATEHPUR-I | 139.73
8 | NR140122 | 400KV ALLD-FATEHPUR-I | 139.73 |  | 400KV BAREILLY-MEERUT-I | 5899:12 | ALLD-FATEHPUR-II
9 | NR140123 | 400KV ALLD-FATEHPUR-II | 139.73 |  | 400KV BAREILLY-MEERUT-II | 5899:12 | ALLD-FATEHPUR-III | 148.934
10 | NR140104 | 400KV ALLD-FATEHPUR-III | 148.93 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 6241:13 | ALLD-KNP-II | 0
11 | NR140012 | 400KV ALLD-KNP-II | 219.183 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 6241:13 | BALIA-MAU-I | 13
12 | NR140163 | 400KV ALLD-VARANASI | 98.791 | NR140046 | 400KV GORKH-GORAKH-I | 1102:35 | BALIA-MAU-II
13 | NR140016 | 400KV ALLD-SASARAM | 189.53 | NR140047 | 400KV GORKH-GORAKH-II | 1102:35 | BALIA-SOHAWAL-I | 229.163
14 | NR140017 | 400KV BALIA-BIHARSHRF-I | 241.78 | NR140052 | 400KV KNP-AGRA | 5760:00 | BALIA-SOHAWAL-II
15 | NR140018 | 400KV BALIA-BIHARSHRF-II | 241.78 | NR140053 | 400KV KNP-AURAIYA-I | 1754:55 | BAREILLY(400)-BAREILLY(765)-I | 1.559
16 | NR140140 | 400KV BALIA-SOHAWAL-I | 229.163 | NR140054 | 400KV KNP-AURAIYA-II | 1754:55 | BAREILLY(400)-BAREILLY(765)-II
17 | NR140120 | 400KV BALIA-SOHAWAL-II | 229.163 | NR140055 | 400KV KNP-BLBGARH-I | 9256:48 | BAREILLY-BLY(UP)-I | 14.3
18 | NR140150 | 400KV BAREILLY-BAREILLY(765)-I | 1.559 | NR140056 | 400KV KNP-BLBGARH-II | 8898:32 | BAREILLY-BLY(UP)-II | 14.3
19 | NR140157 | 400KV BAREILLY-BAREILLY(765)-II | 1.559 | NR140057 | 400KV KNP-BLBGARH-III | 8898:32 | BAREILLY-MEERUT-I | 249.52
20 | NR140023 | 400KV BAREILLY-BRLY(UP)-I | 14.3 | NR140110 | 400KV KNP-FATEHPUR-I | 2569:54 | BAREILLY-MEERUT-II | 249.52
21 | NR140024 | 400KV BAREILLY-BRLY(UP)-II | 14.3 | NR140105 | 400KV KNP-FATEHPUR-II | 2570:24 | LKO(UP)-BAREILLY | 278.76
22 | NR140025 | 400KV BAREILLY-LKO(UP) | 278.8 | NR140058 | 400KV KNP-PANKI-I | 141:36 | BAREILLY-MORADABAD-I | 92.68
23 | NR140026 | 400KV BAREILLY-MBAD-I | 92.78 | NR140059 | 400KV KNP-PANKI-II | 141:36 | BAREILLY-MORADABAD-II | 92.121
24 | NR140027 | 400KV BAREILLY-MBAD-II | 92.121 | NR140070 | 400KV LUCKNOW-GORAKH-III | 6294:14 | SHAHJAHANPUR-BAREILLY-I | 116.917
25 | NR340010 | 400KV BAREILLY-SHAHJHNPR-I | 116.917 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 6294:14 | SHAHJAHANPUR-BAREILLY-II | 116.917
26 | NR140152 | 400KV BAREILLY-SHAHJHNPR-II | 116.917 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 68:41 | B'GARH-M'PURI-I | 235.952
27 | NR140158 | 400KV BARLY(765)-KASHIPUR-I | 100.659 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 68:41 | B'GARH-M'PURI-II
28 | NR140159 | 400KV BARLY(765)-KASHIPUR-II | 100.659 | NR140072 | 400KV LUCKNOW-LKO(UP) | 1518:29 | FATEHPUR-MAINPURI-I | 260.051
29 | NR140037 | 400KV BLBGRH-MAINPURI-I | 235.952 | NR140114 | 400KV LUCKNOW-ROSA-I | 4248:00 | FATEHPUR-MAINPURI-II
30 | NR140038 | 400KV BLBGRH-MAINPURI-II | 235.952 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 2359:09 | GORAKH-GORAKH-I | 45.941
31 | NR140124 | 400KV FATEHPUR-MAINPURI-I | 260.051 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 2359:09 | GORAKH-GORAKH-II
32 | NR140125 | 400KV FATEHPUR-MAINPURI-II | 260.051 | NR140073 | 400KV LUCKNOW-SULTANPR | 3926:24 |  | 240
33 | NR140046 | 400KV GORAKH-GORAKH-I | 45.941 | NR140074 | 400KV LUCKNOW-UNNAO-I | 1771:49 | KANPUR-AURAIYA-I | 0
34 | NR140047 | 400KV GORAKH-GORAKH-II | 45.941 | NR140075 | 400KV LUCKNOW-UNNAO-II | 1771:49 | KANPUR-AURAIYA-II
35 | NR140052 | 400KV KNP-AGRA | 240 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 747:48 | KNP-B'GARH-I | 385.69
36 | NR140053 | 400KV KNP-AURAIYA-I | 73.1212 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 747:48 | KNP-B'GARH-II | 370.772
37 | NR140054 | 400KV KNP-AURAIYA-II | 73.1212 | NR140084 | 400KV RIHAND-ALLD-I | 6685:47 | KNP-B'GARH-III
38 | NR140055 | 400KV KNP-BLBGARH-I | 385.7 | NR140085 | 400KV RIHAND-ALLD-II | 6685:47 | KNP-FATEHPUR-II | 107.1
39 | NR140056 | 400KV KNP-BLBGARH-II | 370.772 | NR140088 | 400KV VARANASI-BIHARSHRF-I | 3420:00 | KNP-FATEHPUR-I | 107.079
40 | NR140057 | 400KV KNP-BLBGARH-III | 370.772 | NR140089 | 400KV VARANASI-BIHARSHRF-II | 3420:00 | KNP-PANKI-I | 5.924
41 | NR140110 | 400KV KNP-FATEHPUR-I | 107.079 | NR140090 | 400KV SASARAM-VARANASI | 1140:29 | KNP-PANKI-II | 5.863
42 | NR140105 | 400KV KNP-FATEHPUR-II | 107.1 | NR140091 | 400KV SING-ALLD-I | 5422:28 | KASHIPUR-BAREILLY-I | 100.659
43 | NR140058 | 400KV KNP-PANKI-I | 5.9 | NR140092 | 400KV SING-ALLD-II | 4829:02 | KASHIPUR-BAREILLY-II
44 | NR140059 | 400KV KNP-PANKI-II | 5.9 | NR140093 | 400KV SING-ANPARA | 724:38 | KANPUR(400)-KANPUR(765)-I | 21.32
45 | NR140070 | 400KV LUCKNOW-GORAKH-III | 262.26 | NR140111 | 400KV SING-FATEHPUR | 7942:52 | KANPUR(400)-KANPUR(765)-II
46 | NR140071 | 400KV LUCKNOW-GORAKH-IV | 262.26 | NR140095 | 400KV SING-LKO(UP) | 7920:00 | LUCKNOW-GORAKHPUR-III | 263.933
47 | NR140112 | 400KV LUCKNOW-LKO(765)-I | 2.862 | NR140096 | 400KV SING-RIHAND-I | 1008:00 | LUCKNOW-GORAKHPUR-IV
48 | NR140113 | 400KV LUCKNOW-LKO(765)-II | 2.862 | NR140097 | 400KV SING-RIHAND-II | 1008:00 | LUCKNOW(765)-LUCKNOW(400)-I | 2.862
49 | NR140072 | 400KV LUCKNOW-LKO(UP) | 63.27 | N-W40001 | 400KV SING-VINDH-I | 80:11 | LUCKNOW(765)-LUCKNOW(400)-II
50 | NR140114 | 400KV LUCKNOW-ROSA-I | 177 | N-W40002 | 400KV SING-VINDH-II | 40:05 | LUCKNOW-LUCKNOW (UP) | 63.27
51 | NR140153 | 400KV LUCKNOW-SHAHJHNPR-II | 169.729 | NR140164 | 400KV VARANASI-SARNATH-I | 1289:31 | LUCKNOW-SULTANPUR | 163.6
52 | NR140141 | 400KV LUCKNOW-SOHAWAL-I | 98.298 | NR140165 | 400KV VARANASI-SARNATH-II | 1289:31 | LUCKNOW-SHAHJHNPR-I | 169.729
53 | NR140121 | 400KV LUCKNOW-SOHAWAL-II | 98.298 |  |  |  | LUCKNOW-SHAHJHNPR-II
54 | NR140073 | 400KV LUCKNOW-SULTANPR | 163.6 |  | 220 KV TRANS LINES |  | LUCKNOW-SOHAWAL-I | 98.281
55 | NR140074 | 400KV LUCKNOW-UNNAO-I | 73.826 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 525:06 | LUCKNOW-SOHAWAL-II
56 | NR140075 | 400KV LUCKNOW-UNNAO-II | 73.826 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 405:27 | LUCKNOW-UNNAO-I | 73.826
57 | NR140154 | 400KV RIHAND3-VINDH(Pool)-I | 31.158 | BILUP2202 | 220KV ALLD-REWA RD-I | 71:02 | LUCKNOW-UNNAO-II
58 | NR140160 | 400KV RIHAND3-VINDH(Pool)-II | 31.158 | BILUP2203 | 220KV ALLD-REWA RD-II | 71:02 | RIHAND-ALLD-I | 279.245
59 | NR140084 | 400KV RIHAND-ALLD-I | 278.574 | NR122006 | 220KV AUR-SIKANDARA-I | 4380:46 | RIHAND-ALLD-II
60 | NR140085 | 400KV RIHAND-ALLD-II | 278.574 | NR122007 | 220KV AUR-SIKANDARA-II | 4380:46 | RIHAND-VINDHYACHAL Pooling-I | 31.158
61 | NR140088 | 400KV SASARAM-BIHARSHRF-I | 142.5 | NR122012 | 220KV DGANGA-BLY(UP)-II | 5630:10 | RIHAND-VINDHYACHAL Pooling-II
62 | NR140089 | 400KV SASARAM-BIHARSHRF-II | 142.5 | NR122013 | 220KV DGANGA-PITHORAGRH | 1416:14 | SING-ALLD-I | 224
63 | NR140091 | 400KV SING-ALLD-I | 225.936 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 148:05 | SING-ALLD-II | 202
64 | NR140092 | 400KV SING-ALLD-II | 201.21 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 148:05 | SING-ANPARA | 25.057
65 | NR140093 | 400KV SING-ANPARA | 30.193 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 126:52 | SING-FATEHPUR | 330.953
66 | NR140111 | 400KV SING-FATEHPUR | 330.953 | NR122041 | 220KV FATEHPUR-NAUBASTA | 126:52 | SING-LUCKNOW(UP) | 408.6
67 | NR140095 | 400KV SING-LKO(UP)-I | 330 | NR122016 | 220KV KNP-MAINPURI | 3624:00 | SING-RIHAND-I | 42.026
68 | NR140096 | 400KV SING-RIHAND-I | 42 | NR122017 | 220KV KNP-NAUBASTA | 463:41 | SING-RIHAND-II
69 | NR140097 | 400KV SING-RIHAND-II | 42 | NR122018 | 220KV KNP-PANKI-I | 374:24 | SING-VINDH-I | 3.341
70 | N-W40001 | 400KV SING-VINDH-I | 3.341 | NR122019 | 220KV KNP-PANKI-II | 572:38 | SING-VINDH-II
71 | N-W40002 | 400KV SING-VINDH-II | 1.67 | NR122020 | 220KV KNP-UNCHR-I | 3445:16 | HVDC Feeder I | 1.25
72 | NR340001 | 400KV KANPUR-KANPUR(GIS)-I | 21.32 | NR122021 | 220KV KNP-UNCHR-II | 3445:16 | HVDC Feeder I
73 | NR340002 | 400KV KANPUR-KANPUR(GIS)-II | 21.32 | NR122022 | 220KV KNP-UNCHR-III | 3471:07 | HVDC Feeder II | 1.25
74 | NR340003 | 400KV VARANASI-SASARAM(ER) | 139.482 | NR122023 | 220KV KNP-UNCHR-IV | 3471:07 | HVDC Feeder II
75 | NR340004 | 400KV VARANASI-SARNATH-I | 106.7 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88 | VINDHYACHAL POOLING-SASAN | 6.02
76 | NR340005 | 400KV VARANASI-SARNATH-II | 106.7 | NR122025 | 220KV RAIBRLY-CHINHAT |  | BIHARSHARIF-VARANASI-I | 285
77 | NR340006 | 400KV AGRA-FATEHABD(UP)-I | 43.013 | NR122026 | 220KV RAIBRLY-LKO(UP) | 1026:03 | BIHARSHARIF-VARANASI-II
78 | NR340007 | 400KV AGRA(UP)-FATEHABD(UP)-II | 43.013 | NR122032 | 220KV SITARGANJ-BLY(UP) | 2534:47 | VARANASI-SARNATH-I | 106.7
79 | NR340008 | 400KV ALLAHABAD-MEJA(NTPC)-I | 28.19 | NR122033 | 220KV TNKPR-BLY(UP) | 2544:00 | VARANASI-SARNATH-II | 106.7
80 | NR340009 | 400KV ALLAHABAD-MEJA(NTPC)-II | 28.19 | NR122034 | 220KV TNKPR-SITARGANJ | 1026:03 | SASARAM-ALLAHABAD | 213.729
81 | NR140142 | 400KV MEERUT-BAREILLY-I | 249.52 | NR122035 | 220KV UNCHR-RAIBRLY-I | 1025:02 | SASARAM-VARANASI | 139.482
82 | NR140130 | 400KV MEERUT-BAREILLY-II | 249.52 | NR122036 | 220KV UNCHR-RAIBRLY-II | 1025:02 | VARANASI-ALLAHABAD | 98.791
83 | NR340011 | 400KV LUCKNOW-SHAHJHNPR-I | 159.7 | NR122037 | 220KV UNCHR-RAIBRLY-III | 1048:48 | BARH-GORAKHPUR-I | 353
84 | NR340012 | 400KV Lucknow(765)-Kanpur(GIS)-I | 159.7 |  | 220 KV KNP(400KV)-RANIA(UP) | 18.372 | BARH-GORAKHPUR-II
85 | NR340013 | 400KV Lucknow(765)-Kanpur(GIS)-II |  |  | 220 KV RANIA(UP)-PANKI(UP) | 30.39 | BIHARSHARIF-BALIA-I | 242
86 | NR340014 | 400KV Kanpur(GIS)-Allahabad-I |  |  | 132 KV TRANS LINES |  | BIHARSHARIF-BALIA-I
87 | NR340015 | 400KV Kanpur(GIS)-Allahabad-II |  | BILUP13201 | 132KV MAU-BALIA | 57.825 | ALLAHABAD-MEJA-I | 28.19
88 | NR340016 | 400KV ORAI-ORAI(UP)-I |  |  | 132 KV Tankpur - Mahendranagar | 3.06 | ALLAHABAD-MEJA-II
89 | NR340017 | 400KV ORAI-ORAI(UP)-II |  |  |  |  | UCHAHAR-FATEHPUR-I | 53.7
90 | NR140019 | 400KV BALIA-MAU-I | 9.215 |  | 220KV ALLD-JHUSI(UP) | 21.879 | UCHAHAR-FATEHPUR-II
91 | NR140020 | 400KV BALIA-MAU-II | 9.215 |  | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 | PATNA-BALIA-I | 195
92 | NR140021 | 400KV BALIA-PATNA-I | 195.232 |  | 220KV ALLD-REWA RD-I&II | 2.96 | PATNA-BALIA-II
93 | NR140022 | 400KV BALIA-PATNA-II | 195.232 |  | 220KV ALLD-REWA RD-II |  | PATNA-BALIA-III | 185
94 | NR140136 | 400KV BALIA-PATNA-III | 185 |  | 220KV AURAIYA-SIKANDARA-I | 182.532 | PATNA-BALIA-IV
95 | NR140137 | 400KV BALIA-PATNA-IV | 185 |  | 220KV AURAIYA-SIKANDARA-II |  | LUCKNOW-KANPUR-I | 159.7
[5 empty] | 220KV D'GANGA-BRLY(UP)-II | 234.59 | LUCKNOW-KANPUR-II
[5 empty] | 220KV D'GANGA-PITHORAGRH | 59.01 | ALLAHABAD-KANPUR(GIS)-I | 240.39
[5 empty] | 220KV PITHORAGRH-BRLY(UP)-I | 177.88 | ALLAHABAD-KANPUR(GIS)-II
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-I | 6.169 | Total 105 400KV Lines | 10198.266
[5 empty] | 220KV FATEHPUR-FTHPR(UP)-II | 6.169 | HVDC R-D POLE-I | 815
[5 empty] | 220KV FATEHPUR-KNP SOUTH | 5.286 | HVDC R-D POLE-II
[5 empty] | 220KV FATEHPUR-NAUBASTA | 5.286 | HVDC B-B POLE-I | 789.786
[5 empty] | 220KV KNP-MAINPURI | 151 | HVDC B-B POLE-II
[5 empty] | 220KV KNP-RANIA(UP) | 18.372 | BNC-AGRA POLE-I | 1734
[5 empty] | 220KV RANIA(UP)-PANKI(UP) | 30.39 | BNC-AGRA POLE-II
[5 empty] | 220KV KNP-NAUBASTA | 19.32 | CHAMPA-KURUKSHETRA-I | 1305
[5 empty] | 220KV KNP-PANKI-II | 23.86 | CHAMPA-KURUKSHETRA-II
[5 empty] | 220KV KNP-UNCHAHAR-I | 143.553
220KV KNP-UNCHAHAR-II
[5 empty] | 220KV KNP-UNCHAHAR-III | 144.63
220KV KNP-UNCHAHAR-IV
C |  | 220 KV TRANS LINES |  |  | 220KV SITARGANJ-BLY(UP) | 105.72
1 | BILUP2209 | 220KV ALLD-JHUSI(UP) | 21.879 |  | 220KV TNKPR-BLY(UP) | 106
2 | BILUP2210 | 220KV JHUSI(UP)-PHULPUR(UP) | 16.894 |  | 220KV TNKPR-SITARGANJ | 42.55
3 | BILUP2202 | 220KV ALLD-REWA RD-I | 2.96 |  | 220KV RBRLY-CHINHAT | 93.61
4 | BILUP2203 | 220KV ALLD-REWA RD-II | 2.96 |  | 220KV UNCHR-RBRLY-I | 42.71
5 | NR122006 | 220KV AUR-SIKANDARA-I | 182.532 |  | 220KV RBRLY-LKO(UP) | 1.19
6 | NR122007 | 220KV AUR-SIKANDARA-II | 182.532 |  | 220KV UNCHR-RBRLY-II | 42.71
7 | NR122012 | 220KV DGANGA-BLY(UP)-II | 234.59 |  | 220KV UNCHR-RBRLY-III | 43.7
8 | NR122013 | 220KV DGANGA-PITHORAGRH | 59.01 |  | TOTAL 30 Lines
9 | NR122038 | 220KV FATEHPUR-FTHPR(UP)-I | 6.17 |  | 132KV LINES
10 | NR122039 | 220KV FATEHPUR-FTHPR(UP)-II | 6.17 |  | 132KV MAU-BALIA | 57.825
11 | NR122040 | 220KV FATEHPUR-KNP SOUTH | 5.286 |  | 132KV TNKPR-MHNDRNGR | 3.06
12 | NR122041 | 220KV FATEHPUR-NAUBASTA | 5.286
13 | NR122016 | 220KV KNP-MAINPURI | 151
14 | NR122017 | 220KV KNP-NAUBASTA | 19.32
15 | NR122019 | 220KV KNP-PANKI-II | 23.86
16 | NR122020 | 220KV KNP-UNCHR-I | 143.553
17 | NR122021 | 220KV KNP-UNCHR-II | 143.553
18 | NR122022 | 220KV KNP-UNCHR-III | 144.63
19 | NR122023 | 220KV KNP-UNCHR-IV | 144.63
20 | NR122024 | 220KV PITHORAGRH-BRLY(UP) | 177.88
21 | NR122025 | 220KV RAIBRLY-CHINHAT | 93.61
22 | NR122026 | 220KV RAIBRLY-LKO(UP) | 42.752
23 | NR122032 | 220KV SITARGANJ-BLY(UP) | 105.616
24 | NR122033 | 220KV TNKPR-BLY(UP) | 106
25 | NR122034 | 220KV TNKPR-SITARGANJ | 42.752
26 | NR122035 | 220KV UNCHR-RAIBRLY-I | 42.71
27 | NR122036 | 220KV UNCHR-RAIBRLY-II | 42.71
28 | NR122037 | 220KV UNCHR-RAIBRLY-III | 43.7
29 | NR320001 | 220 KV KANPUR(PG) - RANIYA( UP) | 18.372
30 | NR320002 | 220 KV RANIYA( UP) - PANKI (UP) | 30.39
31 | NR320003 | 220KV RAIBRLY-CG CITY(UP)
32 | NR320004 | 220KV RAIBRLY-BACHHRAWAN(UP)
D |  | 132 KV TRANS LINES
1 | BILUP13201 | 132KV MAU-BALIA | 57.825
| Lines | TOTAL FOR T/LS
142 |  | OVERALL SYSTEM AVAILABILITY=
E |  | 765/400 KV ICT'S
1 | NR1ICT707 | 765/400KV ICT-I AGRA
2 | NR1ICT708 | 765/400KV ICT-II AGRA
3 | NR1ICT701 | 765/400KV ICT-I BALIA
4 | NR1ICT702 | 765/400KV ICT-II BALIA
5 | NR1ICT715 | 765/400KV ICT-I BAREILLY
6 | NR1ICT716 | 765/400KV ICT-II BAREILLY
7 | NR1ICT705 | 765/400KV ICT-I FATEHPUR
8 | NR1ICT706 | 765/400KV ICT-II FATEHPUR
9 | NR1ICT703 | 765/400KV ICT-I LUCKNOW
10 | NR1ICT704 | 765/400KV ICT-II LUCKNOW
11 | NR1ICT717 | 765/400KV ICT-I VARANASI
12 | NR1ICT718 | 765/400KV ICT-II VARANASI
13 | NR3ICT701 | 765/400kv ICT-I KANPUR(GIS)
14 | NR3ICT702 | 765/400kv ICT-II KANPUR(GIS)
| NR3ICT703 | 1000MVA ICT-I ORAI(GIS)
| NR3ICT704 | 1000MVA ICT-II ORAI(GIS)
815
F |  | 400/220 KV ICT'S
1 | NR1ICT70 | 315MVA ICT-I AGRA
2 | NR1ICT01 | 315MVA ICT-I ALLAHABAD
3 | NR1ICT02 | 315MVA ICT-II ALLAHABAD | 815
4 | NR1ICT67 | 315MVA ICT-III ALLAHABAD | 789.786
5 | NR1ICT48 | 315MVA ICT-I FATEHPUR | 789.786
6 | NR1ICT49 | 315MVA ICT-II FATEHPUR
7 | NR1ICT14 | 315MVA ICT-I GORAKHPR
8 | NR1ICT15 | 315MVA ICT-II GORAKHPR | 1734
9 | NR1ICT19 | 315MVA ICT-I KANPUR | 1734
10 | NR1ICT20 | 315MVA ICT-II KANPUR
11 | NR1ICT23 | 315MVA ICT-I LUCKNOW
12 | NR1ICT53 | 500MVA ICT-II LUCKNOW
13 | NR1ICT26 | 315MVA ICT-I MAINPURI
14 | NR1ICT27 | 315MVA ICT-II MAINPURI | 0
15 | NR1ICT65 | 500MVA ICT-I SHAHJHNPR | 0
16 | NR1ICT66 | 500MVA ICT-II SHAHJHNPR
17 | NR1ICT59 | 315MVA ICT-I SOHAWAL
18 | NR1ICT60 | 315MVA ICT-II SOHAWAL
| NR3ICT01 | 315MVA ICT-2 at Agra
| NR3ICT02 | 500MVA ICT-3 at Mainpuri
G |  | 220/132 KV ICT'S
1 | NR1ICT43 | 100MVA ICT-I PITHORAGRH
2 | NR1ICT44 | 100MVA ICT-II PITHORAGRH
3 | NR1ICT47 | 100MVA ICT-I RAIBAREILLY
4 | NR1ICT38 | 100MVA ICT-II RAIBAREILLY
5 | NR1ICT39 | 200MVA ICT-III RAIBAREILLY
6 | NR1ICT40 | 100MVA ICT-I SITARGANJ
7 | NR1ICT41 | 100MVA ICT-II SITARGANJ
| NR3ICT03 | 200MVA ICT-3 at Raibareilly
| NR3ICT04 | 200MVA ICT-2 at Raibareilly
TOTAL FOR ICTs
39 |  | HVDC RIHAND-DADRI
H | NR1DCP01 | 500KV HVDC R-D POLE-I
1 | NR1DCP02 | 500KV HVDC R-D POLE-II
2 | NR1DCP03 | 500KV HVDC BALIA-BHWD POLE-I
3 | NR1DCP04 | 500KV HVDC BALIA-BHWD POLE-II
4 |  | TOTAL FOR HVDC line
HVDC AGRA-BNC
J | NRNEDCP01 | 800KV HVDC AGRA-BNC POLE-I
1 | NRNEDCP02 | 800KV HVDC AGRA-BNC POLE-II
| NRNEDCP03 | 800KV HVDC AGRA-APD POLE-III
| NRNEDCP04 | 800KV HVDC AGRA-APD POLE-IV
2 |  | TOTAL of HVDC POLE-I
HVDC BTB VINDHYACHAL
K | NR1DCB01 | VINDH HVDC B/B BLOCK-I
1 | NR1DCB02 | VINDH HVDC B/B BLOCK-II
2 |  | TOTAL FOR HVDC VINDHYACHAL
HVDC BTB SASARAM
L | NEDCB01 | +/-500MW HVDC B/B SASARAM
1 |  | TOTAL FOR HVDC SASARAM
SVC, KANPUR
M | NR1SVC01 | +/-140MVAR SVC-I KANPUR
1 | NR1SVC02 | +/-140MVAR SVC-II KANPUR
2 |  | TOTAL FOR SVC
N |  | Bus & Switch Line Reactor
1 | NR1BRT25 | 125MVAR B/Reactor-I AGRA
2 | NR1BRT26 | 125MVAR B/Reactor-II AGRA
3 | NR1BRT36 | 240MVAR B/Reactor-I AGRA-765
4 | NR1BRT35 | 240MVAR B/Reactor-II AGRA-765
5 | NR1BRT01 | 80MVAR B/Reactor ALLAHABAD
6 | NR1BRT33 | 125MVAR B/Reactor-II ALLAHABAD
7 | NR1BRT02 | 80MVAR B/Reactor-I BALIA
8 | NR1BRT17 | 125MVAR B/Reactor-II BALIA
9 | NR1BRT27 | 125MVAR B/Reactor-III BALIA
10 | NR1BRT20 | 125MVAR B/Reactor-IV BALIA
11 | NR1BRT32 | 240MVAR B/Reactor-I BALIA-765
12 | NR1BRT22 | 240MVAR B/Reactor-II BALIA-765
13 | NR1BRT03 | 80MVAR B/Reactor BAREILLY
14 | NR1BRT44 | 2x50MVAR B/Reactor BAREILLY
15 | NR1BRT45 | 50MVAR B/Reactor-II BAREILLY
16 | NR1BRT50 | 240MVAR B/Reactor-I BAREILLY-765
17 | NR1BRT06 | 80MVAR B/Reactor BIHARSHRF
18 | NR1BRT18 | 125MVAR B/Reactor-I FATEHPUR
19 | NR1BRT19 | 125MVAR B/Reactor-II FATEHPUR
20 | NR1BRT23 | 330MVAR B/Reactor-III FTHPR-765
21 | NR1BRT39 | 125MVAR B/Reactor-I GORAKHPUR
22 | NR1BRT46 | 125MVAR B/Reactor-II GORAKHPUR
23 | NR1BRT10 | 80MVAR B/Reactor LUCKNOW
24 | NR1BRT16 | 125MVAR B/Reactor-II LUCKNOW
25 | NR1BRT21 | 125MVAR B/Reactor-III LUCKNOW
26 | NR1BRT28 | 240MVAR B/Reactor-IV LUCKNOW-765
27 | NR1BRT38 | 125MVAR B/Reactor-1 MAINPURI
28 | NR1BRT49 | 125MVAR B/Reactor-I SHAHJHNPR
29 | NR1BRT13 | 93MVAR B/Reactor VINDH AR1-W
30 | NR1BRT14 | 93MVAR B/Reactor VINDH AR2-N
31 | NR1BRT42 | 125MVAR B/Reactor-I VINDH
32 | NR1BRT43 | 125MVAR B/Reactor-II VINDH
33 | NR1BRT55 | 330MVAR B/Reactor-I VARANASI
34 | NR1BRT56 | 330MVAR B/Reactor-II VARANASI
35 | NR1SRT01 | AGRA 50MVAR S/R BHIWADI-Ckt-I
36 | NR1SRT20 | AGRA 240MVAR S/R FATEHPR line
37 | NR1SRT02 | ALLHBD 50MVAR S/R MNPR Ckt-I
38 | NR1SRT03 | ALLHBD 50MVAR S/R MNPR Ckt-II
39 | NR1SRT18 | BALIA 240MVAR S/R GAYA Line
40 | NR1SRT16 | BALIA 240MVAR S/R LUCKNW Ckt-I | 393.9
41 | NR1SRT04 | BARLLY 50MVAR S/R MND Ckt-I | 393.9
42 | NR1SRT05 | BARLLY 50MVAR S/R MND Ckt-II | 213.729
43 | NR1SRT17 | FATEHPR 330MVAR S/R AGRA line | 285
44 | NR1SRT07 | GORAKH 50MVAR S/R LKO Ckt-I | 285
45 | NR1SRT08 | GORAKH 50MVAR S/R LKO Ckt-II | 238
46 | NR1SRT11 | GORAKH 63MVAR S/R LKO-III LINE | 263.94
47 | NR1SRT12 | GORAKH 63MVAR S/R LKO-IV LINE | 139.482
48 | NR1SRT24 | GORAKH 80MVAR S/R Barh-I line
49 | NR1SRT25 | GORAKH 80MVAR S/R Barh-II line
50 | NR1SRT13 | LUCKNW 63MVAR S/R GKP-III LINE
51 | NR1SRT14 | LUCKNW 63MVAR S/R GKP-IV LINE
52 | NR1SRT15 | LUCKNW 240MVAR S/R BALIA Ckt-I
53 | NR1SRT26 | LUCKNW 240MVAR S/R Bareilly Line
54 | NR3BRT01 | 240MVAR B/Reactor-I KANPUR(GIS)
55 | NR3BRT02 | 240MVAR B/Reactor-II KANPUR(GIS)
56 | NR3SRT01 | VARANASI 240MVAR S/R KNP(GIS)-1
57 | NR3SRT02 | VARANASI 240MVAR S/R KNP(GIS)-2
58 | NR3SRT03 | KNP(GIS) 330MVAR S/R JHATIKRA-1
59 | NR3BRT03 | 125MVAR B/Reactor-III KANPUR(GIS)
60 | NR3BRT04 | 125MVAR B/Reactor-I VARANASI
61 | NR3BRT05 | 125MVAR B/Reactor-I KANPUR
62 | NR3BRT06 | 330MVAR B/Reactor-III VARANASI-765
63 | NR3BRT08 | 330MVAR Bus Reactor-II AT ALIGARH GIS |  |  | 400KV AGRA-SIKAR-I
64 | NR3SLRT06 | ALIGARH 330MVAR Switachable Line Reactor KANPUR LINE |  |  | 400KV AGRA-SIKAR-II
65 | NR3BRT09 | 330MVAR B/Reactor-I ALIGARH |  |  | 400KV ALLAHABAD-SASARAM
66 | NR3LRT07 | ORAI 240MVAR Non Switchable Line Reactor ALIGARH-II LINE |  |  | 400KV VARANASI-BIHARSHRF-I
67 | NR3LRT08 | ALIGARH 240MVAR Non Switchable Line Reactor ORAI-II LINE |  |  | 400KV VARANASI-BIHARSHRF-II
68 | NR3BRT10 | 330MVAR Bus Reactor-I ORAI |  |  | 765KV BALIA-GAYA
69 | NR3LRT09 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-I LINE |  |  | 765KV VARANASI-GAYA
70 | NR3LRT10 | ORAI 330MVAR Non-Switchable Line Reactor JABALPUR-II LINE |  |  | 400KV SASARAM-VARANASI
71 | NR3BRT11 | 330MVAR Bus Reactor-II ORAI |  |  | 400KV MOTIHARI-GRKHPR-I
72 | NR3LRT11 | ORAI 240MVAR Non-Switchable Line Reactor SATNA LINE |  |  | 400KV MOTIHARI-GRKHPR-II
73 | NR3LRT12 | ORAI 240MVAR Non-Switchable Line Reactor ALIGARH-I LINE
74 | NR3LRT13 | ALIGARH 240MVAR Non-Switchable Line Reactor ORAI-I LINE
75 | NR3BRT07 | 63MVAR B/Reactor-I SOHAWAL
Note on C7: LILO of Agra-Mrt at Gr Noida by WUPPTCL, March-16.
Note on C12: LILO of 765KV FATEHPUR-GAYA at VARANASI
Note on C13: LILO of 765KV FATEHPUR-GAYA at VARANASI. DOCO-1st April-16
Note on C17: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C18: LILO OF 765KV KANPUR-JHATIKARA AT ALIGARH
Note on C19: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C20: LILO OF 765KV AGRA-GR. NOIDA AT ALIGARH
Note on C37: LILO of Alld-Sarnath at Varanasi. DOCO on 1-4-16
Note on C76: LILO of 400kv Lko-Bly-II line at Shahjahanpur on 11/06/14
Note on F76: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on F77: LILO of Alld-Sarnath at Varanasi on 1-4-16
Note on C102: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C103: LILO of Agra-Agra(UP)-I line at fatehabad on 19-10-16 under Lalitpur project.
Note on C279: DOC-26/05/2014
Note on F325: LILO of 765KV FATEHPUR-GAYA at VARANASI

## Sheet2 (hidden)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
125MVAR B/Reactor-1 Mainpuri | 2017-05-27 22:42 | 2017-05-28 06:46 | 0 | 0 | 0 | 0.33611 | N-2790 | SVRD | H-T for voltage regulation as per NRLDC instruction. Mainpuri=386KV
125MVAR B/Reactor-I GORAKHPUR | 2017-05-22 21:55 | 2017-06-01 | 0 | 0 | 0 | 1900-01-08 02:05 | N-2235 | SVRD | H-T for voltage regulation as per NRLDC instruction. Gorakhpur=393KV
125MVAR B/Reactor-III KANPUR(GIS) | 2017-05-25 23:46 | 2017-05-26 06:58 | 0 | 0 | 0 | 0.3 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. Kanpur=395KV
240MVAR B/Reactor-I BALIA-765 | 2017-05-13 21:25 | 2017-05-27 01:23 | 0 | 0 | 0 | 1900-01-12 03:58 | N-1003 | SVRD | H-T for voltage regulation as per NRLDC instruction. Ballia=744KV
240MVAR B/Reactor-I BAREILLY-765 | 2017-05-25 09:56 | 2017-05-28 05:20 | 0 | 0 | 0 | 1900-01-01 19:24 | N-2455 | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-13 21:24 | 2017-05-14 06:52 | 0 | 0 | 0 | 0.39444 | N-1002 | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=750KV
240MVAR B/Reactor-IV LUCKNOW-765 | 2017-05-16 20:01 | 2017-05-17 07:40 | 0 | 0 | 0 | 0.48542 | N-1534 | SVRD | H-T for voltage regulation as per NRLDC instruction. Lucknow=749KV
330MVAR B/Reactor-II VARANASI | 2017-05-19 15:05 | 2017-05-19 22:00 | 0 | 0 | 0 | 0.28819 | N-1850 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=751KV
330MVAR B/Reactor-II VARANASI | 2017-05-22 21:34 | 2017-05-24 06:25 | 0 | 0 | 0 | 1899-12-31 08:51 | N-2234 | SVRD | H-T for voltage regulation as per NRLDC instruction. Varanasi=761KV
80MVAR B/Reactor BAREILLY | 2017-05-25 23:41 | 2017-05-26 07:02 | 0 | 0 | 0 | 0.30625 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. BRLY=395KV
80MVAR B/Reactor LUCKNOW | 2017-05-25 23:35 | 2017-05-26 06:53 | 0 | 0 | 0 | 0.30417 | **** | SVRD | H-T for voltage regulation as per NRLDC instruction. LKO=396KV
Note on A9: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1
Note on A10: Divya Kushwaha {Divya Kushwaha}: B/REACTOR 1