## SOP
Standard of Performance data for the month of February-2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Tme | Date | Tme | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L1 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- | SRPC | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
2 | SR1L2 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
3 | SR1L3 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
4 | SR1L4 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
5 | SR1L5 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
6 | SR1L6 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
7 | SR1L7 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | 2016-02-02 | 7:26 | 2016-02-02 | 19:43 | -- | -- | -- |  |  |  | 12.2833 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC Code CR02/34 |  | 100
[5 empty] | -- | 2016-02-03 | 7:32 | 2016-02-03 | 18:16 | -- | -- | -- |  |  |  | 10.7333 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC Code CR02/62
[5 empty] | -- | 2016-02-04 | 7:24 | 2016-02-04 | 18:22 | -- | -- | -- |  |  |  | 10.9667 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC Code CR02/92
[5 empty] | -- | 2016-02-05 | 7:20 | 2016-02-05 | 18:04 | -- | -- | -- |  |  |  | 10.7333 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC Code CR02/128
[5 empty] | -- | 2016-02-06 | 7:19 | 2016-02-06 | 18:20 | -- | -- | -- |  |  |  | 11.0167 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC Code CR02/148
[5 empty] | -- | 2016-02-07 | 7:14 | 2016-02-07 | 18:27 | -- | -- | -- |  |  |  | 11.2167 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC Code CR02/167
[5 empty] | -- | 2016-02-08 | 7:52 | 2016-02-08 | 17:58 | -- | -- | -- |  |  |  | 10.1 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC Code CR02/180
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 77.05
8 | SR1L8 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
9 | SR1L9 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
10 | SR1L10 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
11 | SR1L11 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
12 | SR1L12 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
13 | SR1L13 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-01 | 11:04 | -- | -- | -- |  |  |  | 11.0667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 11.0667
14 | SR1L14 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | 2016-02-22 | 6:48 | 2016-02-22 | 7:18 | -- | -- | -- | 0.5 |  |  |  | N/A | N/A | N/A | Tripped on RN fault. Dist:173.3KM,from Hyderabad,Dist:52.17KM ,FC-5.053KA |  | 99.9282
[7 empty] | Sub Total --> | [5 empty] | 0.5 | 0 | 0 | 0
15 | SR1L15 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
16 | SR1L16 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
17 | SR1L17 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-01 | 11:12 | -- | -- | -- |  |  |  | 11.2 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage |  | 100
[5 empty] | -- |  | Sub Total --> | [5 empty] | 0 | 0 | 0 | 11.2
18 | SR1L18 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
19 | SR1L19 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
20 | SR1L20 | KURNOOL(NEW) - GOOTY | 112.609 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-01 | 8:52 | -- | -- | -- |  |  |  | 8.8667 | -- | -- | -- | Line was kept open as per SRLDC instruction for containing over voltage |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 8.8667
21 | SR1L21 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
22 | SR1L22 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | 2016-02-19 | 7:45 | 2016-02-19 | 18:58 | -- | -- | -- |  |  |  | 11.2167 | -- | -- | -- | Shutdown availed by M/s TSTRANSCO vide CR02/493 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 11.2167
23 | SR1L23 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
24 | SR1L24 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
25 | SR1L25 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-01 | 12:47 | -- | -- | -- |  |  |  | 12.7833 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-01/418 |  | 99.1499
[5 empty] | -- | 2016-02-01 | 12:54 | 2016-02-01 | 18:49 | -- | -- | -- | 5.9167 |  |  |  | N/A | N/A | N/A | Tripped on YN fault, 256.6 KM & 1.20 KA from VJA end
[5 empty] | -- | 2016-02-20 | 10:49 | 2016-03-01 | 0:00 | -- | -- | -- |  |  |  | 229.1833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/547
[7 empty] | Sub Total --> | [5 empty] | 5.9167 | 0 | 0 | 241.9667
26 | SR1L26 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2016-02-01 | 6:21 | 2016-02-01 | 6:32 | -- | -- | -- | 0.18333 |  |  |  | N/A | N/A | N/A | Tripped on YN fault at NLR end only , 15.46 KM & 11.28 KA from VJA end |  | 99.9737
[5 empty] | -- | 2016-02-07 | 22:33 | 2016-02-20 | 10:41 | -- | -- | -- |  |  |  | 300.1333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/174
[7 empty] | Sub Total --> | [5 empty] | 0.18333 | 0 | 0 | 300.1333
27 | SR1L27 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2016-02-17 | 9:28 | 2016-02-17 | 18:08 | -- | -- | -- |  |  |  | 8.6667 | N/A | N/A | N/A | Shutdown by M/s APTRANSCO for general maintenance works vide SRLDC code CR02/407 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 8.6667
28 | SR1L28 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | 2016-02-19 | 10:44 | 2016-02-19 | 14:30 | -- | -- | -- |  |  |  | 3.7667 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO vide CR02/504 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 3.7667
29 | SR1L29 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
30 | SR1L30 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
31 | SR1L31 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
32 | SR1L32 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
33 | SR1L33 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
34 | SR1L34 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
35 | SR1L35 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
36 | SR1L36 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
37 | SR1L37 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
38 | SR1L38 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
39 | SR1L39 | KURNOOL - GOOTY | 84.19 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
40 | SR1L40 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
41 | SR1L41 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | 2016-02-09 | 8:11 | 2016-02-09 | 20:20 | -- | -- | -- |  |  |  | 12.15 | -- | -- | -- | Shutdown availed for replacement of porcelain insulators with CLR insulators in polluted streches near RTPS vide SRLDC Code CR02/216 |  | 100
[5 empty] | -- | 2016-02-11 | 8:43 | 2016-02-11 | 20:24 | -- | -- | -- |  |  |  | 11.6833 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators in polluted streches near RTPS vide SRLDC Code CR02/285
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 23.8333
42 | SR1L42 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
43 | SR1L43 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | 2016-02-10 | 8:18 | 2016-02-10 | 19:41 | -- | -- | -- |  |  |  | 11.3833 | -- | -- | -- | Shutdown availed for replacement of porcelain insulators with CLR insulators in polluted streches near RTPS vide SRLDC Code CR02/239 |  | 100
[5 empty] | -- | 2016-02-12 | 8:09 | 2016-02-12 | 18:47 | -- | -- | -- |  |  |  | 10.6333 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators in polluted streches near RTPS vide SRLDC Code CR02/311
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 22.0167
44 | SR1L44 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | 2016-02-04 | 16:22 | 2016-02-04 | 17:02 | -- | -- | -- | 0.66667 |  |  |  | -- | -- | -- | Shutdown availed by Nelamangala for attending line isolator hot spot vide SRLDC code CR02/112 |  | 99.9042
[7 empty] | Sub Total --> | [5 empty] | 0.66667 | 0 | 0 | 0
45 | SR1L45 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
46 | SR1L46 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
47 | SR1L47 | MEPL - NELLOREPS | 3.83 | SR-I | -- | 2016-02-04 | 6:38 | 2016-02-04 | 20:57 | -- | -- | -- |  |  |  | 14.3167 | -- | -- | -- | SD availed by MEPL for attending gantry hotspot at MEPL end vide SRLDC Code CR02/91 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 14.3167
48 | SR1L48 | SEPL - NELLOREPS | 3.83 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
49 | SR1L49 | GOOTY - NELLOREPS - I | 289.004 | SR-I | -- | 2016-02-18 | 12:49 | 2016-02-18 | 12:49 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Autoreclosed succcessful on R-N transient fault. FLR: 268.0 kms from Gooty end |  | 100
[5 empty] | -- | 2016-02-23 | 16:31 | 2016-02-23 | 16:31 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Autoreclosed successfully on R-N transient fault. FLR: 246 kms from Gooty end
[5 empty] | -- | 2016-02-24 | 7:32 | 2016-02-25 | 19:04 | -- | -- | -- |  |  |  | 35.5333 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for line crossing works of 400 kV Jammalamadugu-Orvakonda line vide SRLDC code CR02/655
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 35.5333
50 | SR1L50 | GOOTY - NELLOREPS - II | 289.004 | SR-I | -- | 2016-02-24 | 7:34 | 2016-02-25 | 19:50 | -- | -- | -- |  |  |  | 36.2667 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for line crossing works of 400 kV Jammalamadugu-Orvakonda line vide SRLDC code CR02/656 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 36.2667
51 | SR1L51 | NELLOREPS - NCC | 32.4881 | SR-I | -- | 2016-02-19 | 10:25 | 2016-02-19 | 18:03 | -- | -- | -- |  |  |  | 7.6333 | N/A | N/A | N/A | Shutdown availed for OPGW stringing works vide CR02/502 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 7.6333
52 | SR1L52 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
53 | SR1L53 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
54 | SR1L54 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
55 | SR1L55 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
56 | SR1L56 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | 2016-02-08 | 0:25 | 2016-02-08 | 7:25 | -- | -- | -- |  |  |  | 7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/176 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 7
57 | SR1L57 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | 2016-02-10 | 12:45 | 2016-02-10 | 13:01 | -- | -- | -- | 0.26667 |  |  |  | N/A | N/A | N/A | Tripped due to receipt of DT at RCN end. Line was holding from Solapur end |  | 99.9617
[7 empty] | Sub Total --> | [5 empty] | 0.26667 | 0 | 0 | 0
58 | SR1L58 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | 2016-02-15 | 18:59 | 2016-02-15 | 21:51 | -- | -- | -- | 2.87 |  |  |  | N/A | N/A | N/A | Shutdown availed for repairing failed jumper at Loc.No.392. vide SRLDC code CR02/372 |  | 99.5876
[7 empty] | Sub Total --> | [5 empty] | 2.87 | 0 | 0 | 0
59 | SR1L59 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
60 | SR1L60 | KURNOOL(NEW) - RAICHUR(NEW) - I | 120.482 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-01 | 14:47 | -- | -- | -- | 14.7833 |  |  |  | N/A | N/A | N/A | Shutdown availed for insulators replacement and jumpers rectification vide SRLDC code CR01/835 |  | 97.8727
[5 empty] | -- | 2016-02-28 | 18:00 | 2016-02-28 | 18:39 | -- | -- | -- |  |  | 0.65 |  | N/A | N/A | N/A | Line tripped on operation of overvoltage protection at Kurnool end.
[5 empty] | -- | 2016-02-29 | 18:02 | 2016-02-29 | 18:26 | -- | -- | -- |  |  | 0.4 |  | N/A | N/A | N/A | Line tripped on operation of overvoltage protection at Kurnool end.
[7 empty] | Sub Total --> | [5 empty] | 14.7833 | 0 | 1.05 | 0
61 | SR1L61 | KURNOOL(NEW) - RAICHUR(NEW) - II | 118.423 | SR-I | -- | 2016-02-28 | 18:00 | 2016-02-28 | 19:01 | -- | -- | -- |  |  | 1.0167 |  | N/A | N/A | N/A | Line tripped on operation of overvoltage protection at Kurnool end. |  | 100
[5 empty] | -- | 2016-02-29 | 18:02 | 2016-02-29 | 18:29 | -- | -- | -- |  |  | 0.45 |  | N/A | N/A | N/A | Line tripped on operation of overvoltage protection at Kurnool end.
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 1.4667 | 0
62 | SR1L62 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-24 | 7:07 | -- | -- | -- |  |  |  | 559.1167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage |  | 100
[5 empty] | -- | 2016-02-26 | 20:18 | 2016-03-01 | 0:00 | -- | -- | -- |  |  |  | 75.7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/742
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 634.8167
63 | SR1L63 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-03 | 9:29 | -- | -- | -- |  |  |  | 57.4833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 57.4833
64 | SR1L64 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2016-02-11 | 14:30 | 2016-02-11 | 19:56 | -- | -- | -- |  |  | 5.4333 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at Thiruvallum end. Direct Trip signal received at Kurnool end. |  | 100
[5 empty] | -- | 2016-02-11 | 19:56 | 2016-02-22 | 12:13 | -- | -- | -- |  |  |  | 256.2833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage
[5 empty] | -- | 2016-02-23 | 0:28 | 2016-02-28 | 11:32 | -- | -- | -- |  |  |  | 131.0667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/623
[5 empty] | -- | 2016-02-28 | 18:00 | 2016-02-28 | 18:05 | -- | -- | -- |  |  | 0.083333 |  | N/A | N/A | N/A | Line tripped on operation of overvoltage protection at Kurnool end.
[5 empty] | -- | 2016-02-28 | 18:05 | 2016-02-29 | 10:03 | -- | -- | -- |  |  |  | 15.9667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage
[5 empty] | -- | 2016-02-29 | 18:02 | 2016-02-29 | 18:10 | -- | -- | -- |  |  | 0.13333 |  | N/A | N/A | N/A | Line tripped on operation of overvoltage protection at Kurnool end.
[5 empty] | -- | 2016-02-29 | 18:10 | 2016-03-01 | 0:00 | -- | -- | -- |  |  |  | 5.8333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 5.65 | 409.15
65 | SR1L65 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-11 | 19:22 | -- | -- | -- |  |  |  | 259.3667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 259.3667
66 | SR1L66 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
67 | SR1L67 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
68 | SR1L68 | TPCIL - NCC | 5.168 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
69 | SR1L69 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-12 | 17:33 | -- | -- | -- |  |  |  | 281.55 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage vide msg No CP-12/488 |  | 100
[5 empty] | -- | 2016-02-22 | 18:02 | 2016-02-22 | 18:10 | -- | -- | -- |  |  | 0.13333 |  | N/A | N/A | N/A | Tripped due to operation of overvoltage protection at Tumkur
[5 empty] | -- | 2016-02-22 | 18:10 | 2016-03-01 | 0:00 | -- | -- | -- |  |  |  | 173.8333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0.13333 | 455.3833
70 | SR1L70 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | 2016-02-01 | 0:00 | 2016-02-09 | 10:14 | -- | -- | -- |  |  |  | 202.2333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltage |  | 100
[5 empty] | -- | 2016-02-12 | 17:31 | 2016-03-01 | 0:00 | -- | -- | -- |  |  |  | 414.4833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/324
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 616.7167
71 | SR1L71 | KHAMMAM - N'SAGAR II | 144.416 | SR-I | -- | 2016-02-27 | 7:07 | 2016-02-27 | 19:59 | 42374.9049 | -- | -- |  |  |  | 12.8667 | N/A | N/A | N/A | Shutdown availed for OPGW Strining works vide SRLDC code CR02/746 |  | 100
[5 empty] | -- | 2016-02-28 | 6:40 | 2016-03-01 | 0:00 | 42375.934 | -- | -- |  |  |  | 41.3333 | N/A | N/A | N/A | Shutdown availed for OPGW Strining works vide SRLDC code CR02/765
[5 empty] | -- |  | Sub Total --> | [5 empty] | 0 | 0 | 0 | 54.2
72 | SR1L72 | KHAMMAM - N'SAGAR III | 144.416 | SR-I | -- | 2016-02-27 | 7:09 | 2016-02-27 | 20:03 | -- | -- | -- |  |  |  | 12.9 | N/A | N/A | N/A | Shutdown availed for OPGW Strining works vide SRLDC code CR02/747 |  | 100
[5 empty] | -- | 2016-02-28 | 6:41 | 2016-02-28 | 20:53 | -- | -- | -- |  |  |  | 14.2 | N/A | N/A | N/A | Shutdown availed for OPGW Strining works vide SRLDC code CR02/766
[5 empty] | -- |  | Sub Total --> | [5 empty] | 0 | 0 | 0 | 27.1
73 | SR1T1 | CUDDAPAH ICT I | 315 | SR-I | -- | 2016-02-25 | 9:52 | 2016-02-25 | 18:43 | -- | -- | -- |  |  |  | 8.85 | -- | -- | -- | Shutdown availed for OTI retrofitting works vide SRLDC code CR02/695 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 8.85
74 | SR1T2 | CUDDAPAH ICT II | 315 | SR-I | -- | 2016-02-25 | 14:23 | 2016-02-25 | 14:36 | -- | -- | -- |  |  |  | 0.21667 | -- | -- | -- | Tripped on operation of 220kV side Back up O/C Protection for fault in 400kV KDP-KLR line |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0.21667
75 | SR1T3 | GAJUWAKA ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
76 | SR1T4 | GAZUWAKA ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
77 | SR1T5 | GOOTY ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
78 | SR1T6 | GOOTY ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
79 | SR1T7 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
80 | SR1T8 | HYDERABAD ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
81 | SR1T9 | HYDERABAD ICT - III | 315 | SR-I | -- | 2016-02-09 | 10:18 | 2016-02-09 | 19:03 | -- | -- | -- |  |  |  | 8.75 | -- | -- | -- | Shutdown availed for OTI retrofitting works vide SRLDC code CR02/222 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 8.75
82 | SR1T10 | KHAMMAM ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
83 | SR1T11 | KHAMMAM ICT II | 315 | SR-I | -- | 2016-02-25 | 10:03 | 2016-02-25 | 13:42 | -- | -- | -- |  |  |  | 3.65 | -- | -- | -- | Shutdown availed for OTI retrofitting works vide SRLDC code CR02/699 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 3.65
84 | SR1T12 | MUNIRABAD ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
85 | SR1T13 | MUNIRABAD ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
86 | SR1T14 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
87 | SR1T15 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
88 | SR1T16 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | 2016-02-17 | 10:14 | 2016-02-17 | 12:32 | -- | -- | -- |  |  |  | 2.3 | -- | -- | -- | Shutdown by M/s APTRANSCO for attending hotspot on Yph CT at their end vide SRLDC code CR02/413 |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 2.3
89 | SR1T17 | VIJAYAWADA ICT I | 315 | SR-I | -- | 2016-02-02 | 5:51 | 2016-02-02 | 13:17 | -- | -- | -- |  | 7.4333 |  |  | -- | -- | -- | Tripped on 220kV side only due to operation of Busbar protection at APTRANSCO Nunna end |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 7.4333 | 0 | 0
90 | SR1T18 | VIJAYAWADA ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
91 | SR1T19 | WARANGAL ICT I | 315 | SR-I | -- | 2016-02-19 | 11:27 | 2016-02-19 | 14:25 | -- | -- | -- | 2.9667 |  |  |  | N/A | N/A | N/A | Shutdown availed for attending Hotspot in 40389isolator vide SRLDC code CR02/508 |  | 99.5738
[7 empty] | Sub Total --> | [5 empty] | 2.9667 | 0 | 0 | 0
92 | SR1T20 | WARANGAL ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
93 | SR1T21 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
94 | SR1T22 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
95 | SR1T23 | NELLOREPS ICT - II | 1500 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
96 | SR1T24 | NELLOREPS ICT - III | 1500 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
97 | SR1T25 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
98 | SR1T26 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
99 | SR1R1 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | 2016-02-16 | 9:01 | 2016-02-16 | 17:58 | -- | -- | -- |  |  |  | 8.95 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/377 |  | 100
[5 empty] | -- | 2016-02-17 | 9:58 | 2016-02-17 | 17:35 | -- | -- | -- |  |  |  | 7.6167 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/417
[5 empty] | -- | 2016-02-18 | 9:56 | 2016-02-18 | 19:13 | -- | -- | -- |  |  |  | 9.2833 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/467
[5 empty] | -- | 2016-02-19 | 9:18 | 2016-02-19 | 17:50 | -- | -- | -- |  |  |  | 8.5333 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/497
[5 empty] | -- | 2016-02-20 | 9:56 | 2016-02-20 | 18:16 | -- | -- | -- |  |  |  | 8.3333 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/542
[5 empty] | -- | 2016-02-21 | 9:15 | 2016-02-21 | 19:21 | -- | -- | -- |  |  |  | 10.1 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/542
[5 empty] | -- | 2016-02-22 | 9:32 | 2016-02-22 | 18:22 | -- | -- | -- |  |  |  | 8.8333 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/542
[5 empty] | -- | 2016-02-23 | 9:25 | 2016-02-23 | 18:14 | -- | -- | -- |  |  |  | 8.8167 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/
[5 empty] | -- | 2016-02-24 | 10:05 | 2016-02-24 | 12:55 | -- | -- | -- |  |  |  | 2.8333 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR02/664
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 73.3
98 | SR1R2 | GOOTY BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
99 | SR1R3 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
100 | SR1R4 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
101 | SR1R5 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | 2016-02-24 | 9:42 | 2016-02-24 | 17:48 | -- | -- | -- | 8.1 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC code CR02/660 |  | 98.8362
[7 empty] | Sub Total --> | [5 empty] | 8.1 | 0 | 0 | 0
102 | SR1R6 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2016-02-08 | 15:11 | 2016-02-08 | 17:47 | -- | -- | -- | 2.6 |  |  |  | N/A | N/A | N/A | Shutdown availed for CT replacement vide SRLDC code CR02/196 |  | 99.6264
[7 empty] | Sub Total --> | [5 empty] | 2.6 | 0 | 0 | 0
103 | SR1R7 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
104 | SR1R8 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
105 | SR1R9 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
106 | SR1R10 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
107 | SR1R11 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
108 | SR1R12 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
109 | SR1R13 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
110 | SR1R14 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
111 | SR1R15 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
112 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | 2016-02-23 | 10:13 | 2016-02-23 | 19:58 | -- | -- | -- | 9.75 |  |  |  | N/A | N/A | N/A | Tripped due to operation of Valve power supply unit failure of YYLV valve of south R-Phase |  | 98.5991
[7 empty] | Sub Total --> | [5 empty] | 9.75 | 0 | 0 | 0
113 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
114 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
115 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[7 empty] | Sub Total --> | [5 empty] | 0 | 0 | 0 | 0
|  |  | Note in type of failure column please indicate following : | [9 empty] | 48.6033 | 7.4333 | 8.3 | 3431.8167
[8 empty] | 2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc | 2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse