## SOP
Standard of Performance data for the month of March-2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L1 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- | SRPC | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
2 | SR1L2 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
3 | SR1L3 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
4 | SR1L4 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
5 | SR1L5 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
6 | SR1L6 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
7 | SR1L7 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | 2016-03-27 | 22:05 | 2016-03-27 | 22:37 | -- | -- | -- | 0.53333 |  |  |  | -- | -- | -- | Tripped on Y-N fault; FL:146.3 KM from RDM & 27.16 KM from CPR. Iy=1.69 kA at RDM end |  | 99.9283
[6 empty] | Sub Total --> | [6 empty] | 0.53333 | 0 | 0 | 0
8 | SR1L8 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | 2016-03-07 | 19:38 | 2016-03-07 | 20:50 | -- | -- | -- | 1.2 |  |  |  | -- | -- | -- | Tripped on R-B fault; FL:69 KM from RDM & 127.5 KM from CPR. Ir=6.1 kA & Ib=6.2 kA at RDM end |  | 99.6909
[5 empty] | -- | 2016-03-08 | 23:55 | 2016-03-09 | 1:01 | -- | -- | -- | 1.1 |  |  |  | N/A | N/A | N/A | Tripped on R-B fault; FL:69 KM from RDM & 127.5 KM from CPR. Ir=6.1 kA & Ib=6.2 kA at RDM end
[6 empty] | Sub Total --> | [6 empty] | 2.3 | 0 | 0 | 0
9 | SR1L9 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR1L10 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
11 | SR1L11 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | 2016-03-15 | 11:00 | 2016-03-15 | 11:31 | -- | -- | -- |  | 0.51667 |  |  | N/A | N/A | N/A | Tripped at Ramagundam end only due to mal-operation of AR L/O relay at NTPC end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.51667 | 0 | 0
12 | SR1L12 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR1L13 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
14 | SR1L14 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
15 | SR1L15 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | 2016-03-12 | 12:13 | 2016-03-12 | 13:23 | -- | -- | -- |  |  |  | 1.1667 | N/A | N/A | N/A | Tripped on Y-N fault, 2.147 KA & 137.4 KM from NSR end due to agri fire at location No 339-340 |  | 100
[5 empty] | -- | 2016-03-14 | 16:55 | 2016-03-14 | 16:55 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Auto-reclosed successfully for R-N fault, FL:41.03 KM from N'sagar & 237.97 KM from KDP end. 6.9 KA at N'sagar
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.1667
16 | SR1L16 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
17 | SR1L17 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | 2016-03-20 | 6:10 | 2016-03-20 | 18:20 | -- | -- | -- |  |  |  | 12.1667 | N/A | N/A | N/A | SD availed by TSTRANSCO for construction works vide CR03/482 |  | 100
[5 empty] | -- | 2016-03-22 | 11:11 | 2016-03-22 | 11:11 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Auto-reclosed successfully for B-N fault, FL:145 KM from N'sagar and 2.3 KM from KMM end & 3.073 KA at N'sagar
[5 empty] | -- | 2016-03-22 | 11:12 | 2016-03-22 | 11:12 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Auto-reclosed successfully for B-N fault, FL:145 KM from N'sagar and 2.3 KM from KMM end & 3.078 KA at N'sagar
[5 empty] | -- | 2016-03-22 | 11:12 | 2016-03-22 | 12:09 | -- | -- | -- |  |  |  | 0.95 | N/A | N/A | N/A | Tripped for B-N fault, FL:145 KM from N'sagar and 2.3 KM from KMM end & 3.106 KA at N'sagar (Agri-fire at Loc. No.6-7)
[5 empty] | -- | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.1167
18 | SR1L18 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | 2016-03-15 | 6:16 | 2016-03-15 | 18:52 | -- | -- | -- |  |  |  | 12.6 | -- | -- | -- | SD availed by TSTRANSCO for construction works vide CR03/360 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.6
19 | SR1L19 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | 2016-03-11 | 15:24 | 2016-03-11 | 15:57 | -- | -- | -- |  |  |  | 0.55 | N/A | N/A | N/A | Tripped on R-N fault due to agrifire at Loc:85-86 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.55
20 | SR1L20 | KURNOOL(NEW) - GOOTY | 112.609 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
21 | SR1L21 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR1L22 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | 2016-03-18 | 9:15 | 2016-03-18 | 15:57 | -- | -- | -- |  |  |  | 6.7 | N/A | N/A | N/A | Shutdown availed by M/s TSTRANSCO for general maintenance and MRT works vide SRLDC code:CR03/445 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.7
23 | SR1L23 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
24 | SR1L24 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | 2016-03-16 | 9:10 | 2016-03-16 | 19:18 | -- | -- | -- | 10.1333 |  |  |  | -- | -- | -- | Shutdown availed for AMP works vide SRLDC code CR03/395 |  | 98.638
[6 empty] | Sub Total --> | [6 empty] | 10.1333 | 0 | 0 | 0
25 | SR1L25 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2016-03-01 | 0:00 | 2016-03-02 | 17:53 | -- | -- | -- |  |  |  | 41.8833 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/547 |  | 100
[5 empty] | -- | 2016-03-07 | 8:53 | 2016-03-07 | 10:29 | -- | -- | -- |  |  |  | 1.6 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for passage of Prabhas to kotappakonda temple vide SRLDC code CR03/147
[5 empty] | -- | 2016-03-08 | 9:23 | 2016-03-08 | 12:09 | -- | -- | -- |  |  |  | 2.7667 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for passage of Prabhas to kotappakonda temple vide SRLDC code CR03/165
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 46.25
26 | SR1L26 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2016-03-07 | 8:55 | 2016-03-07 | 10:15 | -- | -- | -- |  |  |  | 1.3333 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for passage of Prabhas to kotappakonda temple vide SRLDC code CR03/148 |  | 100
[5 empty] | -- | 2016-03-07 | 10:15 | 2016-03-08 | 12:28 | -- | -- | -- |  |  |  | 26.2167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.55
27 | SR1L27 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2016-03-17 | 9:17 | 2016-03-17 | 19:54 | -- | -- | -- |  |  |  | 10.6167 | N/A | N/A | N/A | SD availed by TRANSCO for construction works vide CR03/425 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.6167
28 | SR1L28 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | 2016-03-17 | 9:18 | 2016-03-17 | 19:57 | -- | -- | -- |  |  |  | 10.65 | N/A | N/A | N/A | SD availed by TRANSCO for construction works vide CR03/426 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.65
29 | SR1L29 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | 2016-03-04 | 9:19 | 2016-03-04 | 20:01 | -- | -- | -- |  |  |  | 10.7 | -- | -- | -- | Shutdown availed by M/s APTRANSCO for general maintenance works vide SRLDC code CR03/70 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.7
30 | SR1L30 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | 2016-03-11 | 9:05 | 2016-03-11 | 18:31 | -- | -- | -- |  |  |  | 9.4333 | -- | -- | -- | Shutdown availed by M/s NTPC for maintenance works vide SRLDC code CR03/276 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.4333
31 | SR1L31 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | 2016-03-10 | 10:11 | 2016-03-10 | 18:28 | -- | -- | -- |  |  |  | 8.2833 | -- | -- | -- | Shutdown availed by M/s APTRANSCO for general maintenance works vide SRLDC code CR03/247 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.2833
32 | SR1L32 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR1L33 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | 2016-03-10 | 12:31 | 2016-03-10 | 13:28 | -- | -- | -- |  |  | 0.95 |  | -- | -- | -- | Line tripped due to operation of overvoltage protection at Jeypore end. Direct Trip signal received at Gajuwaka end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.95 | 0
34 | SR1L34 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | 2016-03-10 | 12:31 | 2016-03-10 | 14:17 | -- | -- | -- |  |  | 1.7667 |  | -- | -- | -- | Line tripped due to operation of overvoltage protection at Jeypore end. Direct Trip signal received at Gajuwaka end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.7667 | 0
35 | SR1L35 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | 2016-03-09 | 17:20 | 2016-03-09 | 19:34 | -- | -- | -- | 2.2333 |  |  |  | -- | -- | -- | Shutdown availed by siriperumbdur for isolator rectification works vide SRLDC code CR03/228 |  | 99.6998
[6 empty] | Sub Total --> | [6 empty] | 2.2333 | 0 | 0 | 0
36 | SR1L36 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR1L37 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR1L38 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR1L39 | KURNOOL - GOOTY | 84.19 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR1L40 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | 2016-03-31 | 17:03 | 2016-03-31 | 17:03 | -- | -- | -- |  |  |  |  | -- | -- | -- | Auto-reclosed successfully for B-N fault, FL:139.9 KM and 2.76 KA From Gooty |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR1L41 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR1L42 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | 2016-03-31 | 17:09 | 2016-03-31 | 17:09 | -- | -- | -- | 0 |  |  |  | -- | -- | -- | Auto-reclosed successfully for B-N fault, FL:140 KM and 2.67 KA From Gooty |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
43 | SR1L43 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR1L44 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR1L45 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR1L46 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR1L47 | MEPL - NELLOREPS | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR1L48 | SEPL - NELLOREPS | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SR1L49 | GOOTY - NELLOREPS - I | 289.004 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SR1L50 | GOOTY - NELLOREPS - II | 289.004 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR1L51 | NELLOREPS - NCC | 32.4881 | SR-I | -- | 2016-03-18 | 9:46 | 2016-03-18 | 18:11 | -- | -- | -- |  |  |  | 8.4167 | N/A | N/A | N/A | H/T vide SRLDC code CR03/448 for removal of LILO and restoration of NPS-TPCIL-1 line |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.4167
52 | SR1L52 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | 2016-03-01 | 11:18 | 2016-03-01 | 19:23 | -- | -- | -- |  |  |  | 8.0833 | N/A | N/A | N/A | Shutdown availed by M/s TPCIL for attending hotspot vide SRLDC code CR03/13 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.0833
53 | SR1L53 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SR1L54 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR1L55 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | 2016-03-08 | 11:11 | 2016-03-08 | 17:15 | -- | -- | -- | 6.0667 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC code CR03/173 |  | 99.1846
[6 empty] | Sub Total --> | [6 empty] | 6.0667 | 0 | 0 | 0
56 | SR1L56 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | 2016-03-09 | 10:52 | 2016-03-09 | 16:12 | -- | -- | -- | 5.3333 |  |  |  | N/A | N/A | N/A | Shutdown availed for terminal equipment AMP works vide SRLDC code CR03/211 |  | 99.2832
[6 empty] | Sub Total --> | [6 empty] | 5.3333 | 0 | 0 | 0
57 | SR1L57 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | 2016-03-31 | 20:40 | 2016-03-31 | 20:40 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Auto-reclosed successfully for R-N fault, FL:57.8 KM from Raichur end; 147.2KM from Solapur end and 6.8KA at Raichur end |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
58 | SR1L58 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR1L59 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR1L60 | KURNOOL(NEW) - RAICHUR(NEW) - I | 120.482 | SR-I | -- | 2016-03-05 | 18:03 | 2016-03-05 | 18:58 | -- | -- | -- |  |  | 0.91667 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at Kurnool end. Direct Trip signal received at Raichur end. |  | 100
[5 empty] | -- | 2016-03-28 | 18:01 | 2016-03-28 | 18:30 | -- | -- | -- |  |  | 0.48333 |  | N/A | N/A | N/A | Tripped on O/V protection at KLN end
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.4 | 0
61 | SR1L61 | KURNOOL(NEW) - RAICHUR(NEW) - II | 118.423 | SR-I | -- | 2016-03-05 | 18:03 | 2016-03-05 | 19:18 | -- | -- | -- |  |  | 1.25 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at Kurnool end. Direct Trip signal received at Raichur end. |  | 100
[5 empty] | -- | 2016-03-06 | 17:11 | 2016-03-06 | 20:19 | -- | -- | -- |  |  |  | 3.1333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code CR-03/138
[5 empty] | -- | 2016-03-07 | 17:26 | 2016-03-07 | 20:14 | -- | -- | -- |  |  |  | 2.8 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code CR-03/154
[5 empty] | -- | 2016-03-08 | 17:16 | 2016-03-08 | 18:27 | -- | -- | -- |  |  |  | 1.18 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/185
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.25 | 7.1133
62 | SR1L62 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2016-03-01 | 0:00 | 2016-04-01 | 0:00 | -- | -- | -- |  |  |  | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/742 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
63 | SR1L63 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR1L64 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2016-03-01 | 0:00 | 2016-03-01 | 10:49 | -- | -- | -- |  |  |  | 10.8167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage |  | 100
[5 empty] | -- | 2016-03-01 | 14:38 | 2016-03-02 | 12:13 | -- | -- | -- |  |  |  | 21.5833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/20
[5 empty] | -- | 2016-03-02 | 17:20 | 2016-03-03 | 10:18 | -- | -- | -- |  |  |  | 16.9667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/44
[5 empty] | -- | 2016-03-03 | 17:39 | 2016-03-04 | 10:37 | -- | -- | -- |  |  |  | 16.9667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/59
[5 empty] | -- | 2016-03-05 | 18:03 | 2016-03-05 | 19:07 | -- | -- | -- |  |  | 1.0667 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at Kurnool end. Direct Trip signal received at Thiruvallum end.
[5 empty] | -- | 2016-03-21 | 17:25 | 2016-03-22 | 15:15 | -- | -- | -- |  |  |  | 21.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/520
[5 empty] | -- | 2016-03-22 | 17:38 | 2016-03-28 | 12:49 | -- | -- | -- |  |  |  | 139.1833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/549
[5 empty] | -- | 2016-03-29 | 17:08 | 2026-07-29 | 0:00 | -- | -- | -- |  |  |  | 54.8667 | N/A | N/A | N/A | Hand tripped as per SRLDC instructions for voltage regulation in the system vide SRLDC code no. CR-03/715
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.0667 | 282.2167
65 | SR1L65 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2016-03-04 | 23:03 | 2016-03-05 | 12:09 | -- | -- | -- |  |  |  | 13.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code CR-03/98 |  | 100
[5 empty] | -- | 2016-03-05 | 18:03 | 2016-03-05 | 18:15 | -- | -- | -- |  |  | 0.2 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at Thiruvallum end. Direct Trip signal received at Kurnool end.
[5 empty] | -- | 2016-03-05 | 18:15 | 2016-03-07 | 12:42 | -- | -- | -- |  |  |  | 42.45 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage
[5 empty] | -- | 2016-03-07 | 16:32 | 2016-03-08 | 10:56 | -- | -- | -- |  |  |  | 18.4 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code CR-03/153
[5 empty] | -- | 2016-03-08 | 16:45 | 2016-03-21 | 11:13 | -- | -- | -- |  |  |  | 306.4667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/183
[5 empty] | -- | 2016-03-28 | 18:01 | 2016-03-28 | 18:05 | -- | -- | -- |  |  | 0.066667 |  | N/A | N/A | N/A | Tripped on O/V protection at TRVLM end
[5 empty] | -- | 2016-03-28 | 18:05 | 2016-03-29 | 9:45 | -- | -- | -- |  |  |  | 15.6667 | N/A | N/A | N/A | Kept Out as per SRLDC instruction for voltage regulation in the system vide SRLDC e-mail
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.26667 | 396.0833
66 | SR1L66 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR1L67 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
68 | SR1L68 | TPCIL - NCC | 5.168 | SR-I | -- | 2016-03-18 | 9:46 | 2016-03-18 | 18:11 | -- | -- | -- |  |  |  | 8.4167 | N/A | N/A | N/A | H/T vide SRLDC code CR03/448 for removal of LILO and restoration of NPS-TPCIL-1 line |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.4167
69 | SR1L69 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | 2016-03-01 | 0:00 | 2016-03-04 | 11:18 | -- | -- | -- |  |  |  | 83.3 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage |  | 100
[5 empty] | -- | 2016-03-19 | 11:20 | 2026-07-29 | 0:00 | -- | -- | -- |  |  |  | 300.6667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/311
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 383.9667
70 | SR1L70 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | 2016-03-01 | 0:00 | 2016-03-19 | 11:32 | -- | -- | -- |  |  |  | 443.5333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/324 |  | 100
[5 empty] | -- | 2016-03-28 | 7:51 | 2016-03-28 | 10:34 | -- | -- | -- |  |  | 2.7167 |  | N/A | N/A | N/A | Tripped on O/V protection at Gooty end
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 2.7167 | 443.5333
71 | SR1L71 | KHAMMAM - N'SAGAR II | 144.416 | SR-I | -- | 2016-03-01 | 0:00 | 2016-03-03 | 20:50 | 42374.9049 | -- | -- |  |  |  | 68.8333 | N/A | N/A | N/A | Shutdown availed for OPGW Strining works vide SRLDC code CR02/765 |  | 100
[5 empty] | -- | 2016-03-04 | 7:06 | 2016-03-05 | 20:35 | 42375.934 | -- | -- |  |  |  | 37.4833 | N/A | N/A | N/A | Shutdown availed for OPGW Strining works vide SRLDC code CR03/67
[5 empty] | -- | Sub Total --> | [6 empty] | 0 | 0 | 0 | 106.3167
72 | SR1L72 | KHAMMAM - N'SAGAR III | 144.416 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[5 empty] | -- | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR1L73 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR1L74 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
75 | SR1L75 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR1T1 | CUDDAPAH ICT I | 315 | SR-I | -- | 2016-03-30 | 11:28 | 2016-03-30 | 12:29 | -- | -- | -- |  | 1.0167 |  |  | N/A | N/A | N/A | Tripped due to 220kV BB protection operation at 220 kV Chinakampalli station |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.0167 | 0 | 0
77 | SR1T2 | CUDDAPAH ICT II | 315 | SR-I | -- | 2016-03-30 | 11:14 | 2016-03-30 | 16:51 | -- | -- | -- |  |  |  | 5.6167 | N/A | N/A | N/A | Shutdown availed by APTRANSCO. Construction works vide SRLDC code:CR-03/725. Hand tripped on 220 KV side only. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.6167
78 | SR1T3 | GAJUWAKA ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR1T4 | GAZUWAKA ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR1T5 | GOOTY ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR1T6 | GOOTY ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
82 | SR1T7 | HYDERABAD ICT - I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR1T8 | HYDERABAD ICT - II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
84 | SR1T9 | HYDERABAD ICT - III | 315 | SR-I | -- | 2016-03-13 | 14:10 | 2016-03-13 | 17:52 | -- | -- | -- | 3.7 |  |  |  | -- | -- | -- | SD availed for replacement of 220 kV CVT Y-Ph vide CR03/329 |  | 99.5027
[6 empty] | Sub Total --> | [6 empty] | 3.7 | 0 | 0 | 0
85 | SR1T10 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR1T11 | KHAMMAM ICT II | 315 | SR-I | -- | 2016-03-10 | 12:03 | 2016-03-10 | 12:28 | -- | -- | -- | 0.41667 |  |  |  | -- | -- | -- | Tripped due to 220 KV side LBB relay maloperation |  | 99.944
[6 empty] | Sub Total --> | [6 empty] | 0.41667 | 0 | 0
87 | SR1T12 | MUNIRABAD ICT I | 315 | SR-I | -- | 2016-03-09 | 10:41 | 2016-03-09 | 20:34 | -- | -- | -- |  |  |  | 9.8833 | -- | -- | -- | Shutdown availed for isolator rectification works vide SRLDC code CR03/210 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.8833
88 | SR1T13 | MUNIRABAD ICT II | 315 | SR-I | -- | 2016-03-11 | 9:39 | 2016-03-12 | 7:51 | -- | -- | -- |  |  |  | 22.2 | -- | -- | -- | Shutdown availed for isolator rectification works vide SRLDC code CR03/278 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 22.2
89 | SR1T14 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | 2016-03-10 | 10:55 | 2016-03-10 | 13:04 | -- | -- | -- |  |  |  | 2.15 | -- | -- | -- | Shutdown availed by M/s APTRANSCO for attending hotspot in their yard vide SRLDC code: CR03/246 |  | 100
[5 empty] | -- | 2016-03-28 | 9:50 | 2016-03-28 | 19:09 | -- | -- | -- |  |  |  | 9.3167 | N/A | N/A | N/A | H/T For OTI retrofitting vide SRLDC Code:CR-03/667
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.4667
90 | SR1T15 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR1T16 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR1T17 | VIJAYAWADA ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR1T18 | VIJAYAWADA ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR1T19 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR1T20 | WARANGAL ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR1T21 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR1T22 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR1T23 | NELLOREPS ICT - II | 1500 | SR-I | -- | 2016-03-09 | 12:22 | 2016-03-09 | 17:42 | -- | -- | -- | 5.3333 |  |  |  | -- | -- | -- | Shutdown availed for tandelta point rectification works vide SRLDC code CR03/214 |  | 99.2832
[6 empty] | Sub Total --> | [6 empty] | 5.3333 | 0 | 0 | 0
99 | SR1T24 | NELLOREPS ICT - III | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR1T25 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | 2016-03-01 | 12:09 | 2016-03-01 | 17:29 | -- | -- | -- |  |  |  | 5.3333 | -- | -- | -- | Shutdown availed for retunning of CSD vide SRLDC code CR03/14 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.3333
101 | SR1T26 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | 2016-03-02 | 11:11 | 2016-03-02 | 16:30 | -- | -- | -- |  |  |  | 5.32 | -- | -- | -- | Shutdown availed for retunning of CSD vide SRLDC code CR03/34 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.32
102 | SR1R1 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | 2016-03-16 | 9:10 | 2016-03-16 | 19:40 | -- | -- | -- |  |  |  | 10.5 | -- | -- | -- | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR03/396 |  | 100
[5 empty] | -- | 2016-03-17 | 9:58 | 2016-03-17 | 17:40 | -- | -- | -- |  |  |  | 7.7 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR03/396
[5 empty] | -- | 2016-03-18 | 11:53 | 2016-03-18 | 18:53 | -- | -- | -- |  |  |  | 7 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR03/452
[5 empty] | -- | 2016-03-19 | 9:39 | 2016-03-19 | 19:05 | -- | -- | -- |  |  |  | 9.4333 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR03/470
[5 empty] | -- | 2016-03-20 | 9:24 | 2016-03-20 | 17:26 | -- | -- | -- |  |  |  | 8.0333 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR03/488
[5 empty] | -- | 2016-03-21 | 10:29 | 2016-03-21 | 19:20 | -- | -- | -- |  |  |  | 8.85 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR03/47
[5 empty] | -- | 2016-03-22 | 8:18 | 2016-03-22 | 18:07 | -- | -- | -- |  |  |  | 9.8167 | N/A | N/A | N/A | Shutdown availed for construction of firewall under Bay Extension works-SRSS-XX vide SRLDC code CR03/530
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 43.1333
103 | SR1R2 | GOOTY BUS REACTOR | 63 | SR-I | -- | 2016-03-04 | 9:46 | 2016-03-04 | 16:59 | -- | -- | -- |  |  |  | 7.2167 | -- | -- | -- | Shutdown availed for CSD commissioning works vide SRLDC code CR03/72 |  | 100
[5 empty] | -- | 2016-03-28 | 10:36 | 2026-07-29 | 0:00 | -- | -- | -- |  |  |  | 85.4 | N/A | N/A | N/A | H/T Under voltage regulation vide SRLDC Code:CR-03/82
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 92.6167
104 | SR1R3 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | 2016-03-09 | 9:56 | 2016-03-09 | 14:52 | -- | -- | -- |  |  |  | 4.9333 | -- | -- | -- | Shutdown availed for CSD tuning works vide SRLDC code CR03/205 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.9333
105 | SR1R4 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | 2016-03-08 | 11:14 | 2016-03-08 | 18:40 | -- | -- | -- |  |  |  | 7.43 | -- | -- | -- | Shutdown availed for CSD tuning works vide SRLDC code CR03/172 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.43
106 | SR1R5 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR1R6 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2016-03-29 | 9:12 | 2016-03-29 | 16:26 | -- | -- | -- |  |  |  | 7.2333 | -- | -- | -- | H/T For OTI retrofitting vide SRLDC Code:CR-03/706 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.2333
108 | SR1R7 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR1R8 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR1R9 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | 2016-03-02 | 9:46 | 2026-07-29 | 0:00 | -- | -- | -- |  |  |  | 710.2333 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/03 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 710.2333
111 | SR1R10 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR1R11 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | 2016-03-10 | 9:32 | 2016-03-10 | 18:12 | -- | -- | -- | 8.6667 |  |  |  | -- | -- | -- | Shut availed for AMP works vide SRLDC code:CR03/243 |  | 98.8351
[6 empty] | Sub Total --> | [6 empty] | 8.6667 | 0 | 0 | 0
113 | SR1R12 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | 2016-03-08 | 11:57 | 2016-03-08 | 17:48 | -- | -- | -- | 5.85 |  |  |  | -- | -- | -- | Shutdown availed for AMP works vide SRLDC code CR03/175 |  | 99.2137
[6 empty] | Sub Total --> | [6 empty] | 5.85 | 0 | 0 | 0
114 | SR1R13 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR1R14 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR1R15 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | 2016-03-10 | 12:31 | 2016-03-10 | 13:38 | -- | -- | -- |  |  |  | 1.1167 | N/A | N/A | N/A | Blocked due to tripping of Jeypore-Gajuwaka 1&2 lines on overvoltage protection |  | 100
[5 empty] | -- | 2016-03-31 | 15:09 | 2026-07-29 | 0:00 | -- | -- | -- |  |  |  | 8.85 | N/A | N/A | N/A | Tripped due to commutation failure caused by resonance in eastern side AC link
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.9667
118 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | 2016-03-10 | 12:31 | 2016-03-10 | 13:45 | -- | -- | -- |  |  |  | 1.2333 | N/A | N/A | N/A | Blocked due to tripping of Jeypore-Gajuwaka 1&2 lines on overvoltage protection |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.2333
119 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | 2016-03-22 | 8:20 | 2016-03-22 | 9:07 | -- | -- | -- | 0.78333 |  |  |  | N/A | N/A | N/A | VESDA operated at Talcher end and receipt of ESOS at Kolar end |  | 99.8947
[6 empty] | Sub Total --> | [6 empty] | 0.78333 | 0 | 0 | 0
120 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | 2016-03-08 | 5:54 | 2016-03-08 | 9:15 | -- | -- | -- | 3.35 |  |  |  | N/A | N/A | N/A | Blocked on LFL operation. 94.28 KM from Kolar end |  | 99.5497
[6 empty] | Sub Total --> | [6 empty] | 3.35 | 0 | 0 | 0
|  |  | Note in type of failure column please indicate following : | [9 empty] | 54.7 | 1.5333 | 9.4167 | 3491.4633
[16 empty] | 7.1167 |  |  |  | 3498.58
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse