## SOP
Standard of Performance data for the month of November-2015
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date and Time | Date and Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L1 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- | SRPC | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
2 | SR1L2 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
3 | SR1L3 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
4 | SR1L4 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
5 | SR1L5 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | 2015-11-20 00:11 | 2015-11-20 07:23 | -- | -- | -- |  |  |  | 7.2 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/513 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 7.2
6 | SR1L6 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
7 | SR1L7 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
8 | SR1L8 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | 2015-11-26 08:56 | 2015-11-26 19:10 | -- | -- | -- |  |  |  | 10.2333 | N/A | N/A | N/A | Shut down availed for replacement of critical disc insulator strings with CLR insulators vide SRLDC code CR-11/701 |  | 100
[5 empty] | -- | 2015-11-27 08:35 | 2015-11-27 18:32 | -- | -- | -- |  |  |  | 9.95 | N/A | N/A | N/A | Shut down availed for replacement of critical disc insulator strings with CLR insulators vide SRLDC code CR-11/735
[5 empty] | -- | 2015-11-28 08:37 | 2015-11-28 19:30 | -- | -- | -- |  |  |  | 10.8833 | N/A | N/A | N/A | Shutdown availed for replacing the disc insulators with CLR in the critical locations vide SRLDC code no. CR-11/766
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 31.0667
9 | SR1L9 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
10 | SR1L10 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
11 | SR1L11 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
12 | SR1L12 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | 2015-11-20 10:05 | 2015-11-20 16:10 | -- | -- | -- | 6.0833 |  |  |  | N/A | N/A | N/A | Shutdown availed for retrofitting of OTI of L/R at Khammam end vide SRLDC code no. CR-11/525 |  | 99.1823
[6 empty] | Sub Total --> |  |  |  |  | 6.0833 | 0 | 0 | 0
13 | SR1L13 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
14 | SR1L14 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | 2015-11-30 01:17 | 2015-11-30 09:59 | -- | -- | -- |  |  |  | 8.7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/815 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 8.7
15 | SR1L15 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
16 | SR1L16 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | 2015-11-11 00:14 | 2015-11-12 11:46 | -- | -- | -- |  |  |  | 35.5333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/238 |  | 100
[5 empty] | -- | 2015-11-13 23:06 | 2015-12-01 | -- | -- | -- |  |  |  | 408.9 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/322
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 444.4333
17 | SR1L17 | KHAMMAM - N'SAGAR | 144.577 | SR-I | -- | 2015-11-22 23:56 | 2015-11-23 00:32 | -- | -- | -- |  |  | 0.6 |  | N/A | N/A | N/A | Tripped on operation of over voltage protection at NSG end. DT recd at KHM end. |  | 100
[5 empty] | -- | 2015-11-23 00:32 | 2015-11-23 08:19 | -- | -- | -- |  |  |  | 7.7833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltages vide msg No CP-11/657
[5 empty] | -- | 2015-11-30 13:46 | 2015-11-30 17:04 | -- | -- | -- |  |  |  | 3.3 | N/A | N/A | N/A | S/D availed for Construction works vide SRLDC code no. CR-11/829
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0.6 | 11.0833
18 | SR1L18 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
19 | SR1L19 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
20 | SR1L20 | KURNOOL(NEW) - GOOTY | 112.609 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
21 | SR1L21 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
22 | SR1L22 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
23 | SR1L23 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | 2015-11-16 05:09 | 2015-11-16 05:09 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Line A/R successful on B-N transient fault. FLR: 70Km from Raichur SS |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
24 | SR1L24 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | 2015-11-13 12:43 | 2015-11-13 12:43 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Line Auto reclosed successful on B-N fault. FLR: 338.9 Km from GJW. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
25 | SR1L25 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2015-11-25 09:56 | 2015-11-25 16:33 | -- | -- | -- |  |  |  | 6.6167 | N/A | N/A | N/A | S/D availed for retrofitting of OTI for SCADA and AMP works vide SRLDC code no. CR-11/665 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 6.6167
26 | SR1L26 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2015-11-13 23:16 | 25-11-2015 09:42 | -- | -- | -- |  |  |  | 274.4333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/323 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 274.4333
27 | SR1L27 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
28 | SR1L28 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | 2015-11-26 10:40 | 2015-11-26 15:11 | -- | -- | -- |  |  |  | 4.5167 | -- | -- | -- | Shut down availed for retrofitting of OTI for SCADA & AMP works vide SRLDC code CR-11/712 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 4.5167
29 | SR1L29 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | 2015-11-17 22:29 | 2015-11-18 07:50 | -- | -- | -- |  |  |  | 9.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/443 |  | 100
[5 empty] | -- | 2015-11-19 23:01 | 2015-11-20 07:02 | -- | -- | -- |  |  |  | 8.0167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/512
[5 empty] | -- | 2015-11-20 23:08 | 2015-11-21 07:45 | -- | -- | -- |  |  |  | 8.6167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/544
[5 empty] | -- | 2015-11-21 23:46 | 2015-11-22 14:41 | -- | -- | -- |  |  |  | 14.9167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/564
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 40.9
30 | SR1L30 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | 2015-11-23 08:46 | 2015-11-23 19:47 | -- | -- | -- |  |  |  | 11.0167 | N/A | N/A | N/A | Shut Down availed for re-fixing of aviation globes vide SRLDC code no. CR-11/582. |  | 100
[5 empty] | -- | 2015-11-24 07:39 | 2015-11-24 19:41 | -- | -- | -- |  |  |  | 12.0333 | N/A | N/A | N/A | Line Shut Down availed for re-fixing of aviation globes vide SRLDC code no.CR-11/607
[5 empty] | -- | 2015-11-25 07:32 | 2015-11-25 20:11 | -- | -- | -- |  |  |  | 12.65 | N/A | N/A | N/A | Line Shut Down availed for re-fixing of aviation globes vide SRLDC code no.CR-11/652
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 35.7
31 | SR1L31 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
32 | SR1L32 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | 2015-11-23 08:46 | 2015-11-23 19:47 | -- | -- | -- |  |  |  | 11.0167 | N/A | N/A | N/A | Shut Down availed for re-fixing of aviation globes vide SRLDC code no. CR-11/583. |  | 100
[5 empty] | -- | 2015-11-24 07:40 | 2015-11-24 19:40 | -- | -- | -- |  |  |  | 12 | N/A | N/A | N/A | Line Shut Down availed for re-fixing of aviation globes vide SRLDC code no.CR-11/608
[5 empty] | -- | 2015-11-25 07:33 | 2015-11-25 20:12 | -- | -- | -- |  |  |  | 12.65 | N/A | N/A | N/A | Line Shut Down availed for re-fixing of aviation globes vide SRLDC code no.CR-11/653
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 35.6667
33 | SR1L33 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
34 | SR1L34 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
35 | SR1L35 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | 2015-11-10 02:30 | 2015-11-10 02:50 | -- | -- | -- |  |  | 0.33333 |  | N/A | N/A | N/A | Tripped on operation of Over voltage protection at SPDR end, DT received at NLR end. |  | 100
[5 empty] | -- | 2015-11-10 02:50 | 2015-11-11 09:14 | -- | -- | -- |  |  |  | 30.4 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltages vide msg No CPCC-11/276
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0.33333 | 30.4
36 | SR1L36 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
37 | SR1L37 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
|  | ALMATHY - THIRUVALAM II | 40.969 |  | -- | 2015-11-23 23:03 | 2015-12-01 | -- | -- | -- |  |  |  | 168.95 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/603 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 168.95
38 | SR1L38 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | 2015-11-06 16:12 | 2015-11-06 18:02 | -- | -- | -- | 1.8333 |  |  |  | N/A | N/A | N/A | S/D availed for tightening the pilot suspension clamp at loc No: 197 vide SRLDC code no. CR-11/132 |  | 99.7536
[6 empty] | Sub Total --> |  |  |  |  | 1.8333 | 0 | 0 | 0
39 | SR1L39 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
40 | SR1L40 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
41 | SR1L41 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
42 | SR1L42 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
43 | SR1L43 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | 2015-11-12 00:20 | 2015-11-12 01:12 | -- | -- | -- | 0.86667 |  |  |  | N/A | N/A | N/A | Tripped on R-N fault. FLR : 92.87KM from GTY end. |  | 99.8835
[6 empty] | Sub Total --> |  |  |  |  | 0.86667 | 0 | 0 | 0
44 | SR1L44 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | 2015-11-10 15:37 | 2015-11-10 16:36 | -- | -- | -- |  |  | 0.98333 |  | N/A | N/A | N/A | Tripped due to DC earth fault at NLR end.DT received at NPS end |  | 100
[5 empty] | -- | 2015-11-16 17:28 | 2015-11-16 17:48 | -- | -- | -- |  |  | 0.33333 |  | N/A | N/A | N/A | Tripped due to DC earth fault at Nellore end due to heavy rain and water logging in the switch yard
[5 empty] | -- | 2015-11-16 17:52 | 2015-11-17 18:39 | -- | -- | -- |  |  | 24.7833 |  | N/A | N/A | N/A | Tripped due to DC earth fault at Nellore end due to heavy rain and water logging in the switch yard
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 26.1 | 0
45 | SR1L45 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
46 | SR1L46 | MEPL - NELLOREPS | 3.83 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
47 | SR1L47 | SEPL - NELLOREPS | 3.83 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
48 | SR1L48 | GOOTY - NELLOREPS - I | 289.004 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
49 | SR1L49 | GOOTY - NELLOREPS - II | 289.004 | SR-I | -- | 2015-11-11 21:40 | 2015-12-01 | -- | -- | -- |  |  |  | 458.3333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-11/261 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 458.3333
50 | SR1L50 | NELLOREPS - NCC | 32.4881 | SR-I | -- | 2015-11-24 10:30 | 2015-11-24 20:08 | -- | -- | -- |  |  |  | 9.6333 | N/A | N/A | N/A | Shut down availed by M/s TPCIL for attending hotspot on Y-Ph LA at NCC end vide SRLDC code CR-11/617 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 9.6333
51 | SR1L51 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
52 | SR1L52 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
53 | SR1L53 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
54 | SR1L54 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
55 | SR1L55 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
56 | SR1L56 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
57 | SR1L57 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | 2015-11-14 14:04 | 2015-11-14 16:28 | -- | -- | -- | 2.4 |  |  |  | N/A | N/A | N/A | Tripped due to mal-operation of B-phase line reactor PRD at Nellore end |  | 99.5901
[5 empty] | -- | 2015-11-24 12:12 | 2015-11-24 12:51 | -- | -- | -- | 0.65 |  |  |  | N/A | N/A | N/A | Tripped due to mal-operation of L/R PRD at NLR end. DT received at THVLM end.
[6 empty] | Sub Total --> |  |  |  |  | 3.05 | 0 | 0 | 0
58 | SR1L58 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | 2015-11-19 23:04 | 2015-11-19 23:10 | -- | -- | -- |  |  | 0.1 |  | N/A | N/A | N/A | Tripped on O/V protection at TRVLM end. DT recd at NLR. |  | 100
[5 empty] | -- | 2015-11-19 23:10 | 2015-11-20 07:52 | -- | -- | -- |  |  |  | 8.7 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltages vide msg No CPCC-11/572
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0.1 | 8.7
59 | SR1L59 | KURNOOL(NEW) - RAICHUR(NEW) - II | 118.423 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
60 | SR1L60 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
61 | SR1L61 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2015-10-20 12:12 | 2015-12-01 | -- | -- | -- |  |  |  | 720 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-10/712 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 720
62 | SR1L62 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2015-11-02 00:47 | 02-11-2015 01:00 | -- | -- | -- |  |  | 0.21667 |  | N/A | N/A | N/A | Tripped on operation of O/V protection at Thiruvalam end.DT received at KRNL end. |  | 100
[5 empty] | -- | 2015-11-02 01:00 | 19-11-15 12:14 | -- | -- | -- |  |  |  | 419.2333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltages vide msg No CPCC-11/31
[5 empty] | -- | 2015-11-20 02:58 | 2015-11-20 03:05 | -- | -- | -- |  |  | 0.11667 |  | N/A | N/A | N/A | Tripped on operation of over voltage protection at TRVLM end. DT recd at KRNL.
[5 empty] | -- | 2015-11-20 03:05 | 2015-11-20 10:32 | -- | -- | -- |  |  |  | 7.45 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltages vide msg No CPCC-11/574
[5 empty] | -- | 2015-11-21 03:54 | 2015-11-21 04:05 | -- | -- | -- |  |  | 0.18333 |  | N/A | N/A | N/A | Tripped on operation of O/V protection at THVLM end.DT received at KRNL end
[5 empty] | -- | 2015-11-21 04:05 | 2015-11-21 09:03 | -- | -- | -- |  |  |  | 4.9667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltages vide msg No CPCC-11/619
[5 empty] | -- | 2015-11-23 00:01 | 2015-11-23 00:06 | -- | -- | -- |  |  | 0.083333 |  | N/A | N/A | N/A | Tripped on operation of over voltage protection at TRVLM end. DT recd at KRNL end.
[5 empty] | -- | 2015-11-23 00:06 | 2015-11-23 09:54 | -- | -- | -- |  |  |  | 9.8 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltages vide msg No CP-11/656
[5 empty] | -- | 2015-11-24 01:53 | 2015-11-24 01:58 | -- | -- | -- |  |  | 0.083333 |  | N/A | N/A | N/A | Tripped on operation of over voltage protection at TRVLM end. DT recd at KRNL end.
[5 empty] | -- | 2015-11-24 01:58 | 2015-11-24 07:12 | -- | -- | -- |  |  |  | 5.2333 | N/A | N/A | N/A | Line kept open as per SRLDC instruction to contain over voltages vide msg No CP-11/689
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0.68333 | 446.6833
63 | SR1L63 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 19-10-2015 16:02 | 02-11-2015 13:34 | -- | -- | -- |  |  |  | 37.5667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-09/681 |  | 100
[5 empty] | -- | 2015-11-09 02:59 | 2015-11-09 03:05 | -- | -- | -- |  |  | 0.1 |  | N/A | N/A | N/A | Tripped on operation of O/V protection at TRVLM end. DT recd at KRNL end
[5 empty] | -- | 2015-11-09 03:05 | 2015-11-09 10:47 | -- | -- | -- |  |  |  | 7.7 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltages vide msg No CPCC-11/248
[5 empty] | -- | 2015-11-09 21:59 | 2015-11-09 22:05 | -- | -- | -- |  |  | 0.1 |  | N/A | N/A | N/A | Tripped on operation of Over voltage protection at THVLM end, DT received at KRNL end.
[5 empty] | -- | 2015-11-09 22:05 | 2015-11-11 10:22 | -- | -- | -- |  |  |  | 36.2833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltages vide msg No CPCC-11/270
[5 empty] | -- | 2015-11-11 23:58 | 2015-11-12 00:03 | -- | -- | -- |  |  | 0.083333 |  | N/A | N/A | N/A | Tripped on operation of over voltage protection at THVLM end. DT received at KRNL end.
[5 empty] | -- | 2015-11-12 00:03 | 2015-11-12 09:53 | -- | -- | -- |  |  |  | 9.8333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltages vide msg No CPCC-11/312
[5 empty] | -- | 2015-11-15 23:32 | 2015-11-15 23:40 | -- | -- | -- |  |  | 0.13333 |  | N/A | N/A | N/A | Tripped on O/V protection at Thiruvalm end. DT recd at KRNL end.
[5 empty] | -- | 2015-11-15 23:40 | 2015-11-16 09:23 | -- | -- | -- |  |  |  | 9.7167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for contining over voltages vide msg No CP-11/432
[5 empty] | -- | 2015-11-17 01:47 | 2015-11-17 01:55 | -- | -- | -- |  |  | 0.13333 |  | N/A | N/A | N/A | Tripped on operation of O/V protn at TRVLM. DT recd at KRNL
[5 empty] | -- | 2015-11-17 01:55 | 2015-11-17 09:41 | -- | -- | -- |  |  |  | 7.7667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for contining over voltages vide msg No CP-11/470
[5 empty] | -- | 2015-11-19 01:00 | 2015-11-19 01:07 | -- | -- | -- |  |  | 0.11667 |  | N/A | N/A | N/A | Tripped on operation of Over voltage protection at THVLM end. DT received at KRNL end.
[5 empty] | -- | 2015-11-19 01:07 | 2015-12-01 | -- | -- | -- |  |  |  | 286.8833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction for containing over voltages vide msg No CPCC-11/536
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0.66667 | 395.75
64 | SR1L64 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
66 | SR1L65 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
66 | SR1L66 | TPCIL - NCC | 5.168 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
67 | SR1T1 | CUDDAPAH ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
68 | SR1T2 | CUDDAPAH ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
69 | SR1T3 | GAJUWAKA ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
70 | SR1T4 | GAZUWAKA ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
71 | SR1T5 | GOOTY ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
72 | SR1T6 | GOOTY ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
73 | SR1T7 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
74 | SR1T8 | HYDERABAD ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
75 | SR1T9 | HYDERABAD ICT - III | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
76 | SR1T10 | KHAMMAM ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
77 | SR1T11 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
78 | SR1T12 | MUNIRABAD ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
79 | SR1T13 | MUNIRABAD ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
80 | SR1T14 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
81 | SR1T15 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
82 | SR1T16 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
83 | SR1T17 | VIJAYAWADA ICT I | 315 | SR-I | -- | 2015-11-06 11:06 | 2015-11-06 16:43 | -- | -- | -- |  |  |  | 5.6167 | N/A | N/A | N/A | S/D availed by M/s APTRANSCO for attending hotspots in 220KV Nunna-PGCIL line I at APTRANSCO end vide SRLDC code no. CR-11/125 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 5.6167
84 | SR1T18 | VIJAYAWADA ICT II | 315 | SR-I | -- | 2015-11-07 10:58 | 2015-11-07 14:54 | -- | -- | -- |  |  |  | 3.9333 | N/A | N/A | N/A | S/D availed by M/s APTRANSCO for CT tan delta measurement at Nunna S/S vide SRLDC code no. CR-11/155 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 3.9333
85 | SR1T19 | WARANGAL ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
86 | SR1T20 | WARANGAL ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
87 | SR1T21 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
88 | SR1T22 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
89 | SR1T23 | NELLOREPS ICT - II | 1500 | SR-I | -- | 2015-11-14 01:03 | 2015-11-14 02:59 | -- | -- | -- | 1.9333 |  |  |  | N/A | N/A | N/A | Tripped on suspected mal-operation of B-Ph PRD. |  | 99.7401
[6 empty] | Sub Total --> |  |  |  |  | 1.9333 | 0 | 0 | 0
90 | SR1T24 | NELLOREPS ICT - III | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
91 | SR1T25 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | 2015-11-25 10:18 | 2015-11-25 19:56 | -- | -- | -- |  |  |  | 9.6333 | N/A | N/A | N/A | S/D availed for CSD commissioning works vide SRLDC code no. CR-11/668 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 9.6333
92 | SR1T26 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | 2015-11-24 09:50 | 2015-11-24 21:50 | -- | -- | -- |  |  |  | 12 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code CR-11/615 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 12
93 | SR1R1 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
94 | SR1R2 | GOOTY BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
95 | SR1R3 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
96 | SR1R4 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
97 | SR1R5 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
98 | SR1R6 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
99 | SR1R7 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
100 | SR1R8 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
101 | SR1R9 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
102 | SR1R10 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
103 | SR1R11 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
104 | SR1R12 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
105 | SR1R13 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
106 | SR1R14 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
107 | SR1R15 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
108 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
109 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
110 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
111 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
|  |  | Note in type of failure column please indicate following : | [7 empty] | 13.7667 | 0 | 28.4833 | 3169.95
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse