## SOP
Standard of Performance data for the month of MAY -2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2017-05-01 | 0:00 | 2017-05-18 | 10:09 |  |  |  | 0 | 0 | 0 | 418.15 |  |  |  | H/T for voltage regulation vide SRLDC code SR004/703 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 418.15 | [6 empty] | 744
2 | SR1L02 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2017-05-07 | 14:05 | 2017-05-07 | 17:18 |  |  |  | 3.2167 | 0 | 0 | 0 |  |  |  | Tripped on Y-N fault. A/R Unsuccessful at NPS end and A/R Successful at Kurnool end. And immediately O/V protn optd at NPS and DT Send to Kurnool End. (NPS End: 302.20KM, 2.10KA ; KLN End: 3.28KM, 16.6KA) |  | 99.5677 | 744
[6 empty] | 2017-05-18 | 10:25 | 2017-05-25 | 16:21 |  |  |  | 0 | 0 | 0 | 173.9333 |  |  |  | H/T for voltage regulation vide code SR005/872 |  |  | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 3.2167 | 0 | 0 | 173.9333 | [6 empty] | 744
3 | SR1L03 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2017-05-18 | 9:19 | 2017-05-19 | 20:59 |  |  |  | 0 | 0 | 0 | 35.6667 |  |  |  | H/T for voltage regulation vide SRLDC code SR05/866 |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 35.6667 | [6 empty] | 744
4 | SR1L04 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2017-05-01 | 0:00 | 2017-05-02 | 10:59 |  |  |  | 0 | 0 | 0 | 34.9833 |  |  |  | Line kept out for voltage regulation as per SRLDC instructions |  | 99.8723 | 744
[6 empty] | 2017-05-04 | 18:03 | 2017-05-15 | 10:53 |  |  |  | 0 | 0 | 0 | 256.8333 |  |  |  | H/T for voltage regulation vide code SR05/179 |  |  | 744
[6 empty] | 2017-05-19 | 20:03 | 2017-05-19 | 21:00 |  |  |  | 0.95 | 0 | 0 | 0 |  |  |  | Line tripped on RN fault. SR-2 informed that heavy sparking observed in LA at TVLM ss.Later line kept under LVRD |  |  | 744
[6 empty] | 2017-05-19 | 21:00 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 291 |  |  |  | Line kept out of service for voltage regulation as per the instruction from SRLDC |  |  | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0.95 | 0 | 0 | 582.8167 | [6 empty] | 744
5 | SR1L05 | RAICHUR(NEW) - KURNOOL(NEW) - I | 120.482 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
6 | SR1L06 | RAICHUR(NEW) - KURNOOL(NEW) - II | 118.423 | SR-I | -- | 2017-05-25 | 17:37 | 2017-05-25 | 17:37 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Autor reclose successful on Y-N fault Dist:86.89KM FC 3.89KA from KNL . No tripping at RCN end |  | 100 | 744
744
744
744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
7 | SR1L07 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | 2017-05-06 | 16:24 | 2017-05-06 | 17:04 |  |  |  | 0.66667 | 0 | 0 | 0 |  |  |  | Line tripped on B-N fault. Dist 150.4kms, FC-3.5kA from RCN and Dist:61kms, FC-6.25 kA from SLPR end. |  | 99.9104 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0.66667 | 0 | 0 | 0 | [6 empty] | 744
8 | SR1L08 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
9 | SR1L09 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
10 | SR1L10 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[5 empty] | -- | [11 empty] | N/A | N/A | N/A |  |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
11 | SR1L11 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
12 | SR1L12 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | [5 empty] | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
13 | SR1L13 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
14 | SR1L14 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
15 | SR1L15 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
16 | SR1L16 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | 2017-05-19 | 2:30 | 2017-05-22 | 9:03 |  |  |  | 0 | 0 | 0 | 78.55 |  |  |  | H/T for voltage regulation videSRLDC code SR416 |  | 100 | 744
[6 empty] | 2017-05-27 | 1:29 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 118.5167 |  |  |  | H/T for voltage regulation vide SR 1290 |  |  | 744
744
744
744
744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 197.0667 | [6 empty] | 744
17 | SR1L17 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | [16 empty] | 100 | 744
744
744
744
744
744
744
744
744
744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
18 | SR1L18 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | 2017-05-01 | 0:00 | 2017-05-02 | 15:11 |  |  |  | 0 | 0 | 0 | 39.1833 |  |  |  | Line kept out for voltage regulation as per SRLDC instructions |  | 100 | 744
[5 empty] | -- | 2017-05-02 | 18:01 | 2017-05-02 | 18:05 |  |  |  | 0 | 0 | 0.066667 | 0 |  |  |  | Line tripped on O/V prot stg-1 at KNL end & DT recvd at HYD end. |  |  | 744
[6 empty] | 2017-05-02 | 18:05 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 701.9167 |  |  |  | Line kept out for voltage regulation as per SRLDC instructions |  |  | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.066667 | 741.1 | [6 empty] | 744
19 | SR1L19 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | 2017-05-16 | 9:13 | 2017-05-16 | 21:35 |  |  |  | 0 | 0 | 0 | 12.3667 |  |  |  | For CVT replacement works under add-cap at NSR and Hyderabad |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.3667 | [6 empty] | 744
20 | SR1L20 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | 2017-05-04 | 7:54 | 2017-05-04 | 19:41 |  |  |  | 0 | 0 | 0 | 11.7833 |  |  |  | S/D availed for RTV coating works at GWK |  | 99.7872 | 744
[6 empty] | 2017-05-05 | 7:18 | 2017-05-05 | 19:12 |  |  |  | 0 | 0 | 0 | 11.9 |  |  |  | S/D availed for RTV coating works at GWK |  |  | 744
[6 empty] | 2017-05-06 | 17:01 | 2017-05-06 | 17:01 |  |  |  | -6.2086e-11 | 0 | 0 | 0 |  |  |  | Auto reclose successful at both ends on R-N fault. Dist 114.5kms, FC-1.674kA from GWK end. |  |  | 744
[6 empty] | 2017-05-06 | 17:12 | 2017-05-06 | 17:38 |  |  |  | 0.43333 | 0 | 0 | 0 |  |  |  | Tripped due to receipt of DT from Jeypore end. Line was holding from Jeypore end. |  |  | 744
[6 empty] | 2017-05-06 | 17:58 | 2017-05-06 | 19:07 |  |  |  | 1.15 | 0 | 0 | 0 |  |  |  | Line tripped on B-N fault & week infeed prot optd at GWK. Dist 26kms, FC-3.6kA from GWK end. A/R successful at Jeypore & Line was holding from Jeypore end. |  |  | 744
[6 empty] | 2017-05-06 | 20:06 | 2017-05-06 | 20:10 |  |  |  | 0 | 0 | 0.066667 | 0 |  |  |  | Tripped due to receipt of DT from Jeypore end. O/V prot optd at Jeypore end. |  |  | 744
[6 empty] | 2017-05-06 | 20:10 | 2017-05-06 | 21:48 |  |  |  | 0 | 0 | 0 | 1.6333 |  |  |  | Tripped due to receipt of DT from Jeypore end. O/V prot optd at Jeypore end. |  |  | 744
[6 empty] | 2017-05-08 | 13:35 | 2017-05-08 | 13:35 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Auto reclose successful at both ends on B-N fault. Dist 154kms, FC-0.5kA from GWK end. Dist:43.8 kms, FC:3.22kA from Jeypore end. |  |  | 744
[6 empty] | 2017-05-08 | 14:42 | 2017-05-08 | 14:42 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Auto reclose successful at both ends on B-N fault. Dist 166.20kms, FC-0.73kA from GWK end. Dist:14.33kms, FC:3.53kA from Jeypore end. |  |  | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 1.5833 | 0 | 0.066667 | 25.3167 | [6 empty] | 744
21 | SR1L21 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | 2017-05-06 | 7:27 | 2017-05-06 | 22:19 |  |  |  | 0 | 0 | 0 | 14.8667 |  |  |  | S/D availed for RTV coating works at GWK |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 14.8667 | [6 empty] | 744
22 | SR1L22 | KADAPA - NPKUNTA | 9.512 | SR-I | -- | 2017-05-16 | 11:52 | 2017-05-16 | 15:54 |  |  |  | 0 | 0 | 0 | 4.0333 |  |  |  | For mounting of POD sensor and doing the wiring - STATCOM construction works |  | 100 | 744
[6 empty] | 2017-05-25 | 11:03 | 2017-05-25 | 11:59 |  |  |  | 0 | 0 | 0 | 0.93333 |  |  |  | H/T for construction Works - STATCOM analysis |  |  | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.9667 | [6 empty] | 744
23 | SR1L23 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
24 | SR1L24 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
25 | SR1L25 | KURNOOL(PG) - GOOTY | 112.609 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
26 | SR1L26 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | 2017-05-24 | 11:51 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 180.15 |  |  |  | H/T on request of APTRANSCO vide code SR1157 |  | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 180.15 | [6 empty] | 744
27 | SR1L27 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | 2017-05-31 | 17:44 | 2017-05-31 | 19:26 |  |  |  | 0 | 1.7 | 0 | 0 |  |  |  | line tripped on operation of Z3 due to uncleared fault in APTRANSCO system |  | 100 | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.7 | 0 | 0 | [6 empty] | 744
28 | SR1L28 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | 2017-05-31 | 17:44 | 2017-05-31 | 19:38 |  |  |  | 0 | 1.9 | 0 | 0 |  |  |  | line tripped on operation of Z3 due to uncleared fault in APTRANSCO system |  | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.9 | 0 | 0 | [6 empty] | 744
29 | SR1L29 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
30 | SR1L30 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | [16 empty] | 100 | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
31 | SR1L31 | NELLOREPS - GOOTY - I | 289.004 | SR-I | -- | 2017-05-07 | 16:16 | 2017-05-07 | 16:16 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R Successful both ends on B-N fault. (GTY End: 190.88KM, 2.02KA ; NPS End: 93.77KM, 4.23KA) |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
32 | SR1L32 | NELLOREPS - GOOTY - II | 289.004 | SR-I | -- | 2017-05-07 | 13:40 | 2017-05-07 | 13:40 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R Successful both ends on Y-N fault. (Gooty End: Dist: 289KM, FC: 1.51KA) |  | 100 | 744
744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
33 | SR1L33 | NELLOREPS - MEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
34 | SR1L34 | NELLOREPS - SEPL | 3.83 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
35 | SR1L35 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | 2017-05-15 | 9:28 | 2017-05-15 | 19:07 |  |  |  | 9.65 | 0 | 0 | 0 |  |  |  | For A/R scheme checking at NPS end. Vide SR05/691 |  | 98.703 | 744
[6 empty] | Sub Total --> | [6 empty] | 9.65 | 0 | 0 | 0 | [6 empty] | 744
36 | SR1L36 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | 2017-05-16 | 9:34 | 2017-05-16 | 19:23 |  |  |  | 9.8167 | 0 | 0 | 0 |  |  |  | For A/R scheme checking at NPS end. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
37 | SR1L37 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
38 | SR1L38 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
39 | SR1L39 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | 2017-05-07 | 14:38 | 2017-05-07 | 14:38 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | A/R Successful both ends on B-N fault. (NLR End: 27.29KM, 10.76KA ; SPDR End: 174.70KM, 1.93KA) |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
40 | SR1L40 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | [16 empty] | 100 | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
41 | SR1L41 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
42 | SR1L42 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
43 | SR1L43 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | [16 empty] | 100 | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
44 | SR1L44 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
45 | SR1L45 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
46 | SR1L46 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
47 | SR1L47 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
48 | SR1L48 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | [16 empty] | 100 | 744
744
744
744
744
744
744
744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
49 | SR1L49 | NPKUNTA - KOLAR | 9.512 | SR-I | -- | 2017-05-16 | 16:39 | 2017-05-16 | 18:07 |  |  |  | 0 | 0 | 0 | 1.4667 |  |  |  | H/T for STATCOM Construction works vide code SR765 |  | 100 | 744
[6 empty] | 2017-05-26 | 18:56 | 2017-05-26 | 19:27 |  |  |  | 0 | 0 | 0 | 0.51667 |  |  |  | H/T for STATCOM analysis vide code 1279 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.9833 | [6 empty] | 744
50 | SR1L50 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | 2017-05-25 | 9:42 | 2017-05-25 | 18:36 |  |  |  | 8.9 | 0 | 0 | 0 |  |  |  | H/T for LR oil leakage arresting at MBD and line works |  | 98.8038 | 744
[6 empty] | Sub Total --> | [6 empty] | 8.9 | 0 | 0 | 0 | [6 empty] | 744
51 | SR1L51 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
52 | SR1L52 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
53 | SR1L53 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | 2017-05-17 | 16:45 | 2017-05-17 | 17:49 |  |  |  | 1.0667 | 0 | 0 | 0 |  |  |  | H/T for taking the L/R into service at Chandrapur end. Vide SR05/828 |  | 99.8566 | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 1.0667 | 0 | 0 | 0 | [6 empty] | 744
54 | SR1L54 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | 2017-05-28 | 7:52 | 2017-05-28 | 20:05 |  |  |  | 0 | 0 | 0 | 12.2167 |  |  |  | H/T for insulator replacement works at Railway & Road Crossing vide code SR-1315,NL-1462 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.2167 | [6 empty] | 744
55 | SR1L55 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | 2017-05-29 | 0:07 | 2017-05-29 | 0:12 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | line tripped on operation of OV at Gajwel end. DT received at Hyderabad |  | 100 | 744
[6 empty] | 2017-05-29 | 0:12 | 2017-05-29 | 15:54 |  |  |  | 0 | 0 | 0 | 15.7 |  |  |  | Line kept out of service for voltage regulation |  |  | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 15.7 | [6 empty] | 744
56 | SR1L56 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | 2017-05-23 | 9:24 | 2017-05-23 | 11:51 |  |  |  | 0 | 0 | 0 | 2.45 |  |  |  | H/T for PMU installation works by NTPC vide SR05/1089 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.45 | [6 empty] | 744
57 | SR1L57 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I |  | 2017-05-23 | 15:40 | 2017-05-23 | 18:47 |  |  |  | 0 | 0 | 0 | 3.1167 |  |  |  | H/T for PMU installation works by NTPC vide SR05/1117 |  | 100 | 744
[6 empty] | 2017-05-28 | 8:27 | 2017-05-28 | 20:03 |  |  |  | 0 | 0 | 0 | 11.6 |  |  |  | H/T for replacement of line insulators with polymer insulator vide SR-1316 |  |  | 744
744
744
744
744
744
744
744
744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 14.7167 | [6 empty] | 744
58 | SR1L58 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | 2017-05-01 | 1:48 | 2017-05-01 | 3:42 |  |  |  | 0 | 0 | 0 | 1.9 |  |  |  | SD availed by NTPC RDM vide SRLDC Code SR1200 |  | 100 | 744
[6 empty] | 2017-05-09 | 23:38 | 2017-05-09 | 23:45 |  |  |  | 0 | 0 | 0.11667 | 0 |  |  |  | line tripped due to over voltage
[6 empty] | 2017-05-09 | 23:45 | 2017-05-10 | 5:52 |  |  |  | 0 | 0 | 0 | 6.1167 |  |  |  | Line kept out of service for voltage regulation as per the instruction from SRLDC
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.11667 | 8.0167 | [6 empty] | 744
59 | SR1L59 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
60 | SR1L60 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | 2017-05-24 | 9:47 | 2017-05-24 | 11:46 |  |  |  | 0 | 0 | 0 | 1.9833 |  |  |  | H/T for PMU installation works at NTPC vide code SR1151 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.9833 | [6 empty] | 744
61 | SR1L61 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | 2017-05-18 | 12:58 | 2017-05-18 | 12:58 |  |  |  | 7.7618e-12 | 0 | 0 | 0 |  |  |  | A/R successfully operated both ends on B-N fault. (WGL End: 70KM, 4.56KA ; RDM End: 21.11KM, 11.6KA) |  | 100 | 744
744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 7.7618e-12 | 0 | 0 | 0 | [6 empty] | 744
62 | SR1L62 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | 2017-05-15 | 13:12 | 2017-05-16 | 19:27 |  |  |  | 0 | 0 | 0 | 30.25 |  |  |  | For dismantling of LR at GWK end for shifting to Vemagiri GIS |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 30.25 | [6 empty] | 744
63 | SR1L63 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | 2017-05-01 | 10:08 | 2017-05-01 | 18:09 |  |  |  | 0 | 0 | 0 | 8.0167 |  |  |  | S/D availed by M/s NTPC vide SRLDC code SR05/13 |  | 100 | 744
[6 empty] | 2017-05-17 | 9:30 | 2017-05-18 | 19:08 |  |  |  | 0 | 0 | 0 | 33.6333 |  |  |  | Dismantling of Line Reactor at Gajuwaka for shifting and commissioning the same at Vemagiri GIS for installation at Vemagiri PG. Vide code SR/803
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 41.65 | [6 empty] | 744
64 | SR1L64 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
65 | SR1L65 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
66 | SR1L66 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
67 | SR1L67 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2017-05-21 | 16:08 | 2017-05-21 | 22:26 |  |  |  | 0 | 0 | 6.3 | 0 |  |  |  | Line tripped due to NLR-1 L/R isolator arm broken and fallen down on heavy wind at Vjayawada |  | 98.9833 | 744
[6 empty] | 2017-05-26 | 11:09 | 2017-05-26 | 18:39 |  |  |  | 7.5 | 0 | 0 | 0 |  |  |  | H/T for replacement of Y-Ph supporting insulator
[6 empty] | Sub Total --> | [6 empty] | 7.5 | 0 | 6.3 | 0 | [6 empty] | 744
68 | SR1L68 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2017-05-21 | 16:08 | 2017-05-22 | 17:09 |  |  |  | 0 | 0 | 25.0167 | 0 |  |  |  | Line tripped due to insulator stack of line isolator broken due to heavy wind at Vjayawada |  | 98.0157 | 744
[6 empty] | 2017-05-23 | 19:13 | 2017-05-24 | 9:29 |  |  |  | 14.2667 | 0 | 0 | 0 |  |  |  | Tripped on R-N fault.Fault current.8kA Fault Dist.28kM from VJA. Top phase decapped at Loc no:94. |  |  | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 14.2667 | 0 | 25.0167 | 0 | [6 empty] | 744
69 | SR1L69 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | 2017-05-20 | 10:21 | 2017-05-20 | 20:26 |  |  |  | 0 | 0 | 0 | 10.0833 |  |  |  | Line H/T for APTRASCO OPGW works as requested by AP TRANSCO vide SR05/973. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.0833 | [6 empty] | 744
70 | SR1L70 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2017-05-23 | 7:21 | 2017-05-23 | 19:17 |  |  |  | 0 | 0 | 0 | 11.9333 |  |  |  | S/D availed for replacement of insulator with CLS Polymer insulators vide SR05/1082 |  | 100 | 744
[6 empty] | 2017-05-28 | 5:03 | 2017-05-28 | 20:33 |  |  |  | 0 | 0 | 0 | 15.5 |  |  |  | H/T for replacement of line insulators with polymer insulator |  |  | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.4333 | [6 empty] | 744
71 | SR1L71 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | 2017-05-21 | 17:43 | 2017-05-22 | 20:35 |  |  |  | 0 | 0 | 26.8667 | 0 |  |  |  | H/T on emergency basis for replacedmernt of failed Y-Phase LA |  | 100 | 744
[6 empty] | 2017-05-23 | 17:11 | 2017-05-24 | 3:53 |  |  |  | 0 | 0 | 10.7 | 0 |  |  |  | H/T on emergency for attending broken R-ph LA
[6 empty] | 2017-05-25 | 7:37 | 2017-05-25 | 19:57 |  |  |  | 0 | 0 | 0 | 12.3333 |  |  |  | H/T for replacement of line insulators with polymer insulator
[6 empty] | 2017-05-26 | 7:05 | 2017-05-26 | 20:14 |  |  |  | 0 | 0 | 0 | 13.15 |  |  |  | H/T for replacement of line insulators with polymer insulator
[6 empty] | 2017-05-27 | 7:01 | 2017-05-27 | 20:43 |  |  |  | 0 | 0 | 0 | 13.7 |  |  |  | H/T for replacement of line insulators with polymer insulator
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 37.5667 | 39.1833 | [6 empty] | 744
72 | SR1L72 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | 2017-05-07 | 14:58 | 2017-05-07 | 14:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R Successful both ends on Y-N fault. (VTPS End: 229.0KM, 0.684KA ) 7 Dist: 25.18 Kms from manubolu end. |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
73 | SR1L73 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
74 | SR1L74 | VEMAGIRI(PG) - GAZUWAKA | 165.454 | SR-I |  | 2017-05-01 | 13:23 | 2017-05-01 | 16:46 |  |  |  | 0 | 0 | 0 | 3.3833 |  |  |  | Shutdown availed for Cold line water washing works of Line terminal equipment due to heavy tracing vide SRLDC code SR05/21 |  | 99.8477 | 744
[6 empty] | 2017-05-04 | 7:42 | 2017-05-04 | 20:25 |  |  |  | 0 | 0 | 0 | 12.7167 |  |  |  | H/T for power regulation vide SRLDC Code |  |  | 744
[6 empty] | 2017-05-05 | 7:02 | 2017-05-05 | 19:27 |  |  |  | 0 | 0 | 0 | 12.4167 |  |  |  | H/T for power regulation vide SRLDC Code |  |  | 744
[6 empty] | 2017-05-06 | 7:06 | 2017-05-06 | 23:36 |  |  |  | 0 | 0 | 0 | 16.5 |  |  |  | H/T for power regulation vide SRLDC Code |  |  | 744
[6 empty] | 2017-05-14 | 16:54 | 2017-05-14 | 18:02 |  |  |  | 1.1333 | 0 | 0 | 0 |  |  |  | Tripped on Y-N fault. FL=99% from GWK end and 15.26KM from VMG end. FC=2.7KA at GWK end and 4.7KA at VMG PG end. |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 1.1333 | 0 | 0 | 45.0167 | [6 empty] | 744
75 | SR1L75 | VIJAYAWADA - VEMAGIRI(PG) | 187.8 | SR-I |  | 2017-05-01 | 0:00 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 744 |  |  |  | H/T for Power regulation vide SRLDC code SR02/721 |  | 100 | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744 | [6 empty] | 744
75 | SR1L76 | MAHESHWARAM-KURNOOL AP | 174.996 | SR-I | [17 empty] | 100 | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L77 | NiZAMABAD-DICHPALLY 2 | 4.428 | SR-I |  | 2017-05-14 | 8:51 | 2017-05-14 | 19:36 |  |  |  | 0 | 0 | 0 | 10.75 |  |  |  | S/D availed by MTL for striging of 400kV NZB-Shankarpalli lines at NZB Gantry vide RS05/641 |  | 99.6864 | 744
[6 empty] | 2017-05-24 | 8:54 | 2017-05-24 | 11:14 |  |  |  | 2.3333 | 0 | 0 | 0 |  |  |  | H/T for replacement of LA vide code SR1146 |  |  | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 2.3333 | 0 | 0 | 10.75 | [6 empty] | 744
75 | SR1L78 | NIZAMABAD-MAHESHWARAM 1 | 243.059 | SR-I | [17 empty] | 100 | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L79 | NIZAMABAD-MAHESHWARAM 2 | 243.059 | SR-I | [17 empty] | 100 | 744
744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L80 | NIZAMABAD-WARDHA 1 | 291.2 | SR-I |  | 2017-05-07 | 18:01 | 2017-05-07 | 18:05 |  |  |  | 0 | 0 | 0.066667 | 0 |  |  |  | Line tripped on operation of OV at Nizamabad end. |  | 97.9924 | 744
[6 empty] | 2017-05-07 | 18:05 | 2017-05-08 | 6:21 |  |  |  | 0 | 0 | 0 | 12.2667 |  |  |  | Line kept out of service for voltage regulation |  |  | 744
[6 empty] | 2017-05-14 | 10:10 | 2017-05-15 | 1:05 |  |  |  | 14.9167 | 0 | 0 | 0 |  |  |  | S/D availed for replacement of broken insulator at Loc 384 vide RS05/645 |  |  | 744
[6 empty] | 2017-05-25 | 18:00 | 2017-05-25 | 18:56 |  |  |  | 0 | 0 | 0.93333 | 0 |  |  |  | Tripped on DT receipt from Wardha end. O/V prot optd at Wardha end. |  |  | 744
[6 empty] | 2017-05-27 | 18:22 | 2017-05-27 | 18:22 |  |  |  | -2.7165e-11 | 0 | 0 | 0 |  |  |  | A/R succesfull on R-N fault.Fault current.1.5kA Fault Dist.195kM from NZB. FC: 7.23kA, Distane:96.2 kms from Wardha end. |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 14.9167 | 0 | 1 | 12.2667 | [6 empty] | 744
75 | SR1L81 | NIZAMABAD-WARDHA 2 | 291.2 | SR-I |  | 2017-05-27 | 17:47 | 2017-05-27 | 19:09 |  |  |  | 1.3667 | 0 | 0 | 0 |  |  |  | Tripped on Y-N fault.Fault current.2kA Fault Dist.175kM from NZB. FC: 8.1kA, Distane:72 kms from Wardha end. |  | 99.7312 | 744
[6 empty] | 2017-05-28 | 20:19 | 2017-05-28 | 20:57 |  |  |  | 0.63333 | 0 | 0 | 0 |  |  |  | Line Tripped on R-N Fault. Distance-153 Km,FC-2.65 KA from Nizamabad end; Distance:123 Km,FC-6 KA from wardha end |  |  | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 2 | 0 | 0 | 0 | [6 empty] | 744
744
744
744
744
75 | SR1L83 | VIJAYAWADA-VEMAGIRI PG | 187.8 | SR-I | [17 empty] | 100 | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L84 | KADAPA- CHITTOOR |  | SR-I | [17 empty] | 100 | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L77 | NiZAMABAD-DICHPALLY1 | 4.428 | SR-I |  | 2017-05-07 | 18:02 | 2017-05-07 | 18:07 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on operation of OV at Nizamabad end. |  | 100 | 744
[6 empty] | 2017-05-07 | 18:02 | 2017-05-07 | 19:27 |  |  |  | 0 | 0 | 0 | 1.4167 |  |  |  | Line kept out of service for voltage regulation |  |  | 744
[6 empty] | 2017-05-14 | 8:35 | 2017-05-14 | 19:34 |  |  |  | 0 | 0 | 0 | 10.9833 |  |  |  | S/D availed by MTL for striging of 400kV NZB-Shankarpalli lines at NZB Gantry vide RS05/640 |  |  | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 12.4 | [6 empty] | 744
76 | SR1T01 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
77 | SR1T02 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
78 | SR1T03 | NELLOREPS ICT - II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
79 | SR1T04 | NELLOREPS ICT - III | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
80 | SR1T05 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | 2017-05-19 | 7:23 | 2017-05-19 | 19:48 |  |  |  | 0 | 0 | 0 | 12.4167 |  |  |  | H/T for RTV Coating works vide code SRLDC SR 921 |  | 99.888 | 744
[6 empty] | 2017-05-25 | 17:37 | 2017-05-25 | 18:27 |  |  |  | 0.83333 | 0 | 0 | 0 |  |  |  | Tripped due to differential protection mal operation
[6 empty] | Sub Total --> | [6 empty] | 0.83333 | 0 | 0 | 12.4167 | [6 empty] | 744
81 | SR1T06 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | 2017-05-20 | 7:31 | 2017-05-20 | 18:45 |  |  |  | 0 | 0 | 0 | 11.2333 |  |  |  | H/T for RTV Coating works vide SRLDC code SR 969 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.2333 | [6 empty] | 744
82 | SR1T07 | CUDDAPAH ICT I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
83 | SR1T08 | CUDDAPAH ICT II | 315 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
84 | SR1T09 | GAJUWAKA ICT I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
85 | SR1T10 | GAZUWAKA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
86 | SR1T11 | GOOTY ICT I | 315 | SR-I | -- | 2017-05-09 | 12:19 | 2017-05-09 | 16:44 |  |  |  | 0 | 0 | 0 | 4.4167 |  |  |  | S/D availed fby AP TRANSCO to attend 220kV side works |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.4167 | [6 empty] | 744
87 | SR1T12 | GOOTY ICT II | 315 | SR-I | -- | 2017-05-18 | 10:40 | 2017-05-18 | 15:25 |  |  |  | 0 | 0 | 0 | 4.75 |  |  |  | S/D availed by AP TRANSCO to attend 220kV side works vide SR05/874 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.75 | [6 empty] | 744
88 | SR1T13 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
89 | SR1T14 | HYDERABAD ICT - II | 315 | SR-I | -- | 2017-05-01 | 0:00 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 744 |  |  |  | H/T for power regulation vide SRLDC code SR02/811 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744 | [6 empty] | 744
90 | SR1T15 | HYDERABAD ICT - III | 315 | SR-I | -- |  |  |  |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
90 | SR1T15 | HYDERABAD ICT - IV | 500 | SR-I | -- | 2017-05-10 | 2:40 | 2017-05-10 | 6:23 |  |  |  | 0 | 3.7167 | 0 | 0 |  |  |  | Tripped due to operation of 220kV Bus Bar protection at TSTRANSCO's 220KV SS |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 3.7167 | 0 | 0 | [6 empty] | 744
91 | SR1T16 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
92 | SR1T17 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
93 | SR1T18 | MUNIRABAD ICT I | 315 | SR-I | -- | 2017-05-03 | 9:28 | 2017-05-03 | 20:48 |  |  |  | 11.3333 | 0 | 0 | 0 |  |  |  | H/T for attending Oil Leakages |  | 98.4767 | 744
[6 empty] | Sub Total --> | [6 empty] | 11.3333 | 0 | 0 | 0 | [6 empty] | 744
94 | SR1T19 | MUNIRABAD ICT II | 315 | SR-I | -- | 2017-05-04 | 9:31 | 2017-05-04 | 20:06 |  |  |  | 0 | 0 | 0 | 10.5833 |  |  |  | H/T for providing HT Tape insulation for tertiary bushing terminals. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.5833 | [6 empty] | 744
95 | SR1T20 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
96 | SR1T21 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | 2017-05-16 | 9:01 | 2017-05-16 | 11:08 |  |  |  | 0 | 0 | 0 | 2.1167 |  |  |  | S/D availed by AP TRANSCO vide RS05/740 |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.1167 | [6 empty] | 744
97 | SR1T22 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
98 | SR1T23 | NPKUNTA ICT - I | 500 | SR-I | -- | 2017-05-23 | 10:52 | 2017-05-23 | 12:24 |  |  |  | 0 | 0 | 0 | 1.5333 |  |  |  | H/T for construction Works - STATCOM analysis |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.5333 | [6 empty] | 744
99 | SR1T24 | NPKUNTA ICT - II | 500 | SR-I | -- | 2017-05-23 | 12:46 | 2017-05-23 | 14:36 |  |  |  | 0 | 0 | 0 | 1.8333 |  |  |  | H/T for construction Works - STATCOM analysis |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.8333 | [6 empty] | 744
100 | SR1T25 | NPKUNTA ICT - III | 500 | SR-I | -- | 2017-05-23 | 15:35 | 2017-05-23 | 16:46 |  |  |  | 0 | 0 | 0 | 1.1833 |  |  |  | H/T for construction Works - STATCOM analysis |  | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.1833 | [6 empty] | 744
101 | SR1T26 | VIJAYAWADA ICT I | 315 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
102 | SR1T27 | VIJAYAWADA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
103 | SR1T28 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
104 | SR1T29 | WARANGAL ICT II | 315 | SR-I | -- | 2017-05-11 | 9:51 | 2017-05-11 | 12:11 |  |  |  | 0 | 0 | 0 | 2.3333 |  |  |  | H/T for construction works of ICT-3 vide SR05/544 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.3333 | [6 empty] | 744
104 | SR1T30 | VEMAGIRI ICT I | 1500 | SR-I | -- | 2017-05-25 | 8:57 | 2017-05-25 | 20:35 |  |  |  | 0 | 0 | 0 | 11.6333 |  |  |  | H/T for CSD installation works |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.6333 | [6 empty] | 744
104 | SR1T31 | VEMAGIRI ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
104 | SR1T32 | NIZAMABAD ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
104 | SR1T33 | NIZAMABAD ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
104 | SR1T34 | MAHESHWRAM ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
104 | SR1T35 | MAHESHWARAM ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
105 | SR1T36 | HYDERABAD ICT IV | 1500 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
105 | SR1R01 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
106 | SR1R02 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | 2017-05-19 | 8:31 | 2017-05-19 | 18:26 |  |  |  | 0 | 0 | 0 | 9.9167 |  |  |  | H/T for RTV Coating works vide SRLDC code SR 927 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.9167 | [6 empty] | 744
107 | SR1R03 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | 2017-05-16 | 7:13 | 2017-05-16 | 17:18 |  |  |  | 0 | 0 | 0 | 10.0833 |  |  |  | S/D availed for RTV coating vide RS05/736 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.0833 | [6 empty] | 744
108 | SR1R04 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | [5 empty] | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
109 | SR1R05 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
110 | SR1R06 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | 2017-05-02 | 10:13 | 2017-05-07 | 21:14 |  |  |  | 0 | 0 | 0 | 131.0167 |  |  |  | H/T for Voltage regulation vide SRLDC Code SR47 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 131.0167 | [6 empty] | 744
111 | SR1R07 | GOOTY BUS REACTOR | 63 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
112 | SR1R08 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
113 | SR1R09 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
114 | SR1R10 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
115 | SR1R11 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | 2017-05-01 | 0:00 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 744 |  |  |  | H/T for Voltage regulation vide SRLDC code SR03/282 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744 | [6 empty] | 744
116 | SR1R12 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
117 | SR1R13 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1R14 | NPKUNTA BUS REACTOR | 125 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
119 | SR1R15 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
120 | SR1R16 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2017-05-01 | 0:00 | 2017-06-01 | 0:00 |  |  |  | 0 | 0 | 0 | 744 |  |  |  | BR kept out of service for voltage regulation vide SRLDC code SR02/44 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744 | [6 empty] | 744
121 | SR1R17 | 765 KV Srikakulam-Vemagiri 2 LR | 240 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
122 | SR1R18 | 765 KV Srikakulam-Vemagiri 1 LR | 240 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R19 | 330MVAR Bus Reactor at SKLM | 330 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R20 | VEMAGIRI 240MVAR BUS REACTOR-I | 240 | SR-I | -- | 2017-05-30 | 10:27 | 2017-05-30 | 19:35 |  |  |  | 0 | 0 | 0 | 9.1333 |  |  |  | H/T for CSD Commissioning works |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.1333 | [6 empty] | 744
123 | SR1R21 | VEMAGIRI 240MVAR BUS REACTOR-II | 240 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R22 | VEMAGIRI 80MVAR BUS REACTOR | 80 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R23 | MAHESHWARAM BUS REACTOR 1 | 240 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R24 | POLE-2 EAST REACTOR | 125 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
124 | SR1R25 | VIJAYWADA BUS REACTOR 3 | 125 | SR-I | -- | 2017-05-21 | 16:08 | 2017-05-21 | 18:30 |  |  |  | 2.3667 | 0 | 0 | 0 |  |  |  | Tripped due to Backup impedence protn. operated. |  | 99.6819 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 2.3667 | 0 | 0 | 0 | [6 empty] | 744
124 | SR1R26 | NAGARJUNA SAGAR BUS REACTOR II | 125 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
124 | SR1R26 | Gooty Bus REACTOR II | 125 | SR-I | -- | 2017-05-02 | 9:52 | 2017-05-07 | 18:38 |  |  |  | 0 | 0 | 0 | 128.7667 |  |  |  | H/T for Voltage regulation videSRLDC Code SR46 |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 128.7667 | [6 empty] | 744
125 | SR1R26 | Nizamabad Bus Reactor | 125 | SR-I | -- | 2017-05-14 | 13:49 | 2017-05-14 | 16:26 |  |  |  | 2.6167 | 0 | 0 | 0 |  |  |  | S/D availed for NCT oil leakage arresting works vide RS05/648 |  | 99.6483 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 2.6167 | 0 | 0 | 0 | [6 empty] | 744
124 | SR1R27 | WARDHA 1 LR AT NIZAMABAD | 240 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
124 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | 2017-05-06 | 7:37 | 2017-05-07 | 8:39 |  |  |  | 25.0333 | 0 | 0 | 0 |  |  |  | Tripped on GPSU exceeded (Thyrister redundancy fail) alarm |  | 94.5363 | 744
[6 empty] | 2017-05-14 | 0:37 | 2017-05-14 | 5:49 |  |  |  | 5.2 | 0 | 0 | 0 |  |  |  | Tripped due to South side VBE Power supply card failure
[6 empty] | 2017-05-18 | 19:32 | 2017-05-19 | 5:18 |  |  |  | 9.7667 | 0 | 0 | 0 |  |  |  | Tripped due to South side Thyrister redundacy failure
[6 empty] | 2017-05-25 | 9:45 | 2017-05-25 | 10:24 |  |  |  | 0.65 | 0 | 0 | 0 |  |  |  | Tripped due to South filter inter zone prot operation
744
[6 empty] | Sub Total --> | [6 empty] | 40.65 | 0 | 0 | 0 | [6 empty] | 744
125 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | 2017-05-06 | 17:12 | 2017-05-06 | 22:02 |  |  |  | 0 | 0 | 4.8333 | 0 |  |  |  | Blocked due to loss of load upon tripping of Jeypore-GWK-1 line on receipt of DT from Jeypore end & Jeypore-GWK-2 under S/D. |  | 100 | 744
[6 empty] | 2017-05-25 | 9:45 | 2017-05-25 | 10:32 |  |  |  | 0.78333 | 0 | 0 | 0 |  |  |  | Tripped due to South filter inter zone prot operation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 4.8333 | 0 | [6 empty] | 744
126 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
127 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
128 | SR1S1 | STATCOM AT NPKUNTA | 200 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
|  |  | Note in type of failure column please indicate following : | [9 empty] | 131.2833 | 7.3167 | 75.1333 | 6001.45
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF MARCH 2017
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
GTY LR at NSR
1 |  | GTY LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWK I LR at VJA
2 |  | GWK I LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWL LR at HYD
3 |  | GWL LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY I LR at GWK
4 |  | JEY I LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY II LR at GWK
5 |  | JEY II LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MBN LR at NSR
6 |  | MBN LR at NSR | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MLK LR at HYD
7 |  | MLK LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR I LR at VJA
8 |  | NLR I LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR II LR at VJA
9 |  | NLR II LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I LR at CDP
10 |  | NSR I LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II LR at CDP
11 |  | NSR II LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR LR at GTY
12 |  | NSR LR at GTY | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II ER at GWK
13 |  | POLE II ER at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II SR at GWK
14 |  | POLE II SR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RCR LR at MBD
15 |  | RCR LR at MBD | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM I LR at NSR
16 |  | RDM I LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM II LR at NSR
17 |  | RDM II LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH I LR at GWK
18 |  | SMH I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH II LR at GWK
19 |  | SMH II LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at GWK
20 |  | VJA I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at NLR
21 |  | VJA I LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA II LR at NLR
22 |  | VJA II LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG III LR at VJA
23 |  | VMG III LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG IV LR at VJA
24 |  | VMG IV LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
WGL LR at KMM
25 |  | WGL LR at KMM | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I FSC at CDP
26 |  | NSR I FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II FSC at CDP
27 |  | NSR II FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-1 at GTY
28 |  | FSC-1 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-2 at GTY
29 |  | FSC-2 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM1 LR at NLR
30 |  | TVLM1 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM2 LR at NLR
31 |  | TVLM2 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VTPS LR at NLRAP
32 |  | VTPS LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA LR at NLRAP
33 |  | VJA LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VJA
34 |  | NLRAP LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VTPS
35 |  | NLRAP LR at VTPS | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL I L/R AT NPS
36 |  | KURNOOL I L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL II L/R AT NPS
37 |  | KURNOOL II L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS I L/R AT KURNOOL
38 |  | NPS I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS II L/R AT KURNOOL
39 |  | NPS II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM I L/R AT KURNOOL
40 |  | TVLM I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM II L/R AT KURNOOL
41 |  | TVLM II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 0 | 0 | 0 | 0