## SOP
Standard of Performance data for the month of SEPTEMBER -2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2017-09-01 | 0:00 | 2017-09-01 | 10:01 |  |  |  | 0 | 0 | 0 | 10.0167 |  |  |  | H/T for Voltage regulation vide code SR520,( continued from last month ) |  | 100 | 720
[6 empty] | 2017-09-19 | 14:31 | 2017-09-23 | 20:46 |  |  |  | 0 | 0 | 0 | 102.25 |  |  |  | H/T for voltage regulation vide code SR 682 |  |  | 720
[6 empty] | 2017-09-24 | 6:11 | 2017-09-24 | 6:11 |  |  |  | 7.3729e-11 | 0 | 0 | 0 |  |  |  | Line Autoreclosed sucessfully both ends on B-N fault. (KNL End: 141.5KM, 3.73KA) (NPS End: 151.5KM, 3.40KA) |  |  | 720
[6 empty] | 2017-09-27 | 12:17 | 2017-09-27 | 12:22 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on OV protn operated at NPS end DT received at KLN end |  |  | 720
[6 empty] | 2017-09-27 | 12:22 | 2017-10-01 | 0:00 |  |  |  | 0 | 0 | 0 | 83.6333 |  |  |  | Line kept out of service under voltage regulations as per SRLDC instructions. |  |  | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 7.3729e-11 | 0 | 0.083333 | 195.9 | [6 empty] | 720
2 | SR1L02 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2017-09-01 | 17:16 | 2017-09-19 | 14:52 |  |  |  | 0 | 0 | 0 | 429.6 |  |  |  | H/T for Voltage regulation vide code SR29,NL25 |  | 100 | 720
[6 empty] | 2017-09-23 | 17:58 | 2017-09-23 | 18:03 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on O/V stg-1 prot at KLN end & DT received at NPS end. |  |  | 720
[6 empty] | 2017-09-23 | 18:03 | 2017-09-27 | 12:27 |  |  |  | 0 | 0 | 0 | 90.4 |  |  |  | Line kept out of service under voltage regulations as per SRLDC instructions. |  |  | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 520 | [6 empty] | 720
3 | SR1L03 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2017-09-13 | 14:18 | 2017-09-23 | 18:11 |  |  |  | 0 | 0 | 0 | 243.8833 |  |  |  | H/T for voltage regulation vide code SR-402 |  | 100 | 720
[5 empty] | -- | [17 empty] | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 243.8833 | [6 empty] | 720
4 | SR1L04 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2017-09-01 | 0:00 | 2017-09-13 | 14:00 |  |  |  | 0 | 0 | 0 | 302 |  |  |  | H/T for voltage regulation vide code SR575,( continued from last month ) |  | 100 | 720
[6 empty] | 2017-09-23 | 17:58 | 2017-09-23 | 18:03 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on O/V stg-1 prot at KLN end & DT received at TVLM end. |  |  | 720
[6 empty] | 2017-09-23 | 18:03 | 2017-10-01 | 0:00 |  |  |  | 0 | 0 | 0 | 173.95 |  |  |  | Line kept out of service under voltage regulations as per SRLDC instructions. |  |  | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 475.95 | [6 empty] | 720
5 | SR1L05 | RAICHUR(NEW) - KURNOOL(NEW) - I | 120.482 | SR-I | -- | 2017-09-22 | 10:11 | 2017-09-22 | 16:35 |  |  |  | 6.4 | 0 | 0 | 0 | -- | -- | -- | S/D availed for alignment of 71289B isolator at RCN end. Vide SR09/844. |  | 99.1111 | 720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 6.4 | 0 | 0 | 0 | [6 empty] | 720
6 | SR1L06 | RAICHUR(NEW) - KURNOOL(NEW) - II | 118.423 | SR-I | -- | 2017-09-03 | 2:16 | 2017-09-06 | 10:31 |  |  |  | 0 | 0 | 0 | 80.25 |  |  |  | H/T for Voltage regulation vide code SR09/62,NL09/64 |  | 100 | 720
[6 empty] | 2017-09-07 | 1:28 | 2017-09-07 | 7:29 |  |  |  | 0 | 0 | 0 | 6.0167 |  |  |  | H/T for Voltage regulation vide code SR09/180 |  |  | 720
[6 empty] | 2017-09-07 | 23:50 | 2017-09-08 | 8:39 |  |  |  | 0 | 0 | 0 | 8.8167 |  |  |  | H/T for Voltage regulation vide code SR09/219 |  |  | 720
[6 empty] | 2017-09-09 | 0:49 | 2017-09-19 | 7:31 |  |  |  | 0 | 0 | 0 | 246.7 |  |  |  | H/T for Voltage regulation vide code SR09/258 |  |  | 720
[6 empty] | 2017-09-19 | 23:22 | 2017-09-22 | 8:50 |  |  |  | 0 | 0 | 0 | 57.4667 |  |  |  | H/T for voltage regulation vide code SR-705 |  |  | 720
[6 empty] | 2017-09-22 | 22:08 | 2017-09-23 | 7:59 |  |  |  | 0 | 0 | 0 | 9.85 |  |  |  | H/T under Voltage regulation vide code SR09/887. |  |  | 720
[6 empty] | 2017-09-23 | 20:38 | 2017-09-26 | 10:18 |  |  |  | 0 | 0 | 0 | 61.6667 |  |  |  | H/T under Voltage regulation vide code SR09/934. |  |  | 720
[6 empty] | 2017-09-27 | 0:23 | 2017-10-01 | 0:00 |  |  |  | 0 | 0 | 0 | 95.6167 |  |  |  | H/T under Voltage regulation vide code SR09/1043. |  |  | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 566.3833 | [6 empty] | 720
7 | SR1L07 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
8 | SR1L08 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
9 | SR1L09 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
10 | SR1L10 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 720
[5 empty] | -- | [11 empty] | N/A | N/A | N/A |  |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
11 | SR1L11 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[5 empty] | -- | [17 empty] | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
12 | SR1L12 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | [5 empty] | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
13 | SR1L13 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
14 | SR1L14 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | [16 empty] | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
15 | SR1L15 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | [16 empty] | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
16 | SR1L16 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | 2017-09-17 | 23:07 | 2017-09-20 | 11:52 |  |  |  | 0 | 0 | 0 | 60.75 |  |  |  | H/T for voltage regulation vide code SR-598 |  | 100 | 720
[6 empty] | 2017-09-25 | 1:45 | 2017-09-25 | 9:26 |  |  |  | 0 | 0 | 0 | 7.6833 |  |  |  | H/T under Voltage regulation vide code SR09/964. |  |  | 720
[6 empty] | 2017-09-25 | 16:46 | 2017-09-25 | 17:05 |  |  |  | 0 | 0 | 0 | 0.31667 |  |  |  | Line tripped while executing the OPGW works by SR-2 on B-N fault. Fault distance:126.4 kms, FC:2.8kA from GTY end. Distance: 109.2kms, FC: 2.36kA from TMKR end. A/R in non-auto mode at both ends for OPGW works. |  |  | 720
[6 empty] | 2017-09-25 | 17:05 | 2017-10-01 | 0:00 |  |  |  | 0 | 0 | 0 | 126.9167 |  |  |  | Line kept out under voltage regulation by SRLDC |  |  | 720
720
720
[5 empty] | -- | [17 empty] | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 195.6667 | [6 empty] | 720
17 | SR1L17 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | 2017-09-10 | 3:14 | 2017-09-11 | 11:21 |  |  |  | 0 | 0 | 0 | 32.1167 |  |  |  | H/T for Voltage regultion vide code SR09/295 |  | 99.8611 | 720
[6 empty] | 2017-09-24 | 18:05 | 2017-09-24 | 19:05 |  |  |  | 1 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault. (Gooty End: 210KM, 1.7KA). at Tumkur end no Distance recorded .FC -4.4KA.A/R kept in non auto mode due to OPGW work by SR-2 |  |  | 720
720
720
720
720
720
720
720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 1 | 0 | 0 | 32.1167 | [6 empty] | 720
18 | SR1L18 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | [16 empty] | 100 | 720
[5 empty] | -- | [17 empty] | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
19 | SR1L19 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[5 empty] | -- | [17 empty] | 720
[5 empty] | -- | [17 empty] | 720
[5 empty] | -- | [17 empty] | 720
[5 empty] | -- | [17 empty] | 720
[5 empty] | -- | [17 empty] | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
20 | SR1L20 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | 2017-09-28 | 19:32 | 2017-09-28 | 20:34 |  |  |  | 0 | 0 | 1.0333 | 0 |  |  |  | H/T from Jeypore end after tripping of both Gajuwaka poles |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.0333 | 0 | [6 empty] | 720
21 | SR1L21 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | 2017-09-28 | 17:30 | 2017-09-28 | 22:04 |  |  |  | 0 | 0 | 4.5667 | 0 |  |  |  | Tripped on DT receipt from Jeypore end.OV operated at Jeypore end. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 4.5667 | 0 | [6 empty] | 720
22 | SR1L22 | KADAPA - NPKUNTA | 9.512 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
23 | SR1L23 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | 2017-09-30 | 20:35 | 2017-10-01 | 0:00 |  |  |  | 0 | 0 | 0 | 3.4167 |  |  |  | H/T for Voltage regulation vide code SR1168 |  | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.4167 | [6 empty] | 720
24 | SR1L24 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | [16 empty] | 100 | 720
[5 empty] | -- | [17 empty] | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
25 | SR1L25 | KURNOOL(PG) - GOOTY | 112.609 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
26 | SR1L26 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | [16 empty] | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
27 | SR1L27 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | [16 empty] | 100 | 720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
28 | SR1L28 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | [16 empty] | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
29 | SR1L29 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | 2017-09-20 | 9:11 | 2017-09-20 | 19:53 |  |  |  | 0 | 0 | 0 | 10.7 |  |  |  | H/T for Maheswaram-Mahaboobnagar line crossing works S/D availed by M/s MTLvied SR 712 |  | 100 | 720
[6 empty] | 2017-09-30 | 3:04 | 2017-09-30 | 3:10 |  |  |  | 0 | 0 | 0.1 | 0 |  |  |  | Line tripped due to receipt of DT from RTPS end.OV stage 1 operated at RTPS end |  |  | 720
[6 empty] | 2017-09-30 | 3:10 | 2017-10-01 | 0:00 |  |  |  | 0 | 0 | 0 | 20.8333 |  |  |  | line kept under Voltage regulation as per instruction of SRLDC |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.1 | 31.5333 | [6 empty] | 720
30 | SR1L30 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | 2017-09-23 | 10:31 | 2017-09-23 | 13:20 |  |  |  | 2.8167 | 0 | 0 | 0 |  |  |  | S/D for taking Hyderabad-Malkaram line reactor into service |  | 98.2269 | 720
[6 empty] | 2017-09-23 | 22:35 | 2017-09-23 | 22:51 |  |  |  | 0.26667 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault. (HYD End: 12.62KM, 12.96KA). Line tripped at HYD end only. A/R sucessful & holding from Malkaram end. Y-Ph V string decapped at Loc:492. |  |  | 720
[6 empty] | 2017-09-24 | 12:48 | 2017-09-24 | 19:33 |  |  |  | 6.75 | 0 | 0 | 0 |  |  |  | S/D availed for attending decapped Y-ph string at Loc:492. |  |  | 720
[6 empty] | 2017-09-15 | 10:58 | 2017-09-15 | 13:54 |  |  |  | 2.9333 | 0 | 0 | 0 |  |  |  | S/D availed for L/R jumper connection works at HYD vide SR09/500. |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 12.7667 | 0 | 0 | 0 | [6 empty] | 720
31 | SR1L31 | NELLOREPS - GOOTY - I | 289.004 | SR-I | -- | 2017-09-08 | 17:41 | 2017-09-08 | 17:41 |  |  |  | 1.5521e-11 | 0 | 0 | 0 |  |  |  | A/R sucessful on R-N fault,From GTY end: Distance:67.2 Km,FC-4.8 KA; From NPS end :FC-2.45 KA, Distance:NA |  | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 1.5521e-11 | 0 | 0 | 0 | [6 empty] | 720
32 | SR1L32 | NELLOREPS - GOOTY - II | 289.004 | SR-I | -- | [16 empty] | 100 | 720
720
720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
33 | SR1L33 | NELLOREPS - MEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
34 | SR1L34 | NELLOREPS - SEPL | 3.83 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
35 | SR1L35 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
36 | SR1L36 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
37 | SR1L37 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
38 | SR1L38 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
39 | SR1L39 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | 2017-09-03 | 18:28 | 2017-09-05 | 13:19 |  |  |  | 42.85 | 0 | 0 | 0 | -- | -- | -- | Tripped on B-N fault. From NLR end : Distance: 46.30 km,FC-7.824 KA; From SPDR end: Distance :151.20 Km,FC:3.80 KA: insulator decapping at loc no 129. |  | 94.0486 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 42.85 | 0 | 0 | 0 | [6 empty] | 720
40 | SR1L40 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | [16 empty] | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
41 | SR1L41 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | 2017-09-14 | 9:50 | 2017-09-14 | 19:20 |  |  |  | 0 | 0 | 0 | 9.5 |  |  |  | S/D availed for construction works of line Reactor at Nellore vide SR09/427. |  | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.5 | [6 empty] | 720
42 | SR1L42 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | 2017-09-15 | 8:21 | 2017-09-15 | 21:16 |  |  |  | 0 | 0 | 0 | 12.9167 |  |  |  | S/D availed for construction works of line Reactor at Nellore for making jumper connection from strung bus to Reactor vide SR09/482. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.9167 | [6 empty] | 720
43 | SR1L43 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | [16 empty] | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
44 | SR1L44 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | [16 empty] | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
45 | SR1L45 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
46 | SR1L46 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | 2017-09-16 | 3:49 | 2017-09-16 | 3:49 |  |  |  | 4.2686e-11 | 0 | 0 | 0 |  |  |  | Line A/R successfully on Y-N fault at both ends .Dist & F/C from KDP: 88.596 KM & 3.170 KA . from NSR :199.99 KM & 2.347 KA respectively. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 4.2686e-11 | 0 | 0 | 0 | [6 empty] | 720
47 | SR1L47 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
48 | SR1L48 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | 2017-09-11 | 7:48 | 2017-09-11 | 21:58 |  |  |  | 0 | 0 | 0 | 14.1667 |  |  |  | SD availed by M/s MTL for Maheshwaram-Velatoor DC line crossing works vide code SR318 |  | 100 | 720
[6 empty] | 2017-09-15 | 11:52 | 2017-09-16 | 7:49 |  |  |  | 0 | 0 | 0 | 19.95 |  |  |  | S/D availed by TSTRANSCO for commissioning of new CGL makePLCC Panels inplace of old BPL make PLCC panels works at both ends vide SR09/497. |  |  | 720
[6 empty] | 2017-09-16 | 2:01 | 2017-09-16 | 7:49 |  |  |  | 0 | 0 | 0 | 5.8 |  |  |  | After S/D line charged from Velatoor end & synchronized at NSR end & Line tripped immediately on receipt of DT from Velatoor due to O/V at Velatoor. Line kept under LVRD as instructed by SRLDC |  |  | 720
[6 empty] | 2017-09-30 | 10:52 | 2017-09-30 | 11:52 |  |  |  | 0 | 1 | 0 | 0 |  |  |  | Line tripped at Mahaboobnagar end only in reverse zone due to fault in TSTRANSCO system |  |  | 720
720
720
720
720
720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 1 | 0 | 39.9167 | [6 empty] | 720
49 | SR1L49 | NPKUNTA - KOLAR | 9.512 | SR-I | -- | 2017-09-19 | 3:28 | 2017-09-19 | 4:00 |  |  |  | 0.53333 | 0 | 0 | 0 | -- | -- | -- | Line tripped on Y-N fault , dist:9.97KM, FC:5.90KA from NPK end ; distance:118.6 Km,FC:3.55 KA at Kolar |  | 99.9259 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0.53333 | 0 | 0 | 0 | [6 empty] | 720
50 | SR1L50 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | 2017-09-03 | 2:01 | 2017-09-03 | 2:01 |  |  |  | -6.2088e-11 | 0 | 0 | 0 |  |  |  | Line autoreclosed successfully on Y-N fault. (MBD End: 144.7KM, 1.9KA ; RTPS End: 29.7KM) |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | -6.2088e-11 | 0 | 0 | 0 | [6 empty] | 720
51 | SR1L51 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
52 | SR1L52 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
53 | SR1L53 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[5 empty] | -- | [17 empty] | 720
[5 empty] | -- | [17 empty] | 720
[5 empty] | -- | [17 empty] | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
54 | SR1L54 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
55 | SR1L55 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | 2017-09-07 | 8:29 | 2017-09-08 | 19:28 |  |  |  | 0 | 0 | 0 | 34.9833 |  |  |  | For replacement of PLCC at Gajwel end vide code SR |  | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 34.9833 | [6 empty] | 720
56 | SR1L56 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
57 | SR1L57 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I |  | 2017-09-15 | 22:58 | 2017-09-15 | 23:03 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on OV Protn optd at HYD end DT received at Ramagundam end. Line kept under LVRD as instructed by SRLDC |  | 100 | 720
[6 empty] | 2017-09-15 | 23:03 | 2017-09-16 | 7:56 |  |  |  | 0 | 0 | 0 | 8.8833 |  |  |  | Line Kept out of service due to Voltage regulation |  |  | 720
[6 empty] | 2017-09-17 | 2:06 | 2017-09-17 | 2:11 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on OV Protn optd at KLN end DT received at Maheswram end. Line kept under LVRD as instructed by SRLDC |  |  | 720
[6 empty] | 2017-09-17 | 2:11 | 2017-09-18 | 14:57 |  |  |  | 0 | 0 | 0 | 36.7667 |  |  |  | Line Kept out of service due to Voltage regulation |  |  | 720
720
720
720
720
720
720
720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.16667 | 45.65 | [6 empty] | 720
58 | SR1L58 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | 2017-09-01 | 10:27 | 2017-09-01 | 10:27 |  |  |  | 1.1643e-11 | 0 | 0 | 0 |  |  |  | Auto reclosed on B-N fault.Distance-36.57 km,FC-8.5 KA from NTPC end. |  | 99.125 | 720
[6 empty] | 2017-09-02 | 11:16 | 2017-09-02 | 17:34 |  |  |  | 6.3 | 0 | 0 | 0 |  |  |  | H/T for replacement of insulator string at LOC-114 vide code SR45 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 6.3 | 0 | 0 | 0 | [6 empty] | 720
59 | SR1L59 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
60 | SR1L60 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
61 | SR1L61 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | 2017-09-05 | 12:20 | 2017-09-05 | 17:24 |  |  |  | 0 | 0 | 0 | 5.0667 |  |  |  | S/D by M/S NTPC to attend broken Jumper at RDM end vide SR/126 |  | 98.0324 | 720
[6 empty] | 2017-09-06 | 3:23 | 2017-09-06 | 17:33 |  |  |  | 14.1667 | 0 | 0 | 0 |  |  |  | Tripped on Y-N fault.From RDM end Distance:84.86 km,FC:4.72 KA; From WGL end : Distance :10.061 Km,Fc-10.093 KA |  |  | 720
720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 14.1667 | 0 | 0 | 5.0667 | [6 empty] | 720
62 | SR1L62 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
63 | SR1L63 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
64 | SR1L64 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | 2017-09-01 | 0:00 | 2017-09-06 | 12:15 |  |  |  | 0 | 0 | 0 | 132.25 |  |  |  | H/T for Voltage regulation as per instruction of SRLDC vide code SR1015,( continued from last month ) |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
65 | SR1L65 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | [16 empty] | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
66 | SR1L66 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | 2017-09-01 | 0:00 | 2017-09-14 | 13:44 |  |  |  | 0 | 0 | 0 | 325.7333 | -- | -- | -- | H/T for Power regulation vide code SR02/721,( continued from last month ) |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 325.7333 | [6 empty] | 720
67 | SR1L67 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
68 | SR1L68 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | [16 empty] | 100 | 720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
69 | SR1L69 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | 2017-09-05 | 15:50 | 2017-09-05 | 15:50 |  |  |  | -7.761e-11 | 0 | 0 | 0 | -- | -- | -- | A/R successful both the ends on R-N fault 18.7kM,11kA |  | 100 | 720
[6 empty] | 2017-09-26 | 16:18 | 2017-09-26 | 16:18 |  |  |  | 4.6565e-11 | 0 | 0 | 0 |  |  |  | A/R succesful both the ends on R-N fault (At VJA end-35.6kM/7.4kA, At NLR end- 273.47kM /1.295kA
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
70 | SR1L70 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | [16 empty] | 100 | 720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
71 | SR1L71 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | 2017-09-03 | 12:37 | 2017-09-03 | 12:37 |  |  |  | 8.5372e-11 | 0 | 0 | 0 |  |  |  | A/R successful on YN fault. (VJA End: 140.3KM, 2.12KA ; VMG End: 43.3KM, 5.181KA) |  | 99.8981 | 720
[6 empty] | 2017-09-04 | 11:44 | 2017-09-04 | 15:59 |  |  |  | 0 | 0 | 0 | 4.25 |  |  |  | H/T on request of M/s APTRANSCO for replacement of defective Main-2 relay vide code SR82
[6 empty] | 2017-09-16 | 11:02 | 2017-09-16 | 11:46 |  |  |  | 0.73333 | 0 | 0 | 0 |  |  |  | Line tripped on Y-N fault. (VJA End: 100.5KM, 2.92KA ; VMG End: 4.7KA) |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0.73333 | 0 | 0 | 4.25 | [6 empty] | 720
72 | SR1L72 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
73 | SR1L73 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | 2017-09-03 | 9:49 | 2017-09-03 | 11:52 |  |  |  | 2.05 | 0 | 0 | 0 |  |  |  | Line tripped due to Reactor NGR PRD spurious operation |  | 99.7153 | 720
[6 empty] | Sub Total --> | [6 empty] | 2.05 | 0 | 0 | 0 | [6 empty] | 720
74 | SR1L74 | VEMAGIRI(PG) - GAZUWAKA | 165.454 | SR-I |  | 2017-09-18 | 9:18 | 2017-09-18 | 19:49 |  |  |  | 0 | 0 | 0 | 10.5167 |  |  |  | H/T for RTV Coating works vide code SR-609 |  | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.5167 | [6 empty] | 720
75 | SR1L75 | VIJAYAWADA - VEMAGIRI(PG) | 187.8 | SR-I | [17 empty] | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
75 | SR1L76 | MAHESHWARAM-KURNOOL AP | 174.996 | SR-I |  | 2017-09-01 | 3:02 | 2017-09-01 | 3:07 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped due to DT receipt at Maheshwaram end. OV stage1 operated at Kurnool end. |  | 100 | 720
[6 empty] | 2017-09-01 | 3:07 | 2017-09-01 | 9:46 |  |  |  | 0 | 0 | 0 | 6.65 |  |  |  | Line Kept out of service due to Voltage regulation |  |  | 720
[6 empty] | 2017-09-02 | 3:01 | 2017-09-02 | 3:07 |  |  |  | 0 | 0 | 0.1 | 0 |  |  |  | Tripped due to DT receipt at Maheshwaram end. OV stage1 operated at Kurnool end.
[6 empty] | 2017-09-02 | 3:07 | 2017-09-02 | 6:43 |  |  |  | 0 | 0 | 0 | 3.6 |  |  |  | Line Kept out of service due to Voltage regulation
[6 empty] | 2017-09-06 | 1:57 | 2017-09-06 | 2:05 |  |  |  | 0 | 0 | 0.13333 | 0 |  |  |  | Tripped due to DT receipt at Maheshwaram end. OV stage1 operated at Kurnool end.
[6 empty] | 2017-09-06 | 2:05 | 2017-09-06 | 10:24 |  |  |  | 0 | 0 | 0 | 8.3167 |  |  |  | Line Kept out of service due to Voltage regulation
[6 empty] | 2017-09-06 | 23:59 | 2017-09-07 | 0:04 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped due to DT receipt at Maheshwaram end. OV stage1 operated at Kurnool end.
[6 empty] | 2017-09-07 | 0:05 | 2017-09-07 | 9:25 |  |  |  | 0 | 0 | 0 | 9.3333 |  |  |  | Line Kept out of service due to Voltage regulation
[6 empty] | 2017-09-07 | 23:29 | 2017-09-07 | 23:35 |  |  |  | 0 | 0 | 0.1 | 0 |  |  |  | Tripped due to DT receipt at Maheshwaram end. OV stage1 operated at Kurnool end.
[6 empty] | 2017-09-07 | 23:36 | 2017-09-08 | 7:28 |  |  |  | 0 | 0 | 0 | 7.8667 |  |  |  | Line Kept out of service due to Voltage regulation
[6 empty] | 2017-09-08 | 23:53 | 2017-09-08 | 23:58 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped due to DT receipt at Maheshwaram end. OV stage1 operated at Kurnool end.
[6 empty] | 2017-09-08 | 23:58 | 2017-09-09 | 10:06 |  |  |  | 0 | 0 | 0 | 10.1333 |  |  |  | Line Kept out of service due to Voltage regulation
[6 empty] | 2017-09-10 | 0:01 | 2017-09-10 | 0:06 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on OV Protn optd at KLN end DT received at Maheswram end. Line kept under LVRD as instructed by SRLDC
[6 empty] | 2017-09-10 | 0:06 | 2017-09-11 | 13:15 |  |  |  | 0 | 0 | 0 | 37.15 |  |  |  | Line Kept out of service due to Voltage regulation
[6 empty] | 2017-09-15 | 2:41 | 2017-09-15 | 2:47 |  |  |  | 0 | 0 | 0.1 | 0 |  |  |  | Line tripped on OV Protn optd at KLN end DT received at Maheswram end. Line kept under LVRD as instructed by SRLDC
[6 empty] | 2017-09-15 | 2:47 | 2017-09-15 | 9:45 |  |  |  | 0 | 0 | 0 | 6.9667 |  |  |  | Line Kept out of service due to Voltage regulation
[6 empty] | 2017-09-16 | 2:02 | 2017-09-16 | 2:07 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on OV Protn optd at KLN end DT received at Maheswram end. Line kept under LVRD as instructed by SRLDC |  |  | 720
[6 empty] | 2017-09-16 | 2:46 | 2017-09-19 | 8:18 |  |  |  | 0 | 0 | 0 | 77.5333 |  |  |  | Line Kept out of service due to Voltage regulation
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.85 | 167.55 | [6 empty] | 720
75 | SR1L77 | NiZAMABAD-DICHPALLY 1 | 4.428 | SR-I |  | 2017-09-16 | 11:42 | 2017-09-16 | 19:04 |  |  |  | 7.3667 | 0 | 0 | 0 |  |  |  | H/T for Line differential relay protection testing vide code SR09/539. |  | 98.9769 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 7.3667 | 0 | 0 | 0 | [6 empty] | 720
75 | SR1L77 | NiZAMABAD-DICHPALLY 2 | 4.428 | SR-I |  | 2017-09-17 | 1:12 | 2017-09-17 | 13:42 |  |  |  | 12.5 | 0 | 0 | 0 |  |  |  | H/T as a precautionary measure after observing PD in GIB vide code SR09/582. |  | 98.2639 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 12.5 | 0 | 0 | 0 | [6 empty] | 720
75 | SR1L78 | NIZAMABAD-MAHESHWARAM 1 | 243.059 | SR-I |  | 2017-09-02 | 20:56 | 2017-09-04 | 22:57 |  |  |  | 0 | 0 | 0 | 50.0167 |  |  |  | H/T for Voltage regulation vide code SR09/61,NL09/62 |  | 100 | 720
[6 empty] | 2017-09-18 | 22:46 | 2017-09-19 | 7:54 |  |  |  | 0 | 0 | 0 | 9.1333 |  |  |  | H/T for voltage regulation vide code SR 657 |  |  | 720
[6 empty] | 2017-09-28 | 22:12 | 2017-10-01 | 0:00 |  |  |  | 0 | 0 | 0 | 49.8 |  |  |  | H/T under Voltage regulation vide code SR09/1123. |  |  | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 108.95 | [6 empty] | 720
75 | SR1L79 | NIZAMABAD-MAHESHWARAM 2 | 243.059 | SR-I |  | 2017-09-14 | 12:03 | 2017-09-14 | 19:47 |  |  |  | 0 | 0 | 0 | 7.7333 |  |  |  | S/D availed for Line Reactor Bushing(R-Ph) erection works at Maheshwaram vide SR09/439 |  | 99.7708 | 720
[6 empty] | 2017-09-17 | 0:29 | 2017-09-17 | 0:34 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on OV Protn optd at KLN end DT received at Maheswram end. Line kept under LVRD as instructed by SRLDC |  |  | 720
[6 empty] | 2017-09-17 | 0:34 | 2017-09-18 | 9:52 |  |  |  | 0 | 0 | 0 | 33.3 |  |  |  | Line Kept out of service due to Voltage regulation |  |  | 720
[6 empty] | 2017-09-19 | 12:35 | 2017-09-19 | 14:14 |  |  |  | 1.65 | 0 | 0 | 0 |  |  |  | Tripped on RY fault due to flash over at Maheshwaram GID in 70789RS Y-Ph isolator |  |  | 720
[6 empty] | 2017-09-19 | 16:08 | 2017-09-25 | 7:34 |  |  |  | 0 | 0 | 0 | 135.4333 |  |  |  | H/T for voltage regulation vide code SR 692 |  |  | 720
[6 empty] | 2017-09-25 | 13:54 | 2017-09-26 | 9:21 |  |  |  | 0 | 0 | 0 | 19.45 |  |  |  | H/T for voltage regulation vide code SR 985 |  |  | 720
[6 empty] | 2017-09-27 | 21:21 | 2017-09-28 | 7:34 |  |  |  | 0 | 0 | 0 | 10.2167 |  |  |  | H/T under Voltage regulation vide code SR09/1081. |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 1.65 | 0 | 0.083333 | 206.1333 | [6 empty] | 720
75 | SR1L80 | NIZAMABAD-WARDHA 1 | 291.2 | SR-I | [17 empty] | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
75 | SR1L81 | NIZAMABAD-WARDHA 2 | 291.2 | SR-I | [17 empty] | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
720
720
720
720
75 | SR1L83 | VIJAYAWADA-VEMAGIRI PG | 187.8 | SR-I | [17 empty] | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
75 | SR1L84 | KADAPA- CHITTOOR |  | SR-I | [17 empty] | 100 | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
75 | SR1L84 | HYDERABAD-MAHESHWARAM |  | SR-I | -- | 2017-09-01 | 0:00 | 2017-09-04 | 23:47 |  |  |  | 0 | 0 | 0 | 95.7833 |  |  |  | Hyderabad-Kurnool line LILO at Maheshwaram.line kept under power regulation,( continued from last month ) |  | 99.1667 | 720
[6 empty] | 2017-09-13 | 11:27 | 2017-09-13 | 17:27 |  |  |  | 6 | 0 | 0 | 0 |  |  |  | Line tripped on R-N fault,7.6kM/4.2kA from HYD end. 43.7 kms & FC:3.89kA from Maheshwaram end. |  |  | 720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 6 | 0 | 0 | 95.7833 | [6 empty] | 720
76 | SR1T01 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
77 | SR1T02 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
78 | SR1T03 | NELLOREPS ICT - II | 1500 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
79 | SR1T04 | NELLOREPS ICT - III | 1500 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
80 | SR1T05 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
81 | SR1T06 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | 2017-09-18 | 10:37 | 2017-09-18 | 15:07 |  |  |  | 4.5 | 0 | 0 | 0 | -- | -- | -- | H/T for attending Hotspot vide code SR614 |  | 99.375 | 720
[6 empty] | Sub Total --> | [6 empty] | 4.5 | 0 | 0 | 0 | [6 empty] | 720
82 | SR1T07 | CUDDAPAH ICT I | 315 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
83 | SR1T08 | CUDDAPAH ICT II | 315 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
84 | SR1T09 | GAJUWAKA ICT I | 315 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
85 | SR1T10 | GAZUWAKA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
86 | SR1T11 | GOOTY ICT I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
87 | SR1T12 | GOOTY ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
88 | SR1T13 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
89 | SR1T14 | HYDERABAD ICT - II | 315 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
90 | SR1T15 | HYDERABAD ICT - III | 315 | SR-I | -- |  |  |  |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
91 | SR1T16 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
92 | SR1T17 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
93 | SR1T18 | MUNIRABAD ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
94 | SR1T19 | MUNIRABAD ICT II | 315 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
95 | SR1T20 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
96 | SR1T21 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
97 | SR1T22 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
98 | SR1T23 | NPKUNTA ICT - I | 500 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
99 | SR1T24 | NPKUNTA ICT - II | 500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
100 | SR1T25 | NPKUNTA ICT - III | 500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
101 | SR1T26 | VIJAYAWADA ICT I | 315 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
102 | SR1T27 | VIJAYAWADA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
103 | SR1T28 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1T29 | WARANGAL ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1T30 | VEMAGIRI ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1T31 | VEMAGIRI ICT II | 1500 | SR-I | -- | 2017-09-19 | 2:04 | 2017-09-19 | 9:23 |  |  |  | 7.3167 | 0 | 0 | 0 |  |  |  | Tripped on operation of Differential protection due to LA failure in B ph |  | 77.0671 | 720
[6 empty] | 2017-09-21 | 5:38 | 2017-09-27 | 19:26 |  |  |  | 157.8 | 0 | 0 | 0 |  |  |  | Tripped on Differential protection due to 40789T isolator flashover. |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 165.1167 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1T32 | NIZAMABAD ICT I | 1500 | SR-I | -- | 2017-09-11 | 11:19 | 2017-09-11 | 12:23 |  |  |  | 1.0667 | 0 | 0 | 0 |  |  |  | Tripped due to R-Ph fire protection mal-operation |  | 99.8519 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 1.0667 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1T33 | NIZAMABAD ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1T34 | MAHESHWRAM ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1T35 | MAHESHWARAM ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
105 | SR1T36 | HYDERABAD ICT IV | 1500 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
105 | SR1R01 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
106 | SR1R02 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [16 empty] | 720
107 | SR1R03 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
108 | SR1R04 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | [5 empty] | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
109 | SR1R05 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
110 | SR1R06 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
111 | SR1R07 | GOOTY BUS REACTOR | 63 | SR-I | -- | 2017-09-20 | 10:30 | 2017-09-21 | 22:03 |  |  |  | 35.55 | 0 | 0 | 0 | -- | -- | -- | H/T for AMP Works & replacement of 145 KV Neutral bushing vide code SR/732 |  | 95.0625 | 720
[6 empty] | Sub Total --> | [6 empty] | 35.55 | 0 | 0 | 0 | [6 empty] | 720
112 | SR1R08 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
113 | SR1R09 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
114 | SR1R10 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
115 | SR1R11 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | 2017-09-01 | 0:00 | 2017-09-17 | 5:28 |  |  |  | 0 | 0 | 0 | 389.4667 |  |  |  | H/T for Voltage regulation vide code SR03/282,( continued from last month ) |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 389.4667 | [6 empty] | 720
116 | SR1R12 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
117 | SR1R13 | NELLORE BUS REACTOR | 80 | SR-I | -- | 2017-09-18 | 10:31 | 2017-09-18 | 20:56 |  |  |  | 10.4167 | 0 | 0 | 0 | -- | -- | -- | H/T for AMP works vide code SR09/614A |  | 98.5532 | 720
[6 empty] | Sub Total --> | [6 empty] | 10.4167 | 0 | 0 | 0 | [6 empty] | 720
118 | SR1R14 | NPKUNTA BUS REACTOR | 125 | SR-I | -- | 2017-09-01 | 0:00 | 2017-09-29 | 1:27 |  |  |  | 0 | 0 | 0 | 673.45 | -- | -- | -- | H/T for Voltage regulation vide code SR1077,( continued from last month ) |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 673.45 | [6 empty] | 720
119 | SR1R15 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
120 | SR1R16 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
121 | SR1R17 | 765 KV Srikakulam-Vemagiri 2 LR | 240 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
122 | SR1R18 | 765 KV Srikakulam-Vemagiri 1 LR | 240 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
123 | SR1R19 | 330MVAR Bus Reactor at SKLM | 330 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
123 | SR1R20 | VEMAGIRI 240MVAR BUS REACTOR-I | 240 | SR-I | -- | 2017-09-25 | 10:31 | 2017-09-25 | 13:06 |  |  |  | 2.5833 | 0 | 0 | 0 |  |  |  | Tripped on PRD-2 maloperation |  | 99.6412 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 2.5833 | 0 | 0 | 0 | [6 empty] | 720
123 | SR1R21 | VEMAGIRI 240MVAR BUS REACTOR-II | 240 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
123 | SR1R22 | VEMAGIRI 80MVAR BUS REACTOR | 80 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
123 | SR1R23 | MAHESHWARAM BUS REACTOR 1 | 240 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
123 | SR1R24 | POLE-2 EAST REACTOR | 125 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
124 | SR1R25 | VIJAYWADA BUS REACTOR 4 | 125 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
124 | SR1R26 | NAGARJUNA SAGAR BUS REACTOR II | 125 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
124 | SR1R27 | WARDHA 1 LR AT NIZAMABAD | 240 | SR-I | -- | [16 empty] | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
124 | SR1R27 | NIZAMABAD 1 LR AT MAHEWHWARAM | 240 | SR-I | -- | 2017-09-27 | 11:08 | 2017-09-27 | 13:49 |  |  |  | 0 | 0 | 0 | 2.6833 |  |  |  | For CSD fine tuning works vide SR/1059 |  | 100 | 720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.6833 | [6 empty] | 720
124 | SR1R27 | NIZAMABAD 2 LR AT MAHEWHWARAM | 240 | SR-I | -- | 2017-09-01 | 14:38 | 2017-09-01 | 18:41 |  |  |  | 4.05 | 0 | 0 | 0 |  |  |  | H/T for attending abnormal sound in spare reactor vide code SR21,NL24 |  | 99.4375 | 720
[6 empty] | 2017-09-15 | 12:51 | 2017-09-19 | 12:15 |  |  |  | 0 | 0 | 0 | 95.4 |  |  |  | Emergency S/D availed for attending the PD problem in Reactor auxiliary bus vide SR09/506.
[6 empty] | 2017-09-19 | 12:35 | 2017-09-26 | 16:18 |  |  |  | 0 | 0 | 0 | 171.7167 |  |  |  | Tripped due to flash over in 70789RS-Y Ph isolator.
[6 empty] | 2017-09-28 | 10:11 | 2017-09-28 | 12:38 |  |  |  | 0 | 0 | 0 | 2.45 |  |  |  | For CSD fine tuning works vide SR/1098 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 4.05 | 0 | 0 | 269.5667 | [6 empty] | 720
124 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | 2017-09-04 | 7:36 | 2017-09-04 | 12:32 |  |  |  | 4.9333 | 0 | 0 | 0 |  |  |  | Pole-1 blocked due to VBE valve power supply low |  | 98.4236 | 720
[6 empty] | 2017-09-28 | 17:30 | 2017-09-28 | 23:55 |  |  |  | 6.4167 | 0 | 0 | 0 |  |  |  | Tripped due to auxiliary supply disturbance |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 11.35 | 0 | 0 | 0 | [6 empty] | 720
125 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | 2017-09-28 | 17:30 | 2017-09-28 | 20:54 |  |  |  | 0 | 0 | 0 | 3.4 |  |  |  | Tripped on Bus differential protection operation. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.4 | [6 empty] | 720
126 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
127 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
128 | SR1S1 | STATCOM AT NPKUNTA | 200 | SR-I | -- | 2017-09-19 | 3:28 | 2017-09-19 | 4:10 |  |  |  | 0 | 0 | 0 | 0.7 | OSPD | -- | -- | tripped on MV Bus Differentail protection operation. |  | 100 | 720
[6 empty] | 2017-09-22 | 11:01 | 2017-09-22 | 16:37 |  |  |  | 0 | 0 | 0 | 5.6 | SCSD |  |  | S/D availed for commissioning of station transformer. Vide SR09/849.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.3 | [6 empty] | 720
|  |  | Note in type of failure column please indicate following : | [9 empty] | 348.95 | 1 | 7.05 | 4742.7917
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF MARCH 2017
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
GTY LR at NSR
1 |  | GTY LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWK I LR at VJA
2 |  | GWK I LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWL LR at HYD
3 |  | GWL LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY I LR at GWK
4 |  | JEY I LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY II LR at GWK
5 |  | JEY II LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MBN LR at NSR
6 |  | MBN LR at NSR | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MLK LR at HYD
7 |  | MLK LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR I LR at VJA
8 |  | NLR I LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR II LR at VJA
9 |  | NLR II LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I LR at CDP
10 |  | NSR I LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II LR at CDP
11 |  | NSR II LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR LR at GTY
12 |  | NSR LR at GTY | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II ER at GWK
13 |  | POLE II ER at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II SR at GWK
14 |  | POLE II SR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RCR LR at MBD
15 |  | RCR LR at MBD | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM I LR at NSR
16 |  | RDM I LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM II LR at NSR
17 |  | RDM II LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH I LR at GWK
18 |  | SMH I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH II LR at GWK
19 |  | SMH II LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at GWK
20 |  | VJA I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at NLR
21 |  | VJA I LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA II LR at NLR
22 |  | VJA II LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG III LR at VJA
23 |  | VMG III LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG IV LR at VJA
24 |  | VMG IV LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
WGL LR at KMM
25 |  | WGL LR at KMM | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I FSC at CDP
26 |  | NSR I FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II FSC at CDP
27 |  | NSR II FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-1 at GTY
28 |  | FSC-1 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-2 at GTY
29 |  | FSC-2 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM1 LR at NLR
30 |  | TVLM1 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM2 LR at NLR
31 |  | TVLM2 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VTPS LR at NLRAP
32 |  | VTPS LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA LR at NLRAP
33 |  | VJA LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VJA
34 |  | NLRAP LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VTPS
35 |  | NLRAP LR at VTPS | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL I L/R AT NPS
36 |  | KURNOOL I L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL II L/R AT NPS
37 |  | KURNOOL II L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS I L/R AT KURNOOL
38 |  | NPS I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS II L/R AT KURNOOL
39 |  | NPS II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM I L/R AT KURNOOL
40 |  | TVLM I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM II L/R AT KURNOOL
41 |  | TVLM II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 0 | 0 | 0 | 0