## FSC & LRs
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF APRIL 2014 | [8 empty] | 31
Sl.No | ELEMENT NAME | Capacity | TRIP DATE/TIME | REST DATE/TIME | OUTAGE DURATION |  |  |  | Availability | Reason
[5 empty] | POWERGRID SR-1 | OTHERS | SYSTEM CONSTRAINT / NATURAL CALAMITY / MILITANCY | DEEMED AVAILABLE
1 | GTY LR at NSR | 50 | [6 empty] | 100%
2 | GWK I LR at VJA | 63 | [6 empty] | 100%
3 | GWL LR at HYD | 50 | [6 empty] | 100%
4 | JEY I LR at GWK | 80 | [6 empty] | 100%
5 | JEY II LR at GWK | 80 | [6 empty] | 100%
6 | MBN LR at NSR | 63 | [6 empty] | 100%
7 | MLK LR at HYD | 50 | [6 empty] | 100%
8 | NLR I LR at VJA | 50 | [6 empty] | 100%
9 | NLR II LR at VJA | 50 | [6 empty] | 100%
10 | NSR I LR at CDP | 50 | [6 empty] | 100%
11 | NSR II LR at CDP | 50 | [6 empty] | 100%
12 | NSR LR at GTY | 50 | [6 empty] | 100%
13 | POLE II ER at GWK | 80 | [6 empty] | 100%
14 | POLE II SR at GWK | 80 | [6 empty] | 100%
15 | RCR LR at MBD | 63 | [6 empty] | 100%
16 | RDM I LR at NSR | 50 | [6 empty] | 100%
17 | RDM II LR at NSR | 50 | [6 empty] | 100%
18 | SMH I LR at GWK | 63 | [6 empty] | 100%
19 | SMH II LR at GWK | 63 | [6 empty] | 100%
20 | VJA I LR at GWK | 63 | [6 empty] | 100%
21 | VJA I LR at NLR | 50 | [6 empty] | 100%
22 | VJA II LR at NLR | 50 | 19.04.2014 20.37 | 24.04.2014 17.00 | 116.23 | 0 | 0 | 0 | 84.38%
23 | VMG III LR at VJA | 63 | [6 empty] | 100%
24 | VMG IV LR at VJA | 63 | [6 empty] | 100%
25 | WGL LR at KMM | 50 | [6 empty] | 100%
28 | NSR I FSC at CDP | 201.75 | [6 empty] | 100%
29 | NSR II FSC at CDP | 201.75 | [6 empty] | 100%
30 | FSC-1 at GTY | 181.5 | 03.04.2014 16.25 | 03.04.2014/17.12 | 0.42 | 0 | 0 | 0 | 99.94%
31 | FSC-2 at GTY | 181.5 | 03.04.2014/16.25 | 03.04.2014/17.12 | 0.42
|  |  | 05.04.2014 11.23 | 05.04.2014 12.05 | 0 | 0 | 0 | 0.42
|  |  | 25.04.2014 23.45 | 25.04.2014 23.55 | 0 | 0 | 0 | 0.1
[5 empty] | 0.42 | 0 | 0 | 0.52 | 99.94%
13.0167

## LINES
Sl No | Name of Line ICT | Event ID | Trip Date Time | Restoration Date Time | Cate Code | Outage PG | Outage Others | Outage System | Outage Deemed | Remarks | Availability
| RMD-GZL | No Trips
1 | RMD-GZL |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| GZW-HYD I | 304024 | 2014-04-05 19:17 | 2014-04-05 19:42 | OMSU | 0 | 0.41667 | 0 | 0 | Tripped at Gajwel end only due to spurious signal generated at Gajwel (APTRANSCO SS) end.
2 | GZW-HYD I |  |  |  |  | 0 | 0.41667 | 0 | 0 |  | 100%
| RMD-MLK | No Trips
3 | RMD-MLK |  |  |  |  | 0 | 0 | 0 | 0
| MLK-HYD II | 304086 | 2014-04-16 09:33 | 2014-04-16 13:15 | OSPT | 3.7 | 0 | 0 | 0 | Shut down availed to check healthiness of line reactor bushings vide SRLDC code no. CR-04/342.
4 | MLK-HYD II |  |  |  |  | 3.7 | 0 | 0 | 0 |  | 99.49%
| RDM-HYD III | 304101 | 2014-04-18 08:32 | 2014-04-18 08:32 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 158.6 KM from Hyderabad end.
5 | RDM-HYD III |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| RMD-HYD IV | No Trips
6 | RMD-HYD IV |  |  |  |  | 0 | 0 | 0 | 0
| RDM-CPR I | 304098 | 2014-04-18 04:50 | 2014-04-18 05:14 | LNCC | 0 | 0 | 0.4 | 0 | Tripped on B-N (Ph-earth) transient fault due to heavy lightning and thunderstorm. FLR: 56 kM from Chandrapur end.
| RDM-CPR I | 304099 | 2014-04-18 05:49 | 2014-04-18 06:31 | LNCC | 0 | 0 | 0.7 | 0 | Tripped on B-N (Ph-earth) transient fault due to heavy lightning and thunderstorm. FLR: 107 kM from Chandrapur end.
| RDM-CPR I | 304190 | 2014-04-28 14:46 | 2014-04-28 14:59 | LEFT | 0.21667 | 0 | 0 | 0 | Tripped on R-N (Ph-earth) transient fault. FLR: 104.6 kM from Ramagundam end.
7 | RDM-CPR I |  |  |  |  | 0.21667 | 0 | 1.1 | 0 |  | 99.97%
| RDM-CPR II | 304100 | 2014-04-18 06:08 | 2014-04-18 07:30 | LNCC | 0 | 0 | 1.3667 | 0 | Tripped on B-N (Ph-earth) transient fault due to heavy lightning and thunderstorm. FLR: 11.08 kM from Ramagundam end.
8 | RDM-CPR II |  |  |  |  | 0 | 0 | 1.3667 | 0 |  | 100%
| RDM-NSR I | No Trips
9 | RDM-NSR I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| RDM-NSR II | No Trips
10 | RDM-NSR II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| RDM-WGL | No Trips
11 | RDM-WGL |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| WGL-KMM | No Trips
12 | WGL-KMM |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| HYD-NSR | 304079 | 2014-04-13 23:16 | 2014-04-13 23:16 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 159 kM from Nagarjunasagar end.
13 | HYD-NSR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| HYD-KNL | 304053 | 2014-04-09 18:51 | 2014-04-09 18:51 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 200 kM from Hyderabad end.
14 | HYD-KNL |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NSR-KDP I | No Trips
15 | NSR-KDP I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NSR-KDP II | No Trips
16 | NSR-KDP II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KMM-NSR | No Trips
17 | KMM-NSR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KMM-VJA | No Trips
18 | KMM-VJA |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NSR-KLN | 304020 | 2014-04-05 16:25 | 2014-04-05 17:27 | OMST | 1.0333 | 0 | 0 | 0 | Shut down availed for removing concrete mixer machine from switchyard which got stuck near LA vide SRLDC code no. CR-04/114.
| NSR-KLN | 304076 | 2014-04-13 17:08 | 2014-04-13 17:08 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 65.6 kM from Nagarjunasagar end.
| NSR-KLN | 304175 | 2014-04-26 07:38 | 2014-04-26 20:21 | LCSD | 0 | 0 | 0 | 12.7167 | Shut down availed for balance LILO construction works and OPGW termination at LILO point vide SRLDC code no. CR-04/644.
19 | NSR-KLN |  |  |  |  | 1.0333 | 0 | 0 | 12.7167 |  | 99.86%
| KLN-GTY I | 304001 | 2014-04-01 15:43 | 2014-04-01 15:54 | OMST | 0.18333 | 0 | 0 | 0 | Tripped at Gooty end only on receipt of direct trip signal.
| KLN-GTY I | 304012 | 2014-04-03 16:09 | 2014-04-03 16:40 | SBBT | 0.51667 | 0 | 0 | 0 | Tripped on operation of Busbar protection due to 400KV Gooty - New Raichur line I main bay B -phae CT failure at Gooty SS.
| KLN-GTY I | 304038 | 2014-04-07 10:50 | 2014-04-07 11:48 | OMST | 0.96667 | 0 | 0 | 0 | Tripped due to suspected PLCC maloperation at Kurnool new SS.
| KLN-GTY I | 304176 | 2014-04-26 07:41 | 2014-04-26 20:45 | LCSD | 0 | 0 | 0 | 13.0667 | Shut down availed for balance LILO construction works and OPGW termination at LILO point vide SRLDC code no. CR-04/645.
20 | KLN-GTY I |  |  |  |  | 1.6667 | 0 | 0 | 13.0667 |  | 99.77%
| NSR-MBN | No Trips
21 | NSR-MBN |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| MBN-RCR | No Trips
22 | MBN-RCR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| RCR-MBD | 304109 | 2014-04-19 07:03 | 2014-04-19 20:48 | OSPD | 0 | 0 | 0 | 13.75 | Shut down availed by M/s RSTCL for power line crossing works of 765 KV Raichur - Sholapur line vide SRLDC code no. CR-04/397.
23 | RCR-MBD |  |  |  |  | 0 | 0 | 0 | 13.75 |  | 100%
| VJA- GWK | No Trips
24 | VJA- GWK |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| VJA-NLR I | 304037 | 2014-04-07 03:50 | 2014-04-07 14:35 | LHWT | 10.75 | 0 | 0 | 0 | Tripped on Y-N fault due to decapping of Y-phase insulator at loc. 451.
| VJA-NLR I | 304040 | 2014-04-08 06:06 | 2014-04-08 13:10 | LHWT | 7.0667 | 0 | 0 | 0 | Tripped on Y-N fault due to Y-phase insulator decapping at loc. 290.
| VJA-NLR I | 304102 | 2014-04-18 08:33 | 2014-04-19 20:31 | LCSD | 0 | 0 | 0 | 35.9667 | Shut down availed for construction works of new 400KV Vijayawada-Nellore D/C line vide SRLDC code no. CR-04/371.
| VJA-NLR I | 304204 | 2014-04-30 09:16 | 2014-04-30 12:37 | LCSD | 0 | 0 | 0 | 3.35 | Shut down availed for construction works of 765 kV Nellore - Kurnool D/C line vide SRLDC code no. CR-04/769.
25 | VJA-NLR I |  |  |  |  | 17.8167 | 0 | 0 | 39.3167 |  | 97.53%
| VJA-NLR II | 304052 | 2014-04-09 16:14 | 2014-04-09 16:14 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 275 kM from Vijayawada end.
| VJA-NLR II | 304103 | 2014-04-18 09:00 | 2014-04-19 20:37 | LCSD | 0 | 0 | 0 | 35.6167 | Shut down availed for construction works of new 400KV Vijayawada-Nellore D/C line vide SRLDC code no. CR-04/372.
26 | VJA-NLR II |  |  |  |  | 0 | 0 | 0 | 35.6167 |  | 100%
| VJA-VMG III | No Trips
27 | VJA-VMG III |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| VJA-VMG IV | No Trips
28 | VJA-VMG IV |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| VMG-SMD I | No Trips
29 | VMG-SMD I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| SMD-GWK I | 304063 | 2014-04-11 12:17 | 2014-04-11 12:51 | OMSU | 0 | 0.56667 | 0 | 0 | Charging delayed by M/s NTPC Simhadri vide message no: CP 04 /298.
| SMD-GWK I | 304062 | 2014-04-11 10:41 | 2014-04-11 12:17 | OSPT | 1.6 | 0 | 0 | 0 | Shut down availed for replacement of R-Phase & B-Phase CTs at Gajuwaka SS vide SRLDC code no. CR-04/248.
30 | SMD-GWK I |  |  |  |  | 1.6 | 0.56667 | 0 | 0 |  | 99.78%
| VMG-SMD II | No Trips
31 | VMG-SMD II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| SMD-GWK II | No Trips
32 | SMD-GWK II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| JEY-GWK I | 304141 | 2014-04-21 22:40 | 2014-04-21 23:06 | OMST | 0.43333 | 0 | 0 | 0 | Tripped due to tripping of filter bus on operation of BFR protection of Pole I filter main breaker.
33 | JEY-GWK I |  |  |  |  | 0.43333 | 0 | 0 | 0 |  | 99.94%
| JEY-GWK II | No Trips
34 | JEY-GWK II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NLR-ALM | No Trips
35 | NLR-ALM |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NLR-SPDR | No Trips
36 | NLR-SPDR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| ALM-CNI | 304004 | 2014-04-02 04:02 | 2014-04-02 04:02 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 2.06 kM from Sriperumbudur end.
37 | ALM-CNI |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KNL-GTY | 304011 | 2014-04-03 16:09 | 2014-04-03 16:48 | SBBT | 0.65 | 0 | 0 | 0 | Tripped on operation of Busbar protection due to 400KV Gooty - New Raichur line I main bay B -phae CT failure at Gooty SS.
38 | KNL-GTY |  |  |  |  | 0.65 | 0 | 0 | 0 |  | 99.91%
| GTY-RCN I | 304009 | 2014-04-03 16:09 | 2014-04-03 23:52 | SBBT | 7.7167 | 0 | 0 | 0 | Tripped on operation of Busbar protection due to main bay B-phase CT failure at Gooty SS.
39 | GTY-RCN I |  |  |  |  | 7.7167 | 0 | 0 | 0 |  | 98.93%
| RCN-RCR I | No Trips
40 | RCN-RCR I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| GTY-RCN II | 304010 | 2014-04-03 16:09 | 2014-04-03 17:31 | SBBT | 1.3667 | 0 | 0 | 0 | Tripped on operation of Busbar protection due to 400KV Gooty - New Raichur line I main bay B -phae CT failure at Gooty SS.
41 | GTY-RCN II |  |  |  |  | 1.3667 | 0 | 0 | 0 |  | 99.81%
| RCN-RCR II | No Trips
42 | RCN-RCR II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| GTY-NLM | 304018 | 2014-04-05 11:24 | 2014-04-05 12:04 | OSPD | 0 | 0 | 0 | 0.66667 | Shut down availed by M/s KPTCL for new ICT-3 construction works at Nelamangala end vide SRLDC code no. CR-04/102.
43 | GTY-NLM |  |  |  |  | 0 | 0 | 0 | 0.66667 |  | 100%
| NPS-NLR I | No Trips
44 | NPS-NLR I |  |  |  |  | 0 | 0 | 0 | 0
| NPS-NLR II | 304142 | 2014-04-22 01:58 | 2014-04-22 02:42 | OMSU | 0 | 0.73333 | 0 | 0 | Tripped on operation of Zone-2 distance protection due to fault in Manubolu - Krishnapatnam 400 kV APTRANSCO line.
45 | NPS-NLR II |  |  |  |  | 0 | 0.73333 | 0 | 0 |  | 100%
| MEPL-NPS | 304205 | 2014-04-30 10:24 | 2014-04-30 16:06 | OSPD | 0 | 0 | 0 | 5.7 | Shut down availed by M/s MEPL for rectification of sparking at loc. 6 (MEPL portion) vide SRLDC code no. CR-04/771.
46 | MEPL-NPS |  |  |  |  | 0 | 0 | 0 | 5.7 |  | 100%
| SEPL-NPS | 304080 | 2014-04-14 06:35 | 2014-04-14 14:01 | OSPD | 0 | 0 | 0 | 7.4333 | Shut down availed by M/s SEPL for attending hot spot in the SEPL portion of the Line vide SRLDC code no. CR-04/313.
47 | SEPL-NPS |  |  |  |  | 0 | 0 | 0 | 7.4333 |  | 100%
| GTY-NPS I | 304160 | 2014-04-24 06:03 | 2014-04-25 20:00 | LCSD | 0 | 0 | 0 | 37.95 | Shut down availed for construction works of 765 kV Thiruvelam - Kurnool D/C line vide SRLDC code no. CR-04/562.
48 | GTY-NPS I |  |  |  |  | 0 | 0 | 0 | 37.95 |  | 100%
| GTY-NPS II | 304161 | 2014-04-24 06:04 | 2014-04-25 20:00 | LCSD | 0 | 0 | 0 | 37.9333 | Shut down availed for construction works of 765 kV Thiruvelam - Kurnool D/C line vide SRLDC code no. CR-04/563.
49 | GTY-NPS II |  |  |  |  | 0 | 0 | 0 | 37.9333 |  | 100%
| NPS-TPCIL I | No Trips
50 | NPS-TPCIL I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NPS-TPCIL II | No Trips
51 | NPS-TPCIL II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| ALM-VAL I | 304108 | 2014-04-19 03:27 | 2014-04-19 19:51 | OMSU | 0 | 16.4 | 0 | 0 | Auto reclosed successfully at Almathy end on R-N fault due to heavy pollution being released from NTECL Vallur. Tripped at Vallur end only. Line charging delayed by Vallur SS. FLR: 3.1 kM from Vallur end
| ALM-VAL I | 304122 | 2014-04-20 23:10 | 2014-04-21 04:41 | LVRD | 0 | 0 | 0 | 5.5167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/442.
| ALM-VAL I | 304112 | 2014-04-20 03:51 | 2014-04-20 22:03 | OMSU | 0 | 18.2 | 0 | 0 | Auto reclosed successfully at Almathy end on R-N (Ph-earth) transient fault due to heavy pollution being released by NTECL Vallur. Tripped at Vallur end only. FLR: 31.8 KM from Almathy end.
| ALM-VAL I | 304128 | 2014-04-21 04:47 | 2014-04-21 16:44 | OMSU | 0 | 11.95 | 0 | 0 | Tripped on R-N fault due to decapping of R-phase insulator at loc. 105 due to heavy pollution being released from NTECL Vallur.
| ALM-VAL I | 304146 | 2014-04-22 09:00 | 2014-04-22 19:03 | OMSU | 0 | 10.05 | 0 | 0 | Shut down availed to replace disc insulators with polymer insulators in the polluted strech near NTECL Vallur vide SRLDC code CR-04/497.
| ALM-VAL I | 304153 | 2014-04-23 07:55 | 2014-04-23 17:13 | OMSU | 0 | 9.3 | 0 | 0 | Shut down availed to replace disc insulators with polymer insulators in the polluted strech near NTECL Vallur vide SRLDC code CR-04/532.
| ALM-VAL I | 304193 | 2014-04-29 08:13 | 2014-04-29 19:18 | OMSU | 0 | 11.0833 | 0 | 0 | Shut down availed for replacement of porcelain insulators with polymer insulators to avoid frequent tripping of the line due to pollution being released from NTECL Vallur vide SRLDC code no. CR-04/740.
52 | ALM-VAL I |  |  |  |  | 0 | 76.9833 | 0 | 5.5167 |  | 100%
| ALM-VAL II | 304107 | 2014-04-18 18:58 | 2014-04-18 20:24 | OMSU | 0 | 1.4333 | 0 | 0 | Line charging delayed by NTECL Vallur SS.
| ALM-VAL II | 304097 | 2014-04-18 01:55 | 2014-04-18 18:58 | OMSU | 0 | 17.05 | 0 | 0 | Tripped on Y-N fault due to decapping of Y-phase insulator at loc. 55 due to heavy pollution being released from NTECL Vallur.
| ALM-VAL II | 304110 | 2014-04-19 12:33 | 2014-04-19 19:52 | OMSU | 0 | 7.3167 | 0 | 0 | Shut down availed to facilitate replacement of decapped insulator in 400KV Vallur - Almathy line-I which is caused by heavy pollution being released by NTECL Vallur vide SRLDC code no. CR-04/401.
| ALM-VAL II | 304116 | 2014-04-20 03:57 | 2014-04-20 20:32 | OMSU | 0 | 16.5833 | 0 | 0 | Tripped on R-B fault due to heavy pollution being released from NTECL Vallur. FLR: 34.8 kM from Almathy end.
| ALM-VAL II | 304137 | 2014-04-21 10:10 | 2014-04-21 16:44 | OMSU | 0 | 6.5667 | 0 | 0 | Shut down availed to replace disc insulators with polymer insulators in the polluted strech near NTECL Vallur vide SRLDC code CR-04/464.
| ALM-VAL II | 304147 | 2014-04-22 09:01 | 2014-04-22 19:03 | OMSU | 0 | 10.0333 | 0 | 0 | Shut down availed to replace disc insulators with polymer insulators in the polluted strech near NTECL Vallur vide SRLDC code CR-04/498.
| ALM-VAL II | 304154 | 2014-04-23 07:55 | 2014-04-23 17:28 | OMSU | 0 | 9.55 | 0 | 0 | Shut down availed to replace disc insulators with polymer insulators in the polluted strech near NTECL Vallur vide SRLDC code CR-04/533.
| ALM-VAL II | 304194 | 2014-04-29 08:14 | 2014-04-29 19:45 | OMSU | 0 | 11.5167 | 0 | 0 | Shut down availed for replacement of porcelain insulators with polymer insulators to avoid frequent tripping of the line due to pollution being released from NTECL Vallur vide SRLDC code no. CR-04/741.
53 | ALM-VAL II |  |  |  |  | 0 | 80.05 | 0 | 0 |  | 100%
| VAL-KVP I | 304006 | 2014-04-03 06:45 | 2014-04-03 18:12 | OMSU | 0 | 11.45 | 0 | 0 | Tripped on R-N fault due to jumper cut near wave trap inside Vallur (NTECL SS) switch yard due to heavy pollution.
| VAL-KVP I | 304016 | 2014-04-05 05:19 | 2014-04-05 05:19 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 136.3 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304028 | 2014-04-06 06:10 | 2014-04-06 06:10 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 142.2 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304030 | 2014-04-06 06:23 | 2014-04-06 06:23 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 153.8 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304032 | 2014-04-06 06:32 | 2014-04-08 13:05 | OMSU | 0 | 54.55 | 0 | 0 | Tripped on Y-N fault due to conductor snapping inside Vallur (NTECL SS) switch yard due to heavy pollution.
| VAL-KVP I | 304031 | 2014-04-06 06:31 | 2014-04-06 06:31 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 146.7 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304045 | 2014-04-08 21:00 | 2014-04-09 03:28 | OMSU | 0 | 6.4667 | 0 | 0 | Tripped on B-N fault due to insulator flash over inside Vallur (NTECL SS) switch yard due to heavy pollution. FLR : 152.1 km from Kalivindapattu end.
| VAL-KVP I | 304054 | 2014-04-09 19:47 | 2014-04-10 18:01 | OMSU | 0 | 22.2333 | 0 | 0 | Tripped on R-N fault due to Jumper cut inside Vallur (NTECL SS) switch yard.
| VAL-KVP I | 304065 | 2014-04-11 19:37 | 2014-04-11 19:37 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 142.2 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304066 | 2014-04-11 19:51 | 2014-04-11 22:14 | OMSU | 0 | 2.3833 | 0 | 0 | Tripped on B-N fault due to fault inside Vallur (NTECL SS) Switch yard due to heavy pollution. FLR: 147.8 km from Kalivindapattu end.
| VAL-KVP I | 304072 | 2014-04-12 14:40 | 2014-04-12 16:22 | GOMD | 0 | 0 | 0 | 1.7 | Synchronisation delayed due to system constraints.
| VAL-KVP I | 304069 | 2014-04-12 06:43 | 2014-04-12 14:40 | OMSU | 0 | 7.95 | 0 | 0 | Shut down availed for rectification of defect in tension insulator string at loc. 121 in multi circuit portion which got damaged due to heavy pollution being released from NTECL Vallur vide SRLDC code no. CR-04/ 271.
| VAL-KVP I | 304077 | 2014-04-13 21:06 | 2014-04-13 22:11 | SEFT | 0 | 1.08 | 0 | 0 | Tripped on operation of Bus-bar protection due to Vallur-I main bay B-Phase CT failure at Kalivindapattu SS.
| VAL-KVP I | 304075 | 2014-04-13 04:31 | 2014-04-13 04:31 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 133 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304082 | 2014-04-14 21:47 | 2014-04-14 22:28 | OMSU | 0 | 0.68333 | 0 | 0 | Tripped at NTECL Vallur end only due to heavy pollution. Auto reclosed successfully at Kalivinapattu end on R-N fault. FLR:142 km from Kalivindapattu end. Fault is in Vallur switch yard.
| VAL-KVP I | 304081 | 2014-04-14 15:04 | 2014-04-14 19:01 | OSPT | 0 | 3.95 | 0 | 0 | Shut down availed for replacing damaged support insulator stack of 40489A isolator at Kalivindapattu end vide SRLDC code no. CR-04/316.
| VAL-KVP I | 304083 | 2014-04-15 03:08 | 2014-04-16 13:25 | OMSU | 0 | 34.2833 | 0 | 0 | Tripped on Y-B fault due to decapping of B-phase insulator string at loc. 121 due to heavy pollution being released from NTECL Vallur..
| VAL-KVP I | 304096 | 2014-04-17 23:36 | 2014-04-19 18:07 | OMSU | 0 | 42.5167 | 0 | 0 | Tripped at NTECL Vallur end only on R-N fault due to heavy pollution. Auto reclosed successfully at Kalivindapattu end. FLR: 142 kM from Kalivindapattu end. Fault is in NTECL switch yard.
| VAL-KVP I | 304089 | 2014-04-17 03:31 | 2014-04-17 03:31 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 152.4 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304090 | 2014-04-17 04:05 | 2014-04-17 04:05 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 125.1 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304091 | 2014-04-17 04:17 | 2014-04-17 04:17 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 131.9 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304092 | 2014-04-17 06:20 | 2014-04-17 06:20 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 123.9 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304094 | 2014-04-17 21:03 | 2014-04-17 21:03 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 130.7 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304095 | 2014-04-17 22:43 | 2014-04-17 22:43 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 120.2 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304120 | 2014-04-20 04:50 | 2014-04-20 10:29 | OMSU | 0 | 5.65 | 0 | 0 | Tripped on R-N fault due to heavy pollution being released from NTECL vallur. FLR: 125.8 kM from Kalivindapattu end.
| VAL-KVP I | 304114 | 2014-04-20 03:54 | 2014-04-20 03:54 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP I | 304117 | 2014-04-20 03:58 | 2014-04-20 03:58 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP I | 304119 | 2014-04-20 04:07 | 2014-04-20 04:07 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 121 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304123 | 2014-04-21 03:34 | 2014-04-21 03:34 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP I | 304126 | 2014-04-21 04:03 | 2014-04-21 08:25 | OMSU | 0 | 4.3667 | 0 | 0 | Hand tripped as per SRLDC instruction on NTECL Vallur request to avoid tripping due to pollution vide SRLDC code no. CR-04/448.
| VAL-KVP I | 304138 | 2014-04-21 17:02 | 2014-04-21 19:25 | OMSU | 0 | 2.3833 | 0 | 0 | Shut down availed to replace pilot insulators at loc. 120 & 120/1 to avoid tripping due to pollution being released from NTECL Vallur vide SRLDC code no. CR-04/472.
| VAL-KVP I | 304124 | 2014-04-21 03:46 | 2014-04-21 03:46 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP I | 304159 | 2014-04-24 04:28 | 2014-04-24 04:28 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 143.3 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP I | 304166 | 2014-04-25 02:40 | 2014-04-25 18:01 | LVRD | 0 | 0 | 0 | 15.35 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/601.
| VAL-KVP I | 304178 | 2014-04-26 08:11 | 2014-04-26 20:18 | OMSU | 0 | 12.1167 | 0 | 0 | Shut down availed for replacement of decapped insulator at loc no 115 & 116 due to heavy pollution being released by NTECL Vallur vide SRLDC code no. CR-04/646.
54 | VAL-KVP I |  |  |  |  | 0 | 212.0633 | 0 | 17.05 |  | 100%
| VAL-KVP II | 304033 | 2014-04-06 06:48 | 2014-04-06 06:48 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 142.2 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP II | 304046 | 2014-04-08 22:55 | 2014-04-08 22:55 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 123.6 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP II | 304051 | 2014-04-09 15:48 | 2014-04-09 18:31 | OSPD | 0 | 0 | 0 | 2.7167 | Shut down availed by M/s NTECL for replacement of damaged Y phase terminal connector at Vallur end vide SRLDC code no. CR-04/203.
| VAL-KVP II | 304073 | 2014-04-12 14:40 | 2014-04-12 17:04 | GOMD | 0 | 0 | 0 | 2.4 | Synchronisation delayed due to system constraints.
| VAL-KVP II | 304070 | 2014-04-12 07:09 | 2014-04-12 14:40 | OMSU | 0 | 7.5167 | 0 | 0 | Shut down availed to facilitate insulator replacement in 400KV Kalivindapattu- Vallur I in multi-circuit portion which got damaged due to heavy pollution being released from NTECL Vallur vide SRLDC code no. CR-04/272.
| VAL-KVP II | 304078 | 2014-04-13 21:06 | 2014-04-13 21:58 | SEFT | 0 | 5.12 | 0 | 0 | Tripped on operation of Bus-bar protection due to Vallur-I main bay B-Phase CT failure at Kalivindapattu SS.
| VAL-KVP II | 304085 | 2014-04-16 05:28 | 2014-04-16 13:27 | OMSU | 0 | 7.9833 | 0 | 0 | Shut down availed to facilitate rectification of decapping in Kalavindapattu - Vallur line-1 (multi circuit tower) due to heavy pollution being released from NTECL Vallur vide SRLDC code no. CR-04/339.
| VAL-KVP II | 304087 | 2014-04-17 03:16 | 2014-04-17 03:16 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 150.8 kM from Kalivindapattu end due to heavy pollution.
| VAL-KVP II | 304088 | 2014-04-17 03:25 | 2014-04-17 16:06 | OMSU | 0 | 12.6833 | 0 | 0 | Tripped on Y-N fault due to wave trap jumper cut at NTECL Vallur SS due to heavy pollution.
| VAL-KVP II | 304093 | 2014-04-17 20:01 | 2014-04-19 06:10 | OMSU | 0 | 34.15 | 0 | 0 | Tripped on Y-B fault due to fault in NTECL Vallur switch yard due to heavy pollution. FLR:134.9 km from Kalivindapattu end.
| VAL-KVP II | 304118 | 2014-04-20 03:58 | 2014-04-20 10:50 | OMSU | 0 | 6.8667 | 0 | 0 | Tripped on B-N fault due to heavy pollution being released by NTECL Vallur. FLR: 139.3 kM from Kalivindapattu end. Fault occured in Vallur switch yard.
| VAL-KVP II | 304113 | 2014-04-20 03:52 | 2014-04-20 03:52 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304115 | 2014-04-20 03:54 | 2014-04-20 03:54 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304111 | 2014-04-20 03:40 | 2014-04-20 03:40 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304125 | 2014-04-21 03:50 | 2014-04-21 03:50 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304127 | 2014-04-21 04:21 | 2014-04-21 04:21 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304132 | 2014-04-21 06:01 | 2014-04-21 06:01 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304129 | 2014-04-21 04:47 | 2014-04-21 04:47 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304131 | 2014-04-21 05:15 | 2014-04-21 05:15 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304130 | 2014-04-21 04:50 | 2014-04-21 04:50 | LART | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault due to heavy pollution.
| VAL-KVP II | 304139 | 2014-04-21 17:06 | 2014-04-21 19:39 | OMSU | 0 | 2.55 | 0 | 0 | Shut down availed to replace pilot insulators at loc. 120 & 120/1 to avoid tripping due to pollution being released from NTECL Vallur vide SRLDC code no. CR-04/473.
| VAL-KVP II | 304169 | 2014-04-25 08:33 | 2014-04-25 18:05 | OMSU | 0 | 9.5333 | 0 | 0 | Shut down availed for replacement of decapped insulator at loc no 115 due to heavy pollution being released from NTECL Vallur vide SRLDC code no. CR-04/606.
| VAL-KVP II | 304177 | 2014-04-26 08:06 | 2014-04-26 20:19 | OMSU | 0 | 12.2167 | 0 | 0 | Shut down availed for replacement of decapped insulator at loc no 115 & 116 due to heavy pollution being released by NTECL Vallur vide SRLDC code no. CR-04/647.
55 | VAL-KVP II |  |  |  |  | 0 | 98.62 | 0 | 5.1167 |  | 100%
| NLR-TVL I | 304207 | 2014-04-30 17:32 | 2014-04-30 18:59 | OSPD | 0 | 0 | 0 | 1.45 | Hand tripped on SRLDC instruction for testing telemetry data vide SRLDC code no. CR-04/785.
56 | NLR-TVL I |  |  |  |  | 0 | 0 | 0 | 1.45 |  | 100%
| NLR-TVL II | 304206 | 2014-04-30 16:30 | 2014-04-30 17:18 | OSPD | 0 | 0 | 0 | 0.8 | Hand tripped on SRLDC instruction for testing telemetry data vide SRLDC code no. CR-04/782.
57 | NLR-TVL II |  |  |  |  | 0 | 0 | 0 | 0.8 |  | 100%
| KNL-KLN I | No Trips
58 | KNL-KLN I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KNL-KLN II | No Trips
59 | KNL-KLN II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| RCN-SLR I | No Trips
60 | RCN-SLR I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
GRAND TOTAL | [5 empty] | 36.2 | 469.4333 | 2.4667 | 234.0833

## ICT
Sl No | Name of Line ICT | Event ID | Trip Date Time | Restoration Date Time | Cate Code | Outage PG | Outage Others | Outage System | Outage Deemed | Remarks | Availability
| CUDDAPAH ICT I | 304026 | 2014-04-06 01:55 | 2014-04-06 03:15 | OMSU | 0 | 1.3333 | 0 | 0 | Tripped due to CT blasting at 220kV Chinakampalli (APTRANSCO) SS.
1 | CUDDAPAH ICT I |  |  |  |  | 0 | 1.3333 | 0 | 0 |  | 100%
| CUDDAPAH ICT II | 304027 | 2014-04-06 01:55 | 2014-04-06 03:13 | OMSU | 0 | 1.3 | 0 | 0 | Tripped due to CT blasting at 220kV Chinakampalli (APTRANSCO) SS.
2 | CUDDAPAH ICT II |  |  |  |  | 0 | 1.3 | 0 | 0 |  | 100%
| GAJUWAKA ICT I | 304048 | 2014-04-09 07:23 | 2014-04-09 13:04 | OSPD | 0 | 0 | 0 | 5.6833 | Shut down availed by M/s APTRANSCO for cleaning of insulator in their switch yard vide SRLDC code no. CR-04/188.
3 | GAJUWAKA ICT I |  |  |  |  | 0 | 0 | 0 | 5.6833 |  | 100%
| GAZUWAKA ICT II | No Trips
4 | GAZUWAKA ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| GOOTY ICT I | 304013 | 2014-04-03 16:09 | 2014-04-03 16:44 | SBBT | 0.58333 | 0 | 0 | 0 | Tripped on operation of Busbar protection due to 400KV Gooty - New Raichur line I main bay B -phae CT failure at Gooty SS.
5 | GOOTY ICT I |  |  |  |  | 0.58333 | 0 | 0 | 0 |  | 99.92%
| GOOTY ICT II | 304014 | 2014-04-03 16:09 | 2014-04-03 16:51 | SBBT | 0.7 | 0 | 0 | 0 | Tripped on operation of Busbar protection due to 400KV Gooty - New Raichur line I main bay B -phae CT failure at Gooty SS.
6 | GOOTY ICT II |  |  |  |  | 0.7 | 0 | 0 | 0 |  | 99.9%
| HYDERABAD ICT - I | 304064 | 2014-04-11 17:07 | 2014-04-11 17:23 | SCSD | 0 | 0 | 0 | 0.26667 | Tripped 220 kV side only during NTAMC work at Hyderabad SS.
7 | HYDERABAD ICT - I |  |  |  |  | 0 | 0 | 0 | 0.26667 |  | 100%
| HYDERABAD ICT - II | No Trips
8 | HYDERABAD ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| HYDERABAD ICT - III | No Trips
9 | HYDERABAD ICT - III |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KHAMMAM ICT I | No Trips
10 | KHAMMAM ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KHAMMAM ICT II | No Trips
11 | KHAMMAM ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| MUNIRABAD ICT I | No Trips
12 | MUNIRABAD ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| MUNIRABAD ICT II | 304181 | 2014-04-26 10:28 | 2014-04-26 10:41 | OMST | 0.21667 | 0 | 0 | 0 | Tripped 220 kV side only while doing monthly maintenance due to loose contact in PD wiring.
13 | MUNIRABAD ICT II |  |  |  |  | 0.21667 | 0 | 0 | 0 |  | 99.97%
| NAGARJUNASAGAR ICT - I | No Trips
14 | NAGARJUNASAGAR ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NAGARJUNASAGAR ICT - II | No Trips
15 | NAGARJUNASAGAR ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NAGARJUNASAGAR ICT - III | No Trips
16 | NAGARJUNASAGAR ICT - III |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| VIJAYAWADA ICT I | No Trips
17 | VIJAYAWADA ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| VIJAYAWADA ICT II | No Trips
18 | VIJAYAWADA ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| WARANGAL ICT I | No Trips
19 | WARANGAL ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| WARANGAL ICT II | No Trips
20 | WARANGAL ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NEW RAICHUR 765/400kV ICT I | 304019 | 2014-04-05 11:29 | 2014-04-05 12:14 | OMST | 0.75 | 0 | 0 | 0 | Tripped on operation of differential Protection while opening main bay isolator for CT oil sampling.
21 | NEW RAICHUR 765/400kV ICT I |  |  |  |  | 0.75 | 0 | 0 | 0 |  | 99.9%
| NEW RAICHUR 765/400kV ICT II | No Trips
22 | NEW RAICHUR 765/400kV ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| NELLORE PS - 765/400kV ICT-II | 304165 | 2014-04-24 11:24 | 2014-04-24 17:34 | OMST | 6.1667 | 0 | 0 | 0 | Shut down availed for fixing of fire fighting accessories vide SRLDC code no. CR-04/569.
23 | NELLORE PS - 765/400kV ICT-II |  |  |  |  | 6.1667 | 0 | 0 | 0 |  | 99.14%
| NELLORE PS - 765/400kv ICT-III | No Trips
24 | NELLORE PS - 765/400kv ICT-III |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KURNOOL 765/400kV ICT I | No Trips
25 | KURNOOL 765/400kV ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| KURNOOL 765/400kV ICT II | No Trips
26 | KURNOOL 765/400kV ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
GRAND TOTAL | [5 empty] | 8.4167 | 2.6333 | 0 | 5.95

## BR & SWRs
Sl No | Name of Line ICT | Event ID | Trip Date Time | Restoration Date Time | Cate Code | Outage PG | Outage Others | Outage System | Outage Deemed | Remarks | Availability
| CUDDAPAH BUS REACTOR | 303103 | 2014-04-01 | 2014-04-20 22:45 | SVRD | 0 | 0 | 0 | 478.75 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/555.
| CUDDAPAH BUS REACTOR | 304171 | 2014-04-25 09:04 | 2014-05-01 | SVRD | 0 | 0 | 0 | 134.9333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/614.
1 | CUDDAPAH BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 613.6833 |  | 100%
| GOOTY BUS REACTOR | 303032 | 2014-04-01 | 2014-04-25 22:14 | SVRD | 0 | 0 | 0 | 598.2333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/201.
2 | GOOTY BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 598.2333 |  | 100%
| KHAMMAM BUS REACTOR | 304017 | 2014-04-05 09:36 | 2014-04-05 18:51 | OSPT | 9.25 | 0 | 0 | 0 | Shut down availed for LA replacement works and AMP works vide SRLDC code no. CR-04/101.
3 | KHAMMAM BUS REACTOR |  |  |  |  | 9.25 | 0 | 0 | 0 |  | 98.72%
| NAGARJUNASAGAR BUS REACTOR | No Trips
4 | NAGARJUNASAGAR BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| VIJAYAWADA BUS REACTOR | No Trips
5 | VIJAYAWADA BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| VISAKHAPATNAM BUS REACTOR | 304184 | 2014-04-27 11:31 | 2014-05-01 | SVRD | 0 | 0 | 0 | 84.4833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/694.
6 | VISAKHAPATNAM BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 84.4833 |  | 100%
| NELLORE BUS REACTOR | 304173 | 2014-04-25 09:11 | 2014-04-25 22:11 | SVRD | 0 | 0 | 0 | 13 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/613.
7 | NELLORE BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 13 |  | 100%
| HYDERABAD BUS REACTOR | No Trips
8 | HYDERABAD BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| MUNIRABAD BUS REACTOR | 303102 | 2014-04-01 | 2014-05-01 | SVRD | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/528.
9 | MUNIRABAD BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 720 |  | 100%
| NML LR G-N | 303136 | 2014-04-01 | 2014-05-01 | SVRD | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/205.
10 | NML LR G-N |  |  |  |  | 0 | 0 | 0 | 720 |  | 100%
| RAICHUR BUS REACTOR | 303042 | 2014-04-01 | 2014-04-13 19:14 | SVRD | 0 | 0 | 0 | 307.2333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/269.
| RAICHUR BUS REACTOR | 304104 | 2014-04-18 14:50 | 2014-05-01 | SVRD | 0 | 0 | 0 | 297.1667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/376.
11 | RAICHUR BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 604.4 |  | 100%
| NPS BUS REACTOR | 303107 | 2014-04-01 | 2014-04-15 01:49 | SVRD | 0 | 0 | 0 | 337.8167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/560.
| NPS BUS REACTOR | 304172 | 2014-04-25 09:05 | 2014-04-25 21:54 | SVRD | 0 | 0 | 0 | 12.8167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/612.
| NPS BUS REACTOR | 304180 | 2014-04-26 10:05 | 2014-04-26 11:06 | OMST | 1.0167 | 0 | 0 | 0 | Tripped due to suspected DC earth fault.
12 | NPS BUS REACTOR |  |  |  |  | 1.0167 | 0 | 0 | 350.6333 |  | 99.86%
| KURNOOL BUS REACTOR | 304163 | 2014-04-24 11:06 | 2014-04-25 22:39 | SVRD | 0 | 0 | 0 | 35.55 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/571.
13 | KURNOOL BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 35.55 |  | 100%
| 765KV RAICHUR - SOLAPUR-I LR | No Trips
14 | 765KV RAICHUR - SOLAPUR-I LR |  |  |  |  | 0 | 0 | 0 | 0
| 765KV RAICHUR - SOLAPUR-II LR | 303106 | 2014-04-01 | 2014-05-01 | SVRD | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/558.
15 | 765KV RAICHUR - SOLAPUR-II LR |  |  |  |  | 0 | 0 | 0 | 720 |  | 100%
| KURNOOL LINE REACTOR AT NPS | No Trips
16 | KURNOOL LINE REACTOR AT NPS |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
GRAND TOTAL | [5 empty] | 10.2667 | 0 | 0 | 4459.9833

## HVDC
Sl No | Name of Line ICT | Event ID | Trip Date Time | Restoration Date Time | Cate Code | Outage PG | Outage Others | Outage System | Outage Deemed | Remarks | Availability
| VZG BTB P I | 304140 | 2014-04-21 22:40 | 2014-04-21 23:02 | OMST | 0.36667 | 0 | 0 | 0 | Tripped due to tripping of filter bus on operation of BFR protection of Pole I filter main breaker.
1 | VZG BTB P I |  |  |  |  | 0.36667 | 0 | 0 | 0 |  | 99.95%
| VZG BTB P II | 304179 | 2014-04-26 08:43 | 2014-04-26 09:06 | OMSU | 0 | 0.38333 | 0 | 0 | Pole blocked due to fire detection trip in valve hall due to smoke coming from the fire from APTRANSCO 220 kV SS.
2 | VZG BTB P II |  |  |  |  | 0 | 0.38333 | 0 | 0 |  | 100%
| TAL-KLR PI | No Trip
3 | TAL-KLR PI |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
| TAL-KLR PII | No Trip
4 | TAL-KLR PII |  |  |  |  | 0 | 0 | 0 | 0 |  | 100%
GRAND TOTAL | [5 empty] | 0.36667 | 0.38333 | 0 | 0