## I EHV LINES & ICT-P1
AC TRANSMISSION LINE/ICT/STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ HVDC (BACK TO BACK STATIONS AND BIPOLE LINKS)/ LINE REACTORS/BUS REACTORS OUTAGE DETAILS OF SR1 FOR THE MONTH OF JANUARY 2013
SL NO | ELEMENT NAME | TRIP DATE/TIME | REST DATE/TIME | OutageDuration |  |  |  | Reasons | Availability
|  |  |  | POWER GRID (SR-1) | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
| ALM-VLR I | 2013-01-22 16:06 | 2013-01-22 18:36 | 0 | 0 | 0 | 2.5 | shut down availed by M/s NTECL for attending oil leakage in the Circuit Breaker at Vallur end vide SRLDC Code no. CR-01/263.
1 | SUB-TOTAL |  |  | 0 | 0 | 0 | 2.5 |  | 100%
| ALM-VAL II | 2013-01-04 11:25 | 2013-01-04 12:21 | 0 | 0 | 0 | 0.93333 | Shut down availed by M/s TNEB for checking of DC leakage at Almathy end vide SRLDC code no. CR-01/20.
| ALM-VAL II | 2013-01-23 15:09 | 2013-01-23 16:40 | 0 | 0 | 0 | 1.5167 | Shut down availed by M/s NTECL for attending oil leakage in the Circuit Breaker at Vallur end vide SRLDC Code no. CR-01/288.
2 | SUB-TOTAL |  |  | 0 | 0 | 0 | 2.45 |  | 100%
| CDP BR | 2013-01-22 09:36 | 2013-01-22 22:01 | 0 | 0 | 0 | 12.4167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/255.
3 | SUB-TOTAL |  |  | 0 | 0 | 0 | 12.4167 |  | 100%
| GTY LR at NLM | 2013-01-22 08:37 | 2013-02-01 | 0 | 0 | 0 | 231.3833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/249.
4 | SUB-TOTAL |  |  | 0 | 0 | 0 | 231.3833 |  | 100%
| GTY-ICT | 2013-01-31 00:31 | 2013-01-31 00:54 | 0 | 0.38333 | 0 | 0 | LV side tripped due to operation of Bus Bar protection at 220KV SS of M/s APTRANSCO.
5 | SUB-TOTAL |  |  | 0 | 0.38333 | 0 | 0 |  | 100%
| GTY-ICT II | 2013-01-31 00:31 | 2013-01-31 00:55 | 0 | 0.4 | 0 | 0 | LV side tripped due to operation of Bus Bar protection at 220KV SS of M/s APTRANSCO.
6 | SUB-TOTAL |  |  | 0 | 0.4 | 0 | 0 |  | 100%
| GTY-NLM | 2013-01-31 23:46 | 2013-02-01 | 0 | 0.23333 | 0 | 0 | Tripped due to flash over of R-phase LA of Talaguppa line reactor at Nelamangala KPTCL SS. Direct trip signal received at Gooty SS.
7 | SUB-TOTAL |  |  | 0 | 0.23333 | 0 | 0 |  | 100%
| GTY-RCR I | 2013-01-02 17:16 | 2013-01-02 17:38 | 0 | 0.36667 | 0 | 0 | Line tripped at Raichur end only due to B-Phase LA failure in Unit -5 GT at Raichur (KPTCL) end.
8 | SUB-TOTAL |  |  | 0 | 0.36667 | 0 | 0 |  | 100%
| GWK-ICT | 2013-01-10 11:03 | 2013-01-10 13:52 | 0 | 0 | 0 | 2.8167 | Shut down availed by M/s APTRANSCO for attending hot spots at 220KV VSS sub-station vide SRLDC code no. CR-01/109.
9 | SUB-TOTAL |  |  | 0 | 0 | 0 | 2.8167 |  | 100%
| HYD-NSR | 2013-01-23 23:13 | 2013-01-23 23:13 | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 152.9 KM from Nagarjunasagar end.
10 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
| JEY-GWK II | 2013-01-20 10:07 | 2013-01-20 18:29 | 8.3667 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-01/226.
11 | SUB-TOTAL |  |  | 8.3667 | 0 | 0 | 0 |  | 98.88%
| KMM-ICT | 2013-01-27 11:18 | 2013-01-27 13:08 | 1.8333 | 0 | 0 | 0 | Shut down availed for attending hot spot in R-phase terminal connector vide SRLDC code no. CR-01/356.
12 | SUB-TOTAL |  |  | 1.8333 | 0 | 0 | 0 |  | 99.75%
| MBD-ICT | 2013-01-24 00:08 | 2013-01-24 02:05 | 0 | 1.95 | 0 | 0 | Tripped on operation of back up over current protection due to delayed clearance of fault in down stream system.
13 | SUB-TOTAL |  |  | 0 | 1.95 | 0 | 0 |  | 100%
| MBD-ICT II | 2013-01-24 00:08 | 2013-01-24 02:37 | 0 | 2.4833 | 0 | 0 | Tripped on operation of back up over current protection due to delayed clearance of fault in down stream system.
14 | SUB-TOTAL |  |  | 0 | 2.4833 | 0 | 0 |  | 100%
| NLR BR | 2013-01-12 06:57 | 2013-01-13 14:25 | 0 | 0 | 0 | 31.4667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/132.
| NLR BR | 2013-01-23 08:03 | 2013-01-23 22:04 | 0 | 0 | 0 | 14.0167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/278.
15 | SUB-TOTAL |  |  | 0 | 0 | 0 | 45.4833 |  | 100%
| NSR-CDP I | 2013-01-08 07:10 | 2013-01-09 14:35 | 0 | 0 | 0 | 31.4167 | Shut down availed for construction of new 400kV Nellore-Gooty D/C line vide SRLDC code no. CR-01/76.
16 | SUB-TOTAL |  |  | 0 | 0 | 0 | 31.4167 |  | 100%
| NSR-CDP II | 2013-01-05 07:10 | 2013-01-06 17:35 | 0 | 0 | 0 | 34.4167 | Shut down availed for stringing works of new 400kV Nellore-Gooty D/C line vide SRLDC code no. CR-01/29.
17 | SUB-TOTAL |  |  | 0 | 0 | 0 | 34.4167 |  | 100%
| NSR-GTY | 2013-01-14 18:03 | 2013-01-14 18:46 | 0 | 0 | 0.71667 | 0 | Line tripped on operation of over voltage protection at Gooty end. Direct trip signal received at Nagarjunasagar end.
18 | SUB-TOTAL |  |  | 0 | 0 | 0.71667 | 0 |  | 100%
| NSR-ICT II | 2013-01-13 10:20 | 2013-01-13 12:16 | 0 | 0 | 0 | 1.9333 | Shut down availed by M/s APTRANSCO to attend hot spots at 220kV Tallapalli SS vide SRLDC Code no.CR-01/151.
19 | SUB-TOTAL |  |  | 0 | 0 | 0 | 1.9333 |  | 100%
| RDM-CPR II | 2013-01-15 12:24 | 2013-01-15 12:57 | 0 | 0 | 0.55 | 0 | Line tripped on operation of over voltage protection at Ramagundam end. Direct trip signal received at Chandrapur end.
| RDM-CPR II | 2013-01-15 11:58 | 2013-01-15 12:24 | 0.43333 | 0 | 0 | 0 | Tripped on R-Y transient fault. FLR: 10.54 KM from Ramagundam end.
| RDM-CPR II | 2013-01-29 11:54 | 2013-01-29 12:07 | 0 | 0 | 0 | 0.21667 | Hand tripped for taking Line reactor at Chandrapur into service for voltage regulation as per SRLDC instructions vide code no. CR-01/407.
20 | SUB-TOTAL |  |  | 0.43333 | 0 | 0.55 | 0.21667 |  | 99.94%
| RDM-NSR I | 2013-01-23 10:21 | 2013-01-23 11:55 | 1.5667 | 0 | 0 | 0 | Shut down availed to attend oil leakage from B phase CVT at Nagarjunasagar end vide SRLDC code no. CR-01/284.
21 | SUB-TOTAL |  |  | 1.5667 | 0 | 0 | 0 |  | 99.79%
| RDM-NSR II | 2013-01-12 10:48 | 2013-01-12 11:55 | 0 | 1.1167 | 0 | 0 | Tripped due to mal-operation of reactor back up protection at Ramagundam end.
22 | SUB-TOTAL |  |  | 0 | 1.1167 | 0 | 0 |  | 100%
| VAL-CNI I | 2013-01-22 16:07 | 2013-01-22 18:08 | 0 | 0 | 0 | 2.0167 | Shut down availed by M/s NTECL for attending oil leakage in the Circuit Breaker at Vallur end vide SRLDC Code no. CR-01/264.
23 | SUB-TOTAL |  |  | 0 | 0 | 0 | 2.0167 |  | 100%
| VAL-CNI II | 2013-01-23 14:58 | 2013-01-23 17:00 | 0 | 0 | 0 | 2.0333 | Shut down availed by M/s NTECL for attending oil leakage in the Circuit Breaker at Vallur end vide SRLDC Code no. CR-01/287.
24 | SUB-TOTAL |  |  | 0 | 0 | 0 | 2.0333 |  | 100%
| VJA-GWK | 2013-01-17 12:08 | 2013-01-20 09:43 | 0 | 0 | 0 | 69.5833 | Shut down availed for line diversion works as per the requirement of M/s Anrak Aluminium ltd. vide SRLDC code no. CR-01/198.
| VJA-GWK | 2013-01-21 10:07 | 2013-01-21 13:10 | 0 | 0 | 0 | 3.05 | Shut down availed for completing the balance OPGW works in the diverted section of the line as requested by M/s Anrak Aluminium Ltd. vide SRLDC code no. CR-01/241.
25 | SUB-TOTAL |  |  | 0 | 0 | 0 | 72.6333 |  | 100%
| VJA-ICT II | 2013-01-11 04:05 | 2013-01-11 04:13 | 0 | 0 | 0.13333 | 0 | Tripped on operation of over load protection.
26 | SUB-TOTAL |  |  | 0 | 0 | 0.13333 | 0 |  | 100%
| VJA-VMG III | 2013-01-20 18:13 | 2013-01-20 18:38 | 0.41667 | 0 | 0 | 0 | Tripped on operation of reactor back up impedance protection at Vijayawada end due to suspected CVT voltage problem.
| VJA-VMG III | 2013-01-20 18:47 | 2013-01-20 19:16 | 0.48333 | 0 | 0 | 0 | Tripped on operation of reactor back up impedance protection at Vijayawada end due to suspected CVT voltage problem.
27 | SUB-TOTAL |  |  | 0.9 | 0 | 0 | 0 |  | 99.88%
| VMG-SMD I | 2013-01-31 07:50 | 2013-02-01 | 0 | 0 | 0 | 16.1667 | Shut down availed for line diversion works as per the requirement of M/s Anrak Aluminium ltd. vide SRLDC code no. CR-01/441.
28 | SUB-TOTAL |  |  | 0 | 0 | 0 | 16.1667 |  | 100%
| VMG-SMD II | 2013-01-31 08:00 | 2013-02-01 | 0 | 0 | 0 | 16 | Shut down availed for line diversion works as per the requirement of M/s Anrak Aluminium ltd. vide SRLDC code no. CR-01/442.
29 | SUB-TOTAL |  |  | 0 | 0 | 0 | 16 |  | 100%
| VSP BR | 2013-01-23 07:00 | 2013-01-23 22:55 | 15.9167 | 0 | 0 | 0 | Shut down availed for AMP works and replacement of 3 Lightning arrestors vide SRLDC code no. CR-01/276.
30 | SUB-TOTAL |  |  | 15.9167 | 0 | 0 | 0 |  | 97.86%
| VSPHVDCB2BPOLE II | 2013-01-04 10:33 | 2013-01-04 10:52 | 0.31667 | 0 | 0 | 0 | Pole blocked on absolute minimum filter not fulfilled due to loss of connectivity.
31 | SUB-TOTAL |  |  | 0.31667 | 0 | 0 | 0 |  | 99.96%
CDP ICT I
32 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
CDP ICT II
33 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
GTY BR
34 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
GTY-RCR II
35 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
GWK ICT II
36 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
GWK-SMH I
37 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
GWK-SMH II
38 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
GWL-HYD
39 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
HYD BR
40 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
HYD ICT I
41 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
HYD ICT II
42 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
HYD ICT III
43 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
HYD-KNL
44 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
HYD-MLK
45 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
JEY-GWK I
46 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
KMM BR
47 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
KMM ICT II
48 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
KMM-NSR
49 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
KMM-VJA
50 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
KNL-GTY
51 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
MBD BR
52 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
MBN-RCR
53 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
NLR-ALM I
54 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
NLR-ALM II
55 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
NSR BR
56 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
NSR ICT I
57 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
NSR ICT III
58 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
NSR-MBN
59 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
RCR-MBD
60 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
RDM-CPR I
61 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
RDM-GWL
62 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
RDM-HYD III
63 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
RDM-HYD IV
64 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
RDM-MLK
65 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
RDM-WGL
66 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
VJA BR
67 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
VJA ICT I
68 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
VJA-NLR I
69 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
VJA-NLR II
70 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
VJA-VMG IV
71 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
VZG BTB P I
72 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
WGL ICT I
73 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
WGL ICT II
74 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
WGL-KMM
75 | SUB-TOTAL |  |  | 0 | 0 | 0 | 0 |  | 100%
|  |  |  | 29.3333 | 6.9333 | 1.4 | 471.3833

## I LR & FSC- P2
AC TRANSMISSION LINE/ICT/STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ HVDC (BACK TO BACK STATIONS AND BIPOLE LINKS)/ LINE REACTORS/BUS REACTORS OUTAGE DETAILS FOR THE MONTH OF JANUARY 2013 | [8 empty] | 31
Sl.No | ELEMENT NAME | Capacity | TRIP DATE/TIME | REST DATE/TIME | OUTAGE DURATION |  |  |  | Availability | Reason
[5 empty] | POWERGRID SR-1 | OTHERS | SYSTEM CONSTRAINT / NATURAL CALAMITY / MILITANCY | DEEMED AVAILABLE
1 | GTY LR at NSR | 50 | [6 empty] | 100%
2 | GWK I LR at VJA | 63 | [6 empty] | 100%
3 | GWL LR at HYD | 50 | [6 empty] | 100%
4 | JEY I LR at GWK | 80 | [6 empty] | 100%
5 | JEY II LR at GWK | 80 | [6 empty] | 100%
6 | MBN LR at NSR | 63 | [6 empty] | 100%
7 | MLK LR at HYD | 50 | [6 empty] | 100%
8 | NLR I LR at VJA | 50 | [6 empty] | 100%
9 | NLR II LR at VJA | 50 | [6 empty] | 100%
10 | NSR I LR at CDP | 50 | [6 empty] | 100%
11 | NSR II LR at CDP | 50 | [6 empty] | 100%
12 | NSR LR at GTY | 50 | [6 empty] | 100%
13 | POLE II ER at GWK | 80 | [6 empty] | 100%
14 | POLE II SR at GWK | 80 | [6 empty] | 100%
15 | RCR LR at MBD | 63 | [6 empty] | 100%
16 | RDM I LR at NSR | 50 | 2013-01-01 | 2013-02-01 |  |  |  | 744
|  |  |  | Sub Total |  |  |  | 744 | 100%
17 | RDM II LR at NSR | 50 | [6 empty] | 100%
18 | SMH I LR at GWK | 63 | [6 empty] | 100%
19 | SMH II LR at GWK | 63 | [6 empty] | 100%
20 | VJA I LR at GWK | 63 | [6 empty] | 100%
21 | VJA I LR at NLR | 50 | [6 empty] | 100%
22 | VJA II LR at NLR | 50 | [6 empty] | 100%
23 | VMG III LR at VJA | 63 | [6 empty] | 100%
24 | VMG IV LR at VJA | 63 | [6 empty] | 100%
25 | WGL LR at KMM | 50 | [6 empty] | 100%
28 | NSR I FSC at CDP | 201.75 | [6 empty] | 100%
|  |  | 2013-01-08 07:04 | 2013-01-09 14:40 |  |  |  | 30.36 |  | Bypassed for Shutdown of NC-1 line for Nellore-Gooty D/c line stringing works
|  |  |  | Sub Total | 0 |  |  |  | 100%
29 | NSR II FSC at CDP | 201.75 | [6 empty] | 100%
30 | FSC-1 at GTY | 181.5 | 2013-01-28 11:57 | 2013-01-28 14:34 |  |  |  | 2.64 | 100% | FSC-II is bypassed manually due to line tripped on receipt of DT | 181.5 MVAR
31 | FSC-2 at GTY | 181.5 | 2013-01-31 23:52 | 2013-02-01 |  |  |  | 0.13333 | 100%
[5 empty] | 0 | 0 |  | 1521.1333
Availability of Inter Regional HVAC transmission system

## II Exceeded Restoration
ELEMENTS WHERE RESTORATION TIME HAS EXCEEDED THE STANDARDS SPECIFIED IN REGULATION 5(B)
2013-01-01
Element Name | Restoration time as specified in Regulation 5 (b) (in days) | Actual restoration time (in days)
NIL | NIL | NIL

## III-Compensation
DETAILS OF COMPENSATION PAID BY THE INTER-STATE TRANSMISSION LICENSEE
2013-01-01
Element Name | Violation of Regulation 5 (a) |  | Violation of Regulation 5 (b) |  | Compensation paid (in Rs.)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in days) | Actual restoration time (in days)
NIL |  |  |  |  | NIL
Total

## V Failures
2013-01-01
Sl. No. | Types of failures | Restoration Time (Days)
A. | Elements of the Transmission line for Single Circuit (S/C), Double Circuit (D/C) and Multi-Circuit (M/C) towers for each kV class separately
1 | Insulator failure | Terrain type
1 | Insulator failure | Plain | River bed |  | Hilly
1 | (i) Insulator failure in single phase | NA | NA |  | NA
1 | (ii) Insulator failure in two phases | NA | NA |  | NA
1 | (iii) Insulator failure in three phases | NA | NA |  | NA
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C, D/C and M/C separately | NA | NA |  | NA
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C, D/C and M/C separately | NA | NA |  | NA
4 | Tower damage (not collapse)
4 | One arm damage | NA | NA |  | NA
4 | Two arms damage | NA | NA |  | NA
5 | Snapping of phase conductor
5 | Conductor snapping in single phase | NA | NA |  | NA
5 | Conductor snapping in two phases | NA | NA |  | NA
5 | Conductor snapping in three phases | NA | NA |  | NA
6 | Failure of earth wire | NA | NA |  | NA
7 | Insulator failure with conductor snapping | NA | NA |  | NA
8 | Any other combination of failures | NA | NA |  | NA
B. | Elements of the sub-station for each kV class separately
1 | Failure of Inter Connecting Transformers (ICTs)
1 | Restoration of the failed ICT
1 | Other major failures in ICTs | Single phase unit |  | Three phase unit
1 | (i) Replacement of faulty bushings | NA | NA |  | NA
1 | (ii) Replacement of failed/ blasted bushings | NA | NA |  | NA
1 | (iii) Replacement of faulty tap changers | NA | NA |  | NA
2 | Failure of Reactors
2 | Restoration of the failed reactor | NA | NA |  | NA