## I-LINES
AC TRANSMISSION LINE/ICT/STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ HVDC (BACK TO BACK STATIONS AND BIPOLE LINKS)/ LINE REACTORS/BUS REACTORS OUTAGE DETAILS OF SR1 FOR THE MONTH OF JUNE 2013
| ELEMENT NAME | EVENT NO | TRIP DATE/TIME | REST DATE/TIME | OutageDuration |  |  |  | TRIP CODE | Reasons | % Availability
[5 empty] | POWER GRID (SR-1) | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
AC TRANSMISSION LINES
| ALM-CNI II | No Trip |  |  | 0 | 0 | 0 | 0
1 | ALM-CNI II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| ALM-VLR I | No Trip |  |  | 0 | 0 | 0 | 0
2 | ALM-VLR I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| ALM-VLR II | No Trip |  |  | 0 | 0 | 0 | 0
3 | ALM-VLR II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY-NLM | No Trip |  |  | 0 | 0 | 0 | 0
4 | GTY-NLM | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY-NPS I | 306006 | 01-06-2013 06:38:00 | 01-06-2013 06:52:00 | 0.23333 | 0 | 0 | 0 | OMST | Tripped at Gooty end only due to DC earth fault.
| GTY-NPS I | 306006 | 01-06-2013 07:32:00 | 01-06-2013 11:12:00 | 3.6667 | 0 | 0 | 0 | OMST | Tripped at Gooty end only due to DC earth fault.
| GTY-NPS I | 306044 | 06-06-2013 00:14:00 | 10-06-2013 15:49:00 | 0 | 0 | 0 | 111.5833 | LVRD | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-06/140
| GTY-NPS I | 306279 | 25-06-2013 21:47:00 | 02-07-2013 17:18:00 | 0 | 0 | 0 | 122.2167 | LVRD | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-06/795
5 | GTY-NPS I | Subtotal |  |  | 3.9 | 0 | 0 | 233.8 |  |  | 99.4583
| GTY-NPS II | 305184 | 2013-06-01 | 05-06-2013 13:17:00 | 0 | 0 | 0 | 109.28 | LVRD | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-05/735
| GTY-NPS II | 306095 | 11-06-2013 08:34:00 | 18-06-2013 09:54:00 | 0 | 0 | 0 | 169.3333 | LVRD | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-06/280
| GTY-NPS II | 306211 | 20-06-2013 12:46:00 | 20-06-2013 13:06:00 | 0.33333 | 0 | 0 | 0 | OMST | Tripped at NPS end only on receipt of DT at NPS due to suspected DC E/F at GTY.
| GTY-NPS II | 306241 | 24-06-2013 | 24-06-2013 00:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection NPS end. Direct trip signal received at Gooty end .
| GTY-NPS II | 306245 | 24-06-2013 00:05:00 | 24-06-2013 08:16:00 | 0 | 0 | 0 | 8.1833 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide msg. no. CP-06/813
| GTY-NPS II | 306286 | 26-06-2013 12:44:00 | 26-06-2013 12:54:00 | 0.16667 | 0 | 0 | 0 | OMST | Tripped at Gooty end only due to DC earth fault while extending cables for new bays.
6 | GTY-NPS II | Subtotal |  |  | 0.5 | 0 | 0.083333 | 286.8 |  |  | 99.9305
| GTY-RCR I | 306225 | 21-06-2013 20:10:00 | 21-06-2013 20:21:00 | 0.18333 | 0 | 0 | 0 | LEFT | Tripped at Raichur end only on R-N (Ph-earth) transient fault. FLR: 47.95 KM from Gooty end. Auto reclosure successful at Gooty end.
7 | GTY-RCR I | Subtotal |  |  | 0.18333 | 0 | 0 | 0 |  |  | 99.9745
| GTY-RCR II | No Trip |  |  | 0 | 0 | 0 | 0
8 | GTY-RCR II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GWL-HYD | 306167 | 16-06-2013 07:38:00 | 16-06-2013 08:41:00 | 0 | 0 | 0 | 1.05 | LVRD | Hand tripped for taking Line reactor at Hyderabad into service for voltage regulation as per SRLDC instructions vide code no. CR-06/464
9 | GWL-HYD | Subtotal |  |  | 0 | 0 | 0 | 1.05 |  |  | 100
| HYD-KNL | 306027 | 04-06-2013 04:03:00 | 04-06-2013 04:08:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Kurnool end. Direct trip signal received at Hyderabad end.
| HYD-KNL | 306028 | 04-06-2013 04:08:00 | 04-06-2013 07:54:00 | 0 | 0 | 0 | 3.7667 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/77
10 | HYD-KNL | Subtotal |  |  | 0 | 0 | 0.083333 | 3.7667 |  |  | 100
| HYD-NSR | 306076 | 08-06-2013 00:19:00 | 10-06-2013 08:54:00 | 0 | 0 | 0 | 56.5833 | LVRD | H/T for voltage regulation vide SRLDC code CR-06/194
11 | HYD-NSR | Subtotal |  |  | 0 | 0 | 0 | 56.5833 |  |  | 100
| JEY-GWK I | No Trip |  |  | 0 | 0 | 0 | 0
12 | JEY-GWK I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| JEY-GWK II | No Trip |  |  | 0 | 0 | 0 | 0
13 | JEY-GWK II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| KMM-NSR | 306003 | 01-06-2013 01:58:00 | 01-06-2013 02:05:00 | 0 | 0 | 0.11667 | 0 | GOVC | Line tripped on operation of over voltage protection at Khammam end. Direct trip signal received at Nagarjunasagar end.
| KMM-NSR | 306004 | 01-06-2013 02:05:00 | 01-06-2013 08:21:00 | 0 | 0 | 0 | 6.2667 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/02
| KMM-NSR | 306068 | 08-06-2013 00:03:00 | 08-06-2013 00:08:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on overvoltage protection at Kmm , D/T received at N'Sagar
| KMM-NSR | 306069 | 08-06-2013 00:08:00 | 08-06-2013 09:29:00 | 0 | 0 | 0 | 9.35 | LVRD | kept open as per SRLDC instruction for voltage regulation vide msg. no. CP-06/209A
| KMM-NSR | 306081 | 09-06-2013 13:59:00 | 09-06-2013 14:05:00 | 0 | 0 | 0.1 | 0 | GOVC | Tripped onoperation of over voltage protection at KHM. D/T received at NSG.
| KMM-NSR | 306082 | 09-06-2013 14:05:00 | 09-06-2013 19:06:00 | 0 | 0 | 0 | 5.0167 | LVRD | Kept open as per SRLDC instruction for voltage regulation vide msg. no. CP-06/246
| KMM-NSR | 306091 | 10-06-2013 18:03:00 | 10-06-2013 18:44:00 | 0 | 0 | 0.68333 | 0 | GOVC | Line tripped on operation of Over voltage protection at Khammam end. Direct trip signal received at Nagarjuna Sagar end
14 | KMM-NSR | Subtotal |  |  | 0 | 0 | 0.98333 | 20.6333 |  |  | 100
| KMM-VJA | 306090 | 10-06-2013 18:03:00 | 10-06-2013 19:34:00 | 0 | 0 | 1.5167 | 0 | GOVC | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-11/
| KMM-VJA | 306268 | 25-06-2013 01:49:00 | 25-06-2013 01:55:00 | 0 | 0 | 0.1 | 0 | GOVC | Line tripped on operation of over voltage protection at KHM end. Direct trip signal received at VJA end.
| KMM-VJA | 306271 | 25-06-2013 01:55:00 | 25-06-2013 15:11:00 | 0 | 0 | 0 | 13.2667 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/853
15 | KMM-VJA | Subtotal |  |  | 0 | 0 | 1.6167 | 13.2667 |  |  | 100
| KNL-GTY | 306057 | 2013-06-07 02:24 | 2013-06-07 02:29 | 0 | 0 | 0.08 | 0 | GOVC | Line tripped on operation of over voltage protection at Kurnool end. Direct trip signal received at Gooty end
| KNL-GTY | 306057 | 07-06-2013 02:29:00 | 10-06-2013 08:14:00 | 0 | 0 | 0 | 77.75 | LVRD | Kept open as per SRLDC instruction for voltage regulation vide msg. no. CP-06/175
16 | KNL-GTY | Subtotal |  |  | 0 | 0 | 0.08 | 77.75 |  |  | 100
| MBN-RCR | 306002 | 01-06-2013 | 03-06-2013 10:25:00 | 0 | 0 | 0 | 58.4167 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/01
| MBN-RCR | 306073 | 08-06-2013 02:52:00 | 08-06-2013 02:58:00 | 0 | 0 | 0.1 | 0 | GOVC | Tripped on O/V at Mehboobnagar , D/T received at Raichur end
| MBN-RCR | 306075 | 08-06-2013 02:58:00 | 08-06-2013 07:47:00 | 0 | 0 | 0 | 4.8167 | LVRD | kept open as per SRLDC instruction for voltage regulation vide msg. no. CP-06/213A
| MBN-RCR | 306132 | 13-06-2013 23:59:00 | 14-06-2013 00:05:00 | 0 | 0 | 0.1 | 0 | GOVC | Line tripped on operation of O/V stage I protection at MBN . DT recd at RCR.
| MBN-RCR | 306134 | 14-06-2013 00:05:00 | 14-06-2013 06:45:00 | 0 | 0 | 0 | 6.6667 | LVRD | Line kept opened for voltage regulation vide SRLDC MSG No. CP-06/422
| MBN-RCR | 306162 | 16-06-2013 02:59:00 | 16-06-2013 03:04:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on operation of over voltage protection at Mehboobnagar , D\T Received at Raichur end
| MBN-RCR | 306164 | 16-06-2013 03:04:00 | 16-06-2013 06:40:00 | 0 | 0 | 0 | 3.6 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06\513
| MBN-RCR | 306173 | 16-06-2013 17:57:00 | 16-06-2013 18:02:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Mahaboobnagar end. Direct trip signal received at Raichur end.
| MBN-RCR | 306175 | 16-06-2013 18:02:00 | 17-06-2013 09:26:00 | 0 | 0 | 0 | 15.4 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/537
| MBN-RCR | 306210 | 20-06-2013 12:31:00 | 20-06-2013 14:17:00 | 0 | 0 | 0 | 1.7667 | OSPD | H/T to attend hot sopt in B ph CT clamp at RCR (KPTCL) vide SRLDC code no CR-06/636
| MBN-RCR | 306233 | 22-06-2013 10:50:00 | 22-06-2013 11:10:00 | 0 | 0 | 0 | 0.33333 | LVRD | Hand tripped for taking out L/R at Raichur end vide SRLDC Code CR-06/697
| MBN-RCR | 306243 | 24-06-2013 | 24-06-2013 00:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Mehboobnagar end. Direct trip signal received at Raichur end.
| MBN-RCR | 306247 | 24-06-2013 00:05:00 | 24-06-2013 07:09:00 | 0 | 0 | 0 | 7.0667 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide msg. no. CP-06/814
| MBN-RCR | 306263 | 24-06-2013 23:43:00 | 24-06-2013 23:50:00 | 0 | 0 | 0.11667 | 0 | GOVC | Line tripped on operation of over voltage protection at MBN end. Direct trip signal received at RCR end.
| MBN-RCR | 306265 | 24-06-2013 23:50:00 | 26-06-2013 09:32:00 | 0 | 0 | 0 | 33.7 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/852
17 | MBN-RCR | Subtotal |  |  | 0 | 0 | 0.57 | 131.7667 |  |  | 100
| MEP-NPS | No Trip |  |  | 0 | 0 | 0 | 0
18 | MEP-NPS | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| MLK-HYD | 306127 | 13-06-2013 23:47:00 | 13-06-2013 23:52:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of O/V stage I protection at MALKARAM . DT recd at HYD.
| MLK-HYD | 306129 | 13-06-2013 23:52:00 | 14-06-2013 06:20:00 | 0 | 0 | 0 | 6.4667 | LVRD | Line kept opened for voltage regulation vide SRLDC MSG No. CP-06/421
| MLK-HYD | 306150 | 15-06-2013 | 15-06-2013 00:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on operation of O/V stage-I protection at HYD end . DT recd at MLKRM end.
| MLK-HYD | 306151 | 15-06-2013 00:05:00 | 15-06-2013 08:00:00 | 0 | 0 | 0 | 7.9167 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06/474.
| MLK-HYD | 306159 | 2013-06-16 00:21 | 16-06-2013 00:26:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on operation of over voltage protection at Malkaram , Direct trip signal received at Hyderabad
| MLK-HYD | 306161 | 16-06-2013 00:26:00 | 16-06-2013 10:07:00 | 0 | 0 | 0 | 9.6833 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06\510
| MLK-HYD | 306170 | 16-06-2013 17:48:00 | 16-06-2013 17:55:00 | 0 | 0 | 0.11667 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at Hyderabad end.
| MLK-HYD | 306171 | 16-06-2013 17:55:00 | 17-06-2013 08:34:00 | 0 | 0 | 0 | 14.65 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/536
| MLK-HYD | 306184 | 17-06-2013 18:02:00 | 17-06-2013 18:05:00 | 0 | 0 | 0.05 | 0 | GOVC | Tripped on operation of O/V stage -I protection at MLKRM end. DT recd at HYD .
| MLK-HYD | 306186 | 17-06-2013 18:05:00 | 18-06-2013 09:09:00 | 0 | 0 | 0 | 15.0667 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06/572.
| MLK-HYD | 306198 | 18-06-2013 18:13:00 | 18-06-2013 18:18:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at Hyderabad end
| MLK-HYD | 306199 | 18-06-2013 18:18:00 | 19-06-2013 08:38:00 | 0 | 0 | 0 | 14.3333 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/625A
| MLK-HYD | 306239 | 23-06-2013 18:00:00 | 23-06-2013 18:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on over voltage protection operated at Malkaram end , Direct trip signal received at Hyderabad end.
| MLK-HYD | 306240 | 23-06-2013 18:05:00 | 24-06-2013 08:14:00 | 0 | 0 | 0 | 14.15 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide msg. no. CP-06/811
| MLK-HYD | 306260 | 24-06-2013 23:22:00 | 24-06-2013 23:30:00 | 0 | 0 | 0.13333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at HYD end.
| MLK-HYD | 306261 | 24-06-2013 23:30:00 | 26-06-2013 09:08:00 | 0 | 0 | 0 | 33.6333 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/851
| MLK-HYD | 306289 | 27-06-2013 02:55:00 | 27-06-2013 03:00:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at Hyderabad end.
| MLK-HYD | 306290 | 27-06-2013 03:00:00 | 27-06-2013 08:38:00 | 0 | 0 | 0 | 5.6333 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/932
| MLK-HYD | 306302 | 27-06-2013 23:54:00 | 27-06-2013 23:59:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at Hyderabad end.
| MLK-HYD | 306303 | 27-06-2013 23:59:00 | 28-06-2013 07:08:00 | 0 | 0 | 0 | 7.15 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/973
| MLK-HYD | 306319 | 30-06-2013 17:55:00 | 30-06-2013 18:00:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on over voltage protection at Malkaram , D/T received at Hyderabad
| MLK-HYD | 306321 | 30-06-2013 18:00:00 | 2013-07-01 | 0 | 0 | 0 | 6 | LVRD | Line kept open for voltage regulation vide msg no. CP-06/ 1033
19 | MLK-HYD | Subtotal |  |  | 0 | 0 | 0.97 | 134.68 |  |  | 100
| NLR-ALM II | No Trip |  |  | 0 | 0 | 0 | 0
20 | NLR-ALM II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NLR-CNI I | No Trip |  |  | 0 | 0 | 0 | 0
21 | NLR-CNI I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NPS-NLR I | 306222 | 21-06-2013 15:10:00 | 21-06-2013 20:26:00 | 5.2667 | 0 | 0 | 0 | OSPT | Shut down availed for isolator realignment works at Nellore PS end vide SRLDC code no. CR-06/671.
| NPS-NLR I | 306228 | 22-06-2013 07:43:00 | 22-06-2013 20:02:00 | 12.3167 | 0 | 0 | 0 | OSPT | Shutdown availed for isolator realignment works vide SRLDC Code CR-06/691
22 | NPS-NLR I | Subtotal |  |  | 17.5833 | 0 | 0 | 0 |  |  | 97.5579
| NPS-NLR II | 306212 | 20-06-2013 12:46:00 | 20-06-2013 13:07:00 | 0.35 | 0 | 0 | 0 | OMST | Tripped at NPS end only by default as Bus -I is under S/D and Both the lines are in same dia.
| NPS-NLR II | 306275 | 25-06-2013 15:30:00 | 25-06-2013 18:59:00 | 3.4833 | 0 | 0 | 0 | OSPT | Shut down availed for isolator realignment works at Nellore PS end vide SRLDC code no. CR-06/783
| NPS-NLR II | 306280 | 26-06-2013 07:22:00 | 26-06-2013 19:55:00 | 12.55 | 0 | 0 | 0 | OSPT | Shut down availed for isolator realignment works at Nellore PS end vide SRLDC code no. CR-06/802
| NPS-NLR II | 306291 | 27-06-2013 09:39:00 | 27-06-2013 19:10:00 | 9.5167 | 0 | 0 | 0 | OSPT | Shut down availed for isolator realignment works at Nellore PS end vide SRLDC code no. CR-06/840
23 | NPS-NLR II | Subtotal |  |  | 25.9 | 0 | 0 | 0 |  |  | 96.4028
| NSR-CDP I | 306078 | 08-06-2013 09:35:00 | 16-06-2013 15:09:00 | 0 | 0 | 0 | 197.5667 | LCSD | H/T for realignment of line for construction of Railway line vide SRLDC code CR-06/207
24 | NSR-CDP I | Subtotal |  |  | 0 | 0 | 0 | 197.5667 |  |  | 100
| NSR-CDP II | 306274 | 25-06-2013 11:51:00 | 2013-07-01 | 0 | 0 | 0 | 132.15 | LCSD | S/D availed for line realignment works for railway line construction (other utility), vide SRLDC code no. CR-06/775
25 | NSR-CDP II | Subtotal |  |  | 0 | 0 | 0 | 132.15 |  |  | 100
| NSR-GTY | 306266 | 25-06-2013 01:49:00 | 25-06-2013 01:55:00 | 0 | 0 | 0.1 | 0 | GOVC | Line tripped on operation of over voltage protection at NSG end. Direct trip signal received at GTY end.
| NSR-GTY | 306269 | 25-06-2013 01:55:00 | 25-06-2013 07:33:00 | 0 | 0 | 0 | 5.6333 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/853
26 | NSR-GTY | Subtotal |  |  | 0 | 0 | 0.1 | 5.6333 |  |  | 100
| NSR-MBN | 306001 | 01-06-2013 | 03-06-2013 08:21:00 | 0 | 0 | 0 | 56.35 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/01
| NSR-MBN | 306072 | 08-06-2013 02:52:00 | 08-06-2013 02:58:00 | 0 | 0 | 0.1 | 0 | GOVC | Tripped on O/V at Mehboobnagar , D/T received at N'Sagar
| NSR-MBN | 306074 | 08-06-2013 02:58:00 | 08-06-2013 06:58:00 | 0 | 0 | 0 | 4 | LVRD | kept open as per SRLDC instruction for voltage regulation vide msg. no. CP-06/213A
| NSR-MBN | 306131 | 13-06-2013 23:59:00 | 14-06-2013 00:05:00 | 0 | 0 | 0.1 | 0 | GOVC | Line tripped on operation of O/V stage I protection at MBN . DT recd at NSG.
| NSR-MBN | 306133 | 14-06-2013 00:05:00 | 14-06-2013 05:48:00 | 0 | 0 | 0 | 5.7167 | LVRD | Line kept opened for voltage regulation vide SRLDC MSG No. CP-06/422
| NSR-MBN | 306163 | 16-06-2013 02:59:00 | 16-06-2013 03:04:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on operation of over voltage protection at Mehboobnagar , D\T Received at N'sagar end
| NSR-MBN | 306165 | 16-06-2013 03:04:00 | 16-06-2013 06:41:00 | 0 | 0 | 0 | 3.6167 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06\512
| NSR-MBN | 306172 | 16-06-2013 17:57:00 | 16-06-2013 18:02:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Mahaboobnagar end. Direct trip signal received at Nagarjunasagar end.
| NSR-MBN | 306174 | 16-06-2013 18:02:00 | 17-06-2013 05:37:00 | 0 | 0 | 0 | 11.5833 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/537
| NSR-MBN | 306242 | 24-06-2013 | 24-06-2013 00:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Mehboobnagar end. Direct trip signal received at N' Sagar end.
| NSR-MBN | 306246 | 24-06-2013 00:05:00 | 24-06-2013 06:18:00 | 0 | 0 | 0 | 6.2167 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide msg. no. CP-06/813
| NSR-MBN | 306262 | 24-06-2013 23:43:00 | 24-06-2013 23:50:00 | 0 | 0 | 0.11667 | 0 | GOVC | Line tripped on operation of over voltage protection at MBN end. Direct trip signal received at NSG end.
| NSR-MBN | 306264 | 24-06-2013 23:50:00 | 25-06-2013 06:42:00 | 0 | 0 | 0 | 6.8667 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/852
| NSR-MBN | 306276 | 25-06-2013 17:55:00 | 25-06-2013 18:05:00 | 0 | 0 | 0.16667 | 0 | GOVC | Line tripped on operation of over voltage protection at Mahaboobnagar end. Direct trip signal received at Nagarjunasagar end.
| NSR-MBN | 306277 | 25-06-2013 18:05:00 | 26-06-2013 05:54:00 | 0 | 0 | 0 | 11.8167 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/889
27 | NSR-MBN | Subtotal |  |  | 0 | 0 | 0.73 | 106.1667 |  |  | 100
| RCR-MBD | 306166 | 16-06-2013 07:13:00 | 16-06-2013 21:07:00 | 0 | 0 | 0 | 13.9 | LCSD | Shut down availed for stringing works of 765kV Raichur-Sholapur line vide SRLDC code no. CR-06/463
28 | RCR-MBD | Subtotal |  |  | 0 | 0 | 0 | 13.9 |  |  | 100
| RDM-CPR I | No Trip |  |  | 0 | 0 | 0 | 0
29 | RDM-CPR I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| RDM-CPR II | No Trip |  |  | 0 | 0 | 0 | 0
30 | RDM-CPR II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| RDM-GWL | 306011 | 01-06-2013 18:16:00 | 01-06-2013 19:01:00 | 0 | 0 | 0.75 | 0 | GOVC | Tripped on over voltage protection optd at Gajuwel end,. D/T received at Ramagundam end.
| RDM-GWL | 306083 | 09-06-2013 18:00:00 | 09-06-2013 19:19:00 | 0 | 0 | 1.3167 | 0 | GOVC | Tripped onoperation of over voltage protection at GJVL. D/T received at RGDM.
| RDM-GWL | 306093 | 11-06-2013 01:05:00 | 11-06-2013 01:10:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of Over voltage protection at Gajwel end. Direct trip signal received at Ramagundam end
| RDM-GWL | 306094 | 11-06-2013 01:10:00 | 11-06-2013 06:57:00 | 0 | 0 | 0 | 5.7833 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/297
| RDM-GWL | 306104 | 11-06-2013 18:02:00 | 11-06-2013 18:15:00 | 0 | 0 | 0.21667 | 0 | GOVC | Line tripped on operation of Over voltage protection at Gajwel end. Direct trip signal received at Ramagundam end
| RDM-GWL | 306105 | 11-06-2013 18:15:00 | 12-06-2013 06:23:00 | 0 | 0 | 0 | 12.1333 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/328
| RDM-GWL | 306111 | 13-06-2013 00:03:00 | 13-06-2013 00:10:00 | 0 | 0 | 0.11667 | 0 | GOVC | Tripped on operation of O/V stage -I protection at GJVL end. D/T recd at RGDM.
| RDM-GWL | 306112 | 13-06-2013 00:10:00 | 13-06-2013 06:02:00 | 0 | 0 | 0 | 5.8667 | LVRD | Line kept opened as SRLDC instruction for voltage regulation vide SRLDC Msg. no. CP-06/368
| RDM-GWL | 306135 | 14-06-2013 00:42:00 | 14-06-2013 00:50:00 | 0 | 0 | 0.13333 | 0 | GOVC | Line tripped on operation of O/V stage I protection at GJVL . DT recd at RGDM.
| RDM-GWL | 306136 | 14-06-2013 00:50:00 | 14-06-2013 06:02:00 | 0 | 0 | 0 | 5.2 | LVRD | Line kept opened for voltage regulation vide SRLDC MSG No. CP-06/423
| RDM-GWL | 306148 | 14-06-2013 23:46:00 | 14-06-2013 23:50:00 | 0 | 0 | 0.066667 | 0 | GOVC | Tripped on operation of O/V stage-I protection at GJVL end . DT recd at RGDM end.
| RDM-GWL | 306149 | 14-06-2013 23:50:00 | 15-06-2013 06:54:00 | 0 | 0 | 0 | 7.0667 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06/473.
31 | RDM-GWL | Subtotal |  |  | 0 | 0 | 2.6833 | 36.05 |  |  | 100
| RDM-HYD III | 306025 | 04-06-2013 02:42:00 | 04-06-2013 02:48:00 | 0 | 0 | 0.1 | 0 | GOVC | Line auto reclosed on Y-N fault and tripped on receipt of DT signal from RGDM end.
| RDM-HYD III | 306026 | 04-06-2013 02:48:00 | 04-06-2013 07:39:00 | 0 | 0 | 0 | 4.85 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/75
| RDM-HYD III | 306045 | 06-06-2013 01:33:00 | 06-06-2013 07:05:00 | 0 | 0 | 0 | 5.5333 | LVRD | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-06/142
| RDM-HYD III | 306070 | 08-06-2013 00:51:00 | 08-06-2013 08:55:00 | 0 | 0 | 0 | 8.0667 | LVRD | H/T for voltage regulation vide SRLDC code CR-06/195
32 | RDM-HYD III | Subtotal |  |  | 0 | 0 | 0.1 | 18.45 |  |  | 100
| RDM-HYD IV | No Trip |  |  | 0 | 0 | 0 | 0
33 | RDM-HYD IV | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| RDM-MLK | 306128 | 13-06-2013 23:47:00 | 13-06-2013 23:52:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of O/V stage I protection at MALKARAM . DT recd at RGDM.
| RDM-MLK | 306130 | 13-06-2013 23:52:00 | 14-06-2013 06:56:00 | 0 | 0 | 0 | 7.0667 | LVRD | Line kept opened for voltage regulation vide SRLDC MSG No. CP-06/421
| RDM-MLK | 306158 | 2013-06-16 00:21 | 16-06-2013 00:26:00 | 0 | 0 | 0.08 | 0 | GOVC | Tripped on operation of over voltage protection at Malkaram , Direct trip signal received at Ramagundam
| RDM-MLK | 306160 | 16-06-2013 00:26:00 | 17-06-2013 09:16:00 | 0 | 0 | 0 | 32.8333 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06\510
| RDM-MLK | 306183 | 17-06-2013 18:00:00 | 17-06-2013 18:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on operation of O/V stage -I protection at MLKRM end. DT recd at RGDM .
| RDM-MLK | 306185 | 17-06-2013 18:05:00 | 18-06-2013 09:21:00 | 0 | 0 | 0 | 15.2667 | LVRD | Line kept opened for voltage regulation vide SRLDC msg no CP-06/572.
| RDM-MLK | 306235 | 22-06-2013 18:00:00 | 22-06-2013 18:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on over voltage protetion optd at Malkaram end, D/T received at RGDM
| RDM-MLK | 306236 | 22-06-2013 18:05:00 | 24-06-2013 08:21:00 | 0 | 0 | 0 | 38.2667 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide msg. no. CP-06/788A
| RDM-MLK | 306256 | 24-06-2013 18:00:00 | 24-06-2013 18:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at RGDM end.
| RDM-MLK | 306257 | 24-06-2013 18:05:00 | 26-06-2013 09:38:00 | 0 | 0 | 0 | 39.55 | LVRD | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/842.
| RDM-MLK | 306287 | 26-06-2013 18:00:00 | 26-06-2013 18:05:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at Ramagundam end.
| RDM-MLK | 306288 | 26-06-2013 18:05:00 | 27-06-2013 09:23:00 | 0 | 0 | 0 | 15.3 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/925
| RDM-MLK | 306296 | 18-06-2013 18:00:00 | 18-06-2013 18:20:00 | 0 | 0 | 0.33333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at Ramagundam end.
| RDM-MLK | 306297 | 18-06-2013 18:20:00 | 19-06-2013 09:21:00 | 0 | 0 | 0 | 15.0167 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/625B
| RDM-MLK | 306304 | 28-06-2013 02:45:00 | 28-06-2013 02:50:00 | 0 | 0 | 0.083333 | 0 | GOVC | Line tripped on operation of over voltage protection at Malkaram end. Direct trip signal received at Ramagundam end.
| RDM-MLK | 306305 | 28-06-2013 02:50:00 | 28-06-2013 09:43:00 | 0 | 0 | 0 | 6.8833 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/974
| RDM-MLK | 306320 | 30-06-2013 17:56:00 | 30-06-2013 18:01:00 | 0 | 0 | 0.083333 | 0 | GOVC | Tripped on over voltage protection at Malkaram , D/T received at RGDM end
| RDM-MLK | 306322 | 30-06-2013 18:01:00 | 01-07-2013 07:07:00 | 0 | 0 | 0 | 5.9833 | LVRD | Line kept open for voltage regulation vide msg no. CP-06/ 1035
34 | RDM-MLK | Subtotal |  |  | 0 | 0 | 1 | 176.17 |  |  | 100
| RDM-NSR I | No Trip |  |  | 0 | 0 | 0 | 0
35 | RDM-NSR I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| RDM-NSR II | No Trip |  |  | 0 | 0 | 0 | 0
36 | RDM-NSR II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| RDM-WGL | No Trip |  |  | 0 | 0 | 0 | 0
37 | RDM-WGL | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| SEP-NPS | No Trip |  |  | 0 | 0 | 0 | 0
38 | SEP-NPS | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| SMD-GWK I | No Trip |  |  | 0 | 0 | 0 | 0
39 | SMD-GWK I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| SMD-GWK II | No Trip |  |  | 0 | 0 | 0 | 0
40 | SMD-GWK II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VAL-KVP I | 306293 | 27-06-2013 10:09:00 | 27-06-2013 10:24:00 | 0 | 0.25 | 0 | 0 | OMSU | Tripped due to suspected PLCC maloperation at Vallur (NTECL)end.
| VAL-KVP I | 306316 | 30-06-2013 08:18:00 | 30-06-2013 15:01:00 | 0 | 0 | 0 | 6.7167 | LCSD | Shut down availed for OPGW striging works vide SRLDC code no. CR-06/899
41 | VAL-KVP I | Subtotal |  |  | 0 | 0.25 | 0 | 6.7167 |  |  | 100
| VAL-KVP II | No Trip |  |  | 0 | 0 | 0 | 0
42 | VAL-KVP II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA-GWK I | No Trip |  |  | 0 | 0 | 0 | 0
43 | VJA-GWK I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA-NLR I | No Trip |  |  | 0 | 0 | 0 | 0
44 | VJA-NLR I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA-NLR II | No Trip |  |  | 0 | 0 | 0 | 0
45 | VJA-NLR II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA-VMG III | 305117 | 2013-06-01 | 06-06-2013 09:45:00 | 0 | 0 | 0 | 129.75 | LVRD | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-05/503
46 | VJA-VMG III | Subtotal |  |  | 0 | 0 | 0 | 129.75 |  |  | 100
| VJA-VMG IV | No Trip |  |  | 0 | 0 | 0 | 0
47 | VJA-VMG IV | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VMG-SMH I | No Trip |  |  | 0 | 0 | 0 | 0
48 | VMG-SMH I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VMG-SMH II | No Trip |  |  | 0 | 0 | 0 | 0
49 | VMG-SMH II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| WGL-KMM | 306092 | 10-06-2013 18:03:00 | 10-06-2013 19:27:00 | 0 | 0 | 1.4 | 0 | GOVC | Line tripped on operation of Over voltage protection at Khammam end. Direct trip signal received at Warangal end
| WGL-KMM | 306267 | 25-06-2013 01:49:00 | 25-06-2013 01:55:00 | 0 | 0 | 0.1 | 0 | GOVC | Line tripped on operation of over voltage protection at WGL end. Direct trip signal received at KHM end.
| WGL-KMM | 306270 | 25-06-2013 01:55:00 | 26-06-2013 08:29:00 | 0 | 0 | 0 | 30.5667 | LVRD | Line kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/853
50 | WGL-KMM | Subtotal |  |  | 0 | 0 | 1.5 | 30.5667 |  |  | 100
ICTS
| CDP ICT I | No Trip |  |  | 0 | 0 | 0 | 0
1 | CDP ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| CDP ICT II | No Trip |  |  | 0 | 0 | 0 | 0
2 | CDP ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY ICT I | No Trip |  |  | 0 | 0 | 0 | 0
3 | GTY ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY ICT II | No Trip |  |  | 0 | 0 | 0 | 0
4 | GTY ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GWK ICT I | 306295 | 27-06-2013 11:34:00 | 27-06-2013 18:05:00 | 0 | 0 | 0 | 6.5167 | OSPD | S/D availed by M/s APTRANSCO to attend hot spots at 220 KV VSS sub-station vide SRLDC code no. CR-06/847
5 | GWK ICT I | Subtotal |  |  | 0 | 0 | 0 | 6.5167 |  |  | 100
| GWK ICT II | No Trip |  |  | 0 | 0 | 0 | 0
6 | GWK ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD ICT I | No Trip |  |  | 0 | 0 | 0 | 0
7 | HYD ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD ICT II | No Trip |  |  | 0 | 0 | 0 | 0
8 | HYD ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD ICT III | No Trip |  |  | 0 | 0 | 0 | 0
9 | HYD ICT III | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| KMM ICT I | No Trip |  |  | 0 | 0 | 0 | 0
10 | KMM ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| KMM ICT II | No Trip |  |  | 0 | 0 | 0 | 0
11 | KMM ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| MBD ICT I | No Trip |  |  | 0 | 0 | 0 | 0
12 | MBD ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| MBD ICT II | No Trip |  |  | 0 | 0 | 0 | 0
13 | MBD ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR ICT I | No Trip |  |  | 0 | 0 | 0 | 0
14 | NSR ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR ICT II | No Trip |  |  | 0 | 0 | 0 | 0
15 | NSR ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR ICT III | No Trip |  |  | 0 | 0 | 0 | 0
16 | NSR ICT III | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA ICT I | No Trip |  |  | 0 | 0 | 0 | 0
17 | VJA ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA ICT II | No Trip |  |  | 0 | 0 | 0 | 0
18 | VJA ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| WGL ICT I | No Trip |  |  | 0 | 0 | 0 | 0
19 | WGL ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| WGL ICT II | No Trip |  |  | 0 | 0 | 0 | 0
20 | WGL ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
SWITCHABLE LR AND BUS REACTORS
| CDP BR | No Trip |  |  | 0 | 0 | 0 | 0
1 | CDP BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY BR | No Trip |  |  | 0 | 0 | 0 | 0
2 | GTY BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY LR AT NLM | No Trip |  |  | 0 | 0 | 0 | 0
3 | GTY LR AT NLM | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GWK BR | No Trip |  |  | 0 | 0 | 0 | 0
4 | GWK BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD BR | No Trip |  |  | 0 | 0 | 0 | 0
5 | HYD BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| KMM BR | No Trip |  |  | 0 | 0 | 0 | 0
6 | KMM BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| MBD BR | No Trip |  |  | 0 | 0 | 0 | 0
7 | MBD BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NLR BR | No Trip |  |  | 0 | 0 | 0 | 0
8 | NLR BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR BR | No Trip |  |  | 0 | 0 | 0 | 0
9 | NSR BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA BR | No Trip |  |  | 0 | 0 | 0 | 0
10 | VJA BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
HVDC
| VZG BTB P I | No Trip |  |  | 0 | 0 | 0 | 0
1 | VZG BTB P I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VZG BTB P II | No Trip |  |  | 0 | 0 | 0 | 0
2 | VZG BTB P II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100

## I-ICT
| ELEMENT NAME | EVENT NO | TRIP DATE/TIME | REST DATE/TIME | OutageDuration |  |  |  | TRIP CODE | Reasons | % Availability
[5 empty] | POWER GRID (SR-1) | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
| CDP ICT I | No Trip |  |  | 0 | 0 | 0 | 0
1 | CDP ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| CDP ICT II | No Trip |  |  | 0 | 0 | 0 | 0
2 | CDP ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY ICT I | No Trip |  |  | 0 | 0 | 0 | 0
3 | GTY ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY ICT II | No Trip |  |  | 0 | 0 | 0 | 0
4 | GTY ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GWK ICT I | 306295 | 27-06-2013 11:34:00 | 27-06-2013 18:05:00 | 0 | 0 | 0 | 6.5167 | OSPD | S/D availed by M/s APTRANSCO to attend hot spots at 220 KV VSS sub-station vide SRLDC code no. CR-06/847
5 | GWK ICT I | Subtotal |  |  | 0 | 0 | 0 | 6.5167 |  |  | 100
| GWK ICT II | No Trip |  |  | 0 | 0 | 0 | 0
6 | GWK ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD ICT I | No Trip |  |  | 0 | 0 | 0 | 0
7 | HYD ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD ICT II | No Trip |  |  | 0 | 0 | 0 | 0
8 | HYD ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD ICT III | No Trip |  |  | 0 | 0 | 0 | 0
9 | HYD ICT III | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| KMM ICT I | No Trip |  |  | 0 | 0 | 0 | 0
10 | KMM ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| KMM ICT II | No Trip |  |  | 0 | 0 | 0 | 0
11 | KMM ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| MBD ICT I | No Trip |  |  | 0 | 0 | 0 | 0
12 | MBD ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| MBD ICT II | No Trip |  |  | 0 | 0 | 0 | 0
13 | MBD ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR ICT I | No Trip |  |  | 0 | 0 | 0 | 0
14 | NSR ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR ICT II | No Trip |  |  | 0 | 0 | 0 | 0
15 | NSR ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR ICT III | No Trip |  |  | 0 | 0 | 0 | 0
16 | NSR ICT III | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA ICT I | No Trip |  |  | 0 | 0 | 0 | 0
17 | VJA ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA ICT II | No Trip |  |  | 0 | 0 | 0 | 0
18 | VJA ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| WGL ICT I | No Trip |  |  | 0 | 0 | 0 | 0
19 | WGL ICT I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| WGL ICT II | No Trip |  |  | 0 | 0 | 0 | 0
20 | WGL ICT II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100

## I-BR & SWR
| ELEMENT NAME | EVENT NO | TRIP DATE/TIME | REST DATE/TIME | OutageDuration |  |  |  | TRIP CODE | Reasons | % Availability
[5 empty] | POWER GRID (SR-1) | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
| CDP BR | No Trip |  |  | 0 | 0 | 0 | 0
1 | CDP BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY BR | No Trip |  |  | 0 | 0 | 0 | 0
2 | GTY BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GTY LR AT NLM | No Trip |  |  | 0 | 0 | 0 | 0
3 | GTY LR AT NLM | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| GWK BR | No Trip |  |  | 0 | 0 | 0 | 0
4 | GWK BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| HYD BR | No Trip |  |  | 0 | 0 | 0 | 0
5 | HYD BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| KMM BR | No Trip |  |  | 0 | 0 | 0 | 0
6 | KMM BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| MBD BR | No Trip |  |  | 0 | 0 | 0 | 0
7 | MBD BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NLR BR | No Trip |  |  | 0 | 0 | 0 | 0
8 | NLR BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| NSR BR | No Trip |  |  | 0 | 0 | 0 | 0
9 | NSR BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VJA BR | No Trip |  |  | 0 | 0 | 0 | 0
10 | VJA BR | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100

## I-LR & FSC
AC TRANSMISSION LINE/ICT/STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ HVDC (BACK TO BACK STATIONS AND BIPOLE LINKS)/ LINE REACTORS/BUS REACTORS OUTAGE DETAILS FOR THE MONTH OF JUNE 2013 | [8 empty] | 31
Sl.No | ELEMENT NAME | Capacity | TRIP DATE/TIME | REST DATE/TIME | OUTAGE DURATION |  |  |  | Availability | Reason
[5 empty] | POWERGRID SR-1 | OTHERS | SYSTEM CONSTRAINT / NATURAL CALAMITY / MILITANCY | DEEMED AVAILABLE
1 | GTY LR at NSR | 50 | [6 empty] | 100%
2 | GWK I LR at VJA | 63 | [6 empty] | 100%
3 | GWL LR at HYD | 50 | [6 empty] | 100%
4 | JEY I LR at GWK | 80 | [6 empty] | 100%
5 | JEY II LR at GWK | 80 | [6 empty] | 100%
6 | MBN LR at NSR | 63 | [6 empty] | 100%
7 | MLK LR at HYD | 50 | [6 empty] | 100%
8 | NLR I LR at VJA | 50 | [6 empty] | 100%
9 | NLR II LR at VJA | 50 | [6 empty] | 100%
10 | NSR I LR at CDP | 50 | [6 empty] | 100%
11 | NSR II LR at CDP | 50 | [6 empty] | 100%
12 | NSR LR at GTY | 50 | [6 empty] | 100%
13 | POLE II ER at GWK | 80 | [6 empty] | 100%
14 | POLE II SR at GWK | 80 | [6 empty] | 100%
15 | RCR LR at MBD | 63 | [6 empty] | 100%
16 | RDM I LR at NSR | 50 | 2013-06-01 | 2013-07-01 |  |  |  | 720
|  |  |  | Sub Total |  |  |  | 720 | 100%
17 | RDM II LR at NSR | 50 | [6 empty] | 100%
18 | SMH I LR at GWK | 63 | [6 empty] | 100%
19 | SMH II LR at GWK | 63 | [6 empty] | 100%
20 | VJA I LR at GWK | 63 | [6 empty] | 100%
21 | VJA I LR at NLR | 50 | [6 empty] | 100%
22 | VJA II LR at NLR | 50 | [6 empty] | 100%
23 | VMG III LR at VJA | 63 | [6 empty] | 100%
24 | VMG IV LR at VJA | 63 | [6 empty] | 100%
25 | WGL LR at KMM | 50 | [6 empty] | 100%
28 | NSR I FSC at CDP | 201.75 | [6 empty] | 100%
29 | NSR II FSC at CDP | 201.75 | [6 empty] | 100%
30 | FSC-1 at GTY | 181.5 | [6 empty] | 100% |  | 181.5 MVAR
|  |  | 2013-06-02 14:51 | 2013-06-05 21:44 |  |  |  | 78.53 |  | FSC-I was taken out from service for voltage regulation vide cpcc code CP06/42 and taken into service vide cpcc code CP06/132.
|  |  | 2013-06-09 23:25 | 2013-06-01 06:40 |  |  |  | 7.15 |  | FSC-I was taken out from service for voltage regulation vide cpcc code CP06/257 and taken into service vide cpcc code CP06/260
85.68
31 | FSC-2 at GTY | 181.5
[5 empty] | 0 | 0 |  | 1611.36
|  |  | 2013-06-02 14:51 | 2013-06-05 21:45 |  |  |  | 78.54 |  | FSC-II was taken out from service for voltage regulation vide cpcc code CP06/43 and taken into service vide cpcc code CP06/133.
|  |  | 2013-06-09 23:25 | 2013-06-10 06:41 |  |  |  | 7.16 |  | FSC-II was taken out from service for voltage regulation vide cpcc code CP06/258 and taken into service vide cpcc code CP06/261
|  |  |  | Sub Total | 0 |  |  | 85.7 | 100%

## I-HVDC
| ELEMENT NAME | EVENT NO | TRIP DATE/TIME | REST DATE/TIME | OutageDuration |  |  |  | TRIP CODE | Reasons | % Availability
[5 empty] | POWER GRID (SR-1) | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
| VZG BTB P I | No Trip |  |  | 0 | 0 | 0 | 0
3 | VZG BTB P I | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100
| VZG BTB P II | No Trip |  |  | 0 | 0 | 0 | 0
4 | VZG BTB P II | Subtotal |  |  | 0 | 0 | 0 | 0 |  |  | 100

## II Exceeded Restoration
AC TRANSMISSION LINE/ICT/STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ HVDC (BACK TO BACK STATIONS AND BIPOLE LINKS)/ LINE REACTORS/BUS REACTORS OUTAGE DETAILS FOR THE MONTH OF
2013-06-01
2013-06-01
Element Name | Restoration time as specified in Regulation 5 (b) (in days) | Actual restoration time (in days)
NIL | NIL | NIL

## III-Compensation
AC TRANSMISSION LINE/ICT/STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ HVDC (BACK TO BACK STATIONS AND BIPOLE LINKS)/ LINE REACTORS/BUS REACTORS OUTAGE DETAILS FOR THE MONTH OF
2013-06-01
2013-06-01
Element Name | Violation of Regulation 5 (a) |  | Violation of Regulation 5 (b) |  | Compensation paid (in Rs.)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in days) | Actual restoration time (in days)
NIL |  |  |  |  | NIL
Total

## V Failures
AC TRANSMISSION LINE/ICT/STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ HVDC (BACK TO BACK STATIONS AND BIPOLE LINKS)/ LINE REACTORS/BUS REACTORS OUTAGE DETAILS FOR THE MONTH OF
2013-06-01
2013-06-01
| Types of failures | Restoration Time (Days)
A. | Elements of the Transmission line for Single Circuit (S/C), Double Circuit (D/C) and Multi-Circuit (M/C) towers for each kV class separately
1 | Insulator failure | Terrain type
1 | Insulator failure | Plain | River bed |  | Hilly
1 | (i) Insulator failure in single phase | NA | NA |  | NA
1 | (ii) Insulator failure in two phases | NA | NA |  | NA
1 | (iii) Insulator failure in three phases | NA | NA |  | NA
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C, D/C and M/C separately | NA | NA |  | NA
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C, D/C and M/C separately | NA | NA |  | NA
4 | Tower damage (not collapse)
4 | One arm damage | NA | NA |  | NA
4 | Two arms damage | NA | NA |  | NA
5 | Snapping of phase conductor
5 | Conductor snapping in single phase | NA | NA |  | NA
5 | Conductor snapping in two phases | NA | NA |  | NA
5 | Conductor snapping in three phases | NA | NA |  | NA
6 | Failure of earth wire | NA | NA |  | NA
7 | Insulator failure with conductor snapping | NA | NA |  | NA
8 | Any other combination of failures | NA | NA |  | NA
B. | Elements of the sub-station for each kV class separately
1 | Failure of Inter Connecting Transformers (ICTs)
1 | Restoration of the failed ICT
1 | Other major failures in ICTs | Single phase unit |  | Three phase unit
1 | (i) Replacement of faulty bushings | NA | NA |  | NA
1 | (ii) Replacement of failed/ blasted bushings | NA | NA |  | NA
1 | (iii) Replacement of faulty tap changers | NA | NA |  | NA
2 | Failure of Reactors
2 | Restoration of the failed reactor | NA | NA |  | NA