## SOP
Standard of Performance data for the month of March-2015
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date and Time | Date and Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L1 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | SRPC | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
2 | SR1L2 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
3 | SR1L3 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | 2015-03-17 16:59 | 2015-03-17 18:14 | -- | -- | -- | 1.25 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for 1452 CB PIR removal work at Ramagundam end vide SRLDC code no. CR-03/375. |  | 99.832
[6 empty] | Sub Total --> |  |  |  |  | 1.25 | 0 | 0 | 0
4 | SR1L4 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
5 | SR1L5 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
6 | SR1L6 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
7 | SR1L7 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
8 | SR1L8 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
9 | SR1L9 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
10 | SR1L10 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
11 | SR1L11 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
12 | SR1L12 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
13 | SR1L13 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
14 | SR1L14 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
15 | SR1L15 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
16 | SR1L16 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | 2015-03-12 11:09 | 2015-03-12 15:20 | -- | -- | -- | 0 | 0 | 0 | 4.1833 | N/A | N/A | N/A | Shut down availed for OPGW stringing works vide SRLDC code no. CR-03/277. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 4.1833
17 | SR1L17 | KHAMMAM - N'SAGAR | 144.577 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
18 | SR1L18 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
19 | SR1L19 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
20 | SR1L20 | KURNOOL(NEW) - GOOTY | 112.609 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
21 | SR1L21 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
22 | SR1L22 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | 2015-03-09 06:36 | 2015-03-09 07:55 | -- | -- | -- | 0 | 1.3167 | 0 | 0 | N/A | N/A | N/A | Tripped at Mahaboobnagar end only due to fault in RTPS switchyard. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 1.3167 | 0 | 0
23 | SR1L23 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
24 | SR1L24 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | 2015-03-11 10:26 | 2015-03-11 13:47 | -- | -- | -- | 0 | 0 | 0 | 3.35 | N/A | N/A | N/A | Shut down availed for OTI modification works on line reactor at Gajuwaka end for SCADA works vide SRLDC code no. CR-03/238. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 3.35
25 | SR1L25 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2015-03-01 07:28 | 2015-03-02 20:11 | -- | -- | -- | 0 | 0 | 0 | 36.7167 | N/A | N/A | N/A | Shut down availed for restoration of the line from ERS towers for the proposed railway crossing works between loc. 855-859 vide SRLDC code no. CR-03/05. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 36.7167
26 | SR1L26 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2015-03-03 07:19 | 2015-03-04 19:34 | -- | -- | -- | 0 | 0 | 0 | 36.25 | N/A | N/A | N/A | Shut down availed for restoration of the line from ERS towers for the proposed railway crossing works between loc. 855-859 vide SRLDC code no. CR-03/50. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 36.25
27 | SR1L27 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2015-03-01 | 2015-03-02 11:02 | -- | -- | -- | 0 | 0 | 0 | 35.0333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/415. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 35.0333
28 | SR1L28 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | 2015-03-11 23:11 | 2015-03-25 09:32 | -- | -- | -- | 0 | 0 | 0 | 322.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/266. |  | 98.2303
[5 empty] | -- | 2015-03-25 09:50 | 2015-03-25 09:50 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 154 kM from Vijayawada end.
[5 empty] | -- | 2015-03-25 09:56 | 2015-03-25 09:56 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 155 kM from Vijayawada end.
[5 empty] | -- | 2015-03-26 07:31 | 2015-03-26 20:41 | -- | -- | -- | 13.1667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of decapped tention insulators at loc. 460 vide SRLDC code no. CR-03/613.
[6 empty] | Sub Total --> |  |  |  |  | 13.1667 | 0 | 0 | 322.35
29 | SR1L29 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | 2015-03-05 10:10 | 2015-03-05 13:24 | -- | -- | -- | 0 | 0 | 0 | 3.2333 | N/A | N/A | N/A | Shut down availed by M/s APTRANSCO for maintenance works at Vemagiri end. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 3.2333
30 | SR1L30 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | 2015-03-09 10:17 | 2015-03-09 14:12 | -- | -- | -- | 0 | 0 | 0 | 3.9167 | N/A | N/A | N/A | Shut down availed for OTI modification works on line reactor at Gajuwaka end for SCADA works vide SRLDC code no. CR-03/185. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 3.9167
31 | SR1L31 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | 2015-03-11 09:36 | 2015-03-11 12:40 | -- | -- | -- | 0 | 0 | 0 | 3.0667 | N/A | N/A | N/A | Shut down availed by M/s APTRANSCO for routine maintenance works at Vemagiri end vide SRLDC code no. CR-03/227. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 3.0667
32 | SR1L32 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | 2015-03-10 10:17 | 2015-03-10 13:01 | -- | -- | -- | 0 | 0 | 0 | 2.7333 | N/A | N/A | N/A | Shut down availed for OTI modification works on line reactor at Gajuwaka end for SCADA works vide SRLDC code no. CR-03/211. |  | 100
[5 empty] | -- | 2015-03-31 12:26 | 2015-03-31 16:09 | -- | -- | -- | 0 | 0 | 0 | 3.7167 | N/A | N/A | N/A | Shut down availed by M/s NTPC to attend isolator problem at Simhadri end vide SRLDC code no. CR-03/732.
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 6.45
33 | SR1L33 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | 2015-03-14 17:12 | 2015-03-14 19:02 | -- | -- | -- | 0 | 0 | 1.8333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Gajuwaka end. Direct trip signal received at Jeypore end. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 1.8333 | 0
34 | SR1L34 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | 2015-03-14 17:12 | 2015-03-14 17:12 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 146.6 kM from Gajuwaka end. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
35 | SR1L35 | NELLORE - ALMATHY | 194.44 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
36 | SR1L36 | NELLORE - SIRIPERUMBUDUR | 189 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
37 | SR1L37 | ALMATHY - SIRIPERUMBUDUR | 75.973 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
38 | SR1L38 | KURNOOL - GOOTY | 84.19 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
39 | SR1L39 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | 2015-03-04 12:31 | 2015-03-04 12:45 | -- | -- | -- | 0 | 0 | 0 | 0.23333 | N/A | N/A | N/A | Tripped due to spurious signal generated during NTAMC wiring works. |  | 99.9597
[5 empty] | -- | 2015-03-25 10:44 | 2015-03-25 10:54 | -- | -- | -- | 0 | 0 | 0 | 0.16667 | N/A | N/A | N/A | Tripped due to spurious signal generated during NTAMC wiring works at Gooty end.
[5 empty] | -- | 2015-03-28 19:34 | 2015-03-28 19:52 | -- | -- | -- | 0.3 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at New Raichur end only due to mal-opertaion of Group-B master trip relay while resetting it manually.
[6 empty] | Sub Total --> |  |  |  |  | 0.3 | 0 | 0 | 0.4
40 | SR1L40 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | 2015-03-09 06:36 | 2015-03-09 08:18 | -- | -- | -- | 0 | 1.7 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N fault. FLR:22.53 km from Raichur new end. Fault occured in RTPS switch yard. |  | 98.9268
[5 empty] | -- | 2015-03-11 09:27 | 2015-03-11 17:25 | -- | -- | -- | 7.9667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of flashed over insulators with CLR insulators at loc. 1 & 2 vide SRLDC code no. CR-03/229.
[5 empty] | -- | 2015-03-28 06:21 | 2015-03-28 20:26 | -- | -- | -- | 0 | 0 | 0 | 14.0833 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for stringing of 400 kV Yeramaras LILO line vide SRLDC code no. CR-03/668.
[5 empty] | -- | 2015-03-29 08:00 | 2015-03-29 18:41 | -- | -- | -- | 0 | 0 | 0 | 10.6833 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for stringing of 400 kV Yeramaras LILO line vide SRLDC code no. CR-03/688.
[6 empty] | Sub Total --> |  |  |  |  | 7.9667 | 1.7 | 0 | 24.7667
41 | SR1L41 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
42 | SR1L42 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | 2015-03-09 06:36 | 2015-03-09 08:02 | -- | -- | -- | 0 | 1.4333 | 0 | 0 | N/A | N/A | N/A | Tripped at RTPS end only due to fault in RTPS switchyard. |  | 100
[5 empty] | -- | 2015-03-28 06:23 | 2015-03-28 20:27 | -- | -- | -- | 0 | 0 | 0 | 14.0667 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for stringing of 400 kV Yeramaras LILO line vide SRLDC code no. CR-03/669.
[5 empty] | -- | 2015-03-29 08:15 | 2015-03-29 18:42 | -- | -- | -- | 0 | 0 | 0 | 10.45 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for stringing of 400 kV Yeramaras LILO line vide SRLDC code no. CR-03/689.
[6 empty] | Sub Total --> |  |  |  |  | 0 | 1.4333 | 0 | 24.5167
43 | SR1L43 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | 2015-03-19 14:22 | 2015-03-19 14:44 | -- | -- | -- | 0.36667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N (Ph-earth) transient fault. FLR: 257.5 kM from Gooty end. |  | 99.9507
[6 empty] | Sub Total --> |  |  |  |  | 0.36667 | 0 | 0 | 0
44 | SR1L44 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
45 | SR1L45 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
46 | SR1L46 | MEPL - NELLOREPS | 3.83 | SR-I | -- | 2015-03-17 11:22 | 2015-03-17 22:09 | -- | -- | -- | 0 | 0 | 0 | 10.7833 | N/A | N/A | N/A | Shut down availed by M/s MEPL for insulators cold line washing at MEPL end vide SRLDC code no. CR-03/364. |  | 100
[5 empty] | -- | 2015-03-18 09:04 | 2015-03-18 20:46 | -- | -- | -- | 0 | 0 | 0 | 11.7 | N/A | N/A | N/A | Shut down availed by M/s MEPL for insulators cold line washing at MEPL end vide SRLDC code no. CR-03/388.
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 22.4833
47 | SR1L47 | SEPL - NELLOREPS | 3.83 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
48 | SR1L48 | GOOTY - NELLOREPS - I | 289.004 | SR-I | -- | 2015-03-19 13:00 | 2015-03-22 22:28 | -- | -- | -- | 0 | 0 | 0 | 81.4667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/427. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 81.4667
49 | SR1L49 | GOOTY - NELLOREPS - II | 289.004 | SR-I | -- | 2015-03-11 23:17 | 2015-03-12 16:26 | -- | -- | -- | 0 | 0 | 0 | 17.15 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/267. |  | 100
[5 empty] | -- | 2015-03-19 13:00 | 2015-04-01 | -- | -- | -- | 0 | 0 | 0 | 299 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/428.
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 316.15
50 | SR1L50 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
51 | SR1L51 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
52 | SR1L52 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | 2015-03-04 10:14 | 2015-03-06 18:27 | -- | -- | -- | 0 | 0 | 0 | 56.2167 | N/A | N/A | N/A | Shut down availed by M/s NTECL for replacement of GIS PRD at Vallur end vide SRLDC code no. CR-03/75. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 56.2167
53 | SR1L53 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
54 | SR1L54 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
55 | SR1L55 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
56 | SR1L56 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
57 | SR1L57 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
58 | SR1L58 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
59 | SR1L59 | KURNOOL(NEW) - RAICHUR(NEW) - II | 118.423 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
60 | SR1L60 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2015-03-01 | 2015-03-11 07:32 | -- | -- | -- | 0 | 0 | 0 | 247.5333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-02/566. |  | 99.9081
[5 empty] | -- | 2015-03-13 13:57 | 2015-03-13 14:00 | -- | -- | -- | 0 | 0 | 0.05 | 0 | N/A | N/A | N/A | Tripped on operation of over voltage protection at Nellore PS end while charging from Kurnool end.
[5 empty] | -- | 2015-03-13 13:16 | 2015-03-13 13:57 | -- | -- | -- | 0.68333 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to DC earth fault at Kurnool end. DT received at Nellore PS end.
[5 empty] | -- | 2015-03-13 14:00 | 2015-03-17 08:54 | -- | -- | -- | 0 | 0 | 0 | 90.9 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-03/467.
[5 empty] | -- | 2015-03-19 12:20 | 2015-03-24 11:35 | -- | -- | -- | 0 | 0 | 0 | 119.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/425.
[6 empty] | Sub Total --> |  |  |  |  | 0.68333 | 0 | 0.05 | 457.6833
61 | SR1L61 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2015-03-01 18:10 | 2015-03-16 08:30 | -- | -- | -- | 0 | 0 | 0 | 350.3333 | N/A | N/A | N/A | Line kept opened as per SRLDC instruction for voltage regulation vide SRLDC msg no. CP-12/408 |  | 99.8342
[5 empty] | -- | 2015-03-01 18:01 | 2015-03-01 18:10 | -- | -- | -- | 0 | 0 | 0.15 | 0 | N/A | N/A | N/A | Tripped due to Operation of O/V relay at NPS end.DT received at KRNL end
[5 empty] | -- | 2015-03-16 20:11 | 2015-03-16 20:20 | -- | -- | -- | 0 | 0 | 0.15 | 0 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-01/94
[5 empty] | -- | 2015-03-16 20:20 | 2015-04-01 | -- | -- | -- | 0 | 0 | 0 | 363.6667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-01/94
[5 empty] | -- | 2015-03-16 18:57 | 2015-03-16 20:11 | -- | -- | -- | 1.2333 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-01/439
[6 empty] | Sub Total --> |  |  |  |  | 1.2333 | 0 | 0.3 | 714
62 | SR1L62 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2015-03-11 09:56 | 2015-03-19 20:27 | -- | -- | -- | 0 | 0 | 0 | 202.5167 | N/A | N/A | N/A | Shut down availed for commissioning of ICT 1 & 2 bays at Thiruvalam end vide SRLDC code no. CR-03/234. |  | 100
[5 empty] | -- | 2015-03-20 22:00 | 2015-04-01 | -- | -- | -- | 0 | 0 | 0 | 266 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/485.
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 468.5167
63 | SR1L63 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2015-03-14 08:26 | 2015-03-19 20:30 | -- | -- | -- | 0 | 0 | 0 | 132.0667 | N/A | N/A | N/A | Shut down availed for commissioning of ICT 1 & 2 bays at Thiruvalam end vide SRLDC code no. CR-03/314. |  | 99.1219
[5 empty] | -- | 2015-03-19 20:30 | 2015-03-20 22:07 | -- | -- | -- | 0 | 0 | 0 | 25.6167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-03/702.
[5 empty] | -- | 2015-03-22 21:16 | 2015-03-23 09:54 | -- | -- | -- | 0 | 0 | 0 | 12.6333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-03/793.
[5 empty] | -- | 2015-03-22 14:44 | 2015-03-22 21:16 | -- | -- | -- | 6.5333 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to maloperation of Main-2 relay due to failure of card at Kurnool new end.
[6 empty] | Sub Total --> |  |  |  |  | 6.5333 | 0 | 0 | 170.3167
64 | SR1T1 | CUDDAPAH ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
65 | SR1T2 | CUDDAPAH ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
66 | SR1T3 | GAJUWAKA ICT I | 315 | SR-I | -- | 2015-03-27 11:07 | 2015-03-27 13:01 | -- | -- | -- | 1.9 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending oil leakage from Y & B phase turrets vide SRLDC code no. CR-03/647. |  | 99.7446
[6 empty] | Sub Total --> |  |  |  |  | 1.9 | 0 | 0 | 0
67 | SR1T4 | GAZUWAKA ICT II | 315 | SR-I | -- | 2015-03-30 16:36 | 2015-03-30 17:28 | -- | -- | -- | 0.86667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending hot spots in 33 kV AB switch vide SRLDC code no. CR-03/712. |  | 99.8835
[6 empty] | Sub Total --> |  |  |  |  | 0.86667 | 0 | 0 | 0
68 | SR1T5 | GOOTY ICT I | 315 | SR-I | -- | 2015-03-03 10:05 | 2015-03-03 16:58 | -- | -- | -- | 0 | 0 | 0 | 6.8833 | N/A | N/A | N/A | Hand tripped for OTI modification for SCADA reporting works vide SRLDC code no. CR-03/57. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 6.8833
69 | SR1T6 | GOOTY ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
70 | SR1T7 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
71 | SR1T8 | HYDERABAD ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
72 | SR1T9 | HYDERABAD ICT - III | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
73 | SR1T10 | KHAMMAM ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
74 | SR1T11 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
75 | SR1T12 | MUNIRABAD ICT I | 315 | SR-I | -- | 2015-03-08 19:40 | 2015-03-08 20:52 | -- | -- | -- | 0 | 1.2 | 0 | 0 | N/A | N/A | N/A | Tripped on operation of DEF protection due to flashover of LA at 220 kV Lingapur (KPTCL SS) end. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 1.2 | 0 | 0
76 | SR1T13 | MUNIRABAD ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
77 | SR1T14 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
78 | SR1T15 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
79 | SR1T16 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
80 | SR1T17 | VIJAYAWADA ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
81 | SR1T18 | VIJAYAWADA ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
82 | SR1T19 | WARANGAL ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
83 | SR1T20 | WARANGAL ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
84 | SR1T21 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | 2015-03-03 12:23 | 2015-03-03 13:26 | -- | -- | -- | 1.05 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to spurious signal generated during CSD commissioning works on bus reactor. |  | 99.8589
[5 empty] | -- | 2015-03-04 12:10 | 2015-03-04 20:54 | -- | -- | -- | 0 | 0 | 0 | 8.7333 | N/A | N/A | N/A | Shut down availed for tertiary and CSD commissioning works vide SRLDC code no. CR-03/85.
[5 empty] | -- | 2015-03-05 09:15 | 2015-03-05 11:15 | -- | -- | -- | 0 | 0 | 0 | 2 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-03/102.
[6 empty] | Sub Total --> |  |  |  |  | 1.05 | 0 | 0 | 10.7333
85 | SR1T22 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | 2015-03-05 11:28 | 2015-03-05 20:28 | -- | -- | -- | 0 | 0 | 0 | 9 | N/A | N/A | N/A | Shut down availed for CSD and tertiary commissioning works vide SRLDC code no. CR-03/112. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 9
86 | SR1T23 | NELLOREPS ICT - II | 1500 | SR-I | -- | 2015-03-26 08:42 | 2015-03-26 23:19 | -- | -- | -- | 0 | 0 | 0 | 14.6167 | N/A | N/A | N/A | Shut down availed for connecting tertiary transformer bus to ICT-2 tertiary vide SRLDC code no. CR-03/616. |  | 98.685
[5 empty] | -- | 2015-03-31 09:26 | 2015-03-31 19:13 | -- | -- | -- | 9.7833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacing R-phase LA due to high THRC vide SRLDC code no. CR-03/729.
[6 empty] | Sub Total --> |  |  |  |  | 9.7833 | 0 | 0 | 14.6167
87 | SR1T24 | NELLOREPS ICT - III | 1500 | SR-I | -- | 2015-03-24 09:39 | 2015-03-24 18:25 | -- | -- | -- | 8.7667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for collecting bushing oil samples vide SRLDC code no. CR-03/566. |  | 98.8217
[6 empty] | Sub Total --> |  |  |  |  | 8.7667 | 0 | 0 | 0
88 | SR1T25 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | 2015-03-07 10:04 | 2015-03-07 22:27 | -- | -- | -- | 0 | 0 | 0 | 12.3833 | N/A | N/A | N/A | Shut down availed for commissioning of teritiary vide SRLDC code no. CR-03/152. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 12.3833
89 | SR1T26 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | 2015-03-04 10:34 | 2015-03-04 17:00 | -- | -- | -- | 0 | 0 | 0 | 6.4333 | N/A | N/A | N/A | Shut down availed for tertiary commissioning works vide SRLDC code no. CR-03/83. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 6.4333
90 | SR1R1 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
91 | SR1R2 | GOOTY BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
92 | SR1R3 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
93 | SR1R4 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
94 | SR1R5 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
95 | SR1R6 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2015-03-26 15:54 | 2015-03-26 17:49 | -- | -- | -- | 1.9167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending oil leakage vide SRLDC code no. CR-03/624. |  | 99.7424
[6 empty] | Sub Total --> |  |  |  |  | 1.9167 | 0 | 0 | 0
96 | SR1R7 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
97 | SR1R8 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
98 | SR1R9 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
99 | SR1R10 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | 2015-03-20 10:07 | 2015-04-01 | -- | -- | -- | 0 | 0 | 0 | 277.8833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/463. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 277.8833
100 | SR1R11 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | 2015-03-03 09:26 | 2015-03-03 21:34 | -- | -- | -- | 0 | 0 | 0 | 12.1333 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-03/08. |  | 100
[5 empty] | -- | 2015-03-04 09:50 | 2015-03-04 11:31 | -- | -- | -- | 0 | 0 | 0 | 1.6833 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-03/22.
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 13.8167
101 | SR1R12 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | 2015-03-03 12:05 | 2015-03-03 17:36 | -- | -- | -- | 5.5167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-03/10. |  | 99.2585
[6 empty] | Sub Total --> |  |  |  |  | 5.5167 | 0 | 0 | 0
102 | SR1R13 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
103 | SR1R14 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
104 | SR1R15 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
105 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | 2015-03-14 17:12 | 2015-03-14 23:16 | -- | -- | -- | 6.0667 | 0 | 0 | 0 | N/A | N/A | N/A | Blocked on operation of instantaneous over current protection due to tripping of all filters of east side bus due to LA failure. |  | 99.1846
[6 empty] | Sub Total --> |  |  |  |  | 6.0667 | 0 | 0 | 0
106 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | 2015-03-14 17:12 | 2015-03-14 17:36 | -- | -- | -- | 0.4 | 0 | 0 | 0 | N/A | N/A | N/A | Blocked on B-phase differential current trip due to fault occurred in pole-I. |  | 99.9462
[6 empty] | Sub Total --> |  |  |  |  | 0.4 | 0 | 0 | 0
107 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
108 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
[11 empty] | 67.7667 | 5.65 | 2.1833 | 3142.8167
Note in type of failure column please indicate following :
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF MARCH 2015
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
GTY LR at NSR
1 |  | GTY LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWK I LR at VJA
2 |  | GWK I LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWL LR at HYD
3 |  | GWL LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY I LR at GWK
4 |  | JEY I LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY II LR at GWK
5 |  | JEY II LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MBN LR at NSR
6 |  | MBN LR at NSR | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MLK LR at HYD
7 |  | MLK LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR I LR at VJA
8 |  | NLR I LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR II LR at VJA
9 |  | NLR II LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I LR at CDP
10 |  | NSR I LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II LR at CDP
11 |  | NSR II LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR LR at GTY
12 |  | NSR LR at GTY | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II ER at GWK
13 |  | POLE II ER at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II SR at GWK
14 |  | POLE II SR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RCR LR at MBD
15 |  | RCR LR at MBD | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM I LR at NSR
16 |  | RDM I LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM II LR at NSR
17 |  | RDM II LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH I LR at GWK
18 |  | SMH I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH II LR at GWK
19 |  | SMH II LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at GWK
20 |  | VJA I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at NLR
21 |  | VJA I LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA II LR at NLR
22 |  | VJA II LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG III LR at VJA
23 |  | VMG III LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG IV LR at VJA
24 |  | VMG IV LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
WGL LR at KMM
25 |  | WGL LR at KMM | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
|  | NSR I FSC at CDP |  |  | NA | 2015-03-16 21:02 | 2015-03-16 23:06 | NA | NA | 2.67 | 0 | 0 | 0 | NA | NA | NA | MOV temp. high alarm.
|  | NSR I FSC at CDP |  |  | NA | 2015-03-17 06:15 | 2015-03-17 13:15 | NA | NA | 7 | 0 | 0 | 0 | NA | NA | NA | MOV temp. high alarm.
26 |  | NSR I FSC at CDP | 201.75 | SR1 |  | NO OUTAGES |  |  |  | 9.67 | 0 | 0 | 0 |  |  |  |  | SRPC | 98.7%
NSR II FSC at CDP
27 |  | NSR II FSC at CDP | 201.75 | SR1 | [13 empty] | SRPC | 100%
FSC-1 at GTY
28 |  | FSC-1 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-2 at GTY
29 |  | FSC-2 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM1 LR at NLR
30 |  | TVLM1 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM2 LR at NLR
31 |  | TVLM2 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL I L/R AT NPS
32 |  | KURNOOL I L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL II L/R AT NPS
33 |  | KURNOOL II L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS I L/R AT KURNOOL
34 |  | NPS I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS II L/R AT KURNOOL
35 |  | NPS II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM I L/R AT KURNOOL
36 |  | TVLM I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM II L/R AT KURNOOL
37 |  | TVLM II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 9.67 | 0 | 0 | 0